## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-06-2026 | during | 08-06-2026 | during | 08-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 345 | 369 | 412 | 412 | 390 | 390 | AGC+Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 0 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 290 | 304 | 335 | 335 | 310 | 310 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35.5 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 144 | 75 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15 | 15 | 33 | 33 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 42 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 32 | 300 | 300 | 33 | 112 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 79 | 149 | 149 | 35 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 88 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 435 | 450 | 584 | 584 | 480 | 480 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 295 | 305 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1954 | 2127.5 | 5822.22 | 5792.22 | 2417.12 | 2723.12
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 8 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 33 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 95 | 89 | 100 | 100 | 100 | 100 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 70 | 97 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 31 | 0 | 0 | 48 | 64 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 49 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 12 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 78 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.98 | 0 | 4.83 | 0 | 4.83 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 36 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 60 | 106 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 46 | 94 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 23 | 16 | 163 | 163 | 35 | 147 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1164 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 5 | 15 | 4 | 15 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1040 | 1120 | 1150 | 1150 | 1150 | 1150 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2819.98 | 3229.5 | 3963.69 | 4004.86 | 3249.21 | 3454.38
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 197 | 188 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 353 | 356 | 350.01 | 350.01 | 291 | 291 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 36 | 342.01 | 342.01 | 231 | 231 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 390 | 235 | 393 | 393 | 281 | 281 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 34 | 36 | 41.65 | 41.65 | 11 | 11 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 30 | 5 | 52.82 | 52.82 | 11 | 11 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 26 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 92 | 139 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 32 | 37 | 40 | 40 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 88 | 92 | 163 | 163 | 94 | 94 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 112 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 156 | 168 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 14 | 17 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 17 | 27 | 113 | 113 | 0 | 0 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0.96 | 87 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 56 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1595.96 | 1657.2 | 2757.44 | 2696.44 | 1851.47 | 1947.47
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-06-2026 | during | 08-06-2026 | during | 08-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 25 | 25 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.9 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 87 | 77 | 80 | 80 | 9 | 9 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 65 | 70 | 70 | 90 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42.64 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 159.54 | 159 | 506.7 | 436.5 | 211.2 | 141
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 39 | 39 | 41 | 41 | 41 | 41 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 28 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 149 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 86 | 100 | 150 | 150 | 150 | 150 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 27 | 28 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 83 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 99 | 101 | 101 | 101 | 101 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 16 | 16 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 314 | 301 | 350 | 350 | 320 | 320 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1169 | 1153 | 1337 | 1337 | 1228.02 | 1228.02
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 932 | 931 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 34 | 35 | 35 | 35 | 35 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 47 | 50 | 50 | 32 | 32 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 124 | 95 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 105 | 105 | 95 | 95 | FGMO
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 62.2 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1190 | 1195 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2308.2 | 2352 | 3590.2 | 3505.2 | 2731 | 2646
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 494 | 496 | 500 | 500 | 500 | 500 | Unit1 Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 128 | 127 | 130 | 130 | 130 | 130 | STG Under Maintenance
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1096 | 1170 | 1244 | 1244 | 1244 | 1244 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 0 | 150 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 284 | 230 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.72 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2238.72 | 2313 | 2662 | 2661 | 2492 | 2641
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 52.95 | 0 | 57 | 0 | 57 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 41 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 130 | 220 | 220 | 130 | 130 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 130 | 220 | 220 | 130 | 130 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 17 | 32 | 32 | 32 | 32 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 99 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 18 | 50 | 113 | 113 | 35 | 105 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 35 | 113 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.81 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1337.3 | 1410.03 | 1435.88 | 1435.88 | 1356 | 1356 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 50.37 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 64 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2201.43 | 2375.03 | 3019.57 | 2795.87 | 2438.31 | 2454.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 40 | 40 | 41 | 41 | 41 | 41 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 100 | 113 | 113 | 35 | 100 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.1 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 44 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 21 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 172 | 0 | 153.16 | 0 | 153.16 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 283.1 | 255 | 478.16 | 289 | 380.16 | 256
System Total |  |  |  |  | 28843.2 | 29290.237 | 14729.93 | 15621.23 | 24136.98 | 23518.09 | 16998.49 | 17491.6
Forecast Scenario (08-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15810 |  | 0 |  | 15810
|  |  |  | 1:00 | 15580 |  | 0 |  | 15580
|  |  |  | 2:00 | 15220 |  | 0 |  | 15220
|  |  |  | 3:00 | 14860 |  | 0 |  | 14860
|  |  |  | 4:00 | 14500 |  | 0 |  | 14500
|  |  |  | 5:00 | 14330 |  | 0 |  | 14330
|  |  |  | 6:00 | 13640 |  | 0 |  | 13640
|  |  |  | 7:00 | 13480 |  | 0 |  | 13480
|  |  |  | 8:00 | 13230 |  | 0 |  | 13230
|  |  |  | 9:00 | 13450 |  | 0 |  | 13450
|  |  |  | 10:00 | 13820 |  | 0 |  | 13820
|  |  |  | 11:00 | 14060 |  | 0 |  | 14060
|  |  |  | 12:00 | 14670 |  | 0 |  | 14670
|  |  |  | 13:00 | 15040 |  | 0 |  | 15040
|  |  |  | 14:00 | 15180 |  | 0 |  | 15180
|  |  |  | 15:00 | 15380 |  | 0 |  | 15380
|  |  |  | 16:00 | 15170 |  | 0 |  | 15170
|  |  |  | 17:00 | 14390 |  | 0 |  | 14390
|  |  |  | 18:00 | 13440 |  | 0 |  | 13440
|  |  |  | 18:30 | 14300 |  | 0 |  | 14300
|  |  |  | 19:00 | 14960 |  | 0 |  | 14960
|  |  |  | 19:30 | 15720 |  | 0 |  | 15720
|  |  |  | 20:00 | 15850 |  | 0 |  | 15850
|  |  |  | 21:00 | 16000 |  | 0 |  | 16000
|  |  |  | 22:00 | 16010 |  | 0 |  | 16010
|  |  |  | 23:00 | 15900 |  | 0 |  | 15900
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 14670.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 353.97 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:45 hrs on 08-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-06-2026 | [28 empty] | Date: | 07-06-2026 | [28 empty] | Date: | 07-06-2026 | [28 empty] | Date: | 07-06-2026 | [28 empty] | Date: | 07-06-2026 | [18 empty] | Date: | 07-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [18 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 35 | 17 | 35 | 45 | 114 | 30 | 35 | 90 | 0 | 0 | 0 | 583 | 0 | 0 | 240 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 320 | 86 | 16 | 70 | 0 | 1 | 50 | 53 | 37 | 12 | 12 | 0 | 100 | 108 | 29 | 1080 | 5 | 0 | 50 | 10 | 98 | 217 | 0 | 0 | 0 | 1226 | 0 | 26 | 0 | 220 | 290 | 230 | 51 | 0 | 191 | 33 | 70 | 93 | 105 | 0 | 19 | 17 | 154 | 52.2 | 0 | 30 | 310 | 0 | 382 | 39 | 30 | 146 | 0 | 16 | 0 | 85 | 30 | 20 | 0 | 100 | 17 | 9 | 0 | 78 | 0 | 0 | 0 | 0 | 8298.2 | 905 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1220 | 47 | 0 | 0 | 1464.95 | 0 | 0 | 0 | 90 | 113 | 0 | 92 | 19 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 41 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 15 | 110 | 0 | 462 | 1244 | 35 | 7278.95 | 15577.15 | 75.25
01:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 22 | 45 | 114 | 15 | 35 | 35 | 0 | 0 | 0 | 583 | 0 | 0 | 240 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 320 | 94 | 16 | 29 | 0 | 5 | 50 | 53 | 37 | 12 | 12 | 0 | 100 | 106 | 13 | 1080 | 32 | 0 | 50 | 25.5 | 97 | 219 | 0 | 0 | 0 | 1145 | 0 | 26 | 0 | 220 | 290 | 230 | 51 | 0 | 199 | 36 | 0 | 92 | 139 | 0 | 19 | 52 | 152 | 52.2 | 0 | 30 | 315 | 0 | 283 | 40 | 30 | 136 | 0 | 16 | 0 | 86 | 30 | 68 | 0 | 100 | 17 | 9 | 0 | 78 | 0 | 0 | 0 | 0 | 8028.7 | 905 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1216 | 67 | 0 | 0 | 1422.83 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 18 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 41 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 264 | 60 | 110 | 0 | 421 | 1188 | 43 | 6957.83 | 14986.53 | 75.22
02:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 17 | 15 | 114 | 15 | 35 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 280 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 450 | 92 | 0 | 24 | 0 | 8 | 0 | 23 | 0 | 12 | 12 | 0 | 100 | 107 | 14 | 1080 | 0 | 0 | 50 | 0 | 96 | 219 | 0 | 0 | 0 | 1160 | 0 | 26 | 0 | 220 | 290 | 230 | 51 | 0 | 198 | 10 | 0 | 92 | 34 | 0 | 19 | 0 | 152 | 25 | 0 | 24 | 310 | 0 | 295 | 40 | 30 | 137 | 0 | 16 | 0 | 85 | 30 | 15 | 0 | 100 | 17 | 9 | 0 | 78 | 0 | 0 | 0 | 0 | 7500 | 932 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 35 | 0 | 0 | 1381.63 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 40 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 264 | 127 | 110 | 0 | 428 | 1142 | 0 | 6738.63 | 14238.63 | 75.19
03:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 17 | 15 | 15 | 15 | 17 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 290 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 450 | 0 | 0 | 25 | 0 | 5 | 0 | 0 | 0 | 0 | 12 | 0 | 100 | 104 | 14 | 1012 | 0 | 0 | 25 | 0 | 97 | 219 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 220 | 290 | 230 | 51 | 0 | 195 | 10 | 0 | 92 | 0 | 0 | 19 | 0 | 146 | 25 | 0 | 24 | 310 | 0 | 309 | 40 | 30 | 145 | 0 | 0 | 0 | 85 | 30 | 63 | 0 | 101 | 0 | 9 | 0 | 78 | 0 | 0 | 0 | 0 | 7091 | 932 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1214 | 0 | 0 | 0 | 1366.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 38 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 129 | 125 | 0 | 447 | 1130 | 0 | 6647.32 | 13738.32 | 75.16
04:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 290 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 475 | 0 | 0 | 17 | 0 | 6 | 0 | 0 | 0 | 0 | 12 | 0 | 100 | 0 | 14 | 1000 | 0 | 0 | 0 | 0 | 34 | 219 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 220 | 290 | 230 | 51 | 0 | 197 | 10 | 0 | 92 | 0 | 0 | 17 | 0 | 142 | 0 | 0 | 16 | 315 | 0 | 309 | 40 | 30 | 144 | 0 | 0 | 0 | 86 | 30 | 146 | 0 | 100 | 0 | 9 | 0 | 78 | 0 | 0 | 0 | 0 | 6889 | 932 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1217 | 0 | 0 | 0 | 1358.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 38 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 130 | 170 | 0 | 450 | 1110 | 0 | 6581.53 | 13470.53 | 75.13
05:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 286 | 0 | 0 | 0 | 142 | 19 | 22 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 16 | 962 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1164 | 0 | 0 | 0 | 280 | 290 | 230 | 51 | 0 | 192 | 10 | 0 | 93 | 0 | 0 | 17 | 0 | 134 | 0 | 0 | 0 | 310 | 0 | 309 | 40 | 30 | 141 | 0 | 0 | 0 | 86 | 30 | 145 | 0 | 101 | 0 | 9 | 0 | 78 | 0 | 0 | 0 | 0 | 6690 | 932 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1176 | 0 | 0 | 0 | 1303.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 39 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 130 | 220 | 0 | 429 | 1137 | 0 | 6476.41 | 13166.41 | 75.1
06:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 293 | 0 | 0 | 2 | 142 | 19 | 22 | 0 | 440 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.05 | 96 | 0 | 12 | 923 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1160 | 2 | 0 | 0 | 280 | 290 | 230 | 51 | 0 | 195 | 10 | 0 | 93 | 0 | 0 | 17 | 0 | 130 | 0 | 0 | 0 | 310 | 0 | 309 | 40 | 30 | 136 | 0 | 16 | 0 | 86 | 30 | 145 | 0 | 101 | 0 | 9 | 1.5 | 78 | 0 | 0.1 | 2.32 | 0 | 6711.97 | 932 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1134 | 0 | 0 | 0 | 1247.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.36 | 3 | 0 | 0 | 3.9 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0.37 | 0 | 38 | 0 | 2 | 34 | 0 | 0 | 0 | 0.5 | 6 | 0.02 | 0 | 214 | 130 | 220 | 0 | 407 | 1090 | 0 | 6296.03 | 13008 | 75.07
07:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 17 | 20 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 294 | 0 | 0 | 6 | 142 | 19 | 22 | 0 | 480 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0.52 | 91 | 0 | 12 | 948 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 280 | 290 | 230 | 51 | 2 | 200 | 15 | 0 | 92 | 0 | 0 | 17 | 0 | 126 | 0 | 6 | 0 | 315 | 0 | 309 | 40 | 30 | 140 | 1 | 0 | 0 | 86 | 30 | 147 | 0 | 101 | 0 | 9 | 3.68 | 78 | 0 | 0.5 | 12.27 | 0 | 6815.97 | 932 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1054 | 0 | 0 | 0 | 1261.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.48 | 7 | 0 | 0 | 7.53 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0.93 | 0 | 38 | 0 | 6 | 34 | 0 | 0 | 0 | 0.7 | 16 | 0.11 | 0 | 217 | 126 | 220 | 0 | 427 | 1070 | 0 | 6264.81 | 13080.78 | 75.04
08:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 17 | 45 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 297 | 0 | 0 | 13 | 142 | 16 | 22 | 0 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 94 | 0 | 2 | 952 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 280 | 290 | 230 | 51 | 10 | 215 | 36 | 0 | 91 | 0 | 0 | 17 | 0 | 130 | 0 | 10 | 0 | 310 | 0 | 309 | 40 | 30 | 143 | 5 | 0 | 0 | 83 | 30 | 147 | 0 | 101 | 0 | 9 | 7 | 78 | 0 | 1 | 21.16 | 0 | 6918.21 | 932 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 1050 | 0 | 0 | 0 | 1234.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.84 | 45 | 0 | 0 | 17.21 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 1.52 | 0 | 40 | 0 | 4 | 34 | 0 | 0 | 0 | 0.8 | 89 | 0.17 | 0 | 223 | 128 | 220 | 0 | 416 | 1096 | 0 | 6391.78 | 13309.99 | 75.01
09:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 17 | 60 | 15 | 15 | 4 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 301 | 0 | 0 | 19 | 142 | 16 | 22 | 0 | 455 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 2.57 | 96 | 0 | 2 | 1060 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 240 | 290 | 100 | 51 | 10 | 202 | 32 | 0 | 90 | 0 | 0 | 17 | 0 | 136 | 0 | 14 | 0 | 310 | 0 | 315 | 40 | 30 | 144 | 6 | 16 | 0 | 83 | 30 | 143 | 0 | 102 | 0 | 9 | 5.5 | 78 | 0 | 1 | 19.2 | 0 | 6910.27 | 932 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 1090 | 0 | 0 | 0 | 1276.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.98 | 73 | 0 | 0 | 18.6 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 2.02 | 0 | 41 | 0 | 15 | 34 | 0 | 0 | 0 | 5 | 140 | 0.31 | 0 | 248 | 128 | 220 | 0 | 474 | 1100 | 0 | 6700.75 | 13611.02 | 74.99
10:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 17 | 90 | 32 | 15 | 17 | 17 | 0 | 0 | 0 | 295 | 0 | 17 | 288 | 0 | 0 | 23 | 142 | 16 | 22 | 0 | 430 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 12 | 1.97 | 97 | 7 | 2 | 1035 | 0 | 0 | 3 | 0 | 14 | 220 | 0 | 0 | 0 | 1160 | 1 | 16 | 0 | 330 | 354 | 0 | 43 | 10 | 196 | 34 | 0 | 89 | 13 | 0 | 17 | 0 | 142 | 5 | 28 | 0 | 315 | 0 | 315 | 40 | 30 | 144 | 8 | 16 | 0 | 83 | 30 | 119 | 0 | 101 | 0 | 9 | 12.62 | 87 | 0 | 0.7 | 35.01 | 0 | 7079.3 | 932 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 1185 | 0 | 0 | 0 | 1322.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.29 | 54 | 0 | 0 | 51.44 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 4.87 | 0 | 41 | 0 | 17 | 0 | 0 | 0 | 0 | 6.9 | 98 | 0.27 | 6 | 272 | 128 | 220 | 0 | 485 | 1100 | 0 | 6829 | 13908.3 | 74.97
11:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 22 | 90 | 32 | 15 | 30 | 17 | 0 | 0 | 0 | 290 | 0 | 0 | 295 | 0 | 0 | 26 | 142 | 16 | 14 | 0 | 450 | 32 | 16 | 0 | 0 | 3 | 0 | 0 | 1 | 12 | 12 | 2.95 | 95 | 34 | 2 | 1040 | 5 | 0 | 24 | 0 | 46 | 219 | 0 | 0 | 0 | 1161 | 3 | 70 | 8 | 380 | 351 | 0 | 43 | 22 | 200 | 34 | 0 | 88 | 34 | 1 | 17 | 0 | 144 | 16 | 52 | 0 | 305 | 0 | 314 | 39 | 30 | 145 | 9 | 16 | 0 | 82 | 30 | 37 | 0 | 102 | 0 | 9 | 14.83 | 87 | 0 | 1.2 | 19.94 | 0 | 7318.92 | 932 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1190 | 0 | 0 | 0 | 1301.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.12 | 93 | 0 | 0 | 52.04 | 0 | 0 | 130 | 0 | 130 | 0 | 390 | 0 | 4.81 | 0 | 40 | 0 | 19 | 0 | 0 | 0 | 0 | 6.6 | 164 | 0.48 | 16 | 257 | 128 | 180 | 0 | 437 | 1095 | 0 | 6751.28 | 14070.2 | 74.95
12:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 35 | 144 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 295 | 0 | 0 | 290 | 0 | 0 | 28 | 142 | 15 | 14 | 0 | 435 | 46 | 16 | 0 | 0 | 6 | 0 | 0 | 17 | 12 | 12 | 2.98 | 95 | 60 | 2 | 1040 | 23 | 0 | 33 | 0 | 70 | 217 | 0 | 0 | 0 | 1160 | 8 | 92 | 26 | 390 | 353 | 0 | 43 | 30 | 197 | 34 | 0.96 | 88 | 34 | 17 | 17 | 14 | 156 | 16 | 56 | 32 | 310 | 0 | 314 | 39 | 30 | 153 | 10 | 16 | 0 | 82 | 27 | 86 | 0 | 102 | 0 | 9 | 20 | 87 | 0 | 0.9 | 42.64 | 0 | 7698.48 | 932 | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.2 | 1190 | 0 | 0 | 0 | 1337.3 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 52.95 | 64 | 0 | 0 | 50.37 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 4.81 | 0 | 40 | 44 | 21 | 0 | 0 | 0 | 0 | 6.1 | 172 | 0.72 | 16 | 284 | 128 | 220 | 0 | 494 | 1096 | 0 | 7031.45 | 14729.93 | 74.93
13:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 35 | 144 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 300 | 0 | 0 | 295 | 0 | 0 | 30 | 133 | 16 | 14 | 0 | 490 | 94 | 16 | 13 | 0 | 10 | 0 | 15 | 17 | 12 | 12 | 3.49 | 96 | 74 | 6 | 1050 | 58 | 0 | 40 | 1 | 96 | 214 | 0 | 0 | 0 | 1175 | 8 | 107 | 0 | 275 | 346 | 70 | 43 | 21 | 196 | 34 | 19 | 87 | 84 | 17 | 19 | 37 | 148 | 52.2 | 72 | 31 | 310 | 0 | 314 | 39 | 30 | 152 | 9 | 16 | 0 | 82 | 27 | 0 | 0 | 102 | 0 | 9 | 10.3 | 87 | 0 | 1.3 | 26.75 | 0 | 7902.04 | 932 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.33 | 1192 | 0 | 0 | 0 | 1445.57 | 0 | 0 | 0 | 5 | 35 | 0 | 0 | 0 | 0 | 47.96 | 93 | 0 | 0 | 36.64 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 4.4 | 0 | 40 | 70 | 30 | 0 | 0 | 0 | 0 | 7 | 182 | 0.14 | 16 | 289 | 127 | 220 | 0 | 501 | 1105 | 0 | 7207.04 | 15109.08 | 74.91
14:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 35 | 144 | 32 | 0 | 35 | 17 | 0 | 0 | 0 | 300 | 0 | 0 | 301 | 0 | 0 | 26 | 142 | 0 | 14 | 0 | 490 | 100 | 16 | 26 | 0 | 7 | 0 | 15 | 17 | 12 | 12 | 3.8 | 98 | 92 | 2 | 1035 | 120 | 0 | 4 | 16 | 103 | 214 | 0 | 0 | 0 | 1170 | 0 | 53 | 0 | 255 | 350 | 70 | 51 | 5 | 194 | 32 | 35 | 87 | 137 | 13 | 19 | 102 | 158 | 52.2 | 36 | 31 | 315 | 0 | 314 | 39 | 28 | 151 | 6 | 16 | 0 | 82 | 27 | 0 | 0 | 100 | 0 | 9 | 14.28 | 87 | 0 | 1.2 | 26.75 | 0 | 7966.23 | 932 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 1194 | 0 | 0 | 0 | 1446.12 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 8 | 43.57 | 85 | 0 | 0 | 46.01 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 4.26 | 0 | 42 | 93 | 20 | 0 | 0 | 0 | 0 | 2.4 | 113 | 0.11 | 16 | 281 | 127 | 220 | 0 | 486 | 1125 | 2 | 7183.47 | 15149.7 | 74.89
15:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 35 | 144 | 32 | 0 | 35 | 17 | 0 | 0 | 0 | 160 | 0 | 0 | 320 | 0 | 0 | 20 | 142 | 15 | 14 | 0 | 560 | 96 | 16 | 34 | 0 | 31 | 0 | 15 | 17 | 12 | 12 | 1.81 | 99 | 94 | 2 | 1115 | 142 | 0 | 16 | 14 | 102 | 214 | 0 | 0 | 0 | 1224 | 0 | 20 | 0 | 235 | 350 | 70 | 51 | 5 | 195 | 32 | 33 | 87 | 154 | 8 | 19 | 108 | 166 | 52.2 | 23 | 29 | 315 | 0 | 300 | 39 | 28 | 150 | 5 | 16 | 0 | 81 | 20 | 0 | 0 | 98 | 0 | 9 | 1.15 | 87 | 0 | 1.3 | 11.3 | 7 | 8012.76 | 932 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 1 | 1213 | 0 | 0 | 0 | 1436.21 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 52.2 | 29.38 | 75 | 0 | 0 | 33.48 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 3.52 | 0 | 41 | 94 | 21 | 0 | 0 | 0 | 0 | 4.7 | 130 | 0.09 | 16 | 286 | 126 | 220 | 0 | 499 | 1110 | 17 | 7249.58 | 15262.34 | 74.87
16:00 | 0 | 72 | 24 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17 | 0 | 35 | 144 | 32 | 33 | 35 | 17 | 0 | 0 | 0 | 215 | 0 | 0 | 301 | 0 | 0 | 1 | 142 | 0 | 14 | 0 | 550 | 96 | 16 | 38 | 0 | 29 | 0 | 15 | 17 | 12 | 12 | 1.77 | 99 | 95 | 2 | 1015 | 140 | 0 | 39 | 14 | 98 | 215 | 0 | 0 | 0 | 1160 | 0 | 20 | 0 | 240 | 290 | 70 | 51 | 5 | 209 | 32 | 34 | 90 | 165 | 9 | 19 | 108 | 168 | 52.2 | 11 | 29 | 305 | 0 | 301 | 39 | 28 | 142 | 4 | 16 | 0 | 80 | 25 | 0 | 0 | 97 | 0 | 9 | 5.74 | 87 | 0 | 1.2 | 3.02 | 12 | 7856.93 | 932 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3.47 | 1181 | 0 | 0 | 0 | 1447.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 4.46 | 40 | 0 | 0 | 25.41 | 0 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 2.29 | 0 | 40 | 93 | 14 | 0 | 0 | 0 | 0 | 0.2 | 46 | 0.11 | 16 | 280 | 126 | 180 | 0 | 481 | 1120 | 0 | 6737.43 | 14594.36 | 74.85
17:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 35 | 12 | 33 | 144 | 32 | 55 | 0 | 17 | 0 | 0 | 0 | 250 | 0 | 35 | 293 | 0 | 0 | 0 | 142 | 0 | 14 | 0 | 430 | 60 | 16 | 38 | 0 | 54 | 0 | 15 | 17 | 12 | 12 | 0 | 95 | 85 | 2 | 900 | 82 | 0 | 50 | 16 | 93 | 216 | 0 | 0 | 0 | 1160 | 2 | 20 | 0 | 320 | 290 | 18 | 51 | 5 | 190 | 35 | 44 | 90 | 136 | 26 | 6 | 70 | 166 | 25 | 8 | 38 | 310 | 0 | 301 | 39 | 28 | 137 | 2 | 16 | 0 | 84 | 30 | 70 | 0 | 98 | 1 | 9 | 6.03 | 87 | 0 | 0.6 | 7.46 | 8 | 7655.09 | 932 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.79 | 1144 | 0 | 0 | 0 | 1466.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 14 | 0 | 0 | 13.33 | 0 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 1.24 | 0 | 40 | 93 | 6 | 20 | 0 | 0 | 0 | 0.6 | 12 | 0.04 | 16 | 238 | 127 | 220 | 0 | 416 | 1070 | 0 | 6542.36 | 14197.45 | 74.83
18:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 35 | 17 | 35 | 75 | 32 | 55 | 17 | 17 | 0 | 0 | 0 | 245 | 0 | 35 | 294 | 0 | 0 | 0 | 142 | 0 | 14 | 0 | 350 | 45 | 16 | 44 | 0 | 20 | 0 | 23 | 17 | 12 | 12 | 0.16 | 92 | 50 | 4 | 900 | 78 | 0 | 19 | 17 | 68 | 198 | 0 | 0 | 0 | 1065 | 1 | 20 | 0 | 290 | 290 | 33 | 51 | 5 | 192 | 36 | 54 | 50 | 109 | 8 | 11 | 50 | 142 | 16 | 2 | 38 | 305 | 0 | 289 | 39 | 28 | 124 | 0 | 20 | 0 | 83 | 20 | 100 | 0 | 98 | 17 | 9 | 1.39 | 87 | 0 | 0.2 | 3.53 | 12 | 7083.28 | 932 | 95 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1111 | 0 | 0 | 0 | 1339.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 1.68 | 0 | 0 | 0 | 4.86 | 0 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0.46 | 0 | 40 | 70 | 2 | 67 | 0 | 0 | 0 | 0.7 | 13 | 0.02 | 16 | 175 | 127 | 220 | 0 | 398 | 965 | 0 | 6217.62 | 13300.9 | 74.81
19:00 | 0 | 70 | 42 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 35.5 | 17 | 68 | 75 | 32 | 30 | 35 | 100 | 0 | 0 | 0 | 280 | 0 | 0 | 308 | 0 | 0 | 0 | 142 | 15 | 14 | 0 | 460 | 46 | 16 | 51 | 0 | 12 | 49 | 31 | 17 | 12 | 12 | 0 | 90 | 62 | 12 | 1115 | 80 | 0 | 21 | 17 | 70 | 216 | 0 | 0 | 0 | 1145 | 0 | 22 | 0 | 280 | 340 | 18 | 51 | 5 | 202 | 36 | 56 | 92 | 118 | 8 | 14 | 17 | 170 | 20 | 0 | 37 | 310 | 0 | 300 | 39 | 28 | 145 | 0 | 24 | 0 | 83 | 30 | 100 | 0 | 99 | 17 | 56 | 0 | 67 | 0 | 0 | 0 | 0 | 7972.5 | 932 | 94 | 0 | 32 | 30 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1072 | 0 | 0 | 0 | 1322.81 | 0 | 41 | 0 | 25 | 4 | 0 | 99 | 27 | 8 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 42 | 90 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 221 | 127 | 220 | 0 | 492 | 898 | 4 | 6536.81 | 14509.31 | 74.79
19:30 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 35.5 | 17 | 70 | 75 | 32 | 30 | 35 | 108 | 0 | 0 | 0 | 310 | 0 | 0 | 301 | 0 | 0 | 0 | 142 | 15 | 14 | 0 | 422 | 80 | 16 | 70 | 0 | 7 | 49 | 31 | 17 | 12 | 12 | 0 | 88 | 91 | 5 | 1130 | 16 | 0 | 50 | 25.5 | 97 | 217 | 0 | 0 | 0 | 1160 | 0 | 110 | 0 | 280 | 355 | 40 | 51 | 5 | 189 | 36 | 90 | 92 | 113 | 27 | 16 | 17 | 166 | 43 | 0 | 37 | 310 | 0 | 300 | 39 | 28 | 148 | 0 | 24 | 0 | 83 | 30 | 100 | 0 | 99 | 17 | 66 | 0 | 67 | 0 | 0 | 0 | 0 | 8255 | 932 | 93 | 0 | 39 | 60 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1130 | 0 | 0 | 0 | 1343.05 | 0 | 41 | 0 | 50 | 50 | 0 | 99 | 27 | 8 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 41 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 226 | 127 | 220 | 0 | 482 | 1080 | 54 | 7018.05 | 15273.05 | 74.77
20:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35.5 | 17 | 76 | 75 | 32 | 30 | 35 | 108 | 0 | 0 | 0 | 300 | 0 | 17 | 300 | 0 | 0 | 0 | 142 | 15 | 14 | 0 | 390 | 86 | 16 | 78 | 0 | 1 | 49 | 31 | 36 | 12 | 12 | 0 | 89 | 93 | 12 | 1120 | 15 | 0 | 50 | 25.5 | 98 | 217 | 0 | 0 | 0 | 1162 | 0 | 117 | 0 | 265 | 355 | 40 | 51 | 5 | 185 | 36 | 89 | 91 | 111 | 27 | 19 | 16 | 166 | 43 | 0 | 37 | 310 | 0 | 300 | 39 | 28 | 145 | 0 | 16 | 0 | 83 | 30 | 100 | 0 | 99 | 17 | 65 | 0 | 67 | 0 | 0 | 0 | 0 | 8241 | 932 | 94 | 0 | 34 | 63 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1184 | 0 | 0 | 0 | 1310.93 | 0 | 41 | 0 | 50 | 50 | 0 | 99 | 28 | 8 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 40 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 229 | 127 | 220 | 0 | 465 | 1100 | 54 | 7108.93 | 15349.93 | 74.77
21:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 35.5 | 17 | 79 | 75 | 32 | 0 | 35 | 108 | 0 | 0 | 0 | 305 | 0 | 17 | 304 | 0 | 0 | 0 | 142 | 15 | 14 | 0 | 450 | 94 | 16 | 78 | 0 | 5 | 49 | 31 | 36 | 12 | 12 | 0 | 89 | 106 | 12 | 1120 | 16 | 0 | 50 | 25.5 | 97 | 217 | 0 | 0 | 0 | 1164 | 0 | 139 | 0 | 235 | 356 | 36 | 51 | 5 | 188 | 36 | 87 | 92 | 112 | 27 | 19 | 17 | 168 | 52.2 | 0 | 37 | 310 | 0 | 301 | 39 | 28 | 149 | 0 | 16 | 0 | 83 | 28 | 100 | 0 | 99 | 17 | 65 | 0 | 77 | 0 | 0 | 0 | 0 | 8326.2 | 931 | 95 | 0 | 34 | 47 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1195 | 0 | 0 | 0 | 1410.03 | 0 | 41 | 0 | 50 | 50 | 0 | 99 | 26 | 8 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 40 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 230 | 127 | 220 | 0 | 496 | 1170 | 54 | 7295.03 | 15621.23 | 74.75
22:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 35.5 | 17 | 47 | 135 | 32 | 0 | 35 | 108 | 0 | 0 | 0 | 300 | 0 | 17 | 300 | 0 | 0 | 0 | 139 | 15 | 14 | 0 | 430 | 96 | 16 | 76 | 0 | 11 | 49 | 31 | 36 | 12 | 12 | 0 | 89 | 108 | 16 | 1110 | 15 | 0 | 50 | 25.5 | 98 | 217 | 0 | 0 | 0 | 1165 | 0 | 137 | 0 | 220 | 330 | 25 | 51 | 5 | 206 | 36 | 69 | 92 | 113 | 28 | 19 | 16 | 174 | 52.2 | 0 | 37 | 315 | 0 | 301 | 39 | 28 | 154 | 0 | 22 | 0 | 83 | 30 | 100 | 0 | 99 | 17 | 68 | 0 | 77 | 0 | 0 | 0 | 0 | 8311.2 | 932 | 88 | 0 | 34 | 46 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1197 | 0 | 0 | 0 | 1448.19 | 0 | 41 | 0 | 50 | 50 | 0 | 100 | 19 | 8 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 40 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 295 | 127 | 220 | 0 | 497 | 1172 | 54 | 7390.19 | 15701.39 | 74.73
23:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 35.5 | 17 | 20 | 149 | 32 | 0 | 35 | 108 | 0 | 0 | 0 | 305 | 0 | 17 | 308 | 0 | 0 | 0 | 142 | 15 | 21 | 0 | 460 | 95 | 16 | 70 | 0 | 9 | 50 | 30 | 36 | 12 | 12 | 0 | 64 | 107 | 18 | 1115 | 15 | 0 | 50 | 25.5 | 97 | 217 | 0 | 0 | 0 | 1172 | 0 | 46 | 0 | 220 | 330 | 58 | 51 | 5 | 208 | 36 | 60 | 91 | 117 | 28 | 19 | 17 | 170 | 52.2 | 0 | 37 | 310 | 0 | 301 | 40 | 28 | 154 | 0 | 22 | 0 | 83 | 30 | 100 | 0 | 100 | 17 | 68 | 0 | 77 | 0 | 0 | 0 | 0 | 8235.2 | 931 | 84 | 0 | 29 | 47 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1197 | 0 | 0 | 0 | 1456.98 | 0 | 41 | 0 | 50 | 50 | 0 | 100 | 18 | 8 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 40 | 95 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 127 | 220 | 0 | 499 | 1174 | 54 | 7384.98 | 15620.18 | 74.71
Total KWH | 0 | 2127360 | 748320 | 0 | 0 | 0 | 0 | 0 | 8557200 | 0 | 0 | 293400 | 143640 | 769104 | 2025120 | 816960 | 425969 | 535068 | 797760 | 0 | 0 | 0 | 7390060 | 0 | 175732 | 7083376 | 0 | 0 | 184894 | 3476400 | 345600 | 427320 | 0 | 10786363.64 | 1354909 | 243382 | 719040 | 0 | 238080 | 335634 | 396790 | 392008 | 202560 | 225600 | 23527 | 2249180 | 1610800 | 209280 | 24938181.82 | 966836 | 0 | 695520 | 266002.2 | 1686109 | 5265126 | 0 | 0 | 0 | 27970906 | 30780 | 978545 | 33455 | 6531500 | 7980100 | 2740000 | 1198936 | 168480 | 4902000 | 682776 | 697920 | 2118386 | 1842240 | 238560 | 418140 | 655500 | 3630720 | 694440 | 319909 | 538656 | 7548000 | 0 | 7445000 | 931000 | 694560 | 3475718.18 | 65637 | 358800 | 0 | 2006400 | 674688 | 1943000 | 0 | 2401550 | 165240 | 506400 | 98906 | 1924800 | 0 | 11300 | 249410 | 42960 | 184043529.84 | 22493818 | 3032352 | 0 | 169440 | 230400 | 0 | 0 | 0 | 0 | 0 | 466272 | 310320 | 28065460 | 141600 | 0 | 0 | 32635309 | 0 | 238092 | 0 | 442464 | 549120 | 0 | 562576 | 157034 | 122990 | 301805 | 625300 | 170256 | 0 | 333488 | 0 | 0 | 3372800 | 0 | 3380936 | 0 | 9599781 | 0 | 30660 | 0 | 953454 | 1593117 | 185186 | 1148592 | 0 | 0 | 0 | 42968.16 | 1228320 | 2500 | 280800 | 6152000 | 2901000 | 4903440 | 0 | 11010909 | 27102545.45 | 376800 | 165313904.61 | 349357434.45

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 07-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14729.93 | MW | 12:00 Hr. | Energy Generated |  |  | 349.3574 |  | MKWHr.
| Day Peak Demand |  |  | 15190.93 | MW | 12:00 Hr. | Energy Unserverd |  |  | 6.789 |  | MKWHr.
| Evening Peak Generation |  |  | 15621.23 | MW | 21:00 Hr. | Energy Demand |  |  | 356.1464 |  | MKWHr.
| Evening Peak Demand |  |  | 16048.23 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.2 |  | °C
| Minimum Generation of the Day |  |  | 13008 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 900.93 |  | MMCFD
| Maximum Generation of the Day |  |  | 15701.39 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 6.5556 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.5899 | 0 | 12.3348 | 0 | 0 | 0.18489 | 0 | 0 | 47.1096 | Gas | 121.5071 | Gas | 423507631.1944
| Chattogram Zone |  |  | 5.4744 | 52.9091 | 9.0952 | 0 | 2.2492 | 0.054307 | 0 | 0.23808 | 70.0203 | Coal | 126.1935 | Coal | 829517675.8021
| Cumilla Zone |  |  | 26.7738 | 0 | 5.6459 | 0 | 0 | 0.31991 | 3.6307 | 0 | 36.3703 | HFO | 36.3648 | HFO | 629898351.914
| Mymensingh Zone |  |  | 0 | 0 | 2.6394 | 0 | 0 | 0.35962 | 0 | 0 | 2.999 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.4787 | 0 | 0 | 0 | 0 | 0.065637 | 0 | 0 | 27.5444 | Hydro | 2.2492 | Hydro | 224918
| Khulna Zone |  |  | 3.0324 | 28.0655 | 1.0077 | 0 | 0 | 0.31032 | 22.4938 | 0 | 54.9097 | Solar | 4.0449 | Solar | 64037665.7932
| Barishal Zone |  |  | 7.8044 | 44.2655 | 0.6576 | 0 | 0 | 0.0025 | 0 | 0 | 52.73 | Import | 58.7598 | Import | 339550616.6
| Rajshahi Zone |  |  | 16.3535 | 0 | 2.2425 | 0 | 0 | 1.2913 | 32.6353 | 0 | 52.5226 | Wind | 0.23808 | Wind | 3502156.8
| Rangpur Zone |  |  | 0 | 0.95345 | 2.7417 | 0 | 0 | 1.4565 | 0 | 0 | 5.1516
| Total |  |  | 121.5071 | 126.1935 | 36.3648 | 0 | 2.2492 | 4.0449 | 58.7598 | 0.23808 | 349.3574
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 423507631.1944 |  | Hydro | 224918
|  |  |  | Coal | 829517675.8021 |  | Solar | 64037665.7932
|  |  |  | HFO | 629898351.914 |  | Import | 339550616.6
|  |  |  | HSD | 0 |  | Wind | 3502156.8
[5 empty] | Total: | 229,02,39,016 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.4938 | Peak Hr Flow | 931.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 48278000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.6353 | Peak Hr Flow | 1410.03 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2044 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.6307 | Peak Hr Flow | 168.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2684 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 58.7598 | Peak Hr Flow | 2509.03 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 130 |  | 5517
|  |  |  | Chattogram |  | 8 |  | 1562
|  |  |  | Cumilla |  | 8 |  | 1600
|  |  |  | Mymensingh |  | 231 |  | 1298
|  |  |  | Sylhet |  | 17 |  | 519
|  |  |  | Khulna |  | 0 |  | 1797
|  |  |  | Barishal |  | 0 |  | 499
|  |  |  | Rajshahi |  | 0 |  | 1584
|  |  |  | Rangpur |  | 15 |  | 1146
|  |  |  | Total |  | 409 |  | 15522
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:40 | 09:47 | Chowmuhani 230/132/33kV S/S TR1-415T LT Forced S/D Due to 33 KV Maijdee Feeder Raising | [7 empty] | 40.0MW load
|  |  | Loop Red Hot Maintanence | [7 empty] | interrup.
| 08:49 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- ST
| 09:12 | 18:27 | Maijdee 132/33kV S/S Chowmuhoni-Maijdee ckt -01 Scheduled S/D Due to project work
| 09:13 | 18:27 | Chowmuhani 230/132/33kV S/S Maijdee-01 Scheduled S/D Due to Project work
| 09:18 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- GT
| 09:19 |  | Satkhira 132/33kV S/S Transformer-3(T-3) LT Forced S/D Due to Due to oil leakage from
conservator tank.
| 09:19 |  | Satkhira 132/33kV S/S Transformer-3(T-3) HT Forced S/D Due to Due to oil leakage from
conservator tank.
| 09:19 |  | Ashuganj South 360 MW CCPP tripped.
| 10:40 | 13:31 | Sonargaon 132/33kV S/S OPSL(IEL-2) Scheduled S/D Due to OPSL end 132KV CB relay faulty
signals.
| 10:50 |  | Hasnabad-Sitalakhya 132kV Ckt-1 Tripped from Hasnabad 132/33kV end showing Distance | [7 empty] | 86.0MW load
|  |  | relay,Over current, Main protection Trip (86T) relays Due to The wire on the Shitalakkhya | [7 empty] | interrup. Hasnabad
|  |  | (Y - phase) line broke at From 88 to 91 Tower Spam. | [7 empty] | 132/33kV end
| 10:50 | 11:28 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Tripped showing Distance relay, Over | [7 empty] | 76.0MW load
|  |  | Current relay, Main Protection trip relay relays Due to The wire on the Shitalakkhya (Y | [7 empty] | interrup.
- phase) line broke at From 88 to 91 Tower Spam.
|  | 11:08 | Barishal 230/132kV S/S T-5 HT is restored.
|  | 11:10 | Barishal 230/132kV S/S T-5 LT is restored.
| 11:30 | 12:45 | Shomvuganj 400/132kV S/S Transformer-3 ( TR-3) HT Scheduled S/D Due to Oil Leakage
| 11:30 | 12:45 | Shomvuganj 400/132kV S/S Transformer-3 ( TR-3) LT Scheduled S/D Due to Oil Leakage
| 11:42 |  | Hasnabad-Sitalakhya 132kV Ckt-1 Forced S/D from Hasnabad 132/33kV end Due to The wire on
the Shitalakkhya (Y - phase) line broke at From 88 to 91 Tower Spam.
| 12:09 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 12:09 |  | Ashuganj South 360 MW CCPP GT was sync.
|  | 12:28 | Hasnabad 132/33kV S/S 132kV Main Bus is restored.
| 12:44 |  | Shahjibazar 330 MW CCPP was shutdown.
| 13:57 | 16:10 | Coxsbazar 132/33kV S/S T3 HT Forced S/D Due to 33kv incomer fire | [7 empty] | 80.0MW load
interrup.
| 15:40 |  | Coxsbazar 132/33kV S/S 415T-T2 HT Project Work S/D Due to 33kv LA installation
| 16:02 | 16:46 | Madaripur 132/33kV S/S T1-405T LT Tripped showing Over current, Earth fault relays Due to
Thunderstorm
| 16:02 | 16:47 | Madaripur 132/33kV S/S T2-415T LT Tripped showing Over current, Earth fault relays Due to
Thunderstorm
| 16:02 |  | Chandpur 132/33kV S/S 422T(T-5) HT Scheduled S/D Due to OLTC oil centrifuging
| 17:43 | 18:32 | Jhenaidah 132/33kV S/S Transformer T-3 LT Tripped showing No Relay operate. relays Due to | [7 empty] | 16.0MW load
|  |  | WZPDCL 33kV Magura Feeder Fault. | [7 empty] | interrup.
| 17:54 | 18:59 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Tripped showing E/F relays. | [7 empty] | 80.0MW load
interrup.
| 17:54 | 18:59 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Tripped showing E/F relays. | [7 empty] | 80.0MW load
interrup.
| 20:12 | 20:43 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Tripped showing Micom p142 relays Due to PBS 33 | [7 empty] | 19.0MW load
|  |  | kv Kalai feeder fault | [7 empty] | interrup.
| 23:05 |  | At Chorfashion SS,T2-33 KV CB is closed.
| 23:28 |  | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Due to
flashing on Tower no 96
| 02:14 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 05:37 |  | Jashore 132/33kV S/S T-1 LT Scheduled S/D Due to Repair work of 33/.04 kv 200 kVA | [7 empty] | 4.0MW load
|  |  | Auxiliary transformer | [7 empty] | interrup.
| 05:37 |  | Jashore 132/33kV S/S T-1 HT Scheduled S/D Due to Repair work of 33/.04 kv 200 kVA | [7 empty] | 4.0MW load
|  |  | Auxiliary transformer | [7 empty] | interrup.
| 05:40 |  | Coxsbazar 132/33kV S/S 405T-T1 HT Project Work S/D Due to Tr 01 & Tr 02 shutdown for | [7 empty] | 48.0MW load
|  |  | supply separately to incomer 1 from Tr 01 and incomer 2 from Tr 2 | [7 empty] | interrup.
| 07:23 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to 33kv Babuganj Feeder R phase Ds
problem
| 07:24 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to 33kv Babuganj Ds problem
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Under Maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 369 | 8557200 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 425969 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 304 | 7083376 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35.5 | 293400 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 75 | 2025120 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 535068 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 175732 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 345600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 427320 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 42 | 748320 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 32 | 816960 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 79 | 769104 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 2127360 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 797760 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 184894 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 143640 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 10786363.64 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 305 | 7390060 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3476400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2127.5 | 47109646.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 266002.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 30780 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 695520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 89 | 2249180 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5265126 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 97 | 1686109 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 31 | 396790 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 49 | 335634 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 202560 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 12 | 209280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 78 | 719040 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23527 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 243382 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 36 | 392008 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 106 | 1610800 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 225600 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 94 | 1354909 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 16 | 966836 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1164 | 27970906 | AGC
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 5 | 238080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1120 | 24938181.82 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 3229.5 | 70020251.02
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 188 | 4902000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 356 | 7980100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 36 | 2740000 | Unable to on FGMO>machine under observation.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 235 | 6531500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 682776 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 168480 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 33455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1198936 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 139 | 978545 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 538656 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 92 | 2118386 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 112 | 1842240 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 168 | 3630720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 694440 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 418140 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 655500 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 238560 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 87 | 697920 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 319909 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1657.2 | 36370263
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 98906 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 77 | 1924800 | Avil100%,NEO cut for BPDB late pay PPA Sec.13.2(j)
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 65 | 506400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 249410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 42960 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 165240 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 159 | 2999016
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 65637 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 39 | 931000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 694560 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3475718.18 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 100 | 1943000 | ps availability is less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 674688 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 2006400 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 99 | 2401550 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 358800 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7548000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 301 | 7445000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1153 | 27544353.18
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 931 | 22493818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 34 | 169440 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 47 | 230400 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 95 | 3032352 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 141600 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 466272 | FGMO
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 310320 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1195 | 28065460 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2352 | 54909662
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 496 | 11010909 | Unit1 Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 280800 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 127 | 2901000 | STG Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1170 | 27102545.45 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 4903440 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 376800 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 230 | 6152000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2500 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2313 | 52729994.45
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 301805 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 41 | 238092 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 157034 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Shutdown due to maintenance.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 130 | 3372800 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 130 | 3380936 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9599781 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 17 | 170256 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 122990 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 99 | 562576 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 549120 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 442464 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30660 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1410.03 | 32635309 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 333488 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 625300 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2375.03 | 52522611
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 40 | 953454 | U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 100 | 1148592 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42968.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1593117 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 185186 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1228320 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 255 | 5151637.16
Eastern Grid Total |  |  |  |  | 17438.042 | 8326.2 | 184043529.84
Western Grid Total |  |  |  |  | 11852.195 | 7295.03 | 165313904.61
National Grid Total |  |  |  |  | 29290.237 | 15621.23 | 349357434.45
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-06-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10102.58 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5010.4 | MW
i) Dhaka area |  |  | 5387.38 |  | MW | i) Khulna area |  |  |  | 1796.6 | MW
ii) Chattogram area |  |  | 1554.2 |  | MW | ii) Barishal area |  |  |  | 498.6 | MW
iii) Cumilla area |  |  | 1592 |  | MW | iii) Rajshahi area |  |  |  | 1584.2 | MW
iv) Mymensingh area |  |  | 1067 |  | MW | iv) Rangpur area |  |  |  | 1131 | MW
v) Sylhet area |  |  | 502 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15112.98 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 85 | 21:00 | 133 | Natore | 158 | 21:00
2 | AKSML | 143 | 02:00 | 68 | Hathazari | 100 | 00:00 | 134 | Nawabganj | 64.8 | 22:00
3 | Aftabnagar | 42 | 13:00 | 69 | Hatirjheel | 51 | 15:00 | 135 | Netrakona | 139 | 18:00
4 | Agargaon | 128 | 15:00 | 70 | Ishurdi | 83 | 15:00 | 136 | New | 84 | 15:00
5 | Agrabad | 74 | 15:00 | 71 | Jaldhaka | 93 | 20:00 | 137 | Niamatpur | 82 | 22:00
6 | Amnura | 32 | 22:00 | 72 | Jamalpur | 98 | 23:00 | 138 | Noapara | 52 | 20:00
7 | Ashuganj | 107 | 23:00 | 73 | Jashore | 151 | 14:00 | 139 | PHP | 12 | 12:00
8 | BSRM | 195 | 23:00 | 74 | Jhenaidah | 106 | 14:00 | 140 | Pabna | 98 | 20:00
9 | Bagerhat | 91 | 22:00 | 75 | Joydebpur | 144 | 11:00 | 141 | Palashbari | 136 | 19:30
10 | Bajitpur | 92 | 00:00 | 76 | Joypurhat | 71 | 22:00 | 142 | Panchagarh | 69 | 20:00
11 | Bakerganj | 15.2 | 00:00 | 77 | Juldah | 16 | 15:00 | 143 | Patiya | 13 | 00:00
12 | Bakulia | 98 | 19:00 | 78 | KSRM | 11 | 11:00 | 144 | Patuakhali | 81 | 00:00
13 | Banani | 66.6 | 13:00 | 79 | Kabirpur | 247 | 11:00 | 145 | Payra | 38 | 01:00
14 | Bangabhaban | 23 | 11:00 | 80 | Kachua | 102 | 21:00 | 146 | Postogola | 59 | 16:00
15 | Barapukuria | 73 | 19:30 | 81 | Kaliganj | 22 | 09:00 | 147 | Pubail | 31 | 19:00
16 | Barguna | 24 | 00:00 | 82 | Kallyanpur | 120 | 13:00 | 148 | Purbachal | 37 | 13:00
17 | Barishal | 111 | 13:00 | 83 | Kalurghat | 40 | 12:00 | 149 | Purbasadipur | 159 | 20:00
18 | Barishal-230 | 108 | 12:00 | 84 | Kamrangirchar | 67 | 13:00 | 150 | Rahanpur | 49 | 00:00
19 | Baroaulia | 68 | 00:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 56 | 01:00
20 | Baroirhat | 77 | 00:00 | 86 | Kasba | 43 | 19:00 | 152 | Rajbari | 84 | 19:30
21 | Bashundhara | 209 | 14:00 | 87 | Kazla | 89 | 02:00 | 153 | Rajendrapur | 115 | 21:00
22 | BashundharaCement | 8 | 23:00 | 88 | Keranigonj | 79 | 19:30 | 154 | Rajshahi | 120 | 23:00
23 | Beanibazar | 88 | 19:30 | 89 | Khagrachori | 36 | 12:00 | 155 | Rajshahi-230 | 100 | 13:00
24 | Benapole | 64 | 14:00 | 90 | Khulna | 76 | 13:00 | 156 | Ramganj | 122 | 00:00
25 | Bhaluka | 157 | 20:00 | 91 | Khulshi | 177 | 22:00 | 157 | Rampur | 50 | 00:00
26 | Bhandaria | 60 | 00:00 | 92 | Kishoreganj | 123 | 06:00 | 158 | Rangamati | 18 | 19:30
27 | Bhangura | 38.8 | 20:00 | 93 | Kodda | 311 | 19:30 | 159 | Rangpur | 158 | 19:30
28 | Bheramara(GK) | 68 | 21:00 | 94 | Kulaura | 63 | 00:00 | 160 | Ruppur | 4.6 | 15:00
29 | Bhulta | 200 | 12:00 | 95 | Kurigram | 76 | 19:30 | 161 | SSM | 10 | 00:00
30 | Bog-Sherpur | 78 | 00:00 | 96 | Kushtia | 164 | 13:00 | 162 | Saidpur | 111 | 19:30
31 | Bogura | 181 | 23:00 | 97 | Laksam | 35 | 03:00 | 163 | Santhia | 38 | 19:00
32 | Borhanuddin | 102 | 02:00 | 98 | Lakshmipur | 47 | 00:00 | 164 | Satkhira | 147 | 00:00
33 | Brahmanbaria | 146 | 20:00 | 99 | Lalbag | 70 | 13:00 | 165 | Satmasjid | 108 | 14:00
34 | Cantonment | 130 | 14:00 | 100 | Lalmonirhat | 73 | 19:30 | 166 | Savar | 216 | 12:00
35 | Chandina | 48 | 19:30 | 101 | MI_Cement | 15.9 | 10:00 | 167 | SevenRings | 11.53 | 19:00
36 | Chandpur | 92 | 00:00 | 102 | Madanganj | 42 | 00:00 | 168 | ShahCement | 24 | 10:00
37 | Chandraghona | 36 | 19:00 | 103 | Madaripur | 126 | 23:00 | 169 | Shahjadpur | 77 | 20:00
38 | Chapai | 79 | 23:00 | 104 | Madartek | 83 | 23:00 | 170 | Shahjibazar | 128 | 00:00
39 | Charsaidpur | 42 | 11:00 | 105 | Madunaghat | 57 | 19:00 | 171 | Shahmirpur | 65 | 00:00
40 | Chauddagram | 83 | 00:00 | 106 | Magura | 65 | 19:30 | 172 | Shariatpur | 103 | 19:30
41 | Chhatak | 46 | 19:30 | 107 | Mahasthangarh | 92 | 00:00 | 173 | Sherpur | 124 | 22:00
42 | Chowmuhani | 172 | 22:00 | 108 | Maijdee | 49 | 00:00 | 174 | Shikalbaha | 35 | 00:00
43 | Chuadanga | 118 | 15:00 | 109 | Manikganj | 131 | 19:30 | 175 | Shitalakhya | 80.9 | 19:00
44 | Coxsbazar | 148 | 18:30 | 110 | Maniknagar | 77 | 14:00 | 176 | Sholosohor | 46 | 19:30
45 | Cumilla(N) | 128 | 01:00 | 111 | Matarbari | 58 | 00:00 | 177 | Shomvuganj | 18 | 19:00
46 | Cumilla(S) | 172 | 19:00 | 112 | Matuail | 68 | 11:00 | 178 | Shyampur | 158 | 13:00
47 | Daganbhuiyan | 40 | 00:00 | 113 | Metrorail_Motijheel | 20 | 08:00 | 179 | Siddhirganj | 124 | 16:00
48 | Daudkandi | 158 | 19:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 108 | 23:00
49 | DhakaUniversity | 90 | 12:00 | 115 | Millgate | 108 | 15:00 | 181 | Sonargaon | 134 | 23:00
50 | Dhamrai | 110 | 19:30 | 116 | Mirpur | 156 | 16:00 | 182 | Sreemongol | 93 | 20:00
51 | Dhanmondi | 126 | 13:00 | 117 | Mirsorai | 13 | 16:00 | 183 | Sreepur | 115 | 19:30
52 | Dohazari | 117 | 20:00 | 118 | Mirzapur | 34 | 21:00 | 184 | Srinagar | 51.5 | 22:00
53 | Faridpur | 166 | 19:30 | 119 | Mithapukur | 70 | 20:00 | 185 | Sunamganj | 58 | 18:30
54 | Fatullah | 86 | 12:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 84 | 00:00
55 | Fenchuganj | 46 | 23:00 | 121 | Mogbazar | 102.7 | 14:00 | 187 | Sylhet-132 | 113 | 19:30
56 | Feni | 112 | 19:30 | 122 | Mongla | 49 | 10:00 | 188 | TK | 28 | 00:00
57 | GPH | 72 | 10:00 | 123 | Motijheel | 54 | 13:00 | 189 | Tangail | 148 | 19:30
58 | Ghatail | 69 | 23:00 | 124 | Muktagacha | 29 | 20:00 | 190 | Taraganj | 29 | 19:30
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 123 | 00:00 | 191 | Tasnim | 15 | 17:00
60 | Ghorashal-230 | 108 | 02:00 | 126 | Muradnagar | 55 | 22:00 | 192 | Thakurgaon | 127 | 20:00
61 | Goalpara | 36 | 13:00 | 127 | Mymensingh | 190 | 19:00 | 193 | Tongi | 160 | 09:00
62 | Gollamari | 112 | 13:00 | 128 | Nabinagar | 102 | 19:30 | 194 | Ullahpara | 41 | 21:00
63 | Gopalganj | 119 | 19:30 | 129 | Naogaon | 153 | 21:00 | 195 | Ullon | 56 | 19:00
64 | Gulshan | 146 | 16:00 | 130 | Narail | 60 | 19:30 | 196 | Uttara | 103 | 13:00
65 | Halishahar | 109 | 15:00 | 131 | Narinda | 70 | 13:00 | 197 | UttaraNew | 54 | 13:00
66 | HaripurSBU | 130 | 15:00 | 132 | Narshingdi | 164 | 01:00 | 198 | Zigatola | 96 | 14:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15577.15 | 437 |  | 16033.82
1:00 | 14986.53 | 254 |  | 15251.96
2:00 | 14238.63 | 240 |  | 14489.63
3:00 | 13738.32 | 224 |  | 13972.32
4:00 | 13470.53 | 189 |  | 13668.53
5:00 | 13166.41 | 198 |  | 13373.41
6:00 | 13008 | 176 |  | 13192
7:00 | 13080.78 | 182 |  | 13270.78
8:00 | 13309.99 | 165 |  | 13481.99
9:00 | 13611.02 | 133 |  | 13750.02
10:00 | 13908.3 | 142 |  | 14056.69
11:00 | 14070.2 | 223 |  | 14303.2
12:00 | 14729.93 | 441 |  | 15190.93
13:00 | 15109.08 | 338 |  | 15462.08
14:00 | 15149.7 | 345 |  | 15510.7
15:00 | 15262.34 | 683 |  | 15976.34
16:00 | 14594.36 | 363 |  | 14973.36
17:00 | 14197.45 | 332 |  | 14544.45
18:00 | 13300.9 | 241 |  | 13552.9
19:00 | 14509.31 | 262 |  | 14783.31
19:30 | 15273.05 | 261 |  | 15546.05
20:00 | 15349.93 | 251 |  | 15611.93
21:00 | 15621.23 | 409 |  | 16048.23
22:00 | 15701.39 | 261 |  | 15974.39
23:00 | 15620.18 | 300 |  | 15934.18
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8298.2 | 7278.95 | 15577.15 | DAILY GENERATION CURVE
00:30 | 8163.45 | 7118.39 | 15281.84
01:00 | 8028.7 | 6957.83 | 14986.53 | 07-06-2026
01:30 | 7764.35 | 6848.23 | 14612.58
02:00 | 7500 | 6738.63 | 14238.63
02:30 | 7295.5 | 6692.975 | 13988.475
03:00 | 7091 | 6647.32 | 13738.32
03:30 | 6990 | 6614.425 | 13604.425
04:00 | 6889 | 6581.53 | 13470.53
04:30 | 6789.5 | 6528.97 | 13318.47
05:00 | 6690 | 6476.41 | 13166.41
05:30 | 6700.985 | 6386.22 | 13087.205
06:00 | 6711.97 | 6296.03 | 13008
06:30 | 6763.97 | 6280.42 | 13044.39
07:00 | 6815.97 | 6264.81 | 13080.78
07:30 | 6867.09 | 6328.295 | 13195.385
08:00 | 6918.21 | 6391.78 | 13309.99
08:30 | 6914.24 | 6546.265 | 13460.505
09:00 | 6910.27 | 6700.75 | 13611.02
09:30 | 6994.785 | 6764.875 | 13759.66
10:00 | 7079.3 | 6829 | 13908.3
10:30 | 7199.11 | 6790.14 | 13989.25
11:00 | 7318.92 | 6751.28 | 14070.2
11:30 | 7508.7 | 6891.365 | 14400.065
12:00 | 7698.48 | 7031.45 | 14729.93
12:30 | 7800.26 | 7119.245 | 14919.505
13:00 | 7902.04 | 7207.04 | 15109.08
13:30 | 7934.135 | 7195.255 | 15129.39
14:00 | 7966.23 | 7183.47 | 15149.7
14:30 | 7989.495 | 7216.525 | 15206.02
15:00 | 8012.76 | 7249.58 | 15262.34
15:30 | 7934.845 | 6993.505 | 14928.35
16:00 | 7856.93 | 6737.43 | 14594.36
16:30 | 7756.01 | 6639.895 | 14395.905
17:00 | 7655.09 | 6542.36 | 14197.45
17:30 | 7369.185 | 6379.99 | 13749.175
18:00 | 7083.28 | 6217.62 | 13300.9
18:30 | 7527.89 | 6377.215 | 13905.105
19:00 | 7972.5 | 6536.81 | 14509.31
19:30 | 8255 | 7018.05 | 15273.05
20:00 | 8241 | 7108.93 | 15349.93
20:30 | 8283.6 | 7201.98 | 15485.58 |  | Executive Engineer
21:00 | 8326.2 | 7295.03 | 15621.23 |  | Network Operation Division
21:30 | 8318.7 | 7342.61 | 15661.31
22:00 | 8311.2 | 7390.19 | 15701.39
22:30 | 8273.2 | 7387.585 | 15660.785
23:00 | 8235.2 | 7384.98 | 15620.18

## En-Curve
QF-LDC-12
Date | 07-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3272 | 1710 | 905 | 0 | 154 | 1464.95 | 100 | 5580 | 0 | 640 | 1750.2 | 0 | 0 | 1 | 437 | DAILY ENERGY CURVE
00:30 | 3274 | 1700 | 905 | 0 | 153 | 1443.89 | 100 | 5467.5 | 0 | 602.5 | 1632.95 | 0 | 0 | 3 | 345.5 | 07-06-2026
01:00 | 3276 | 1690 | 905 | 0 | 152 | 1422.83 | 100 | 5355 | 0 | 565 | 1515.7 | 0 | 0 | 5 | 254
01:30 | 3298 | 1666.5 | 918.5 | 0 | 152 | 1402.23 | 100 | 5344.5 | 0 | 449.5 | 1274.85 | 0 | 0 | 6.5 | 247 | Energy Generated | 349.3574 |  | MKWHr
02:00 | 3320 | 1643 | 932 | 0 | 152 | 1381.63 | 100 | 5334 | 0 | 334 | 1034 | 0 | 0 | 8 | 240 | Energy not Served | 6.789 |  | MKWHr
02:30 | 3364.5 | 1614 | 932 | 0 | 149 | 1373.975 | 100 | 5297 | 0 | 322.5 | 829 | 0 | 0 | 6.5 | 232 | Total Energy Requirement | 356.1464 |  | MKWHr
03:00 | 3409 | 1585 | 932 | 0 | 146 | 1366.32 | 100 | 5260 | 0 | 311 | 624 | 0 | 0 | 5 | 224
03:30 | 3454.5 | 1609 | 932 | 0 | 144 | 1362.425 | 100 | 5253.5 | 0 | 298.5 | 445 | 0 | 0 | 5.5 | 206.5
04:00 | 3500 | 1633 | 932 | 0 | 142 | 1358.53 | 100 | 5247 | 0 | 286 | 266 | 0 | 0 | 6 | 189
04:30 | 3526 | 1600 | 932 | 0 | 138 | 1330.97 | 98.5 | 5202.5 | 0 | 278 | 209.5 | 0 | 0 | 3 | 193.5
05:00 | 3552 | 1567 | 932 | 0 | 134 | 1303.41 | 97 | 5158 | 0 | 270 | 153 | 0 | 0 | 0 | 198
05:30 | 3554 | 1595.5 | 932 | 0 | 132 | 1275.645 | 96.5 | 5062 | 16.06 | 270 | 153 | 0 | 0 | 0.5 | 187
06:00 | 3556 | 1624 | 932 | 0 | 130 | 1247.88 | 96 | 4966 | 32.12 | 270 | 153 | 0 | 0 | 1 | 176
06:30 | 3566 | 1641.5 | 932 | 0 | 128 | 1254.47 | 93.5 | 4940 | 61.42 | 272.5 | 153 | 0 | 0 | 2 | 179
07:00 | 3576 | 1659 | 932 | 0 | 126 | 1261.06 | 91 | 4914 | 90.72 | 275 | 153 | 0 | 0 | 3 | 182
07:30 | 3594 | 1651.5 | 932 | 0 | 128 | 1247.65 | 92.5 | 4925.5 | 173.735 | 296 | 153 | 0 | 0 | 1.5 | 173.5
08:00 | 3612 | 1644 | 932 | 0 | 130 | 1234.24 | 94 | 4937 | 256.75 | 317 | 153 | 0 | 0 | 0 | 165
08:30 | 3518.5 | 1645 | 932 | 0 | 133 | 1255.54 | 95 | 5057.5 | 333.465 | 324.5 | 162.5 | 0 | 0 | 3.5 | 149
09:00 | 3425 | 1646 | 932 | 0 | 136 | 1276.84 | 96 | 5178 | 410.18 | 332 | 172 | 0 | 0 | 7 | 133
09:30 | 3425.5 | 1629.5 | 932 | 0 | 139 | 1299.535 | 96.5 | 5228 | 427.125 | 347 | 231 | 0 | 0 | 4.5 | 137.5
10:00 | 3426 | 1613 | 932 | 0 | 142 | 1322.23 | 97 | 5278 | 444.07 | 362 | 290 | 0 | 0 | 2 | 142
10:30 | 3395.5 | 1601.5 | 932 | 0 | 143 | 1311.73 | 96 | 5249 | 485.52 | 362 | 410.5 | 0 | 0 | 2.5 | 182.5
11:00 | 3365 | 1590 | 932 | 0 | 144 | 1301.23 | 95 | 5220 | 526.97 | 362 | 531 | 0 | 0 | 3 | 223
11:30 | 3401.5 | 1624 | 932 | 0 | 150 | 1319.265 | 95 | 5262 | 564.82 | 396 | 650.98 | 0 | 0 | 4.5 | 332
12:00 | 3438 | 1658 | 932 | 0 | 156 | 1337.3 | 95 | 5304 | 602.67 | 430 | 770.96 | 0 | 0 | 6 | 441
12:30 | 3369 | 1673.5 | 932 | 0 | 152 | 1391.435 | 95.5 | 5328 | 599.49 | 432.5 | 938.08 | 0 | 0 | 8 | 389.5
13:00 | 3300 | 1689 | 932 | 0 | 148 | 1445.57 | 96 | 5352 | 596.31 | 435 | 1105.2 | 0 | 0 | 10 | 338
13:30 | 3290.5 | 1677 | 932 | 0 | 153 | 1445.845 | 97 | 5342.5 | 521.345 | 452 | 1209.7 | 0 | 0 | 8.5 | 341.5
14:00 | 3281 | 1665 | 932 | 0 | 158 | 1446.12 | 98 | 5333 | 446.38 | 469 | 1314.2 | 0 | 0 | 7 | 345
14:30 | 3264.5 | 1636.5 | 932 | 0 | 162 | 1441.165 | 98.5 | 5410.5 | 404.055 | 480 | 1357.8 | 0 | 0 | 19 | 514
15:00 | 3248 | 1608 | 932 | 0 | 166 | 1436.21 | 99 | 5488 | 361.73 | 491 | 1401.4 | 0 | 0 | 31 | 683
15:30 | 3160.5 | 1593.5 | 932 | 0 | 167 | 1441.85 | 99 | 5382.5 | 262.7 | 466 | 1393.3 | 0 | 0 | 30 | 523
16:00 | 3073 | 1579 | 932 | 0 | 168 | 1447.49 | 99 | 5277 | 163.67 | 441 | 1385.2 | 0 | 0 | 29 | 363
16:30 | 3139.5 | 1552 | 932 | 0 | 167 | 1456.91 | 97 | 5122.5 | 121.395 | 446 | 1320.1 | 0 | 0 | 41.5 | 347.5
17:00 | 3206 | 1525 | 932 | 0 | 166 | 1466.33 | 95 | 4968 | 79.12 | 451 | 1255 | 0 | 0 | 54 | 332
17:30 | 3153.5 | 1478.5 | 932 | 0 | 154 | 1403.115 | 93.5 | 4811 | 56.06 | 425 | 1205.5 | 0 | 0 | 37 | 286.5
18:00 | 3101 | 1432 | 932 | 0 | 142 | 1339.9 | 92 | 4654 | 33 | 399 | 1156 | 0 | 0 | 20 | 241
18:30 | 3205.5 | 1532.5 | 932 | 0 | 156 | 1331.355 | 91 | 4819.5 | 16.5 | 557 | 1247.75 | 0 | 0 | 16 | 251.5
19:00 | 3310 | 1633 | 932 | 0 | 170 | 1322.81 | 90 | 4985 | 0 | 715 | 1339.5 | 0 | 0 | 12 | 262
19:30 | 3303 | 1623 | 932 | 0 | 166 | 1343.05 | 88 | 5249 | 0 | 805 | 1757 | 0 | 0 | 7 | 261
20:00 | 3350 | 1580 | 932 | 0 | 166 | 1310.93 | 89 | 5300 | 0 | 804 | 1817 | 0 | 0 | 1 | 251
20:30 | 3337 | 1614.5 | 931.5 | 0 | 167 | 1360.48 | 89 | 5357.5 | 0 | 791 | 1834.6 | 0 | 0 | 3 | 330
21:00 | 3324 | 1649 | 931 | 0 | 168 | 1410.03 | 89 | 5415 | 0 | 778 | 1852.2 | 0 | 0 | 5 | 409
21:30 | 3308.5 | 1646.5 | 931.5 | 0 | 171 | 1429.11 | 89 | 5445.5 | 0 | 803 | 1829.2 | 0 | 0 | 8 | 335
22:00 | 3293 | 1644 | 932 | 0 | 174 | 1448.19 | 89 | 5476 | 0 | 828 | 1806.2 | 0 | 0 | 11 | 261
22:30 | 3313 | 1663.5 | 931.5 | 0 | 172 | 1452.585 | 76.5 | 5490 | 0 | 821 | 1730.7 | 0 | 0 | 10 | 280.5
23:00 | 3333 | 1683 | 931 | 0 | 170 | 1456.98 | 64 | 5504 | 0 | 814 | 1655.2 | 0 | 0 | 9 | 300
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 07-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 146 | -1 | 472 | 162 | 1484 | 238 | Ishurdi-Ghorashal Ckt-1 | Export | 3864000
1:00 | 127 | -6 | 434 | 156 | 1400 | 246
2:00 | 128 | -4 | 440 | 150 | 1390 | 256 |  | Import | 0
3:00 | 138 | 3 | 430 | 168 | 1428 | 286
4:00 | 144 | 4 | 450 | 164 | 1532 | 304 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 147 | 3 | 430 | 142 | 1560 | 290
6:00 | 143 | 5 | 400 | 138 | 1398 | 316 |  | Import | 0
7:00 | 138 | 7 | 390 | 138 | 1430 | 334
8:00 | 160 | 15 | 450 | 160 | 1554 | 376 | Sirajganj-Sreepur Ckt-1 | Export | 2813000
9:00 | 196 | 37 | 560 | 210 | 1834 | 504
10:00 | 200 | 44 | 570 | 218 | 1914 | 538 |  | Import | 0
11:00 | 190 | 43 | 540 | 216 | 1790 | 552
12:00 | 187 | 50 | 540 | 236 | 1728 | 536 | Sirajganj-Sreepur Ckt-2 | Export | 2821000
13:00 | 165 | 37 | 520 | 204 | 1614 | 548
14:00 | 171 | 44 | 540 | 220 | 1670 | 586 |  | Import | 0
15:00 | 191 | 65 | 570 | 248 | 1858 | 740
16:00 | 176 | 61 | 490 | 220 | 1726 | 700 | Gopalganj-Aminbazar Ckt-1 | Export | 19370000
17:00 | 174 | 54 | 480 | 200 | 1658 | 622
18:00 | 188 | 21 | 520 | 160 | 1588 | 506 |  | Import | 0
18:30 | 188 | 23 | 490 | 132 | 1576 | 528
19:00 | 189 | 30 | 480 | 140 | 1546 | 476 | Gopalganj-Aminbazar Ckt-2 | Export | 19410000
19:30 | 162 | 24 | 410 | 150 | 1546 | 488
20:00 | 148 | 18 | 410 | 156 | 1514 | 440 |  | Import | 0
21:00 | 144 | 28 | 410 | 180 | 1490 | 462
22:00 | 142 | 23 | 430 | 162 | 1560 | 446 |  | Total Export | 48278000
23:00 | 134 | 12 | 450 | 180 | 1630 | 466 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 07-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 06:00 | 356 | 15:00 | Madunaghat | 396 | 18:00 | 388 | 10:00
Amtali | 410 | 06:00 | 402 | 13:00 | Meghnaghat | 391 | 01:00 | 357 | 15:00
Ashuganj | 401 | 18:00 | 386 | 10:00 | Payra | 412 | 05:00 | 405 | 13:00
Bhulta | 395 | 06:00 | 370 | 15:00 | Rahanpur | 401 | 18:00 | 386 | 23:00
Bibiana | 395 | 05:00 | 380 | 15:00 | Rampal | 398 | 18:00 | 381 | 13:00
BIPTC | 402 | 07:00 | 395 | 14:00
Bogura | 384 | 18:30 | 367 | 23:00
Gopalganj | 394 | 06:00 | 375 | 15:00
Kaliakoir | 372 | 00:00 | 346 | 15:00
Korerhat | 396 | 01:00 | 379 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 01:00 | 209 | 15:00 | Jhenaidah | 229 | 18:00 | 211 | 13:00
AKSML | 231.3 | 18:00 | 223 | 04:00 | Kachua | 225 | 17:00 | 216 | 10:00
Aminbazar | 232 | 04:00 | 210 | 15:00 | Kaliakoir | 230 | 01:00 | 208 | 15:00
Ashuganj | 225 | 06:00 | 212 | 15:00 | Keranigonj | 226 | 06:00 | 208 | 15:00
Ashuganj-400 | 225 | 06:00 | 212 | 15:00 | Khulna(S) | 227 | 18:00 | 212 | 13:00
Baghabari | 232 | 18:00 | 223 | 22:00 | Korerhat | 225 | 18:00 | 216 | 15:00
Barapukuria | 221 | 18:00 | 204 | 22:00 | Madunaghat | 231 | 17:00 | 225 | 10:00
Barapukuria-230 | 221 | 18:00 | 204 | 22:00 | Madunaghat-400 | 233 | 18:00 | 226 | 10:00
Barishal | 230 | 18:00 | 221 | 13:00 | Maniknagar | 225 | 06:00 | 209 | 11:00
Bheramara | 233 | 17:00 | 221 | 19:30 | Meghnaghat | 234 | 18:30 | 219 | 15:00
Bhulta | 227 | 06:00 | 210 | 12:00 | Meghnaghat-400 | 229 | 18:30 | 212 | 15:00
Bibiana | 229 | 02:00 | 220 | 15:00 | Mirsorai | 233 | 10:00 | 222 | 15:00
BIPTC | 235 | 17:00 | 221 | 11:00 | Naogaon | 215 | 09:00 | 200 | 22:00
Bogura | 238 | 18:30 | 226 | 23:00 | Purbasadipur | 219 | 18:00 | 201 | 21:00
Bogura-400 | 237 | 18:00 | 227 | 22:00 | Rajshahi | 231 | 18:00 | 220 | 12:00
Borhanuddin | 232 | 18:00 | 225 | 00:00 | Rampal | 227 | 18:00 | 212 | 13:00
BSRM | 226 | 18:30 | 216 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 225 | 15:00 | 216 | 10:00 | Rampura | 227 | 06:00 | 208 | 15:00
Cumilla(N) | 225 | 18:00 | 213 | 15:00 | Shikalbaha | 231 | 00:00 | 225 | 08:00
Faridpur | 227 | 06:00 | 216 | 13:00 | Shyampur | 226 | 06:00 | 210 | 12:00
Fenchuganj | 232 | 02:00 | 225 | 12:00 | Siddhirganj | 225 | 03:00 | 212 | 15:00
Feni | 224 | 18:00 | 214 | 15:00 | Sirajgonj | 238 | 18:30 | 231 | 23:00
Ghorashal | 230 | 01:00 | 215 | 12:00 | Sreepur | 225 | 18:30 | 210 | 15:00
Ghorashal-230 | 216 | 01:00 | 197 | 15:00 | Tongi | 223 | 04:00 | 195 | 15:00
Gopalganj | 228 | 06:00 | 218 | 13:00
GPH | 228 | 00:00 | 222 | 10:00
Haripur | 226 | 05:00 | 211 | 12:00
Hasnabad | 226 | 04:00 | 212 | 11:00
Hathazari | 228 | 17:00 | 223 | 07:00
Ishurdi | 234 | 17:00 | 223 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 20:00 | 119 | 12:00 | Madunaghat | 133 | 00:00 | 130 | 09:00
Agargaon | 134 | 01:00 | 122 | 12:00 | Magura | 135 | 18:00 | 121 | 13:00
Agrabad | 132 | 17:00 | 127 | 09:00 | Mahasthangarh | 133 | 18:00 | 124 | 22:00
AKS | 130 | 01:00 | 126 | 08:00 | Maijdee | 126 | 17:00 | 119 | 15:00
Aminbazar | 132 | 03:00 | 118 | 16:00 | Manikganj | 130 | 18:00 | 119 | 15:00
Amnura | 136 | 18:30 | 124 | 22:00 | Maniknagar | 133 | 05:00 | 121 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 127 | 06:00 | 108 | 00:00
Ashuganj-230 | 134 | 08:00 | 126 | 15:00 | Matuail | 131.4 | 06:00 | 122 | 12:00
Bagerhat | 130 | 18:00 | 116 | 13:00 | Metrorail_Motijheel | 133 | 05:00 | 121 | 12:00
Bajitpur | 128 | 18:00 | 116 | 12:00 | Metrorail_Uttara | 135 | 01:00 | 116 | 12:00
Bakerganj | 132 | 18:00 | 127 | 12:00 | Millgate | 135 | 01:00 | 115 | 15:00
Bakulia | 132 | 01:00 | 128 | 09:00 | Mirpur | 131 | 02:00 | 118 | 15:00
Banani | 135 | 18:30 | 119 | 12:00 | Mirzapur | 130 | 18:00 | 119 | 15:00
Bangabhaban | 133 | 04:00 | 121 | 15:00 | Mithapukur | 130 | 18:00 | 121 | 19:30
Barapukuria | 134 | 18:00 | 121 | 22:00 | MI_Cement | 129 | 18:00 | 119.4 | 10:00
Barguna | 132 | 18:00 | 127 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 18:00 | 124 | 13:00 | Mogbazar | 135 | 18:00 | 120 | 12:00
Barishal-230 | 133 | 18:00 | 127 | 12:00 | Mongla | 130 | 15:00 | 118 | 12:00
Baroaulia | 132 | 00:00 | 128 | 09:00 | Motijheel | 133 | 03:00 | 121 | 15:00
Baroirhat | 131 | 01:00 | 127 | 09:00 | Muktagacha | 122 | 08:00 | 113 | 22:00
Bashundhara | 136 | 02:00 | 115 | 15:00 | Munshiganj | 130 | 06:00 | 120 | 12:00
BashundharaCement | 131 | 01:00 | 121 | 12:00 | Muradnagar | 127 | 18:00 | 118 | 15:00
Beanibazar | 128 | 02:00 | 120 | 00:00 | Mymensingh | 121 | 18:30 | 108 | 21:00
Benapole | 134 | 18:00 | 116 | 13:00 | Nabinagar | 131 | 02:00 | 115 | 15:00
Bhaluka | 128 | 18:30 | 117 | 13:00 | Naogaon | 134 | 18:30 | 120 | 22:00
Bhandaria | 130 | 18:00 | 120 | 00:00 | Narail | 135 | 18:00 | 120 | 13:00
Bhangura | 135 | 18:30 | 128 | 13:00 | Narinda | 133 | 05:00 | 121 | 12:00
Bheramara | 136 | 18:00 | 129 | 13:00 | Narshingdi | 128 | 05:00 | 116 | 15:00
Bheramara(GK) | 136 | 18:00 | 129 | 13:00 | Natore | 134 | 18:30 | 126 | 00:00
Bhulta | 130 | 03:00 | 119 | 12:00 | Nawabganj | 135 | 18:00 | 122 | 12:00
Bog-Sherpur | 134 | 18:00 | 127 | 23:00 | Netrakona | 118 | 18:30 | 105 | 13:00
Bogura | 135 | 18:00 | 130 | 14:00 | New | 136 | 01:00 | 116 | 15:00
Bogura-230 | 137 | 18:00 | 130 | 22:00 | Niamatpur | 131 | 18:00 | 124 | 22:00
Brahmanbaria | 127 | 06:00 | 118 | 15:00 | Noapara | 135 | 18:00 | 120 | 13:00
Cantonment | 134 | 01:00 | 122 | 15:00 | Pabna | 135 | 18:00 | 127 | 13:00
Chandina | 130 | 18:30 | 121 | 15:00 | Palashbari | 128 | 18:00 | 117 | 22:00
Chandpur | 132 | 17:00 | 122 | 08:00 | Panchagarh | 138 | 17:00 | 128 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 02:00 | 131 | 09:00 | Patiya | 131 | 16:00 | 126 | 10:00
Chapai | 132 | 18:00 | 125 | 23:00 | Patuakhali | 131 | 05:00 | 126 | 13:00
Charsaidpur | 130 | 04:00 | 121 | 15:00 | Payra | 135 | 06:00 | 132 | 12:00
Chauddagram | 129 | 18:00 | 122 | 11:00 | PHP | 130 | 18:30 | 124 | 13:00
Chhatak | 128 | 02:00 | 117 | 00:00 | Postogola | 132 | 03:00 | 121 | 15:00
Chowmuhani | 125 | 15:00 | 121 | 09:00 | Pubail | 128 | 18:30 | 116 | 14:00
Chuadanga | 134 | 18:00 | 118 | 13:00 | Purbachal | 135 | 01:00 | 115 | 15:00
Coxsbazar | 128 | 06:00 | 108 | 13:00 | Purbasadipur | 132 | 18:00 | 121 | 22:00
Cumilla(N) | 130 | 18:00 | 122 | 15:00 | Rahanpur | 134 | 18:00 | 128 | 13:00
Cumilla(S) | 131 | 05:00 | 122 | 15:00 | Rahanpur-400 | 134 | 18:00 | 128 | 22:00
Daganbhuiyan | 128 | 18:00 | 123 | 10:00 | Rahim | 131 | 06:00 | 122 | 15:00
Daudkandi | 125 | 18:30 | 117 | 11:00 | Rajbari | 129 | 06:00 | 121 | 15:00
DhakaUniversity | 135 | 18:30 | 119 | 12:00 | Rajendrapur | 129 | 18:30 | 119 | 14:00
Dhamrai | 133 | 05:00 | 117 | 15:00 | Rajshahi | 132 | 18:00 | 123 | 13:00
Dhanmondi | 135 | 18:30 | 122 | 12:00 | Rajshahi-230 | 133 | 18:30 | 124 | 22:00
Dohazari | 132 | 06:00 | 122 | 13:00 | Ramganj | 127 | 17:00 | 118 | 03:00
Faridpur | 130 | 06:00 | 125 | 12:00 | Rampur | 132 | 17:00 | 126 | 09:00
Fatullah | 130 | 06:00 | 119 | 12:00 | Rampura | 135 | 20:00 | 120 | 12:00
Fenchuganj | 132 | 02:00 | 127 | 15:00 | Rangamati | 133 | 06:00 | 129 | 10:00
Feni | 129 | 04:00 | 123 | 10:00 | Rangpur | 127 | 18:00 | 118 | 19:30
Feni-230 | 129 | 18:00 | 123 | 11:00 | Ruppur | 137 | 18:00 | 129 | 13:00
Ghatail | 124 | 18:00 | 114 | 11:00 | Saidpur | 132 | 18:00 | 120 | 22:00
Ghorashal | 130 | 18:30 | 118 | 15:00 | Santhia | 135 | 18:30 | 128 | 13:00
Goalpara | 137 | 18:00 | 123 | 13:00 | Satkhira | 131 | 18:00 | 117 | 13:00
Gollamari | 136 | 18:00 | 123 | 13:00 | Satmasjid | 133 | 01:00 | 121 | 15:00
Gopalganj | 132 | 18:00 | 122 | 13:00 | Savar | 133 | 02:00 | 116 | 16:00
Gopalganj-400 | 135 | 06:00 | 126 | 13:00 | SevenRings | 129 | 18:00 | 119 | 12:00
Gulshan | 134 | 18:00 | 119 | 12:00 | ShahCement | 130 | 04:00 | 121 | 12:00
Halishahar | 132 | 00:00 | 127 | 09:00 | Shahjadpur | 137 | 04:00 | 131 | 13:00
Haripur | 132 | 05:00 | 122 | 15:00 | Shahjibazar | 129 | 18:30 | 121 | 15:00
HaripurSBU | 132 | 05:00 | 123 | 12:00 | Shahmirpur | 133 | 16:00 | 127 | 09:00
Hasnabad | 132 | 04:00 | 122 | 10:00 | Shariatpur | 131 | 18:00 | 123 | 13:00
Hathazari | 135 | 04:00 | 130 | 07:00 | Sherpur | 122 | 08:00 | 110 | 03:00
Hatirjheel | 135 | 20:00 | 120 | 12:00 | Shikalbaha | 121 | 00:00 | 118 | 09:00
Ishurdi | 138 | 18:00 | 130 | 13:00 | Shikalbaha-230 | 133 | 00:00 | 129 | 09:00
Jaldhaka | 128 | 17:00 | 117 | 19:30 | Shitalakhya | 129 | 18:00 | 119.4 | 10:00
Jamalpur | 125 | 08:00 | 113 | 03:00 | Sholosohor | 133 | 01:00 | 129 | 09:00
Jashore | 135 | 18:00 | 118 | 13:00 | Shomvuganj | 119 | 18:30 | 112 | 11:00
Jhenaidah | 136 | 18:00 | 122 | 13:00 | Shyampur | 129 | 06:00 | 117 | 15:00
Jhenaidah-230 | 138 | 18:00 | 123 | 14:00 | Shyampur-230 | 128 | 01:00 | 118 | 15:00
Joydebpur | 127 | 18:30 | 116 | 11:00 | Siddhirganj | 139 | 01:00 | 122 | 15:00
Joypurhat | 131 | 18:00 | 122 | 22:00 | Sirajganj | 133 | 18:30 | 125 | 22:00
Juldah | 132 | 00:00 | 126 | 09:00 | Sonargaon | 129 | 05:00 | 121 | 11:00
Kabirpur | 134 | 18:00 | 114 | 11:00 | Sreemongol | 129 | 18:00 | 122 | 15:00
Kachua | 129 | 17:00 | 122 | 10:00 | Sreepur | 132 | 18:30 | 122 | 15:00
Kaliakoir | 136 | 01:00 | 121 | 15:00 | Srinagar | 135 | 18:00 | 122 | 12:00
Kaliganj | 137 | 18:00 | 121 | 13:00 | SSM | 138 | 00:00 | 132 | 09:00
Kallyanpur | 133 | 06:00 | 118 | 15:00 | Sunamganj | 126 | 21:00 | 115 | 00:00
Kalurghat | 133 | 01:00 | 129 | 08:00 | Sylhet | 128 | 02:00 | 121 | 16:00
Kamrangirchar | 136 | 18:00 | 116 | 15:00 | Sylhet-132 | 128 | 03:00 | 122 | 15:00
Kaptai | 136 | 6:00 | 133 | 12:00 | Tangail | 124 | 18:00 | 115 | 15:00
Kasba | 127 | 18:00 | 118 | 11:00 | Taraganj | 131 | 18:00 | 120 | 20:00
Kazla | 135 | 06:00 | 121 | 13:00 | Tasnim | 130 | 06:00 | 121 | 11:00
Keranigonj | 136 | 18:00 | 123 | 12:00 | Thakurgaon | 137 | 17:00 | 126 | 10:00
Khagrachori | 133 | 06:00 | 128 | 11:00 | TK | 133 | 00:00 | 129 | 09:00
Khulna | 135 | 18:00 | 122 | 13:00 | Tongi | 138 | 04:00 | 120 | 15:00
Khulna(S) | 136 | 18:00 | 124 | 13:00 | Ullahpara | 135 | 18:30 | 127 | 13:00
Khulshi | 131 | 01:00 | 126 | 09:00 | Ullon | 134 | 18:00 | 120 | 12:00
Kishoreganj | 127 | 18:00 | 114 | 13:00 | Uttara | 133 | 00:00 | 116 | 12:00
Kodda | 132 | 18:00 | 123 | 09:00 | UttaraNew | 135 | 01:00 | 114 | 15:00
Korerhat | 134 | 01:00 | 127 | 15:00 | Zigatola | 135 | 18:30 | 123 | 13:00
KSRM | 133 | 20:00 | 128 | 09:00
Kulaura | 131 | 03:00 | 125 | 15:00
Kurigram | 126 | 18:00 | 114 | 19:30
Kushtia | 137 | 18:00 | 126 | 13:00
Laksam | 129 | 18:00 | 122 | 03:00
Lakshmipur | 126 | 17:00 | 119 | 15:00
Lalbag | 135 | 18:00 | 124 | 15:00
Lalmonirhat | 125 | 18:00 | 111 | 19:30
Madanganj | 131 | 01:00 | 121 | 12:00
Madaripur | 132 | 05:00 | 125 | 13:00
Madartek | 135 | 20:00 | 118 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division