## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-06-2026 | during | 12-06-2026 | during | 12-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 383 | 385 | 412 | 412 | 0 | 0 | Under Maintenance
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 0 | 0 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 210 | 210 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 315 | 293 | 335 | 335 | 310 | 310 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35.5 | 53.97 | 53.97 | 0 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 145 | 146 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15 | 16 | 33 | 33 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 14 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 50 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 32 | 300 | 300 | 33 | 33 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 70 | 149 | 149 | 17 | 72 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 88 | 105 | 105 | 17 | 88 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 72 | 162 | 162 | 0 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 16 | 0 | 16 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 435 | 370 | 584 | 584 | 430 | 430 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 305 | 308 | 583 | 583 | 380 | 380 | AGC+Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1935 | 2146.5 | 5808.22 | 5792.22 | 1963.36 | 2322.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 7 | 0 | 7 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 6 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 57 | 30 | 60 | 60 | 60 | 60 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 219 | 215 | 220 | 215 | 220 | Machine Problem
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 101 | 102 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 51 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 3 | 7 | 40 | 40 | 10 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 16 | 57 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.73 | 0 | 3.64 | 0 | 3.64 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 25 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 107 | 107 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 96 | 97 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 142 | 146 | 163 | 163 | 35 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 585 | 612 | 612 | 612 | 1204 | 612 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 14 | 11 | 10 | 10 | 10 | 10 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 1125 | 1150 | 1150 | 1150 | 1150 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2552.23 | 2659.5 | 3388.5 | 3382.86 | 3145.14 | 2760.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 208 | 216 | 221.25 | 221.25 | 215 | 215 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 290 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 250 | 250 | 342.01 | 342.01 | 342.01 | 342.01 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 250 | 210 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 11 | 11 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 56 | 20 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 29 | 40 | 40 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 89 | 89 | 163 | 163 | 94 | 94 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 170 | 188 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 176 | 190 | 76 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 107 | 108 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 17 | 27 | 113 | 113 | 0 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 11 | 87 | 115 | 115 | 0 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 26 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1800.2 | 1826.2 | 2724.44 | 2696.44 | 2065.22 | 2238.22
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-06-2026 | during | 12-06-2026 | during | 12-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 21 | 0 | 5 | 0 | 5 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.5 | 0 | 1.5 | 0 | 1.5 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 66 | 87 | 50 | 90 | 50 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 68 | 80 | 70 | 50 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 24.92 | 0 | 20 | 0 | 20 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 170.42 | 155 | 443 | 446.5 | 126.5 | 177
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 28 | 28 | 28 | 28 | 28 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 0 | 0 | 0 | 30 | 30 | Plant availability less
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 151 | 151 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 142 | 141 | 140 | 140 | 100 | 100 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 62 | 41 | 83 | 83 | 83 | 83 | one engine under maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 101 | 101 | 101 | 101 | 101 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.02 | 0.02 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 23 | 25 | 0 | 0 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 344 | 296 | 350 | 350 | 350 | 350 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1237 | 1123 | 1256 | 1256 | 1201.02 | 1201.02
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 920 | 892 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 23 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 58 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 170 | 170 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 85 | 105 | 105 | 0 | 34 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 101 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 96.47 | 0 | 60 | 0 | 60 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1207 | 1203 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2223.47 | 2362 | 3226.2 | 3166.2 | 2521 | 2495
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 491 | 500 | 500 | 500 | 500 | 500 | AGC, Unit1 Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 126 | 126 | 65 | 65 | 130 | 130 | STG Under Maintenance
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1090 | 1176 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 67 | 67 | 67 | 67 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 0 | 72 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 300 | 197 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.65 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2090.65 | 2136 | 2444 | 2443 | 2338 | 2409
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 28.48 | 0 | 30 | 0 | 30 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 168 | 158 | 220 | 220 | 140 | 140 | Gas Restrction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 166 | 159 | 220 | 220 | 130 | 130 | Gas Restrction
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 395 | 386 | 413.79 | 413.79 | 413.79 | 413.79 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 32 | 32 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 86 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 13 | 35 | 113 | 113 | 35 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.34 | 0 | 3.7 | 0 | 3.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1445 | 1473 | 1435.88 | 1435.88 | 1355.88 | 1355.88 | AGC+FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 20.12 | 0 | 35 | 0 | 35 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 86 | 0 | 70 | 0 | 70 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2323.94 | 2466.2 | 2934.57 | 2795.87 | 2402.57 | 2385.87
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 43 | 45 | 45 | 45 | 41 | 41 | Plant availability zero, U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 35 | 50 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.2 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 17 | 0 | 10 | 0 | 10 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 70 | 0 | 60.67 | 0 | 60.67 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 131.2 | 194 | 346.67 | 273 | 264.67 | 206
System Total |  |  |  |  | 28843.2 | 29290.237 | 14464.11 | 15068.4 | 22571.6 | 22252.09 | 16027.48 | 16194.97
Forecast Scenario (12-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15000 |  | 0 |  | 15000
|  |  |  | 1:00 | 14920 |  | 0 |  | 14920
|  |  |  | 2:00 | 14960 |  | 0 |  | 14960
|  |  |  | 3:00 | 14560 |  | 0 |  | 14560
|  |  |  | 4:00 | 14100 |  | 0 |  | 14100
|  |  |  | 5:00 | 13950 |  | 0 |  | 13950
|  |  |  | 6:00 | 13350 |  | 0 |  | 13350
|  |  |  | 7:00 | 12930 |  | 0 |  | 12930
|  |  |  | 8:00 | 12740 |  | 0 |  | 12740
|  |  |  | 9:00 | 12670 |  | 0 |  | 12670
|  |  |  | 10:00 | 12560 |  | 0 |  | 12560
|  |  |  | 11:00 | 12330 |  | 0 |  | 12330
|  |  |  | 12:00 | 12510 |  | 0 |  | 12510
|  |  |  | 13:00 | 12760 |  | 0 |  | 12760
|  |  |  | 14:00 | 12260 |  | 0 |  | 12260
|  |  |  | 15:00 | 12190 |  | 0 |  | 12190
|  |  |  | 16:00 | 11930 |  | 0 |  | 11930
|  |  |  | 17:00 | 11760 |  | 0 |  | 11760
|  |  |  | 18:00 | 11730 |  | 0 |  | 11730
|  |  |  | 18:30 | 12600 |  | 0 |  | 12600
|  |  |  | 19:00 | 13360 |  | 0 |  | 13360
|  |  |  | 19:30 | 14150 |  | 0 |  | 14150
|  |  |  | 20:00 | 14120 |  | 0 |  | 14120
|  |  |  | 21:00 | 14730 |  | 0 |  | 14730
|  |  |  | 22:00 | 14720 |  | 0 |  | 14720
|  |  |  | 23:00 | 14830 |  | 0 |  | 14830
Probable Maximum Temperature: |  |  | 36.50°C
Probable Maximum Demand at Day Peak: |  |  | 12670.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14730.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14730.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 320.97 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:20 hrs on 12-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-06-2026 | [28 empty] | Date: | 11-06-2026 | [28 empty] | Date: | 11-06-2026 | [28 empty] | Date: | 11-06-2026 | [28 empty] | Date: | 11-06-2026 | [18 empty] | Date: | 11-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [18 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 17 | 142 | 32 | 0 | 35 | 35 | 0 | 0 | 0 | 330 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 14.5 | 21 | 0 | 410 | 97 | 16 | 72 | 0 | 17 | 50 | 0 | 40 | 12 | 12 | 0 | 58 | 110 | 19 | 1125 | 135 | 0 | 6 | 25.5 | 100 | 217 | 0 | 0 | 0 | 656 | 0 | 41 | 0 | 220 | 290 | 220 | 51 | 0 | 216 | 0 | 52 | 91 | 176 | 0 | 19 | 109 | 168 | 52.2 | 0 | 37 | 315 | 0 | 344 | 28 | 30 | 151 | 0 | 23 | 0 | 62 | 30 | 143 | 0 | 102 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7702.2 | 928 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 1214 | 34 | 0 | 0 | 1449 | 0 | 40 | 0 | 55 | 35 | 0 | 86 | 21 | 52.2 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 152 | 0 | 149 | 0 | 401 | 0 | 0 | 0 | 42 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 286 | 126 | 66 | 0 | 484 | 1240 | 90 | 7242.2 | 14944.4 | 73.84
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 17 | 136 | 32 | 0 | 35 | 35 | 0 | 0 | 0 | 325 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 14.5 | 21 | 0 | 380 | 95 | 16 | 36 | 0 | 18 | 44 | 0 | 54.36 | 12 | 12 | 0 | 59 | 109 | 13 | 1125 | 143 | 0 | 6 | 25.5 | 99 | 220 | 0 | 0 | 0 | 612 | 0 | 70 | 0 | 220 | 290 | 220 | 51 | 0 | 216 | 0 | 52 | 92 | 177 | 0 | 19 | 109 | 162 | 52.2 | 0 | 37 | 310 | 0 | 344 | 28 | 30 | 150 | 0 | 23 | 0 | 62 | 30 | 140 | 0 | 102 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7580.56 | 928 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 1214 | 34 | 0 | 0 | 1440 | 0 | 39 | 0 | 35 | 35 | 0 | 0 | 20 | 52.2 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 152 | 0 | 149 | 0 | 385 | 0 | 0 | 0 | 41 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 282 | 126 | 65 | 0 | 477 | 1244 | 17 | 7001.2 | 14581.76 | 73.8
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 17 | 137 | 32 | 0 | 35 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 298 | 0 | 0 | 0 | 142 | 14.5 | 21 | 0 | 380 | 92 | 16 | 31 | 0 | 42 | 0 | 0 | 54.36 | 12 | 12 | 0 | 59 | 108 | 13 | 1125 | 120 | 0 | 6 | 25.5 | 96 | 219 | 0 | 0 | 0 | 560 | 0 | 120 | 0 | 220 | 290 | 220 | 51 | 0 | 218 | 0 | 0 | 91 | 176 | 0 | 19 | 108 | 160 | 52.2 | 0 | 37 | 305 | 0 | 344 | 28 | 30 | 140 | 0 | 23 | 0 | 62 | 30 | 140 | 0 | 102 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7401.56 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1212 | 34 | 0 | 0 | 1384 | 0 | 39 | 0 | 35 | 35 | 0 | 0 | 19 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 152 | 0 | 149 | 0 | 374 | 0 | 0 | 0 | 41 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 234 | 126 | 65 | 0 | 436 | 1244 | 17 | 6784 | 14185.56 | 73.8
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 17 | 147 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 302 | 0 | 0 | 0 | 123 | 14.5 | 21 | 0 | 370 | 91 | 16 | 31 | 0 | 12 | 0 | 0 | 35 | 12 | 12 | 0 | 59 | 107 | 18 | 1125 | 0 | 0 | 6 | 8 | 96 | 220 | 0 | 0 | 0 | 560 | 0 | 120 | 0 | 220 | 290 | 220 | 51 | 0 | 216 | 0 | 0 | 91 | 120 | 0 | 19 | 24 | 152 | 52.2 | 0 | 37 | 315 | 0 | 344 | 28 | 30 | 138 | 0 | 23 | 0 | 62 | 30 | 143 | 0 | 102 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7023.7 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1215 | 84 | 0 | 0 | 1341 | 0 | 41 | 0 | 35 | 35 | 0 | 0 | 19 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 152 | 0 | 149 | 0 | 362 | 0 | 0 | 0 | 41 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 202 | 126 | 65 | 0 | 423 | 1242 | 17 | 6739 | 13762.7 | 73.8
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 17 | 146 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 300 | 0 | 0 | 0 | 105 | 14.5 | 21 | 0 | 400 | 94 | 16 | 32 | 0 | 16 | 0 | 0 | 0 | 12 | 12 | 0 | 59 | 106 | 21 | 1125 | 0 | 0 | 6 | 0 | 97 | 220 | 0 | 0 | 0 | 560 | 0 | 120 | 0 | 220 | 290 | 220 | 51 | 0 | 216 | 0 | 0 | 91 | 68 | 0 | 19 | 0 | 152 | 52.2 | 0 | 0 | 310 | 0 | 344 | 28 | 30 | 137 | 0 | 23 | 0 | 62 | 30 | 142 | 0 | 102 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6884.7 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1215 | 53 | 0 | 0 | 1299 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 151 | 0 | 368 | 0 | 0 | 0 | 42 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 217 | 126 | 65 | 0 | 441 | 1244 | 17 | 6476 | 13360.7 | 73.8
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 17 | 146 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 300 | 0 | 0 | 0 | 105 | 14.5 | 21 | 0 | 350 | 91 | 0 | 31 | 0 | 16 | 0 | 0 | 0 | 12 | 12 | 0 | 59 | 108 | 29 | 1125 | 0 | 0 | 6 | 0 | 96 | 220 | 0 | 0 | 0 | 560 | 0 | 120 | 0 | 220 | 290 | 220 | 51 | 0 | 200 | 0 | 0 | 92 | 34 | 0 | 19 | 0 | 140 | 52.2 | 0 | 0 | 305 | 0 | 344 | 28 | 30 | 141 | 0 | 23 | 0 | 62 | 30 | 140 | 0 | 102 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6758.7 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 34 | 0 | 0 | 1264 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 155 | 0 | 355 | 0 | 0 | 0 | 40 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 205 | 126 | 65 | 0 | 419 | 1244 | 17 | 6293 | 13051.7 | 73.8
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 17 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 295 | 0 | 0 | 1 | 105 | 14.5 | 21 | 0 | 390 | 0 | 0 | 31 | 0 | 16 | 0 | 0 | 0 | 12 | 12 | 0 | 59 | 105 | 33 | 1125 | 0 | 0 | 6 | 0 | 68 | 220 | 0 | 0 | 0 | 560 | 1 | 30 | 0 | 250 | 290 | 220 | 51 | 0 | 199 | 0 | 0 | 92 | 0 | 0 | 19 | 0 | 140 | 16 | 4 | 0 | 305 | 0 | 344 | 28 | 30 | 129 | 0 | 23 | 0 | 62 | 30 | 142 | 0 | 102 | 0 | 49 | 0.61 | 48 | 0 | 0 | 1.2 | 0 | 6497.31 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1202 | 0 | 0 | 0 | 1274 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 1.1 | 6 | 0 | 0 | 0.97 | 0 | 0 | 158 | 0 | 158 | 0 | 375 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0.05 | 16 | 214 | 126 | 65 | 0 | 432 | 1244 | 0 | 6275.12 | 12772.43 | 73.8
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 17 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 300 | 0 | 0 | 3 | 105 | 14.5 | 22 | 0 | 410 | 0 | 0 | 31 | 0 | 29 | 0 | 0 | 0 | 12 | 12 | 1.42 | 59 | 49 | 25 | 1115 | 0 | 0 | 6 | 0 | 51 | 219 | 0 | 0 | 0 | 500 | 5 | 12 | 0 | 250 | 290 | 220 | 51 | 0 | 201 | 0 | 0 | 92 | 0 | 0 | 19 | 0 | 140 | 16 | 13 | 0 | 310 | 0 | 344 | 28 | 30 | 152 | 1 | 23 | 0 | 62 | 30 | 142 | 0 | 102 | 0 | 49 | 1.9 | 48 | 0 | 0.2 | 10.01 | 0 | 6444.03 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 1100 | 0 | 0 | 0 | 1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.64 | 21 | 0 | 0 | 4.6 | 0 | 0 | 158 | 0 | 160 | 0 | 403 | 0 | 0 | 0 | 42 | 0 | 1 | 0 | 0 | 0 | 0 | 0.6 | 3 | 0.17 | 16 | 285 | 126 | 65 | 0 | 495 | 1100 | 0 | 6276.01 | 12720.04 | 73.8
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 17 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 310 | 0 | 0 | 10 | 105 | 14.5 | 22 | 0 | 430 | 0 | 0 | 31 | 0 | 16 | 0 | 0 | 0 | 12 | 12 | 1.58 | 60 | 50 | 7 | 1115 | 0 | 0 | 6 | 0 | 50 | 219 | 0 | 0 | 0 | 500 | 6 | 12 | 0 | 250 | 290 | 220 | 51 | 0 | 207 | 0 | 0 | 90 | 0 | 0 | 19 | 0 | 146 | 16 | 39 | 0 | 315 | 0 | 344 | 28 | 30 | 152 | 3 | 23 | 0 | 62 | 30 | 143 | 0 | 102 | 0 | 49 | 8.02 | 48 | 0 | 0.4 | 18.09 | 0 | 6529.59 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 1098 | 0 | 0 | 0 | 1426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.8 | 45 | 0 | 0 | 11.54 | 0 | 0 | 159 | 0 | 161 | 0 | 402 | 0 | 0 | 0 | 41 | 0 | 1 | 0 | 0 | 0 | 0 | 4.1 | 2 | 0.27 | 16 | 296 | 126 | 65 | 0 | 500 | 1100 | 0 | 6429.71 | 12959.3 | 73.8
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 17 | 149 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 17 | 306 | 0 | 0 | 19 | 117 | 15.5 | 21 | 0 | 455 | 5 | 16 | 18 | 0 | 6 | 0 | 0 | 0 | 12 | 12 | 1.72 | 60 | 60 | 2 | 1115 | 12 | 0 | 6 | 2 | 60 | 214 | 0 | 0 | 0 | 580 | 0 | 12 | 0 | 250 | 290 | 220 | 51 | 0 | 202 | 0 | 0 | 90 | 20 | 0 | 12 | 30 | 154 | 25 | 9 | 0 | 305 | 0 | 344 | 28 | 30 | 153 | 5 | 23 | 0 | 62 | 30 | 142 | 0 | 102 | 0 | 49 | 8.51 | 48 | 0 | 0.6 | 14.05 | 0 | 6741.38 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 1132 | 0 | 0 | 0 | 1437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.91 | 49 | 0 | 0 | 19.26 | 0 | 0 | 162 | 0 | 161 | 0 | 392 | 0 | 0 | 0 | 43 | 0 | 10 | 0 | 0 | 0 | 0 | 5.7 | 9 | 0.27 | 16 | 299 | 126 | 65 | 0 | 496 | 1100 | 0 | 6544.14 | 13285.52 | 73.8
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 17 | 148 | 32 | 0 | 0 | 35 | 0 | 0 | 0 | 322 | 0 | 0 | 300 | 0 | 0 | 26 | 142 | 15.5 | 14 | 0 | 375 | 53 | 16 | 18 | 0 | 14 | 0 | 0 | 0 | 12 | 12 | 4.09 | 58 | 92 | 2 | 1125 | 100 | 0 | 6 | 17 | 99 | 214 | 0 | 0 | 0 | 580 | 14 | 26 | 0 | 250 | 290 | 250 | 51 | 0 | 213 | 0 | 0 | 90 | 116 | 4 | 12 | 98 | 170 | 52.2 | 10 | 2 | 295 | 0 | 344 | 28 | 30 | 155 | 10 | 23 | 0 | 62 | 30 | 142 | 0 | 102 | 0 | 49 | 10.66 | 48 | 0 | 1.1 | 24.51 | 0 | 7242.06 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.56 | 1152 | 0 | 0 | 0 | 1395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.3 | 98 | 0 | 0 | 36.14 | 0 | 0 | 165 | 0 | 165 | 0 | 368 | 0 | 0 | 0 | 43 | 0 | 20 | 0 | 0 | 0 | 0 | 3.5 | 45 | 0.66 | 16 | 302 | 126 | 65 | 0 | 431 | 1092 | 0 | 6560.16 | 13802.22 | 73.79
11:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 17 | 0 | 17 | 146 | 32 | 0 | 17 | 35 | 0 | 0 | 0 | 315 | 0 | 0 | 300 | 0 | 0 | 29 | 142 | 15 | 14 | 0 | 395 | 94 | 16 | 21 | 0 | 17 | 0 | 0 | 0 | 12 | 12 | 2.98 | 58 | 102 | 2 | 1125 | 143 | 0 | 6 | 18 | 98 | 214 | 0 | 0 | 0 | 580 | 13 | 44 | 0 | 250 | 290 | 250 | 51 | 0 | 211 | 0 | 0 | 91 | 171 | 17 | 11 | 106 | 162 | 52.2 | 21 | 30 | 305 | 0 | 344 | 28 | 30 | 147 | 7 | 23 | 0 | 61 | 30 | 141 | 0 | 102 | 0 | 48 | 10.05 | 48 | 0 | 0.8 | 24.38 | 0 | 7497.41 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.96 | 1150 | 0 | 0 | 0 | 1411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.37 | 105 | 0 | 0 | 19.05 | 0 | 0 | 167 | 0 | 167 | 0 | 399 | 0 | 3.36 | 0 | 43 | 0 | 5 | 0 | 0 | 0 | 0 | 4.5 | 80 | 0.65 | 16 | 300 | 126 | 65 | 0 | 478 | 1046 | 0 | 6638.89 | 14136.3 | 73.79
12:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 17 | 0 | 17 | 145 | 32 | 0 | 35 | 35 | 0 | 0 | 0 | 305 | 0 | 0 | 315 | 0 | 0 | 30 | 142 | 15 | 21 | 0 | 435 | 96 | 16 | 16 | 0 | 14 | 0 | 0 | 0 | 12 | 12 | 2.73 | 57 | 107 | 3 | 1125 | 142 | 0 | 6 | 25.5 | 101 | 213 | 0 | 0 | 0 | 585 | 19 | 56 | 0 | 250 | 290 | 250 | 51 | 0 | 208 | 0 | 11 | 89 | 170 | 17 | 11 | 107 | 176 | 52.2 | 26 | 36 | 315 | 0 | 344 | 28 | 30 | 151 | 10 | 23 | 0 | 62 | 30 | 142 | 0 | 102 | 0 | 58 | 21 | 66 | 0 | 0.5 | 24.92 | 0 | 7694.85 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.47 | 1207 | 0 | 0 | 0 | 1445 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 28.48 | 86 | 0 | 0 | 20.12 | 0 | 0 | 168 | 0 | 166 | 0 | 395 | 0 | 2.34 | 0 | 43 | 0 | 17 | 0 | 0 | 0 | 0 | 1.2 | 70 | 0.65 | 16 | 300 | 126 | 67 | 0 | 491 | 1090 | 0 | 6769.26 | 14464.11 | 73.79
13:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 17 | 0 | 17 | 148 | 32 | 0 | 35 | 54 | 0 | 0 | 0 | 305 | 0 | 0 | 295 | 0 | 0 | 29 | 142 | 15 | 21 | 0 | 365 | 96 | 16 | 18 | 0 | 24 | 0 | 0 | 0 | 12 | 12 | 1.18 | 58 | 105 | 3 | 1125 | 140 | 0 | 6 | 25.5 | 99 | 213 | 0 | 0 | 0 | 580 | 8 | 98 | 0 | 220 | 290 | 250 | 51 | 0 | 200 | 0 | 34 | 88 | 170 | 16 | 19 | 105 | 182 | 52.2 | 29 | 36 | 320 | 0 | 344 | 28 | 30 | 149 | 10 | 23 | 0 | 61 | 30 | 140 | 0 | 102 | 0 | 58 | 19.93 | 68 | 0 | 1.2 | 10.31 | 0 | 7643.32 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.96 | 1212 | 0 | 0 | 0 | 1428 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 49.59 | 97 | 0 | 0 | 39.13 | 0 | 0 | 162 | 0 | 164 | 0 | 399 | 0 | 4.07 | 0 | 43 | 90 | 7 | 0 | 0 | 0 | 0 | 1.6 | 144 | 0.51 | 16 | 303 | 124 | 66 | 0 | 479 | 1140 | 0 | 7026.86 | 14670.18 | 73.79
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 17 | 0 | 17 | 147 | 32 | 0 | 35 | 54 | 0 | 0 | 0 | 300 | 0 | 0 | 315 | 0 | 0 | 25 | 142 | 15 | 21 | 0 | 445 | 95 | 16 | 19 | 0 | 25 | 0 | 0 | 0 | 12 | 12 | 0.46 | 30 | 106 | 3 | 1125 | 140 | 0 | 6 | 25.5 | 97 | 212 | 0 | 0 | 0 | 580 | 9 | 87 | 0 | 220 | 290 | 250 | 51 | 0 | 201 | 0 | 34 | 87 | 168 | 0 | 19 | 101 | 180 | 52.2 | 60 | 27 | 310 | 0 | 296 | 28 | 30 | 145 | 10 | 25 | 0 | 62 | 30 | 142 | 0 | 100 | 9 | 58 | 17.61 | 68 | 0 | 1 | 25.74 | 0 | 7635.51 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.12 | 1215 | 0 | 0 | 0 | 1433 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 52.2 | 43.88 | 89 | 0 | 0 | 45.3 | 0 | 0 | 157 | 0 | 158 | 0 | 392 | 0 | 4.13 | 0 | 43 | 94 | 5 | 0 | 0 | 0 | 0 | 1.5 | 33 | 0.6 | 16 | 283 | 126 | 66 | 0 | 488 | 1140 | 0 | 6933.73 | 14569.24 | 73.8
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 17 | 145 | 32 | 0 | 23 | 54 | 0 | 0 | 0 | 300 | 0 | 0 | 293 | 0 | 0 | 20 | 142 | 15 | 21 | 0 | 400 | 94 | 16 | 18 | 0 | 34 | 0 | 0 | 0 | 12 | 12 | 0.62 | 30 | 104 | 2 | 1125 | 143 | 0 | 6 | 25.5 | 90 | 213 | 0 | 0 | 0 | 580 | 6 | 53 | 0 | 220 | 290 | 250 | 51 | 0 | 198 | 0 | 34 | 87 | 174 | 0 | 19 | 108 | 184 | 52.2 | 40 | 27 | 310 | 0 | 296 | 28 | 30 | 144 | 1 | 25 | 0 | 41 | 30 | 142 | 0 | 100 | 17 | 58 | 10.02 | 68 | 0 | 0.7 | 31.36 | 5 | 7467.4 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.61 | 1216 | 2 | 0 | 0 | 1416 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 52.2 | 29.48 | 70 | 0 | 0 | 26.04 | 0 | 0 | 153 | 0 | 152 | 0 | 383 | 0 | 2.01 | 0 | 43 | 94 | 7 | 0 | 0 | 0 | 0 | 1.7 | 45 | 0.22 | 16 | 262 | 126 | 66 | 0 | 467 | 1120 | 6 | 6787.26 | 14254.66 | 73.8
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 23 | 148 | 32 | 0 | 34 | 54 | 0 | 0 | 0 | 300 | 0 | 0 | 289 | 0 | 0 | 11 | 142 | 15.5 | 21 | 0 | 350 | 94 | 16 | 19 | 0 | 31 | 0 | 0 | 0 | 12 | 12 | 0.77 | 30 | 107 | 2 | 1125 | 140 | 0 | 6 | 25.5 | 98 | 214 | 0 | 0 | 0 | 580 | 4 | 20 | 0 | 210 | 290 | 250 | 51 | 0 | 195 | 0 | 34 | 87 | 177 | 0 | 19 | 107 | 186 | 52.2 | 35 | 28 | 310 | 0 | 296 | 28 | 0 | 144 | 2 | 25 | 0 | 41 | 28 | 142 | 0 | 100 | 17 | 58 | 8.7 | 68 | 0 | 0.1 | 22.1 | 12 | 7351.87 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.75 | 1219 | 17 | 0 | 0 | 1404 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 52.2 | 16.85 | 8 | 0 | 0 | 12.24 | 0 | 0 | 151 | 0 | 152 | 0 | 373 | 0 | 1.06 | 0 | 44 | 94 | 5 | 0 | 0 | 0 | 0 | 2.8 | 45 | 0.31 | 16 | 249 | 126 | 68 | 0 | 446 | 1090 | 17 | 6580.21 | 13932.08 | 73.7
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 38 | 147 | 32 | 0 | 35 | 54 | 0 | 0 | 0 | 300 | 0 | 35 | 301 | 0 | 0 | 2 | 142 | 15.5 | 21 | 0 | 390 | 94 | 16 | 16 | 0 | 22 | 0 | 0 | 0 | 12 | 12 | 0.12 | 30 | 106 | 6 | 1125 | 118 | 0 | 6 | 8 | 96 | 213 | 0 | 0 | 0 | 580 | 3 | 20 | 0 | 210 | 290 | 250 | 51 | 0 | 214 | 0 | 34 | 87 | 182 | 6 | 19 | 88 | 168 | 45 | 16 | 28 | 305 | 0 | 296 | 28 | 0 | 142 | 1 | 25 | 0 | 41 | 28 | 142 | 0 | 100 | 17 | 58 | 1.11 | 68 | 0 | 0.2 | 10.43 | 12 | 7343.36 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8 | 1195 | 17 | 0 | 0 | 1412 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 25 | 0.24 | 0 | 0 | 0 | 2.16 | 0 | 0 | 151 | 0 | 152 | 0 | 368 | 0 | 0 | 0 | 45 | 94 | 5 | 32 | 0 | 0 | 0 | 3.1 | 41 | 0.12 | 16 | 199 | 126 | 67 | 0 | 443 | 1080 | 17 | 6459.42 | 13802.78 | 73.7
18:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 17 | 0 | 52 | 130 | 32 | 0 | 35 | 54 | 0 | 0 | 0 | 295 | 0 | 35 | 297 | 0 | 0 | 0 | 142 | 15.5 | 14 | 0 | 340 | 95 | 16 | 14 | 0 | 0 | 0 | 0 | 17 | 12 | 12 | 0.09 | 30 | 105 | 9 | 1125 | 112 | 0 | 6 | 8 | 95 | 217 | 0 | 0 | 0 | 580 | 0 | 20 | 0 | 210 | 290 | 250 | 51 | 0 | 216 | 0 | 34 | 87 | 183 | 27 | 19 | 84 | 176 | 52.2 | 5 | 29 | 315 | 0 | 296 | 28 | 0 | 134 | 1 | 25 | 0 | 41 | 30 | 142 | 0 | 101 | 0 | 58 | 0.62 | 68 | 0 | 0 | 1.32 | 0 | 7336.73 | 892 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 5 | 1105 | 22 | 0 | 0 | 1301 | 0 | 40 | 0 | 35 | 35 | 0 | 40 | 5 | 25 | 0 | 0 | 7 | 0 | 1.71 | 0 | 0 | 151 | 0 | 152 | 0 | 352 | 0 | 0.15 | 0 | 45 | 115 | 2 | 33 | 0 | 0 | 0 | 0.7 | 13 | 0.02 | 16 | 196 | 126 | 67 | 0 | 419 | 1045 | 17 | 6293.58 | 13630.31 | 73.7
19:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 35.5 | 0 | 77 | 146 | 32 | 10 | 35 | 72 | 0 | 0 | 0 | 300 | 0 | 35 | 320 | 0 | 0 | 0 | 142 | 15.5 | 14 | 0 | 470 | 91 | 16 | 38 | 0 | 0 | 50 | 0 | 17 | 12 | 12 | 0 | 30 | 106 | 7 | 1125 | 132 | 0 | 6 | 14 | 97 | 217 | 0 | 0 | 0 | 580 | 0 | 20 | 0 | 210 | 290 | 250 | 51 | 0 | 214 | 0 | 51 | 89 | 184 | 27 | 19 | 105 | 192 | 52.2 | 0 | 29 | 310 | 0 | 296 | 28 | 0 | 134 | 0 | 25 | 0 | 41 | 28 | 142 | 0 | 101 | 0 | 67 | 0 | 87 | 0 | 0 | 0 | 0 | 7818.2 | 892 | 0 | 0 | 25 | 12 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1120 | 57 | 0 | 0 | 1488 | 0 | 40 | 0 | 35 | 35 | 0 | 76 | 21 | 52.2 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 155 | 0 | 158 | 0 | 398 | 0 | 0 | 0 | 45 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 1 | 0 | 16 | 217 | 126 | 67 | 0 | 500 | 1035 | 54 | 6845.2 | 14663.4 | 73.7
19:30 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 35.5 | 0 | 72 | 147 | 32 | 55 | 35 | 72 | 0 | 0 | 0 | 305 | 0 | 35 | 310 | 0 | 0 | 0 | 142 | 16 | 14 | 0 | 450 | 95 | 16 | 50 | 0 | 5 | 50 | 0 | 17 | 12 | 12 | 0 | 30 | 106 | 4 | 1125 | 150 | 0 | 6 | 25.5 | 97 | 218 | 0 | 0 | 0 | 590 | 0 | 20 | 0 | 210 | 290 | 250 | 51 | 0 | 215 | 0 | 91 | 89 | 190 | 27 | 19 | 112 | 188 | 52.2 | 0 | 29 | 315 | 0 | 296 | 28 | 0 | 146 | 0 | 25 | 0 | 41 | 28 | 142 | 0 | 101 | 0 | 67 | 0 | 87 | 0 | 0 | 0 | 0 | 7961.2 | 891 | 0 | 0 | 23 | 33 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 1193 | 70 | 0 | 0 | 1465 | 0 | 40 | 0 | 35 | 35 | 0 | 86 | 21 | 52.2 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 157 | 0 | 159 | 0 | 400 | 0 | 0 | 0 | 45 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 203 | 126 | 67 | 0 | 500 | 1150 | 54 | 7061.2 | 15022.4 | 73.7
20:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 35.5 | 0 | 70 | 146 | 32 | 55 | 35 | 72 | 0 | 0 | 0 | 308 | 0 | 35 | 293 | 0 | 0 | 0 | 142 | 16 | 14 | 0 | 370 | 97 | 16 | 57 | 0 | 11 | 50 | 0 | 25 | 12 | 12 | 0 | 30 | 107 | 7 | 1125 | 146 | 0 | 6 | 25.5 | 102 | 219 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 210 | 290 | 250 | 51 | 0 | 216 | 0 | 87 | 89 | 188 | 27 | 19 | 108 | 190 | 52.2 | 0 | 29 | 310 | 0 | 296 | 28 | 0 | 151 | 0 | 25 | 0 | 41 | 30 | 141 | 0 | 101 | 0 | 68 | 0 | 87 | 0 | 0 | 0 | 0 | 7910.2 | 892 | 0 | 0 | 23 | 58 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 1203 | 85 | 0 | 0 | 1473 | 0 | 40 | 0 | 35 | 35 | 0 | 86 | 21 | 52.2 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 158 | 0 | 159 | 0 | 386 | 0 | 0 | 0 | 45 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 197 | 126 | 67 | 0 | 500 | 1176 | 54 | 7158.2 | 15068.4 | 73.7
21:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 35.5 | 0 | 78 | 148 | 32 | 55 | 35 | 72 | 0 | 0 | 0 | 300 | 0 | 35 | 301 | 0 | 0 | 0 | 142 | 16 | 14 | 0 | 380 | 90 | 16 | 69 | 0 | 11 | 50 | 0 | 54.36 | 12 | 12 | 0 | 30 | 108 | 6 | 1125 | 143 | 0 | 6 | 25.5 | 95 | 220 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 210 | 290 | 250 | 51 | 0 | 215 | 0 | 90 | 88 | 186 | 27 | 0 | 107 | 188 | 52.2 | 0 | 29 | 300 | 0 | 296 | 28 | 0 | 129 | 0 | 25 | 0 | 41 | 28 | 142 | 0 | 100 | 0 | 68 | 0 | 87 | 0 | 0 | 0 | 0 | 7855.56 | 891 | 0 | 0 | 23 | 50 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1220 | 67 | 0 | 0 | 1474 | 0 | 32 | 0 | 35 | 35 | 0 | 86 | 21 | 52.2 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 158 | 0 | 159 | 0 | 358 | 0 | 0 | 0 | 45 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 199 | 126 | 26 | 0 | 500 | 1225 | 54 | 7127.2 | 14982.76 | 73.7
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 35.5 | 0 | 78 | 147 | 32 | 55 | 35 | 72 | 0 | 0 | 0 | 300 | 0 | 35 | 298 | 0 | 0 | 0 | 142 | 15.5 | 21 | 0 | 340 | 77 | 16 | 70 | 0 | 11 | 50 | 0 | 54.36 | 12 | 12 | 0 | 30 | 106 | 10 | 1125 | 142 | 0 | 6 | 17 | 97 | 220 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 215 | 290 | 250 | 51 | 0 | 212 | 0 | 72 | 92 | 183 | 27 | 5 | 107 | 184 | 52.2 | 0 | 29 | 310 | 0 | 296 | 28 | 0 | 134 | 0 | 25 | 0 | 41 | 30 | 141 | 0 | 100 | 0 | 68 | 0 | 87 | 0 | 0 | 0 | 0 | 7740.56 | 892 | 0 | 0 | 24 | 46 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1220 | 67 | 0 | 0 | 1487 | 0 | 32 | 0 | 35 | 35 | 0 | 86 | 21 | 52.2 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 159 | 0 | 159 | 0 | 352 | 0 | 0 | 0 | 45 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 199 | 126 | 31 | 0 | 500 | 1230 | 54 | 7143.2 | 14883.76 | 73.7
23:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 35.5 | 0 | 36 | 147 | 32 | 55 | 35 | 35 | 0 | 0 | 0 | 305 | 0 | 35 | 302 | 0 | 0 | 0 | 142 | 15.5 | 21 | 0 | 435 | 70 | 16 | 65 | 0 | 30 | 50 | 0 | 54.36 | 12 | 12 | 0 | 30 | 107 | 16 | 1125 | 145 | 0 | 6 | 17 | 97 | 219 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 220 | 290 | 220 | 51 | 0 | 218 | 0 | 70 | 92 | 181 | 0 | 0 | 108 | 184 | 52.2 | 0 | 29 | 315 | 0 | 296 | 28 | 0 | 142 | 0 | 25 | 0 | 41 | 28 | 142 | 0 | 100 | 0 | 68 | 0 | 87 | 0 | 0 | 0 | 0 | 7732.56 | 892 | 0 | 0 | 24 | 47 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1222 | 67 | 0 | 0 | 1494 | 0 | 32 | 0 | 35 | 35 | 0 | 86 | 15 | 52.2 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 163 | 0 | 160 | 0 | 376 | 0 | 0 | 0 | 45 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 199 | 126 | 31 | 0 | 500 | 1220 | 35 | 7127.2 | 14859.76 | 73.7
Total KWH | 0 | 674880 | 305280 | 0 | 0 | 0 | 0 | 0 | 8629200 | 0 | 0 | 259920 | 50040 | 757440 | 3468960 | 676451 | 287905 | 531969 | 806400 | 0 | 0 | 0 | 7600909 | 0 | 270423 | 7278249 | 0 | 0 | 204786 | 3280800 | 341400 | 469440 | 0 | 9468636.36 | 1839164 | 306109 | 792000 | 0 | 456960 | 336372 | 0 | 487590 | 295680 | 293760 | 21121 | 1079258 | 2432100 | 261120 | 27025454.55 | 2437164 | 0 | 152160 | 387997.2 | 2256509 | 4805665 | 0 | 0 | 0 | 13832726 | 97335 | 1217745 | 0 | 5559000 | 7329300 | 5798000 | 1260920 | 0 | 5171000 | 0 | 706560 | 2121310 | 3265920 | 208320 | 345780 | 1861620 | 4009920 | 1107754 | 318445 | 521712 | 7508000 | 0 | 7892000 | 671000 | 462600 | 3449372.73 | 59921 | 562416 | 0 | 1289280 | 701760 | 3256000 | 0 | 2430170 | 71280 | 1326000 | 111362 | 1476000 | 0 | 7950 | 218840 | 35040 | 177291630.84 | 21948364 | 0 | 0 | 170880 | 211968 | 0 | 0 | 0 | 0 | 0 | 855936 | 683280 | 28530910 | 707040 | 0 | 0 | 33790909 | 0 | 356042 | 0 | 575424 | 690432 | 0 | 504720 | 164133 | 576773 | 323728 | 635090 | 203339 | 0 | 246368 | 0 | 0 | 3990600 | 0 | 4033036 | 0 | 9158181 | 0 | 15840 | 0 | 1013672 | 1694.21 | 81442 | 281491 | 0 | 0 | 0 | 34556.16 | 568800 | 4737 | 401856 | 5979000 | 3020000 | 1451650 | 0 | 11330909 | 28273454.55 | 430800 | 161247054.92 | 338538685.76

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 11-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14464.11 | MW | 12:00 Hr. | Energy Generated |  |  | 338.5387 |  | MKWHr.
| Day Peak Demand |  |  | 14684.11 | MW | 12:00 Hr. | Energy Unserverd |  |  | 5.09 |  | MKWHr.
| Evening Peak Generation |  |  | 15068.4 | MW | 20:00 Hr. | Energy Demand |  |  | 343.6287 |  | MKWHr.
| Evening Peak Demand |  |  | 15556.4 | MW | 20:00 Hr. | Maximum Temperature |  |  | 35.1 |  | °C
| Minimum Generation of the Day |  |  | 12720.04 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 855.5 |  | MMCFD
| Maximum Generation of the Day |  |  | 15068.4 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.836 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.7878 | 0 | 11.3705 | 0 | 0 | 0.20479 | 0 | 0 | 45.3631 | Gas | 116.316 | Gas | 403360155.8528
| Chattogram Zone |  |  | 5.0668 | 40.8582 | 12.0166 | 0 | 1.0793 | 0.11846 | 0 | 0.45696 | 59.5962 | Coal | 115.9861 | Coal | 773494102.994
| Cumilla Zone |  |  | 27.5853 | 0 | 8.8896 | 0 | 0 | 0.31844 | 4.0099 | 0 | 40.8033 | HFO | 41.3176 | HFO | 725844252.3877
| Mymensingh Zone |  |  | 0 | 0 | 2.9083 | 0 | 0 | 0.33815 | 0 | 0 | 3.2465 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.2226 | 0 | 0 | 0 | 0 | 0.059921 | 0 | 0 | 28.2825 | Hydro | 1.0793 | Hydro | 107925.8
| Khulna Zone |  |  | 0 | 28.5309 | 1.9458 | 0 | 0 | 0.68328 | 21.9484 | 0 | 53.1084 | Solar | 3.6336 | Solar | 55763989.9932
| Barishal Zone |  |  | 4.4717 | 45.5834 | 0.83266 | 0 | 0 | 0.004737 | 0 | 0 | 50.8924 | Import | 59.7492 | Import | 348951457.88
| Rajshahi Zone |  |  | 17.1818 | 0 | 3.0709 | 0 | 0 | 1.221 | 33.7909 | 0 | 55.2646 | Wind | 0.45696 | Wind | 6721881.6
| Rangpur Zone |  |  | 0 | 1.0137 | 0.28319 | 0 | 0 | 0.6848 | 0 | 0 | 1.9817
| Total |  |  | 116.316 | 115.9861 | 41.3176 | 0 | 1.0793 | 3.6336 | 59.7492 | 0.45696 | 338.5387
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 403360155.8528 |  | Hydro | 107925.8
|  |  |  | Coal | 773494102.994 |  | Solar | 55763989.9932
|  |  |  | HFO | 725844252.3877 |  | Import | 348951457.88
|  |  |  | HSD | 0 |  | Wind | 6721881.6
[5 empty] | Total: | 231,42,43,766 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9484 | Peak Hr Flow | 892.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 54915818.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.7909 | Peak Hr Flow | 1473.00 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2469 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 4.0099 | Peak Hr Flow | 190.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2979 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 59.7492 | Peak Hr Flow | 2555.00 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 172 |  | 5535
|  |  |  | Chattogram |  | 0 |  | 1491
|  |  |  | Cumilla |  | 0 |  | 1550
|  |  |  | Mymensingh |  | 295 |  | 1305
|  |  |  | Sylhet |  | 0 |  | 653
|  |  |  | Khulna |  | 0 |  | 1587
|  |  |  | Barishal |  | 0 |  | 500
|  |  |  | Rajshahi |  | 0 |  | 1391
|  |  |  | Rangpur |  | 0 |  | 937
|  |  |  | Total |  | 467 |  | 14949
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhola Nutan Biddut BD LTD ST |  |  | 67
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 117
|  |  |  | Total Unavailable Capacity |  |  |  | 417
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:26 | Chandpur 132/33kV S/S 33 kV T-1 Section is restored.
|  | 08:28 | Chandpur 132/33kV S/S 402T (T-01) HT is restored.
|  | 08:28 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
| 08:30 |  | Chandpur 132/33kV S/S 422T(T-5) LT Scheduled S/D Due to OLTC oil centrifuging
| 09:12 | 12:52 | Ishurdi 230/132kV S/S 230 kV Bus 1 Scheduled S/D Due to loop jumper connection of
Transformer T-03 with bus-1
| 09:55 | 12:00 | Muktagacha 132/33kV S/S RPCL-2 Project Work S/D
|  | 11:07 | Ashuganj-Kishoreganj 132kV Ckt-1 is restored.
| 12:32 | 13:35 | Kodda 132/33kV S/S Tr-1 (406T) HT Scheduled S/D Due to 33 kV Section 01 maintenance by | [7 empty] | 30.0MW load
|  |  | PBS | [7 empty] | interrup.
| 12:33 | 13:35 | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D Due to 33kV section 01 maintenance by PBS | [7 empty] | 30.0MW load
interrup.
| 12:37 | 13:55 | Mymensingh RPCL -Mymensingh 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end Due
to Maintenance work RPCL end.
| 12:40 | 13:31 | Daganbhuiyan 132/33kV S/S Transformer-2 LT Forced S/D Due to Tr-02 33 kv load side Earth
Resistence test
| 12:41 | 13:31 | Daganbhuiyan 132/33kV S/S Transformer-2 HT Forced S/D Due to Tr-02 33 kv Load side Earth
Resistence test
| 14:06 | 16:13 | Rajbari 132/33kV S/S Transformer-3 LT Tripped showing 86.1& 86.2 relays Due to WTI TRIP | [7 empty] | 19.0MW load
interrup.
| 14:06 | 16:07 | Rajbari 132/33kV S/S Transformer-3 HT Tripped showing 86.1&2, 86.3&4 relays Due to WTI | [7 empty] | 19.0MW load
|  |  | TRIP | [7 empty] | interrup.
| 15:36 |  | Faridpur-Rajbari ckt-2 is restored
| 16:20 | 18:37 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Tripped showing 86T Lockout Relay. relays
Due to 33 kV LA Blast (R- Phase)
| 16:20 | 18:38 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Tripped showing O/C & E/F Relay relays Due
to 33 kV LA Blast (R- Phase)
| 16:30 | 18:38 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Forced S/D Due to 33 kV LA Replacement
work.
| 16:30 | 18:37 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Forced S/D Due to 33 kV LA Replacement
work.
|  | 18:06 | Shahjibazar 132/33kV S/S TR-06 HT is restored.
| 18:56 |  | Tangail 132/33kV S/S Tr-2 HT Tripped showing K50,86X relays Due to 132 Kv LA Blast. | [7 empty] | 30.0MW load
interrup.
|  | 19:53 | Chowmuhani 230/132/33kV S/S Maijdee-02 is restored.
|  | 19:54 | Maijdee 132/33kV S/S Chowmuhoni-Maijdee ckt -02 is restored.
| 20:00 |  | Evening Peak Generation: 15068 MW.
| 21:43 | 22:05 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to 33 kv cb y phase redhot | [7 empty] | 15.0MW load
interrup.
| 21:44 | 22:04 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to 33 kv cb y phase redhot | [7 empty] | 15.0MW load
interrup.
| 21:59 | 23:27 | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to 33kv bus-1 redhot maintanace | [7 empty] | 35.0MW load
|  |  | work by Md.Abdul Rohim (junior Engineer feni pbs) | [7 empty] | interrup.
| 21:59 | 23:27 | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to 33kv bus-1 redhot maintanace | [7 empty] | 35.0MW load
|  |  | work by Md.Abdul Rohim (junior Engineer feni pbs). | [7 empty] | interrup.
| 22:02 |  | Tangail 132/33kV S/S Tr-2 HT Forced S/D Due to LA Replacement Work
| 22:02 |  | Tangail 132/33kV S/S Tr-2 LT Forced S/D Due to LA Replacement Work
| 00:36 |  | Bhola Notun Bidyut CCPP ST was synchronized.
| 01:51 |  | Bhola 225 MW CCPP GT-1 was shutdown due to maintenance purpose.
| 02:34 |  | Haripur 412 MW CCPP Shutdown with remarks:- ST
| 02:41 |  | Haripur 412 MW CCPP Shutdown with remarks:- GT
| 03:09 |  | Siddhirganj 2*120 MW GT-2 was synchronized.
| 06:35 |  | Chandraghona 132/33kV S/S TR-01(406T) LT Scheduled S/D Due to 33 kv bus loop change | [7 empty] | 27.0MW load
interrup.
| 06:36 |  | Chandraghona 132/33kV S/S TR-01(406T) HT Scheduled S/D | [7 empty] | 27.0MW load
interrup.
| 07:00 |  | Minimum generation 12404 MW.
| 07:15 |  | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Muktagacha 132/33kV end Due to
S/D taken by RPCL
| 07:43 |  | Daganbhuiyan 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Tr-02 33 KV load side PT
change & loop jumpering
| 07:44 |  | Daganbhuiyan 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Tr-02 33 KV load side PT
change & loop jumpering.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 385 | 8629200 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 287905 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 293 | 7278249 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35.5 | 259920 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 146 | 3468960 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 531969 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270423 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16 | 341400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 469440 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 305280 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 32 | 676451 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 70 | 757440 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 674880 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 806400 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 204786 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 50040 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 370 | 9468636.36 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 308 | 7600909 | AGC+Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3280800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2146.5 | 45363088.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 387997.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 97335 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 152160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 1079258 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 4805665 | Machine Problem
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 102 | 2256509 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 336372 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 295680 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 7 | 261120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 57 | 792000 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21121 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 306109 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 25 | 487590 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 107 | 2432100 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 293760 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 97 | 1839164 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 146 | 2437164 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13832726 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 11 | 456960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 27025454.55 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 2659.5 | 59596244.75
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 216 | 5171000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7329300 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 250 | 5798000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 210 | 5559000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1260920 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 20 | 1217745 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 521712 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 89 | 2121310 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 188 | 3265920 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 190 | 4009920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1107754 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 345780 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 108 | 1861620 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 208320 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 87 | 706560 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 318445 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1826.2 | 40803306
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 111362 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1476000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1326000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 218840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 35040 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 71280 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 155 | 3246472
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 59921 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 671000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 462600 | Plant availability less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3449372.73 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 141 | 3256000 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 701760 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 41 | 1289280 | one engine under maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2430170 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 25 | 562416 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7508000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 296 | 7892000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1123 | 28282519.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 892 | 21948364 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 23 | 170880 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 58 | 211968 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 85 | 707040 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 101 | 855936 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 683280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1203 | 28530910 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2362 | 53108378
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 500 | 11330909 | AGC, Unit1 Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 401856 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 126 | 3020000 | STG Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1176 | 28273454.55 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 67 | 1451650 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 430800 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 197 | 5979000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4737 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2136 | 50892406.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 323728 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 356042 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 164133 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 158 | 3990600 | Gas Restrction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 159 | 4033036 | Gas Restrction
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 386 | 9158181 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 203339 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 576773 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 504720 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 690432 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 575424 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 15840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1473 | 33790909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 246368 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 635090 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2466.2 | 55264615
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 45 | 1013672 | Plant availability zero, U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 281491 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34556.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1694.21 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 81442 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 568800 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 194 | 1981655.37
Eastern Grid Total |  |  |  |  | 17438.042 | 7910.2 | 177291630.84
Western Grid Total |  |  |  |  | 11852.195 | 7158.2 | 161247054.92
National Grid Total |  |  |  |  | 29290.237 | 15068.4 | 338538685.76
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-06-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10123.08 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4415.1 | MW
i) Dhaka area |  |  | 5363.38 |  | MW | i) Khulna area |  |  |  | 1586.6 | MW
ii) Chattogram area |  |  | 1546.7 |  | MW | ii) Barishal area |  |  |  | 500.5 | MW
iii) Cumilla area |  |  | 1550 |  | MW | iii) Rajshahi area |  |  |  | 1391 | MW
iv) Mymensingh area |  |  | 1010 |  | MW | iv) Rangpur area |  |  |  | 937 | MW
v) Sylhet area |  |  | 653 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14538.18 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 87 | 19:00 | 133 | Natore | 146 | 00:00
2 | AKSML | 152.7 | 14:00 | 68 | Hathazari | 92 | 19:00 | 134 | Nawabganj | 58.3 | 23:00
3 | Aftabnagar | 44 | 13:00 | 69 | Hatirjheel | 49 | 13:00 | 135 | Netrakona | 126 | 00:00
4 | Agargaon | 133 | 13:00 | 70 | Ishurdi | 79 | 13:00 | 136 | New | 86 | 12:00
5 | Agrabad | 80 | 14:00 | 71 | Jaldhaka | 79 | 00:00 | 137 | Niamatpur | 74 | 00:00
6 | Amnura | 30 | 00:00 | 72 | Jamalpur | 102 | 23:00 | 138 | Noapara | 59 | 13:00
7 | Ashuganj | 88 | 19:00 | 73 | Jashore | 139 | 14:00 | 139 | PHP | 14 | 13:00
8 | BSRM | 187 | 10:00 | 74 | Jhenaidah | 106 | 14:00 | 140 | Pabna | 100 | 15:00
9 | Bagerhat | 98 | 19:30 | 75 | Joydebpur | 142 | 09:00 | 141 | Palashbari | 118 | 20:00
10 | Bajitpur | 82 | 12:00 | 76 | Joypurhat | 65 | 00:00 | 142 | Panchagarh | 59 | 00:00
11 | Bakerganj | 17 | 22:00 | 77 | Juldah | 19 | 12:00 | 143 | Patiya | 12 | 00:00
12 | Bakulia | 101 | 15:00 | 78 | KSRM | 18 | 10:00 | 144 | Patuakhali | 82.5 | 23:00
13 | Banani | 60 | 13:00 | 79 | Kabirpur | 255 | 11:00 | 145 | Payra | 40 | 22:00
14 | Bangabhaban | 21 | 10:00 | 80 | Kachua | 108 | 22:00 | 146 | Postogola | 62 | 13:00
15 | Barapukuria | 61 | 01:00 | 81 | Kaliganj | 16 | 18:00 | 147 | Pubail | 32 | 13:00
16 | Barguna | 26 | 22:00 | 82 | Kallyanpur | 114 | 00:00 | 148 | Purbachal | 37 | 13:00
17 | Barishal | 120 | 13:00 | 83 | Kalurghat | 40 | 09:00 | 149 | Purbasadipur | 142 | 00:00
18 | Barishal-230 | 110 | 19:30 | 84 | Kamrangirchar | 77 | 13:00 | 150 | Rahanpur | 39 | 00:00
19 | Baroaulia | 62 | 15:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 33 | 22:00
20 | Baroirhat | 76 | 23:00 | 86 | Kasba | 37 | 20:00 | 152 | Rajbari | 77 | 00:00
21 | Bashundhara | 205 | 13:00 | 87 | Kazla | 116 | 13:00 | 153 | Rajendrapur | 113 | 19:00
22 | BashundharaCement | 12 | 14:00 | 88 | Keranigonj | 81 | 19:00 | 154 | Rajshahi | 107 | 00:00
23 | Beanibazar | 82 | 19:00 | 89 | Khagrachori | 36 | 19:00 | 155 | Rajshahi-230 | 84 | 00:00
24 | Benapole | 68 | 15:00 | 90 | Khulna | 69 | 13:00 | 156 | Ramganj | 122 | 19:00
25 | Bhaluka | 164 | 21:00 | 91 | Khulshi | 200 | 15:00 | 157 | Rampur | 44 | 00:00
26 | Bhandaria | 65 | 22:00 | 92 | Kishoreganj | 144 | 23:00 | 158 | Rangamati | 19 | 19:00
27 | Bhangura | 36 | 13:00 | 93 | Kodda | 324 | 18:00 | 159 | Rangpur | 130 | 00:00
28 | Bheramara(GK) | 59 | 13:00 | 94 | Kulaura | 57 | 19:30 | 160 | Ruppur | 4.2 | 10:00
29 | Bhulta | 221 | 18:00 | 95 | Kurigram | 68 | 19:30 | 161 | SSM | 4 | 02:00
30 | Bog-Sherpur | 76 | 20:00 | 96 | Kushtia | 155 | 13:00 | 162 | Saidpur | 96 | 00:00
31 | Bogura | 162 | 22:00 | 97 | Laksam | 37 | 00:00 | 163 | Santhia | 34 | 21:00
32 | Borhanuddin | 91 | 21:00 | 98 | Lakshmipur | 48 | 22:00 | 164 | Satkhira | 142 | 19:30
33 | Brahmanbaria | 129 | 19:30 | 99 | Lalbag | 76 | 13:00 | 165 | Satmasjid | 110 | 13:00
34 | Cantonment | 142 | 13:00 | 100 | Lalmonirhat | 62 | 00:00 | 166 | Savar | 218 | 17:00
35 | Chandina | 20 | 11:00 | 101 | MI_Cement | 15.2 | 10:00 | 167 | SevenRings | 15.8 | 16:00
36 | Chandpur | 96 | 19:30 | 102 | Madanganj | 42 | 16:00 | 168 | ShahCement | 42 | 02:00
37 | Chandraghona | 35 | 19:30 | 103 | Madaripur | 117 | 00:00 | 169 | Shahjadpur | 76 | 12:00
38 | Chapai | 71 | 00:00 | 104 | Madartek | 78 | 19:00 | 170 | Shahjibazar | 125 | 21:00
39 | Charsaidpur | 42 | 09:00 | 105 | Madunaghat | 62 | 15:00 | 171 | Shahmirpur | 67 | 01:00
40 | Chauddagram | 81 | 00:00 | 106 | Magura | 61 | 14:00 | 172 | Shariatpur | 99 | 19:00
41 | Chhatak | 40 | 23:00 | 107 | Mahasthangarh | 76 | 00:00 | 173 | Sherpur | 142 | 21:00
42 | Chowmuhani | 181 | 20:00 | 108 | Maijdee | 45 | 23:00 | 174 | Shikalbaha | 36 | 01:00
43 | Chuadanga | 114 | 13:00 | 109 | Manikganj | 126 | 19:00 | 175 | Shitalakhya | 87.5 | 16:00
44 | Coxsbazar | 157 | 19:00 | 110 | Maniknagar | 76 | 13:00 | 176 | Sholosohor | 48 | 16:00
45 | Cumilla(N) | 124 | 19:00 | 111 | Matarbari | 57 | 00:00 | 177 | Shomvuganj | 16 | 22:00
46 | Cumilla(S) | 193 | 19:00 | 112 | Matuail | 88 | 12:00 | 178 | Shyampur | 200 | 01:00
47 | Daganbhuiyan | 19 | 22:00 | 113 | Metrorail_Motijheel | 24 | 10:00 | 179 | Siddhirganj | 132 | 15:00
48 | Daudkandi | 124 | 20:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 96 | 20:00
49 | DhakaUniversity | 94 | 13:00 | 115 | Millgate | 104 | 11:00 | 181 | Sonargaon | 139 | 00:00
50 | Dhamrai | 112 | 17:00 | 116 | Mirpur | 147 | 13:00 | 182 | Sreemongol | 88 | 21:00
51 | Dhanmondi | 129 | 13:00 | 117 | Mirsorai | 39 | 12:00 | 183 | Sreepur | 120 | 18:00
52 | Dohazari | 108 | 00:00 | 118 | Mirzapur | 43 | 18:30 | 184 | Srinagar | 50.6 | 19:00
53 | Faridpur | 167 | 00:00 | 119 | Mithapukur | 64 | 19:30 | 185 | Sunamganj | 62 | 22:00
54 | Fatullah | 95 | 16:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 115 | 19:00
55 | Fenchuganj | 46 | 23:00 | 121 | Mogbazar | 96.8 | 14:00 | 187 | Sylhet_(South) | 77 | 21:00
56 | Feni | 114 | 20:00 | 122 | Mongla | 42 | 10:00 | 188 | TK | 26 | 19:00
57 | GPH | 70 | 06:00 | 123 | Motijheel | 51 | 12:00 | 189 | Tangail | 150 | 16:00
58 | Ghatail | 99 | 19:30 | 124 | Muktagacha | 42 | 19:30 | 190 | Taraganj | 24 | 00:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 123 | 19:00 | 191 | Tasnim | 31 | 18:00
60 | Ghorashal-230 | 106 | 19:00 | 126 | Muradnagar | 53 | 19:30 | 192 | Thakurgaon | 111 | 00:00
61 | Goalpara | 39 | 13:00 | 127 | Mymensingh | 181 | 21:00 | 193 | Tongi | 159 | 11:00
62 | Gollamari | 106 | 12:00 | 128 | Nabinagar | 92 | 18:00 | 194 | Ullahpara | 38 | 19:30
63 | Gopalganj | 101 | 00:00 | 129 | Naogaon | 139 | 00:00 | 195 | Ullon | 54 | 19:00
64 | Gulshan | 142 | 13:00 | 130 | Narail | 57 | 14:00 | 196 | Uttara | 103 | 13:00
65 | Halishahar | 100 | 11:00 | 131 | Narinda | 74 | 13:00 | 197 | UttaraNew | 52 | 13:00
66 | HaripurSBU | 143 | 10:00 | 132 | Narshingdi | 183 | 21:00 | 198 | Zigatola | 84 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14944.4 | 218 |  | 15172.21
1:00 | 14581.76 | 167 |  | 14756.76
2:00 | 14185.56 | 167 |  | 14360.56
3:00 | 13762.7 | 157 |  | 13926.7
4:00 | 13360.7 | 148 |  | 13515.7
5:00 | 13051.7 | 128 |  | 13185.7
6:00 | 12772.43 | 136 |  | 12914.55
7:00 | 12720.04 | 118 |  | 12843.04
8:00 | 12959.3 | 118 |  | 13082.3
9:00 | 13285.52 | 113 |  | 13403.61
10:00 | 13802.22 | 198 |  | 14009.22
11:00 | 14136.3 | 163 |  | 14306.3
12:00 | 14464.11 | 211 |  | 14684.11
13:00 | 14670.18 | 385 |  | 15072.51
14:00 | 14569.24 | 392 |  | 14978.88
15:00 | 14254.66 | 576 |  | 14856.66
16:00 | 13932.08 | 433 |  | 14384.08
17:00 | 13802.78 | 99 |  | 13905.78
18:00 | 13630.31 | 41 |  | 13673.31
19:00 | 14663.4 | 167 |  | 14838.4
19:30 | 15022.4 | 450 |  | 15492.4
20:00 | 15068.4 | 467 |  | 15556.4
21:00 | 14982.76 | 170 |  | 15160.41
22:00 | 14883.76 | 170 |  | 15061.76
23:00 | 14859.76 | 148 |  | 15014.76
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7702.2 | 7242.2 | 14944.4 | DAILY GENERATION CURVE
00:30 | 7641.38 | 7121.7 | 14763.08
01:00 | 7580.56 | 7001.2 | 14581.76 | 11-06-2026
01:30 | 7491.06 | 6892.6 | 14383.66
02:00 | 7401.56 | 6784 | 14185.56
02:30 | 7212.63 | 6761.5 | 13974.13
03:00 | 7023.7 | 6739 | 13762.7
03:30 | 6954.2 | 6607.5 | 13561.7
04:00 | 6884.7 | 6476 | 13360.7
04:30 | 6821.7 | 6384.5 | 13206.2
05:00 | 6758.7 | 6293 | 13051.7
05:30 | 6628.005 | 6284.06 | 12912.065
06:00 | 6497.31 | 6275.12 | 12772.43
06:30 | 6470.67 | 6275.565 | 12746.235
07:00 | 6444.03 | 6276.01 | 12720.04
07:30 | 6486.81 | 6352.86 | 12839.67
08:00 | 6529.59 | 6429.71 | 12959.3
08:30 | 6635.485 | 6486.925 | 13122.41
09:00 | 6741.38 | 6544.14 | 13285.52
09:30 | 6991.72 | 6552.15 | 13543.87
10:00 | 7242.06 | 6560.16 | 13802.22
10:30 | 7369.735 | 6599.525 | 13969.26
11:00 | 7497.41 | 6638.89 | 14136.3
11:30 | 7596.13 | 6704.075 | 14300.205
12:00 | 7694.85 | 6769.26 | 14464.11
12:30 | 7669.085 | 6898.06 | 14567.145
13:00 | 7643.32 | 7026.86 | 14670.18
13:30 | 7639.415 | 6980.295 | 14619.71
14:00 | 7635.51 | 6933.73 | 14569.24
14:30 | 7551.455 | 6860.495 | 14411.95
15:00 | 7467.4 | 6787.26 | 14254.66
15:30 | 7409.635 | 6683.735 | 14093.37
16:00 | 7351.87 | 6580.21 | 13932.08
16:30 | 7347.615 | 6519.815 | 13867.43
17:00 | 7343.36 | 6459.42 | 13802.78
17:30 | 7340.045 | 6376.5 | 13716.545
18:00 | 7336.73 | 6293.58 | 13630.31
18:30 | 7577.465 | 6569.39 | 14146.855
19:00 | 7818.2 | 6845.2 | 14663.4
19:30 | 7961.2 | 7061.2 | 15022.4
20:00 | 7910.2 | 7158.2 | 15068.4
20:30 | 7882.88 | 7142.7 | 15025.58 |  | Executive Engineer
21:00 | 7855.56 | 7127.2 | 14982.76 |  | Network Operation Division
21:30 | 7798.06 | 7135.2 | 14933.26
22:00 | 7740.56 | 7143.2 | 14883.76
22:30 | 7736.56 | 7135.2 | 14871.76
23:00 | 7732.56 | 7127.2 | 14859.76

## En-Curve
QF-LDC-12
Date | 11-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3399 | 1481.5 | 928 | 0 | 168 | 1449 | 58 | 5047 | 0 | 663 | 1733.9 | 0 | 0 | 17 | 218 | DAILY ENERGY CURVE
00:30 | 3390 | 1457.5 | 928 | 0 | 165 | 1444.5 | 58.5 | 5021 | 0 | 620.5 | 1660.58 | 0 | 0 | 17.5 | 192.5 | 11-06-2026
01:00 | 3381 | 1433.5 | 928 | 0 | 162 | 1440 | 59 | 4995 | 0 | 578 | 1587.26 | 0 | 0 | 18 | 167
01:30 | 3369 | 1423.5 | 928 | 0 | 161 | 1412 | 59 | 4923.5 | 0 | 553 | 1524.66 | 0 | 0 | 30 | 167 | Energy Generated | 338.5387 |  | MKWHr
02:00 | 3357 | 1413.5 | 928 | 0 | 160 | 1384 | 59 | 4852 | 0 | 528 | 1462.06 | 0 | 0 | 42 | 167 | Energy not Served | 5.09 |  | MKWHr
02:30 | 3353.5 | 1412.5 | 929 | 0 | 156 | 1362.5 | 59 | 4830 | 0 | 524.5 | 1320.13 | 0 | 0 | 27 | 162 | Total Energy Requirement | 343.6287 |  | MKWHr
03:00 | 3350 | 1411.5 | 930 | 0 | 152 | 1341 | 59 | 4808 | 0 | 521 | 1178.2 | 0 | 0 | 12 | 157
03:30 | 3352 | 1427.5 | 930 | 0 | 152 | 1320 | 59 | 4826 | 0 | 398.5 | 1082.7 | 0 | 0 | 14 | 152.5
04:00 | 3354 | 1443.5 | 930 | 0 | 152 | 1299 | 59 | 4844 | 0 | 276 | 987.2 | 0 | 0 | 16 | 148
04:30 | 3343.5 | 1419.5 | 925 | 0 | 146 | 1281.5 | 59 | 4823.5 | 0 | 276 | 916.2 | 0 | 0 | 16 | 138
05:00 | 3333 | 1395.5 | 920 | 0 | 140 | 1264 | 59 | 4803 | 0 | 276 | 845.2 | 0 | 0 | 16 | 128
05:30 | 3354.5 | 1409 | 920 | 0 | 140 | 1269 | 59 | 4811 | 10.965 | 277.5 | 645.1 | 0 | 0 | 16 | 132
06:00 | 3376 | 1422.5 | 920 | 0 | 140 | 1274 | 59 | 4819 | 21.93 | 279 | 445 | 0 | 0 | 16 | 136
06:30 | 3396.5 | 1450.5 | 920 | 0 | 140 | 1308 | 59 | 4728 | 60.735 | 279 | 382 | 0 | 0 | 22.5 | 127
07:00 | 3417 | 1478.5 | 920 | 0 | 140 | 1342 | 59 | 4637 | 99.54 | 279 | 319 | 0 | 0 | 29 | 118
07:30 | 3432 | 1484.5 | 920 | 0 | 143 | 1384 | 59.5 | 4643.5 | 152.67 | 279 | 319 | 0 | 0 | 22.5 | 118
08:00 | 3447 | 1490.5 | 920 | 0 | 146 | 1426 | 60 | 4650 | 205.8 | 279 | 319 | 0 | 0 | 16 | 118
08:30 | 3440 | 1494 | 919.5 | 0 | 150 | 1431.5 | 60 | 4707.5 | 229.91 | 285 | 394 | 0 | 0 | 11 | 115.5
09:00 | 3433 | 1497.5 | 919 | 0 | 154 | 1437 | 60 | 4765 | 254.02 | 291 | 469 | 0 | 0 | 6 | 113
09:30 | 3453 | 1444.5 | 919.5 | 0 | 162 | 1416 | 59 | 4745 | 337.27 | 304 | 693.6 | 0 | 0 | 10 | 155.5
10:00 | 3473 | 1391.5 | 920 | 0 | 170 | 1395 | 58 | 4725 | 420.52 | 317 | 918.2 | 0 | 0 | 14 | 198
10:30 | 3494 | 1397.75 | 920 | 0 | 166 | 1403 | 58 | 4723.5 | 439.81 | 321.5 | 1030.2 | 0 | 0 | 15.5 | 180.5
11:00 | 3515 | 1404 | 920 | 0 | 162 | 1411 | 58 | 4722 | 459.1 | 326 | 1142.2 | 0 | 0 | 17 | 163
11:30 | 3522 | 1431.5 | 920 | 0 | 169 | 1428 | 57.5 | 4781.5 | 457.755 | 328.5 | 1188.95 | 0 | 0 | 15.5 | 187
12:00 | 3529 | 1459 | 920 | 0 | 176 | 1445 | 57 | 4841 | 456.41 | 331 | 1235.7 | 0 | 0 | 14 | 211
12:30 | 3496 | 1428.5 | 906 | 0 | 179 | 1436.5 | 57.5 | 4861.5 | 501.945 | 332.5 | 1348.7 | 0 | 0 | 19 | 298
13:00 | 3463 | 1398 | 892 | 0 | 182 | 1428 | 58 | 4882 | 547.48 | 334 | 1461.7 | 0 | 0 | 24 | 385
13:30 | 3435 | 1430 | 892 | 0 | 181 | 1430.5 | 44 | 4878 | 502.41 | 325 | 1477.3 | 0 | 0 | 24.5 | 388.5
14:00 | 3407 | 1462 | 892 | 0 | 180 | 1433 | 30 | 4874 | 457.34 | 316 | 1492.9 | 0 | 0 | 25 | 392
14:30 | 3384 | 1428 | 891.5 | 0 | 182 | 1424.5 | 30 | 4843.5 | 409.55 | 315 | 1474.4 | 0 | 0 | 29.5 | 484
15:00 | 3361 | 1394 | 891 | 0 | 184 | 1416 | 30 | 4813 | 361.76 | 314 | 1455.9 | 0 | 0 | 34 | 576
15:30 | 3332.5 | 1370.25 | 891 | 0 | 185 | 1410 | 30 | 4783 | 273.22 | 316 | 1469.9 | 0 | 0 | 32.5 | 504.5
16:00 | 3304 | 1346.5 | 891 | 0 | 186 | 1404 | 30 | 4753 | 184.68 | 318 | 1483.9 | 0 | 0 | 31 | 433
16:30 | 3314 | 1364.5 | 891 | 0 | 177 | 1408 | 30 | 4710 | 138.98 | 326 | 1481.45 | 0 | 0 | 26.5 | 266
17:00 | 3324 | 1382.5 | 891 | 0 | 168 | 1412 | 30 | 4667 | 93.28 | 334 | 1479 | 0 | 0 | 22 | 99
17:30 | 3304 | 1354 | 891.5 | 0 | 172 | 1356.5 | 30 | 4591 | 61.945 | 434.5 | 1510.1 | 0 | 0 | 11 | 70
18:00 | 3284 | 1325.5 | 892 | 0 | 176 | 1301 | 30 | 4515 | 30.61 | 535 | 1541.2 | 0 | 0 | 0 | 41
18:30 | 3345 | 1389.5 | 892 | 0 | 184 | 1394.5 | 30 | 4568.5 | 15.805 | 642.5 | 1685.05 | 0 | 0 | 0 | 104
19:00 | 3406 | 1453.5 | 892 | 0 | 192 | 1488 | 30 | 4622 | 1 | 750 | 1828.9 | 0 | 0 | 0 | 167
19:30 | 3404 | 1453 | 891 | 0 | 188 | 1465 | 30 | 4806 | 0 | 800 | 1980.4 | 0 | 0 | 5 | 450
20:00 | 3377 | 1379 | 892 | 0 | 190 | 1473 | 30 | 4858 | 0 | 855 | 2003.4 | 0 | 0 | 11 | 467
20:30 | 3344 | 1333.5 | 891.5 | 0 | 189 | 1473.5 | 30 | 4892 | 0 | 850 | 2011.08 | 0 | 0 | 11 | 318.5
21:00 | 3311 | 1288 | 891 | 0 | 188 | 1474 | 30 | 4926 | 0 | 845 | 2018.76 | 0 | 0 | 11 | 170
21:30 | 3314.5 | 1285.75 | 891.5 | 0 | 186 | 1480.5 | 30 | 4928.5 | 0 | 808 | 1997.51 | 0 | 0 | 11 | 170
22:00 | 3318 | 1283.5 | 892 | 0 | 184 | 1487 | 30 | 4931 | 0 | 771 | 1976.26 | 0 | 0 | 11 | 170
22:30 | 3328.5 | 1340.5 | 892 | 0 | 184 | 1490.5 | 30 | 4927 | 0 | 760.5 | 1898.26 | 0 | 0 | 20.5 | 159
23:00 | 3339 | 1397.5 | 892 | 0 | 184 | 1494 | 30 | 4923 | 0 | 750 | 1820.26 | 0 | 0 | 30 | 148
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 11-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 168 | 19 | 480 | 128 | 1700 | 416 | Ishurdi-Ghorashal Ckt-1 | Export | 4548145.45
1:00 | 160 | 17 | 452 | 114 | 1666 | 420
2:00 | 153 | 15 | 432 | 106 | 1612 | 404 |  | Import | 0
3:00 | 169 | 24 | 472 | 114 | 1726 | 462
4:00 | 162 | 21 | 458 | 100 | 1680 | 416 | Ishurdi-Ghorashal Ckt-2 | Export | 1672.73
5:00 | 165 | 20 | 464 | 112 | 1692 | 412
6:00 | 171 | 24 | 480 | 40 | 1672 | 436 |  | Import | 0
7:00 | 167 | 19 | 496 | 102 | 1732 | 426
8:00 | 189 | 29 | 552 | 136 | 1850 | 502 | Sirajganj-Sreepur Ckt-1 | Export | 3346000
9:00 | 211 | 46 | 620 | 162 | 1952 | 570
10:00 | 209 | 45 | 560 | 140 | 1882 | 594 |  | Import | 0
11:00 | 212 | 47 | 592 | 154 | 1882 | 618
12:00 | 193 | 39 | 570 | 142 | 1866 | 624 | Sirajganj-Sreepur Ckt-2 | Export | 3360000
13:00 | 186 | 30 | 588 | 128 | 1812 | 524
14:00 | 210 | 47 | 632 | 142 | 2036 | 616 |  | Import | 0
15:00 | 228 | 60 | 668 | 167 | 1942 | 560
16:00 | 227 | 55 | 650 | 182 | 1872 | 568 | Gopalganj-Aminbazar Ckt-1 | Export | 21810000
17:00 | 241 | 57 | 730 | 200 | 2008 | 644
18:00 | 224 | 51 | 660 | 192 | 1856 | 614 |  | Import | 0
18:30 | 219 | 45 | 674 | 192 | 1858 | 602
19:00 | 215 | 42 | 660 | 180 | 1880 | 576 | Gopalganj-Aminbazar Ckt-2 | Export | 21850000
19:30 | 179 | 22 | 530 | 120 | 1774 | 510
20:00 | 171 | 17 | 506 | 106 | 1792 | 486 |  | Import | 0
21:00 | 173 | 20 | 526 | 152 | 1730 | 484
22:00 | 170 | 14 | 520 | 130 | 1690 | 434 |  | Total Export | 54915818.18
23:00 | 176 | 19 | 562 | 174 | 1704 | 466 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 11-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 05:00 | 358 | 12:00 | Madunaghat | 395 | 21:00 | 388 | 09:00
Amtali | 408 | 18:00 | 401 | 12:00 | Meghnaghat | 381 | 05:00 | 364 | 12:00
Ashuganj | 409 | 5:00 | 388 | 12:00 | Payra | 411 | 18:30 | 404 | 12:00
Bhulta | 401 | 05:00 | 378 | 12:00 | Rahanpur | 404 | 18:00 | 391 | 00:00
Bibiana | 395 | 05:00 | 384 | 12:00 | Rampal | 397 | 18:00 | 381 | 12:00
BIPTC | 402 | 06:00 | 394 | 00:00
Bogura | 389 | 18:30 | 373 | 12:00
Gopalganj | 391 | 18:30 | 376 | 12:00
Kaliakoir | 368 | 05:00 | 348 | 12:00
Korerhat | 395 | 22:00 | 385 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 05:00 | 212 | 12:00 | Jhenaidah | 228 | 18:00 | 212 | 12:00
AKSML | 231.5 | 22:00 | 223.8 | 09:00 | Kachua | 227 | 22:00 | 219 | 07:00
Aminbazar | 225 | 05:00 | 211 | 12:00 | Kaliakoir | 228 | 05:00 | 211 | 12:00
Ashuganj | 229 | 06:00 | 220 | 11:00 | Keranigonj | 226 | 05:00 | 210 | 12:00
Ashuganj-400 | 229 | 06:00 | 220 | 11:00 | Khulna(S) | 228 | 18:00 | 213 | 12:00
Baghabari | 233 | 04:00 | 223 | 11:00 | Korerhat | 226 | 22:00 | 219 | 09:00
Barapukuria | 226 | 16:00 | 207 | 19:30 | Madunaghat | 233 | 04:00 | 225 | 07:00
Barapukuria-230 | 226 | 16:00 | 207 | 19:30 | Madunaghat-400 | 233 | 21:00 | 227 | 09:00
Barishal | 228 | 18:00 | 221 | 12:00 | Maniknagar | 227 | 04:00 | 213 | 12:00
Bheramara | 234 | 05:00 | 222 | 12:00 | Meghnaghat | 233 | 20:00 | 222 | 12:00
Bhulta | 230 | 05:00 | 214 | 12:00 | Meghnaghat-400 | 231 | 05:00 | 218 | 12:00
Bibiana | 230 | 05:00 | 223 | 12:00 | Mirsorai | 231 | 22:00 | 224 | 09:00
BIPTC | 236 | 04:00 | 222 | 12:00 | Naogaon | 220 | 15:00 | 204 | 00:00
Bogura | 241 | 18:00 | 230 | 00:00 | Purbasadipur | 228 | 18:00 | 206 | 00:00
Bogura-400 | 241 | 18:30 | 230 | 01:00 | Rajshahi | 233 | 15:00 | 220 | 12:00
Borhanuddin | 229 | 07:00 | 224 | 12:00 | Rampal | 228 | 18:00 | 214 | 12:00
BSRM | 225 | 20:00 | 220 | 09:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 226 | 21:00 | 219 | 09:00 | Rampura | 229 | 05:00 | 212 | 12:00
Cumilla(N) | 226 | 05:00 | 219 | 12:00 | Shikalbaha | 232 | 21:00 | 227 | 07:00
Faridpur | 228 | 18:30 | 217 | 12:00 | Shyampur | 228 | 05:00 | 213 | 12:00
Fenchuganj | 232 | 05:00 | 226 | 19:00 | Siddhirganj | 228 | 00:00 | 219 | 11:00
Feni | 225 | 20:00 | 214 | 10:00 | Sirajgonj | 240 | 06:00 | 233 | 00:00
Ghorashal | 232 | 04:00 | 220 | 09:00 | Sreepur | 224 | 05:00 | 216 | 11:00
Ghorashal-230 | 216 | 05:00 | 199 | 11:00 | Tongi | 216 | 04:00 | 199 | 11:00
Gopalganj | 228 | 18:00 | 218 | 12:00
GPH | 229 | 21:00 | 224 | 08:00
Haripur | 229 | 05:00 | 215 | 12:00
Hasnabad | 225 | 07:00 | 214 | 12:00
Hathazari | 229 | 21:00 | 223 | 09:00
Ishurdi | 237 | 15:00 | 223 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 04:00 | 123 | 12:00 | Madunaghat | 134 | 21:00 | 129 | 15:00
Agargaon | 135 | 04:00 | 124 | 12:00 | Magura | 136 | 18:00 | 122 | 12:00
Agrabad | 131 | 00:00 | 126 | 14:00 | Mahasthangarh | 137 | 15:00 | 127 | 19:30
AKS | 130 | 18:00 | 126 | 08:00 | Maijdee | 126 | 22:00 | 122 | 08:00
Aminbazar | 128 | 03:00 | 119 | 11:00 | Manikganj | 132 | 18:00 | 120 | 10:00
Amnura | 138 | 18:30 | 126 | 00:00 | Maniknagar | 135 | 05:00 | 123 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 117 | 13:00 | 107 | 19:00
Ashuganj-230 | 136 | 05:00 | 130 | 19:00 | Matuail | 133 | 05:00 | 123 | 12:00
Bagerhat | 133 | 18:00 | 118 | 12:00 | Metrorail_Motijheel | 135 | 06:00 | 123 | 12:00
Bajitpur | 127 | 05:00 | 118 | 09:00 | Metrorail_Uttara | 134 | 04:00 | 118 | 11:00
Bakerganj | 132 | 18:00 | 126 | 12:00 | Millgate | 133 | 04:00 | 118 | 12:00
Bakulia | 132 | 23:00 | 127 | 15:00 | Mirpur | 128 | 05:00 | 119 | 12:00
Banani | 134 | 04:00 | 122 | 12:00 | Mirzapur | 131 | 20:00 | 121 | 10:00
Bangabhaban | 134 | 05:00 | 123 | 12:00 | Mithapukur | 135 | 18:00 | 122 | 01:00
Barapukuria | 138 | 16:00 | 123 | 19:30 | MI_Cement | 130 | 07:00 | 116.6 | 12:00
Barguna | 132 | 18:00 | 125 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 18:00 | 125 | 00:00 | Mogbazar | 135 | 05:00 | 124 | 12:00
Barishal-230 | 132 | 18:00 | 126 | 12:00 | Mongla | 133 | 18:00 | 118 | 12:00
Baroaulia | 131 | 00:00 | 128 | 11:00 | Motijheel | 134 | 05:00 | 123 | 12:00
Baroirhat | 131 | 22:00 | 127 | 09:00 | Muktagacha | 126 | 15:00 | 115 | 21:00
Bashundhara | 135 | 04:00 | 118 | 12:00 | Munshiganj | 132 | 22:00 | 122 | 12:00
BashundharaCement | 134 | 07:00 | 126 | 11:00 | Muradnagar | 132 | 22:00 | 123 | 12:00
Beanibazar | 126 | 05:00 | 119 | 19:00 | Mymensingh | 124 | 18:00 | 112 | 18:30
Benapole | 135 | 18:00 | 117 | 12:00 | Nabinagar | 131 | 05:00 | 116 | 12:00
Bhaluka | 130 | 05:00 | 122 | 19:00 | Naogaon | 138 | 15:00 | 123 | 00:00
Bhandaria | 126 | 08:00 | 118 | 22:00 | Narail | 137 | 18:00 | 121 | 12:00
Bhangura | 133 | 03:00 | 128 | 00:00 | Narinda | 135 | 05:00 | 123 | 12:00
Bheramara | 135 | 05:00 | 128 | 12:00 | Narshingdi | 127 | 01:00 | 120 | 11:00
Bheramara(GK) | 135 | 15:00 | 127 | 12:00 | Natore | 136 | 15:00 | 127 | 12:00
Bhulta | 127 | 22:00 | 120 | 12:00 | Nawabganj | 136 | 05:00 | 126 | 12:00
Bog-Sherpur | 138 | 18:30 | 130 | 00:00 | Netrakona | 121 | 13:00 | 110 | 21:00
Bogura | 139 | 15:00 | 131 | 00:00 | New | 134 | 06:00 | 118 | 11:00
Bogura-230 | 140 | 18:00 | 132 | 00:00 | Niamatpur | 133 | 15:00 | 126 | 00:00
Brahmanbaria | 130 | 05:00 | 123 | 19:00 | Noapara | 137 | 18:00 | 121 | 12:00
Cantonment | 135 | 04:00 | 123 | 12:00 | Pabna | 134 | 18:00 | 127 | 12:00
Chandina | 133 | 22:00 | 126 | 12:00 | Palashbari | 134 | 18:00 | 121 | 00:00
Chandpur | 133 | 22:00 | 122 | 08:00 | Panchagarh | 140 | 16:00 | 128 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 133 | 00:00 | 130 | 08:00 | Patiya | 130 | 20:00 | 126 | 14:00
Chapai | 133 | 18:00 | 126 | 00:00 | Patuakhali | 131 | 18:00 | 126 | 12:00
Charsaidpur | 133 | 22:00 | 123 | 12:00 | Payra | 133 | 05:00 | 131 | 12:00
Chauddagram | 131 | 22:00 | 126 | 09:00 | PHP | 130 | 02:00 | 127 | 08:00
Chhatak | 126 | 05:00 | 115 | 23:00 | Postogola | 131 | 03:00 | 120 | 12:00
Chowmuhani | 128 | 22:00 | 122 | 09:00 | Pubail | 133 | 04:00 | 121 | 09:00
Chuadanga | 136 | 18:00 | 121 | 12:00 | Purbachal | 134 | 04:00 | 124 | 13:00
Coxsbazar | 119 | 12:00 | 109 | 19:00 | Purbasadipur | 138 | 18:00 | 125 | 00:00
Cumilla(N) | 132 | 22:00 | 126 | 12:00 | Rahanpur | 135 | 15:00 | 129 | 00:00
Cumilla(S) | 133 | 22:00 | 120 | 128 | Rahanpur-400 | 135 | 15:00 | 130 | 00:00
Daganbhuiyan | 129 | 22:00 | 125 | 08:00 | Rahim | 133 | 05:00 | 124 | 12:00
Daudkandi | 131 | 22:00 | 121 | 09:00 | Rajbari | 130 | 18:00 | 120 | 12:00
DhakaUniversity | 133 | 22:00 | 123 | 12:00 | Rajendrapur | 129 | 04:00 | 123 | 09:00
Dhamrai | 130 | 06:00 | 119 | 12:00 | Rajshahi | 134 | 16:00 | 126 | 00:00
Dhanmondi | 134 | 05:00 | 124 | 12:00 | Rajshahi-230 | 135 | 16:00 | 126 | 12:00
Dohazari | 127 | 20:00 | 122 | 11:00 | Ramganj | 127 | 22:00 | 121 | 07:00
Faridpur | 132 | 18:30 | 124 | 12:00 | Rampur | 132 | 22:00 | 127 | 12:00
Fatullah | 137 | 05:00 | 118 | 12:00 | Rampura | 134 | 05:00 | 123 | 12:00
Fenchuganj | 132 | 05:00 | 127 | 19:00 | Rangamati | 132 | 01:00 | 129 | 11:00
Feni | 129 | 00:00 | 125 | 08:00 | Rangpur | 134 | 17:00 | 119 | 01:00
Feni-230 | 130 | 21:00 | 122 | 10:00 | Ruppur | 136 | 16:00 | 129 | 12:00
Ghatail | 124 | 16:00 | 114 | 10:00 | Saidpur | 135 | 16:00 | 122 | 19:30
Ghorashal | 130 | 04:00 | 123 | 11:00 | Santhia | 135 | 17:00 | 128 | 00:00
Goalpara | 139 | 18:00 | 125 | 12:00 | Satkhira | 133 | 18:00 | 119 | 12:00
Gollamari | 137 | 18:00 | 125 | 12:00 | Satmasjid | 135 | 05:00 | 123 | 12:00
Gopalganj | 136 | 20:00 | 124 | 12:00 | Savar | 127 | 06:00 | 119 | 11:00
Gopalganj-400 | 133 | 18:00 | 119 | 16:00 | SevenRings | 130 | 05:00 | 122 | 09:00
Gulshan | 134 | 05:00 | 123 | 12:00 | ShahCement | 133 | 22:00 | 123 | 12:00
Halishahar | 132 | 22:00 | 128 | 11:00 | Shahjadpur | 136 | 03:00 | 131 | 11:00
Haripur | 133 | 05:00 | 127 | 11:00 | Shahjibazar | 130 | 05:00 | 122 | 19:00
HaripurSBU | 133 | 06:00 | 127 | 11:00 | Shahmirpur | 132 | 21:00 | 128 | 08:00
Hasnabad | 131 | 05:00 | 120 | 12:00 | Shariatpur | 130 | 18:00 | 123 | 12:00
Hathazari | 135 | 22:00 | 130 | 09:00 | Sherpur | 122 | 16:00 | 110 | 21:00
Hatirjheel | 134 | 05:00 | 123 | 12:00 | Shikalbaha | 122 | 00:00 | 117 | 14:00
Ishurdi | 137 | 05:00 | 130 | 12:00 | Shikalbaha-230 | 133 | 18:30 | 130 | 07:00
Jaldhaka | 134 | 06:00 | 121 | 00:00 | Shitalakhya | 130 | 07:00 | 116.6 | 12:00
Jamalpur | 125 | 16:00 | 114 | 03:00 | Sholosohor | 132 | 00:00 | 128 | 11:00
Jashore | 136 | 18:00 | 118 | 12:00 | Shomvuganj | 122 | 04:00 | 114 | 23:00
Jhenaidah | 138 | 18:00 | 126 | 12:00 | Shyampur | 135 | 05:00 | 125 | 12:00
Jhenaidah-230 | 139 | 18:00 | 127 | 12:00 | Shyampur-230 | 137 | 05:00 | 126 | 12:00
Joydebpur | 127 | 05:00 | 117 | 09:00 | Siddhirganj | 133 | 05:00 | 124 | 12:00
Joypurhat | 137 | 15:00 | 127 | 19:30 | Sirajganj | 133 | 18:00 | 127 | 02:00
Juldah | 132 | 21:00 | 109 | 01:00 | Sonargaon | 132 | 22:00 | 122 | 12:00
Kabirpur | 137 | 20:00 | 115 | 11:00 | Sreemongol | 129 | 05:00 | 122 | 19:00
Kachua | 130 | 22:00 | 124 | 08:00 | Sreepur | 131 | 04:00 | 125 | 23:00
Kaliakoir | 137 | 20:00 | 123 | 12:00 | Srinagar | 136 | 05:00 | 126 | 12:00
Kaliganj | 138 | 17:00 | 126 | 13:00 | SSM | 135 | 18:30 | 132 | 00:00
Kallyanpur | 129 | 05:00 | 119 | 12:00 | Sunamganj | 128 | 05:00 | 113 | 19:00
Kalurghat | 134 | 22:00 | 130 | 07:00 | Sylhet | 127 | 07:00 | 122 | 19:00
Kamrangirchar | 137 | 05:00 | 116 | 12:00 | Sylhet_(South) | 128 | 06:00 | 121 | 21:00
Kaptai | 135 | 13:00 | 132 | 16:00 | Tangail | 127 | 20:00 | 116 | 11:00
Kasba | 133 | 22:00 | 122 | 12:00 | Taraganj | 134 | 16:00 | 123 | 00:00
Kazla | 134 | 05:00 | 123 | 12:00 | Tasnim | 132 | 22:00 | 122 | 12:00
Keranigonj | 137 | 05:00 | 127 | 12:00 | Thakurgaon | 140 | 18:00 | 127 | 08:00
Khagrachori | 132 | 20:00 | 128 | 08:00 | TK | 134 | 22:00 | 130 | 11:00
Khulna | 137 | 18:00 | 124 | 12:00 | Tongi | 136 | 04:00 | 122 | 11:00
Khulna(S) | 138 | 18:30 | 126 | 12:00 | Ullahpara | 134 | 17:00 | 128 | 12:00
Khulshi | 130 | 21:00 | 126 | 12:00 | Ullon | 134 | 04:00 | 123 | 12:00
Kishoreganj | 125 | 04:00 | 117 | 09:00 | Uttara | 132 | 04:00 | 117 | 11:00
Kodda | 137 | 20:00 | 121 | 11:00 | UttaraNew | 134 | 04:00 | 118 | 11:00
Korerhat | 132 | 00:00 | 129 | 09:00 | Zigatola | 137 | 04:00 | 127 | 12:00
KSRM | 133 | 05:00 | 128 | 08:00
Kulaura | 131 | 06:00 | 125 | 19:00
Kurigram | 130 | 04:00 | 116 | 19:30
Kushtia | 135 | 05:00 | 126 | 12:00
Laksam | 129 | 22:00 | 124 | 08:00
Lakshmipur | 125 | 18:00 | 122 | 08:00
Lalbag | 136 | 05:00 | 127 | 12:00
Lalmonirhat | 126 | 13:00 | 116 | 01:00
Madanganj | 132 | 04:00 | 126 | 09:00
Madaripur | 131 | 18:00 | 126 | 12:00
Madartek | 133 | 04:00 | 123 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division