## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 14-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-06-2026 | during | 14-06-2026 | during | 14-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 412 | 0 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 0 | 0 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 95 | 40 | 210 | 210 | 100 | 100 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 310 | 304 | 335 | 335 | 310 | 310 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 148 | 149 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 0 | 19 | 33 | 33 | 33 | 33 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 50 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 81 | 300 | 300 | 33 | 33 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 133 | 149 | 149 | 35 | 72 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 35 | 105 | 105 | 34 | 88 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 490 | 520 | 584 | 584 | 530 | 530 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 510 | 565 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 123 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1881 | 2304 | 5408.22 | 5792.22 | 2026.06 | 2679.06
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 18 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 14 | 0 | 14 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 6 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 40 | 60 | 60 | 60 | 60 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 102 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 8 | 8 | 8 | 8 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 50 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 2 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 60 | 63 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.59 | 0 | 2.66 | 0 | 2.66 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 35 | 54.36 | 54.36 | 17 | 17 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 93 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 48 | 100 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 57 | 153 | 163 | 163 | 35 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 612 | 612 | 612 | 612 | Unit1 Under Maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 8 | 10 | 14 | 10 | 14 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 725 | 825 | 1150 | 1150 | 1125 | 1125 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2068.59 | 2391.5 | 3308.52 | 3370.86 | 2529.16 | 2739.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 201 | 189 | 221.25 | 221.25 | 205 | 205 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 290 | 350.01 | 350.01 | 290 | 290 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 220 | 220 | 342.01 | 342.01 | 220 | 220 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 220 | 220 | 393 | 393 | 220 | 220 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 38 | 10 | 41.65 | 41.65 | 38 | 38 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 53 | 150 | 150 | 150 | 33 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 4 | 23 | 36 | 36 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 50 | 163 | 163 | 50 | 50 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 103 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 176 | 154 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 11 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 90 | 109 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 17 | 28 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 15 | 90 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 37 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1535 | 1750.2 | 2753.44 | 2692.44 | 1756.7 | 1861.7
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-06-2026 | during | 14-06-2026 | during | 14-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 19.5 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 0 | 210 | 210 | 25 | 25 | Gas shortage
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 69 | 87 | 70 | 90 | 70 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 48.75 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 202.35 | 172 | 483.6 | 446.5 | 222.1 | 202
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 28 | 28 | 28 | 28 | 28 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 141 | 152 | 163 | 163 | 163 | 163 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 141 | 0 | 145 | 145 | 145 | 145 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 83 | 83 | 83 | 41 | 41 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 101 | 102 | 102 | 102 | 102 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 25 | 23 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 344 | 320 | 320 | 320 | 320 | 320 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1163 | 1052 | 1257 | 1257 | 1181 | 1181
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 891 | 893 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 58 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 68 | 105 | 105 | 0 | 34 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 34 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1107 | 1221 | 1170 | 1170 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2032 | 2301 | 3518 | 3438 | 2371 | 2325
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 485 | 520 | 520 | 520 | 520 | 520 | AGC, Unit1 Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 64 | 64 | 65 | 65 | 65 | 65 | STG Under Maintenance
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1177 | 1190 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 0 | 72 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 306 | 307 | 307 | 307 | 307 | 307 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.37 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2252.37 | 2352 | 2617 | 2616 | 2313 | 2384
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 53.24 | 0 | 57 | 0 | 57 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 24 | 24 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 196 | 193 | 220 | 220 | 200 | 200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 199 | 209 | 220 | 220 | 200 | 200 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 382 | 405 | 413.79 | 413.79 | 400 | 400 | AGC
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 22 | 22 | 30 | 30 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 9 | 35 | 113 | 113 | 35 | 50 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.19 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1478 | 1480 | 1435.88 | 1435.88 | 1356 | 1356 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.96 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 103 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2482.39 | 2539 | 3001.47 | 2777.87 | 2603.8 | 2502.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 40 | 42 | 40 | 40 | 45 | 45 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 35 | 50 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.5 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 94 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 14 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 115 | 0 | 73.21 | 0 | 73.21 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 246.5 | 170 | 397.21 | 288 | 304.21 | 210
System Total |  |  |  |  | 28843.2 | 29290.237 | 13863.2 | 15031.7 | 22744.46 | 22678.89 | 15307.03 | 16084.46
Forecast Scenario (14-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14700 |  | 0 |  | 14700
|  |  |  | 1:00 | 14550 |  | 0 |  | 14550
|  |  |  | 2:00 | 14390 |  | 0 |  | 14390
|  |  |  | 3:00 | 13970 |  | 0 |  | 13970
|  |  |  | 4:00 | 13660 |  | 0 |  | 13660
|  |  |  | 5:00 | 13370 |  | 0 |  | 13370
|  |  |  | 6:00 | 13190 |  | 0 |  | 13190
|  |  |  | 7:00 | 13270 |  | 0 |  | 13270
|  |  |  | 8:00 | 13480 |  | 0 |  | 13480
|  |  |  | 9:00 | 13750 |  | 0 |  | 13750
|  |  |  | 10:00 | 14050 |  | 0 |  | 14050
|  |  |  | 11:00 | 14300 |  | 0 |  | 14300
|  |  |  | 12:00 | 15190 |  | 0 |  | 15190
|  |  |  | 13:00 | 15460 |  | 0 |  | 15460
|  |  |  | 14:00 | 15510 |  | 0 |  | 15510
|  |  |  | 15:00 | 15870 |  | 0 |  | 15870
|  |  |  | 16:00 | 14970 |  | 0 |  | 14970
|  |  |  | 17:00 | 14540 |  | 0 |  | 14540
|  |  |  | 18:00 | 13550 |  | 0 |  | 13550
|  |  |  | 18:30 | 14100 |  | 0 |  | 14100
|  |  |  | 19:00 | 14780 |  | 0 |  | 14780
|  |  |  | 19:30 | 15540 |  | 0 |  | 15540
|  |  |  | 20:00 | 15610 |  | 0 |  | 15610
|  |  |  | 21:00 | 16040 |  | 0 |  | 16040
|  |  |  | 22:00 | 15970 |  | 0 |  | 15970
|  |  |  | 23:00 | 15930 |  | 0 |  | 15930
Probable Maximum Temperature: |  |  | 34.80°C
Probable Maximum Demand at Day Peak: |  |  | 15190.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16040.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16040.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 350.10 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:21 hrs on 14-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 13-06-2026 | [28 empty] | Date: | 13-06-2026 | [28 empty] | Date: | 13-06-2026 | [28 empty] | Date: | 13-06-2026 | [28 empty] | Date: | 13-06-2026 | [18 empty] | Date: | 13-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [18 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 147 | 87 | 0 | 35 | 54 | 0 | 0 | 0 | 510 | 0 | 0 | 300 | 37 | 0 | 0 | 140 | 26 | 21 | 0 | 520 | 91 | 16 | 51 | 0 | 14 | 50 | 0 | 35 | 12 | 12 | 0 | 30 | 110 | 42 | 725 | 152 | 0 | 6 | 25.5 | 102 | 219 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 0 | 208 | 36 | 64 | 92 | 35 | 0 | 19 | 109 | 158 | 52.2 | 0 | 37 | 315 | 0 | 356 | 28 | 0 | 143 | 0 | 25 | 0 | 41 | 30 | 142 | 0 | 101 | 0 | 48 | 0 | 48 | 5 | 0 | 0 | 0 | 7127.7 | 892 | 0 | 0 | 20 | 37 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1225 | 36 | 0 | 0 | 1481 | 0 | 40 | 0 | 35 | 35 | 0 | 91 | 21 | 52.2 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 198 | 0 | 180 | 0 | 396 | 0 | 0 | 0 | 41 | 94 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 257 | 64 | 220 | 0 | 498 | 1230 | 17 | 7335.2 | 14462.9 | 73.84
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 147 | 81 | 0 | 35 | 54 | 0 | 0 | 0 | 500 | 0 | 0 | 295 | 38 | 0 | 0 | 142 | 26 | 21 | 0 | 480 | 90 | 16 | 28 | 0 | 8 | 50 | 0 | 35 | 12 | 12 | 0 | 30 | 107 | 42 | 725 | 142 | 0 | 6 | 25.5 | 98 | 219 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 0 | 212 | 36 | 51 | 92 | 19 | 0 | 19 | 108 | 152 | 52.2 | 0 | 37 | 310 | 0 | 356 | 28 | 0 | 137 | 0 | 25 | 0 | 41 | 30 | 142 | 0 | 101 | 0 | 48 | 20.42 | 48 | 5 | 0 | 0 | 0 | 6957.12 | 893 | 0 | 0 | 20 | 31 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1221 | 53 | 0 | 0 | 1486 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 21 | 52.2 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 198 | 0 | 180 | 0 | 396 | 0 | 0 | 0 | 40 | 94 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 494 | 1230 | 17 | 7302.2 | 14259.32 | 73.85
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 147 | 81 | 0 | 35 | 0 | 0 | 0 | 0 | 505 | 0 | 0 | 314 | 37 | 0 | 0 | 142 | 26 | 21 | 0 | 542 | 92 | 16 | 25 | 0 | 4 | 0 | 0 | 35 | 12 | 12 | 0 | 30 | 108 | 36 | 725 | 150 | 0 | 6 | 25.5 | 100 | 220 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 0 | 212 | 36 | 0 | 51 | 17 | 0 | 19 | 109 | 160 | 52.2 | 0 | 37 | 310 | 0 | 356 | 28 | 0 | 140 | 0 | 25 | 0 | 41 | 30 | 141 | 0 | 101 | 0 | 48 | 0 | 48 | 20 | 0 | 0 | 0 | 6850.7 | 892 | 0 | 0 | 20 | 31 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1214 | 53 | 0 | 0 | 1489 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 21 | 52.2 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 198 | 0 | 180 | 0 | 404 | 0 | 0 | 0 | 42 | 94 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 500 | 1180 | 17 | 7263.2 | 14113.9 | 73.86
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 147 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 0 | 303 | 37 | 0 | 0 | 142 | 26 | 21 | 0 | 495 | 94 | 16 | 24 | 0 | 12 | 0 | 0 | 35 | 12 | 12 | 0 | 30 | 107 | 36 | 725 | 155 | 0 | 6 | 25.5 | 102 | 220 | 0 | 0 | 0 | 612 | 0 | 12 | 0 | 220 | 290 | 220 | 51 | 0 | 220 | 36 | 0 | 50 | 17 | 0 | 19 | 110 | 156 | 52.2 | 0 | 37 | 305 | 0 | 356 | 28 | 0 | 142 | 0 | 23 | 0 | 41 | 30 | 140 | 0 | 101 | 0 | 48 | 0 | 48 | 20 | 0 | 0 | 0 | 6769.7 | 893 | 0 | 0 | 20 | 31 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1215 | 53 | 0 | 0 | 1484 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 21 | 52.2 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 198 | 0 | 180 | 0 | 395 | 0 | 0 | 0 | 41 | 94 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 495 | 1050 | 17 | 7115.2 | 13884.9 | 73.87
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 147 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 300 | 37 | 0 | 0 | 142 | 26 | 21 | 0 | 420 | 92 | 16 | 25 | 0 | 21 | 0 | 0 | 35 | 12 | 12 | 0 | 30 | 108 | 42 | 725 | 143 | 0 | 6 | 17 | 97 | 220 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 0 | 217 | 35 | 0 | 51 | 17 | 0 | 19 | 108 | 152 | 52.2 | 0 | 37 | 300 | 0 | 356 | 28 | 0 | 132 | 0 | 23 | 0 | 41 | 30 | 141 | 0 | 101 | 0 | 48 | 0 | 48 | 20 | 0 | 0 | 0 | 6654.2 | 893 | 0 | 0 | 20 | 27 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1213 | 67 | 0 | 0 | 1492 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 21 | 52.2 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 198 | 0 | 180 | 0 | 357 | 0 | 0 | 0 | 41 | 94 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 458 | 1010 | 17 | 7016.2 | 13670.4 | 73.88
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 108 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 300 | 37 | 0 | 0 | 142 | 26 | 21 | 0 | 380 | 94 | 16 | 25 | 0 | 12 | 0 | 0 | 35 | 12 | 12 | 0 | 30 | 99 | 42 | 725 | 108 | 0 | 6 | 17 | 96 | 220 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 0 | 217 | 35 | 0 | 50 | 17 | 0 | 19 | 41 | 144 | 52.2 | 0 | 38 | 305 | 0 | 356 | 28 | 0 | 130 | 0 | 0 | 0 | 41 | 30 | 141 | 0 | 101 | 0 | 48 | 0 | 48 | 20 | 0 | 0 | 0 | 6394.2 | 892 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 1216 | 67 | 0 | 0 | 1490 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 20 | 8 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 198 | 0 | 180 | 0 | 358 | 0 | 0 | 0 | 41 | 94 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 417 | 1050 | 17 | 6951 | 13345.2 | 73.89
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 108 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 300 | 38 | 0 | 1 | 68 | 26 | 21 | 0 | 380 | 45 | 16 | 0 | 0 | 15 | 0 | 0 | 0 | 12 | 12 | 0.32 | 30 | 93 | 42 | 725 | 42 | 0 | 6 | 0 | 94 | 220 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 0 | 191 | 35 | 0 | 49 | 0 | 0 | 19 | 0 | 144 | 8 | 4 | 0 | 300 | 0 | 356 | 28 | 0 | 128 | 1 | 23 | 0 | 41 | 30 | 142 | 0 | 101 | 0 | 49 | 0 | 48 | 20 | 0 | 0 | 0 | 5931.32 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3.67 | 1214 | 57 | 0 | 0 | 1491 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 1.05 | 6 | 0 | 0 | 1.89 | 0 | 0 | 198 | 0 | 180 | 0 | 355 | 0 | 0.18 | 0 | 40 | 50 | 2 | 0 | 0 | 0 | 0 | 0.5 | 13 | 0 | 16 | 307 | 64 | 220 | 0 | 419 | 1160 | 17 | 6759.29 | 12690.61 | 73.9
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 150 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 0 | 0 | 301 | 38 | 0 | 6 | 68 | 26 | 21 | 0 | 445 | 45 | 16 | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 12 | 0.91 | 30 | 67 | 34 | 725 | 15 | 0 | 6 | 0 | 68 | 220 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 0 | 197 | 35 | 0 | 49 | 0 | 0 | 19 | 0 | 144 | 8 | 14 | 0 | 305 | 0 | 356 | 28 | 0 | 129 | 0 | 17 | 0 | 41 | 30 | 141 | 0 | 101 | 0 | 49 | 2.13 | 48 | 20 | 0 | 0.64 | 0 | 6022.68 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 1216 | 17 | 0 | 0 | 1487 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 6.57 | 19 | 0 | 0 | 4.9 | 0 | 0 | 200 | 0 | 180 | 0 | 384 | 0 | 0.4 | 0 | 40 | 50 | 6 | 0 | 0 | 0 | 0 | 1.9 | 33 | 0.09 | 16 | 307 | 64 | 220 | 0 | 441 | 1190 | 17 | 6848.86 | 12871.54 | 73.91
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 149 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 0 | 0 | 300 | 38 | 0 | 7 | 0 | 25 | 21 | 0 | 440 | 45 | 16 | 0 | 0 | 4 | 0 | 0 | 0 | 12 | 12 | 1.1 | 30 | 65 | 11 | 725 | 15 | 0 | 6 | 0 | 67 | 220 | 0 | 0 | 0 | 612 | 0 | 12 | 0 | 220 | 290 | 220 | 51 | 0 | 198 | 38 | 0 | 50 | 0 | 0 | 19 | 0 | 154 | 8 | 16 | 0 | 305 | 0 | 356 | 28 | 0 | 131 | 0 | 23 | 0 | 41 | 30 | 142 | 0 | 101 | 0 | 49 | 5.65 | 48 | 18 | 0.1 | 12.03 | 0 | 5963.88 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.25 | 1225 | 17 | 0 | 0 | 1478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.5 | 23 | 0 | 0 | 0.16 | 0 | 0 | 199 | 0 | 180 | 0 | 348 | 0 | 0.21 | 0 | 40 | 50 | 13 | 0 | 0 | 0 | 0 | 3.9 | 51 | 0.3 | 16 | 307 | 64 | 220 | 0 | 430 | 1170 | 17 | 6777.32 | 12741.2 | 73.93
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 149 | 48 | 0 | 0 | 12 | 0 | 0 | 0 | 500 | 0 | 0 | 303 | 38 | 0 | 19 | 6 | 21 | 21 | 0 | 410 | 46 | 16 | 0 | 0 | 6 | 0 | 0 | 0 | 12 | 12 | 1.68 | 30 | 66 | 3 | 725 | 14 | 0 | 6 | 0 | 64 | 221 | 0 | 0 | 0 | 612 | 1 | 13 | 0 | 220 | 290 | 220 | 51 | 0 | 198 | 38 | 0 | 50 | 0 | 0 | 16 | 0 | 154 | 8 | 24 | 0 | 305 | 0 | 356 | 28 | 0 | 131 | 0 | 8 | 0 | 41 | 30 | 141 | 0 | 101 | 0 | 49 | 13.66 | 48 | 18 | 1.6 | 27.89 | 0 | 5977.83 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.74 | 1221 | 17 | 0 | 0 | 1455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.81 | 61 | 0 | 0 | 39.76 | 0 | 0 | 197 | 0 | 180 | 0 | 361 | 0 | 3.4 | 0 | 40 | 50 | 20 | 0 | 0 | 0 | 0 | 5.2 | 114 | 0.4 | 16 | 307 | 64 | 220 | 0 | 423 | 1180 | 17 | 6969.31 | 12947.14 | 73.95
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 148 | 32 | 0 | 0 | 17 | 0 | 0 | 0 | 495 | 0 | 17 | 290 | 96 | 0 | 29 | 68 | 20 | 21 | 0 | 450 | 45 | 16 | 0 | 0 | 18 | 17 | 0 | 0 | 12 | 12 | 2.58 | 30 | 65 | 0 | 725 | 0 | 0 | 6 | 0 | 64 | 221 | 0 | 0 | 0 | 612 | 3 | 20 | 0 | 220 | 290 | 220 | 43 | 0 | 201 | 36 | 0 | 50 | 0 | 3 | 16 | 0 | 156 | 8 | 19 | 0 | 305 | 0 | 356 | 28 | 0 | 131 | 1 | 23 | 0 | 41 | 30 | 142 | 0 | 101 | 0 | 49 | 20.75 | 57 | 10 | 1.9 | 29.61 | 0 | 6175.84 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1201 | 0 | 0 | 0 | 1441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.78 | 76 | 0 | 0 | 47.3 | 0 | 0 | 196 | 0 | 200 | 0 | 382 | 0 | 3.97 | 0 | 41 | 35 | 22 | 0 | 0 | 0 | 0 | 2.7 | 138 | 0.33 | 0 | 273 | 64 | 220 | 0 | 456 | 1180 | 0 | 6934.08 | 13109.92 | 73.97
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 148 | 32 | 0 | 17 | 17 | 0 | 0 | 0 | 500 | 0 | 17 | 306 | 95 | 0 | 30 | 76 | 0 | 21 | 0 | 530 | 46 | 16 | 30 | 0 | 4 | 17 | 0 | 0 | 12 | 12 | 3.75 | 30 | 73 | 0 | 725 | 0 | 0 | 6 | 1 | 71 | 219 | 0 | 0 | 0 | 612 | 13 | 52 | 0 | 220 | 290 | 220 | 51 | 0 | 202 | 36 | 0 | 51 | 3 | 18 | 12 | 10 | 168 | 16 | 38 | 0 | 310 | 0 | 344 | 28 | 0 | 135 | 8 | 25 | 0 | 41 | 30 | 141 | 0 | 101 | 0 | 48 | 21.18 | 48 | 8 | 2.1 | 35.11 | 0 | 6444.14 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 1112 | 0 | 0 | 0 | 1484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.63 | 65 | 0 | 0 | 53.5 | 0 | 0 | 196 | 0 | 200 | 0 | 399 | 0 | 4.79 | 0 | 40 | 34 | 13 | 0 | 0 | 0 | 0 | 6.4 | 96 | 0.43 | 0 | 304 | 64 | 220 | 0 | 500 | 1175 | 0 | 6944.75 | 13388.89 | 74
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 52 | 148 | 32 | 0 | 35 | 17 | 0 | 0 | 0 | 510 | 0 | 0 | 310 | 95 | 0 | 31 | 123 | 0 | 21 | 0 | 490 | 48 | 16 | 60 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 2.59 | 30 | 93 | 0 | 725 | 57 | 0 | 6 | 18 | 102 | 216 | 0 | 0 | 0 | 612 | 9 | 53 | 0 | 220 | 290 | 220 | 51 | 0 | 201 | 38 | 15 | 51 | 17 | 17 | 12 | 90 | 176 | 43 | 37 | 4 | 305 | 0 | 344 | 28 | 0 | 141 | 8 | 25 | 0 | 41 | 30 | 141 | 0 | 100 | 0 | 58 | 19.5 | 69 | 5 | 2.1 | 48.75 | 0 | 6849.94 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 1107 | 0 | 0 | 0 | 1478 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 53.24 | 103 | 0 | 0 | 56.96 | 0 | 0 | 196 | 0 | 199 | 0 | 382 | 0 | 5.19 | 0 | 40 | 70 | 14 | 0 | 0 | 0 | 0 | 7.5 | 115 | 0.37 | 0 | 306 | 64 | 220 | 0 | 485 | 1177 | 0 | 7013.26 | 13863.2 | 74.03
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 52 | 131 | 32 | 12 | 35 | 17 | 0 | 0 | 0 | 505 | 0 | 0 | 309 | 95 | 0 | 31 | 142 | 19 | 21 | 0 | 500 | 71 | 16 | 54 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 1.98 | 30 | 95 | 2 | 725 | 154 | 0 | 6 | 25.5 | 105 | 216 | 0 | 0 | 0 | 612 | 10 | 55 | 0 | 220 | 290 | 220 | 51 | 0 | 200 | 38 | 34 | 51 | 17 | 18 | 12 | 109 | 172 | 52.2 | 12 | 18 | 305 | 0 | 331 | 28 | 0 | 137 | 12 | 25 | 0 | 41 | 30 | 141 | 0 | 101 | 0 | 58 | 20.42 | 69 | 5 | 2.1 | 38.04 | 0 | 7028.24 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 86 | 1142 | 0 | 0 | 0 | 1479 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 51.09 | 99 | 0 | 0 | 54.21 | 0 | 0 | 194 | 0 | 195 | 0 | 384 | 0 | 3.49 | 0 | 40 | 75 | 7 | 0 | 0 | 0 | 0 | 5.2 | 137 | 0.22 | 0 | 305 | 63 | 220 | 0 | 487 | 1180 | 0 | 7136.21 | 14164.45 | 74.06
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 52 | 130 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 500 | 0 | 0 | 308 | 94 | 0 | 26 | 142 | 0 | 21 | 0 | 460 | 102 | 16 | 58 | 0 | 0 | 50 | 0 | 0 | 12 | 12 | 4 | 30 | 96 | 5 | 725 | 155 | 0 | 6 | 25.5 | 105 | 216 | 0 | 0 | 0 | 612 | 3 | 53 | 0 | 220 | 290 | 220 | 51 | 0 | 200 | 38 | 34 | 50 | 17 | 0 | 12 | 114 | 180 | 52.2 | 40 | 23 | 310 | 0 | 320 | 28 | 0 | 134 | 12 | 25 | 0 | 41 | 30 | 142 | 0 | 101 | 0 | 58 | 18.77 | 68 | 5 | 1.9 | 44.79 | 0 | 7015.16 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 49 | 1151 | 26 | 0 | 0 | 1468 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 15 | 25 | 46.09 | 70 | 0 | 0 | 47.37 | 0 | 0 | 193 | 0 | 194 | 0 | 378 | 0 | 4.34 | 0 | 38 | 94 | 11 | 0 | 0 | 0 | 0 | 4.4 | 66 | 0.24 | 0 | 304 | 63 | 220 | 0 | 466 | 1222 | 17 | 7131.44 | 14146.6 | 74.09
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 130 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 500 | 0 | 0 | 308 | 96 | 0 | 24 | 142 | 19 | 21 | 0 | 490 | 107 | 16 | 57 | 0 | 1 | 50 | 0 | 0 | 12 | 12 | 1.82 | 30 | 95 | 0 | 725 | 160 | 0 | 6 | 25.5 | 105 | 215 | 0 | 0 | 0 | 612 | 5 | 53 | 0 | 250 | 290 | 220 | 51 | 0 | 197 | 10 | 34 | 50 | 17 | 0 | 0 | 114 | 166 | 43 | 46 | 23 | 315 | 0 | 320 | 28 | 0 | 145 | 8 | 25 | 0 | 41 | 30 | 141 | 0 | 101 | 0 | 58 | 7.7 | 67 | 5 | 1.4 | 30.21 | 6 | 7009.63 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 61 | 1188 | 35 | 0 | 0 | 1489 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 52.2 | 37.11 | 63 | 0 | 0 | 36.31 | 0 | 0 | 194 | 0 | 195 | 0 | 378 | 0 | 3.42 | 0 | 38 | 94 | 8 | 0 | 0 | 0 | 0 | 3 | 138 | 0.3 | 0 | 200 | 63 | 220 | 0 | 472 | 1190 | 17 | 7152.34 | 14161.97 | 74.13
16:00 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 133 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 500 | 0 | 17 | 300 | 97 | 0 | 3 | 142 | 19 | 21 | 0 | 500 | 107 | 16 | 59 | 0 | 1 | 50 | 0 | 0 | 12 | 12 | 2.14 | 30 | 96 | 2 | 725 | 161 | 0 | 6 | 25.5 | 105 | 216 | 0 | 0 | 0 | 612 | 3 | 53 | 0 | 230 | 290 | 220 | 51 | 0 | 200 | 10 | 33 | 50 | 16 | 0 | 0 | 114 | 144 | 43 | 33 | 22 | 305 | 0 | 308 | 28 | 0 | 149 | 5 | 25 | 0 | 41 | 30 | 140 | 0 | 101 | 0 | 58 | 7.5 | 67 | 0 | 1 | 25.9 | 12 | 6942.04 | 892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 46 | 1200 | 35 | 0 | 0 | 1480 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 25 | 29.77 | 42 | 0 | 0 | 13.34 | 0 | 0 | 193 | 0 | 195 | 0 | 381 | 0 | 1.45 | 0 | 39 | 94 | 15 | 0 | 0 | 0 | 0 | 2.2 | 85 | 0.22 | 0 | 200 | 63 | 220 | 0 | 493 | 1180 | 35 | 7044.98 | 13987.02 | 74.17
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 130 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 500 | 0 | 35 | 300 | 96 | 0 | 4 | 142 | 0 | 21 | 0 | 420 | 107 | 16 | 63 | 0 | 8 | 50 | 0 | 0 | 12 | 12 | 0.65 | 30 | 96 | 2 | 725 | 148 | 0 | 6 | 25.5 | 105 | 216 | 0 | 0 | 0 | 612 | 2 | 55 | 0 | 250 | 290 | 220 | 51 | 0 | 196 | 10 | 34 | 50 | 47 | 6 | 0 | 114 | 150 | 52.2 | 10 | 23 | 310 | 0 | 308 | 28 | 0 | 142 | 2 | 25 | 0 | 41 | 30 | 141 | 0 | 101 | 0 | 58 | 5 | 67 | 0 | 0.5 | 14.15 | 12 | 6903 | 893 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 32 | 18 | 1191 | 35 | 0 | 0 | 1479 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 19 | 8 | 3.3 | 21 | 0 | 0 | 6.3 | 0 | 0 | 193 | 0 | 194 | 0 | 365 | 0 | 0.65 | 0 | 39 | 94 | 7 | 22 | 0 | 0 | 0 | 0.7 | 13 | 0.1 | 0 | 200 | 63 | 220 | 0 | 455 | 1180 | 17 | 6808.05 | 13711.05 | 74.21
18:00 | 0 | 17 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 65 | 146 | 81 | 15 | 35 | 17 | 0 | 0 | 0 | 495 | 0 | 35 | 298 | 97 | 0 | 2 | 142 | 0 | 21 | 0 | 420 | 92 | 16 | 63 | 0 | 13 | 50 | 0 | 0 | 12 | 12 | 0.23 | 30 | 102 | 2 | 725 | 98 | 0 | 6 | 25.5 | 105 | 216 | 0 | 0 | 0 | 612 | 0 | 53 | 0 | 260 | 290 | 220 | 51 | 0 | 193 | 10 | 34 | 50 | 103 | 27 | 0 | 66 | 152 | 52.2 | 2 | 23 | 305 | 0 | 314 | 28 | 0 | 135 | 1 | 25 | 0 | 41 | 30 | 140 | 0 | 101 | 0 | 58 | 0.4 | 67 | 0 | 0 | 3.17 | 12 | 6960.5 | 892 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 4 | 1173 | 35 | 0 | 0 | 1372 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 19 | 8 | 3.06 | 7 | 0 | 0 | 0.44 | 0 | 0 | 193 | 0 | 150 | 0 | 379 | 0 | 0.05 | 0 | 38 | 94 | 2 | 27 | 0 | 0 | 0 | 0.1 | 22 | 0.03 | 0 | 200 | 63 | 180 | 0 | 443 | 1180 | 17 | 6624.68 | 13585.18 | 74.23
19:00 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 12 | 91 | 147 | 81 | 15 | 35 | 108 | 0 | 0 | 0 | 515 | 0 | 35 | 323 | 40 | 0 | 0 | 142 | 19 | 21 | 0 | 550 | 94 | 16 | 67 | 0 | 8 | 50 | 0 | 1 | 12 | 12 | 0 | 30 | 110 | 2 | 725 | 120 | 0 | 6 | 25.5 | 105 | 216 | 0 | 0 | 0 | 612 | 0 | 53 | 0 | 260 | 290 | 220 | 51 | 0 | 200 | 10 | 46 | 50 | 102 | 26 | 11 | 109 | 150 | 52.2 | 0 | 23 | 310 | 0 | 314 | 28 | 0 | 145 | 0 | 23 | 0 | 41 | 30 | 141 | 0 | 101 | 0 | 67 | 0 | 86 | 0 | 0 | 0 | 0 | 7404.7 | 892 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1147 | 67 | 0 | 0 | 1488 | 0 | 40 | 0 | 35 | 35 | 0 | 75 | 21 | 8 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 193 | 0 | 190 | 0 | 403 | 0 | 0 | 0 | 40 | 94 | 0 | 29 | 0 | 0 | 0 | 0 | 1 | 0 | 16 | 231 | 64 | 220 | 0 | 520 | 1180 | 35 | 7116 | 14520.7 | 74.29
19:30 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 132 | 147 | 81 | 15 | 35 | 108 | 0 | 0 | 0 | 550 | 0 | 35 | 300 | 40 | 0 | 0 | 142 | 19 | 21 | 0 | 390 | 92 | 16 | 69 | 0 | 6 | 50 | 0 | 17 | 12 | 12 | 0 | 30 | 110 | 2 | 765 | 148 | 0 | 6 | 25.5 | 105 | 217 | 0 | 0 | 0 | 612 | 0 | 90 | 0 | 240 | 290 | 220 | 51 | 0 | 195 | 10 | 90 | 50 | 103 | 27 | 11 | 110 | 156 | 52.2 | 0 | 23 | 310 | 0 | 314 | 28 | 0 | 140 | 0 | 23 | 0 | 41 | 30 | 141 | 0 | 101 | 17 | 67 | 0 | 86 | 0 | 0 | 0 | 0 | 7462.7 | 892 | 0 | 0 | 24 | 53 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1203 | 67 | 0 | 0 | 1483 | 0 | 40 | 0 | 35 | 35 | 0 | 83 | 21 | 8 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 193 | 0 | 205 | 0 | 350 | 0 | 0 | 0 | 40 | 94 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 526 | 1185 | 35 | 7265 | 14727.7
20:00 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 128 | 147 | 81 | 15 | 35 | 108 | 0 | 0 | 0 | 540 | 0 | 35 | 300 | 40 | 0 | 0 | 142 | 19 | 21 | 0 | 475 | 94 | 16 | 69 | 0 | 8 | 50 | 0 | 19 | 12 | 12 | 0 | 30 | 110 | 2 | 765 | 150 | 0 | 6 | 25.5 | 105 | 217 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 240 | 290 | 220 | 51 | 0 | 190 | 10 | 87 | 50 | 103 | 27 | 11 | 105 | 156 | 52.2 | 0 | 23 | 310 | 0 | 314 | 28 | 0 | 140 | 0 | 23 | 0 | 41 | 30 | 141 | 0 | 101 | 17 | 68 | 0 | 87 | 0 | 0 | 0 | 0 | 7590.7 | 892 | 0 | 0 | 37 | 46 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1217 | 67 | 0 | 0 | 1480 | 0 | 40 | 0 | 35 | 35 | 0 | 92 | 22 | 8 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 193 | 0 | 202 | 0 | 386 | 0 | 0 | 0 | 40 | 94 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 520 | 1190 | 35 | 7324 | 14914.7 | 74.33
21:00 | 0 | 35 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 133 | 149 | 81 | 15 | 35 | 108 | 0 | 0 | 0 | 565 | 0 | 35 | 304 | 40 | 0 | 0 | 142 | 19 | 21 | 0 | 520 | 100 | 16 | 63 | 0 | 8 | 50 | 0 | 35 | 12 | 12 | 0 | 40 | 110 | 2 | 825 | 153 | 0 | 6 | 25.5 | 105 | 217 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 220 | 290 | 220 | 51 | 0 | 189 | 10 | 90 | 50 | 103 | 28 | 11 | 109 | 154 | 52.2 | 0 | 23 | 315 | 0 | 320 | 28 | 0 | 152 | 0 | 23 | 0 | 83 | 30 | 0 | 0 | 101 | 17 | 68 | 0 | 87 | 0 | 0 | 0 | 0 | 7669.7 | 893 | 0 | 0 | 29 | 58 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1221 | 68 | 0 | 0 | 1480 | 0 | 40 | 0 | 35 | 35 | 0 | 92 | 22 | 8 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 193 | 0 | 209 | 0 | 405 | 0 | 0 | 0 | 42 | 94 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 520 | 1190 | 35 | 7362 | 15031.7 | 74.37
22:00 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 75 | 149 | 81 | 15 | 35 | 108 | 0 | 0 | 0 | 555 | 0 | 35 | 315 | 39 | 0 | 0 | 142 | 19 | 21 | 0 | 540 | 99 | 16 | 59 | 0 | 8 | 50 | 0 | 35 | 12 | 12 | 0 | 40 | 110 | 8 | 920 | 152 | 0 | 6 | 25.5 | 105 | 218 | 0 | 0 | 0 | 612 | 0 | 43 | 0 | 220 | 290 | 220 | 51 | 0 | 189 | 10 | 72 | 50 | 103 | 19 | 19 | 110 | 152 | 52.2 | 0 | 23 | 315 | 0 | 327 | 28 | 0 | 153 | 0 | 23 | 0 | 83 | 30 | 0 | 0 | 101 | 17 | 68 | 0 | 88 | 0 | 0 | 0 | 0 | 7557.7 | 892 | 0 | 0 | 29 | 44 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1222 | 68 | 0 | 0 | 1473 | 0 | 40 | 0 | 35 | 35 | 0 | 92 | 22 | 8 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 193 | 0 | 206 | 0 | 400 | 0 | 0 | 0 | 40 | 94 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 520 | 1190 | 35 | 7331 | 14888.7 | 74.41
23:00 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 149 | 81 | 15 | 35 | 108 | 0 | 0 | 0 | 557 | 0 | 35 | 305 | 39 | 0 | 0 | 142 | 19 | 21 | 0 | 506 | 99 | 16 | 63 | 0 | 7 | 50 | 0 | 35 | 12 | 12 | 0 | 39 | 110 | 12 | 1060 | 150 | 0 | 6 | 25.5 | 105 | 219 | 0 | 0 | 0 | 580 | 0 | 13 | 0 | 225 | 290 | 220 | 51 | 0 | 189 | 10 | 69 | 50 | 103 | 0 | 19 | 108 | 156 | 52.2 | 0 | 23 | 310 | 0 | 327 | 28 | 0 | 152 | 0 | 23 | 0 | 83 | 30 | 0 | 0 | 101 | 17 | 68 | 0 | 88 | 0 | 0 | 0 | 0 | 7537.7 | 892 | 0 | 0 | 28 | 44 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1223 | 68 | 0 | 0 | 1483 | 0 | 40 | 0 | 35 | 35 | 0 | 92 | 22 | 8 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 193 | 0 | 201 | 0 | 400 | 0 | 0 | 0 | 38 | 94 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 305 | 64 | 220 | 0 | 518 | 1170 | 17 | 7292 | 14829.7 | 74.45
Total KWH | 0 | 163200 | 308160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259560 | 51480 | 1117296 | 3409920 | 1393047 | 187843 | 533598 | 790560 | 0 | 0 | 0 | 12345909 | 0 | 270045 | 7315258 | 1591000 | 0 | 200059 | 2980800 | 444000 | 519480 | 0 | 11481818.18 | 1988455 | 361309 | 971520 | 0 | 192960 | 728371 | 0 | 372257 | 297600 | 284160 | 24242 | 760980 | 2344327 | 404640 | 18145454.55 | 2651273 | 0 | 153600 | 447732 | 2326763 | 5084181 | 0 | 0 | 0 | 14629089 | 51840 | 975200 | 0 | 5611000 | 7377600 | 5468000 | 1242232 | 0 | 4978000 | 653760 | 704640 | 1250279 | 900960 | 199920 | 338520 | 1910640 | 3718080 | 957638 | 315936 | 481600 | 7480000 | 0 | 8229000 | 669000 | 0 | 3357163.64 | 51600 | 517704 | 0 | 1125120 | 718752 | 2721000 | 0 | 2432290 | 74880 | 1324800 | 138398 | 1490400 | 186240 | 14200 | 316880 | 44640 | 165559859.37 | 21579636 | 0 | 0 | 225120 | 407680 | 0 | 0 | 0 | 0 | 0 | 960048 | 498240 | 28618180 | 936480 | 0 | 0 | 35459511 | 0 | 474258 | 0 | 404256 | 709536 | 0 | 476464 | 287000 | 382128 | 354112 | 684866 | 193730 | 0 | 363472 | 0 | 0 | 4903636 | 0 | 4780508 | 0 | 9225090 | 0 | 30840 | 0 | 923345 | 1973346 | 160422 | 422620 | 0 | 0 | 0 | 52434 | 1138320 | 3441 | 251040 | 6807000 | 1528000 | 5415320 | 0 | 11505455 | 28541090.91 | 430800 | 171107424.91 | 336667284.28

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 13-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13863.2 | MW | 12:00 Hr. | Energy Generated |  |  | 336.6673 |  | MKWHr.
| Day Peak Demand |  |  | 14165.2 | MW | 12:00 Hr. | Energy Unserverd |  |  | 14.75 |  | MKWHr.
| Evening Peak Generation |  |  | 15031.7 | MW | 21:00 Hr. | Energy Demand |  |  | 351.4173 |  | MKWHr.
| Evening Peak Demand |  |  | 16615.7 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34 |  | °C
| Minimum Generation of the Day |  |  | 12690.61 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 865.6 |  | MMCFD
| Maximum Generation of the Day |  |  | 15031.7 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.8511 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.6975 | 0 | 11.4655 | 0 | 0 | 0.20006 | 0 | 0 | 45.363 | Gas | 119.3945 | Gas | 417370032.6194
| Chattogram Zone |  |  | 5.4888 | 32.7745 | 12.9274 | 0 | 0.76098 | 0.076082 | 0 | 0.19296 | 52.2208 | Coal | 109.1696 | Coal | 728497061.49
| Cumilla Zone |  |  | 26.9194 | 0 | 6.1306 | 0 | 0 | 0.31594 | 3.7181 | 0 | 37.084 | HFO | 41.9927 | HFO | 732384105.33
| Mymensingh Zone |  |  | 0.18624 | 0 | 2.9347 | 0 | 0 | 0.46948 | 0 | 0 | 3.5904 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.25 | 0 | 0 | 0 | 0 | 0.0516 | 0 | 0 | 27.3016 | Hydro | 0.76098 | Hydro | 76098
| Khulna Zone |  |  | 0 | 28.6182 | 2.5293 | 0 | 0 | 0.49824 | 21.5796 | 0 | 53.2254 | Solar | 4.3993 | Solar | 69067173.45
| Barishal Zone |  |  | 6.9433 | 46.8535 | 0.68184 | 0 | 0 | 0.003441 | 0 | 0 | 54.4821 | Import | 60.7572 | Import | 356311174.92
| Rajshahi Zone |  |  | 18.9092 | 0 | 2.9274 | 0 | 0 | 1.4333 | 35.4595 | 0 | 58.7294 | Wind | 0.19296 | Wind | 2838441.6
| Rangpur Zone |  |  | 0 | 0.92334 | 2.396 | 0 | 0 | 1.3512 | 0 | 0 | 4.6705
| Total |  |  | 119.3945 | 109.1696 | 41.9927 | 0 | 0.76098 | 4.3993 | 60.7572 | 0.19296 | 336.6673
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 417370032.6194 |  | Hydro | 76098
|  |  |  | Coal | 728497061.49 |  | Solar | 69067173.45
|  |  |  | HFO | 732384105.33 |  | Import | 356311174.92
|  |  |  | HSD | 0 |  | Wind | 2838441.6
[5 empty] | Total: | 230,65,44,087 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5796 | Peak Hr Flow | 893.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 53617636.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 35.4595 | Peak Hr Flow | 1480.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2569 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.7181 | Peak Hr Flow | 154.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2961 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 60.7572 | Peak Hr Flow | 2527.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 220 |  | 5635
|  |  |  | Chattogram |  | 23 |  | 1475
|  |  |  | Cumilla |  | 197 |  | 1580
|  |  |  | Mymensingh |  | 269 |  | 1318
|  |  |  | Sylhet |  | 102 |  | 690
|  |  |  | Khulna |  | 280 |  | 2020
|  |  |  | Barishal |  | 130 |  | 560
|  |  |  | Rajshahi |  | 124 |  | 1553
|  |  |  | Rangpur |  | 171 |  | 1116
|  |  |  | Total |  | 1516 |  | 15947
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 350
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:30 | Bhaluka 132/33kV S/S 01. Transformer- 01 HT is restored.
|  | 08:30 | Bhaluka 132/33kV S/S 02. Transformer- 02 LT is restored.
| 08:41 | 11:06 | Gopalganj 132/33kV S/S Transformer-03 LT Forced S/D Due to Bus D's maintenance of Bpbs-1 | [7 empty] | 17.0MW load
interrup.
| 08:42 | 11:05 | Gopalganj 132/33kV S/S Transformer-03 HT Forced S/D Due to Bus D's maintenance of Bpbs-1 | [7 empty] | 17.0MW load
interrup.
|  | 08:55 | Barishal 230/132kV S/S T-5 HT is restored.
|  | 08:57 | Barishal 230/132kV S/S T-5 LT is restored.
| 09:27 | 16:42 | Mymensingh RPCL-Tangail 132kV Ckt-1 Project Work S/D from Muktagacha 132/33kV end Due to
Work by RPCL
| 11:08 | 13:15 | Bhaluka 132/33kV S/S 02. Transformer- 02 HT Scheduled S/D | [7 empty] | 30.0MW load
interrup.
| 11:10 | 17:23 | Feni 230/132kV S/S ATR-3 LT Project Work S/D Due to Training work
| 11:12 | 17:22 | Feni 230/132kV S/S ATR-3 HT Project Work S/D Due to Training work
| 11:15 | 15:39 | Amnura 132/33kV S/S T-1 (406T) LT Scheduled S/D Due to Maintenance in LT Bushing,
Clearance, ALDC, Bogura.
| 11:16 | 15:39 | Amnura 132/33kV S/S T-1 (406T) HT Scheduled S/D Due to Maintenance in LT Bushing,
Clearance, ALDC, Bogura.
| 11:19 | 13:25 | Gopalganj (O) - Gopalgan (N) Ckt-1 Forced S/D from Gopalganj 132/33kV end Due to CT
Y-phase unusual sound trouble and from Gopalganj 400/132kV end Due to Gopalganj 132 KV SS
has taken S/D for CT maintenance at their end
| 12:00 |  | Day Peak Generation is 13863 MW.
| 12:43 |  | Tongi 230/132/33kV S/S Tongi-Tongi 80 MW PS Forced S/D
|  | 12:57 | Ghorasal-Joydeb-B 132kV Ckt-1 is restored.
|  | 12:58 | Ghorasal-Joydeb-B 132kV Ckt-2 is restored.
| 13:23 | 13:33 | Khulna (S)-Satkhira 132kV Ckt-1 Tripped from Khulna(S) 230/132kV end showing Distance
relay relays. and from Satkhira 132/33kV end showing O/C & E/F and Distance relay. relays
Due to Phase-c Earth fault.
| 14:21 |  | Satkhira 132/33kV S/S Transformer-3(T-3) LT Tripped showing Digfferential &,over current,
earth fault relays.
| 14:21 |  | Satkhira 132/33kV S/S Transformer-3(T-3) HT Tripped showing differential &
overcurrent,earth fault. relays Due to differential & overcurrent,earth fault. .
| 15:02 | 18:38 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to To connect new TR-06 transformer | [7 empty] | 60.0MW load
|  |  | to the 33 kv bus | [7 empty] | interrup.
| 15:03 | 18:36 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to To connect new TR-06 transformer | [7 empty] | 60.0MW load
|  |  | to the 33 kv bus | [7 empty] | interrup.
| 20:05 |  | Shahjibazar 330 MW CCPP tripped.
| 20:06 |  | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to To connect 33kv cable with
Transformer
|  | 20:33 | Bheramara P/S-Kustia 132 kV Ckt-1 is restored.
| 02:15 | 03:00 | Jaldhaka 132/33kV S/S 416T-2 LT Tripped showing Over Current Protection P142 relays. | [7 empty] | 20.0MW load
interrup.
| 02:15 | 02:59 | Jaldhaka 132/33kV S/S 406T-1 LT Tripped showing Over Current Protection P142 relays. | [7 empty] | 20.0MW load
interrup.
| 05:40 | 06:10 | Chattak-Sunamganj 132 kV Ckt-1 Tripped from Sunamganj 132/33kV end showing REL670 relays | [7 empty] | 5.0MW load
|  |  | Due to Rainy weather | [7 empty] | interrup. Sunamganj
132/33kV end
| 05:40 | 05:59 | Chattak-Sylhet 132 kV Ckt-2 Tripped from Sylhet 132/33kV end showing SOTF, relays. | [7 empty] | 19.0MW load
interrup. Sylhet
132/33kV end
| 05:56 | 06:40 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Tripped showing 33 kv REF 615 Relay relays Due to | [7 empty] | 10.0MW load
|  |  | Due to PDB 33kV Feeder-3 ( PDB grid incomer-3) Showing Earth fault & Over current trip. | [7 empty] | interrup.
| 06:00 |  | Minimum Generation 13665 MW.
| 06:07 |  | Rangpur 132/33kV S/S T-2 (404T) LT Scheduled S/D Due to Red hot Maintenance work
| 06:08 |  | Rangpur 132/33kV S/S T-2 (404T) HT Scheduled S/D Due to Red hot Maintenance work
| 06:16 |  | Mymensingh 132/33kV S/S Transformer-3 (424T) HT Scheduled S/D
| 06:16 |  | Mymensingh 132/33kV S/S Transformer-3 (424T) LT Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 13-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under Maintenance
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 187843 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 40 | 1591000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 304 | 7315258 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 259560 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 149 | 3409920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 533598 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270045 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 444000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 519480 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 308160 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 81 | 1393047 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 1117296 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 35 | 163200 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 790560 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 200059 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 51480 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 520 | 11481818.18 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 565 | 12345909 | AGC+Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 2980800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2304 | 45363033.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 447732 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 51840 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 153600 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 760980 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5084181 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2326763 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 728371 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 297600 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 404640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 63 | 971520 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24242 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 361309 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 35 | 372257 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2344327 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 284160 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 100 | 1988455 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 153 | 2651273 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14629089 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 192960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 825 | 18145454.55 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 2391.5 | 52220753.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 189 | 4978000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7377600 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 220 | 5468000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5611000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 653760 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1242232 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 975200 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 481600 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1250279 | ST Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 103 | 900960 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 154 | 3718080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 957638 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 11 | 338520 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 109 | 1910640 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 199920 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 704640 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 315936 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1750.2 | 37084005
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 138398 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 186240 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1490400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1324800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 316880 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 44640 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 74880 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 172 | 3590438
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 51600 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 669000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3357163.64 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 2721000 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 718752 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1125120 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2432290 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 517704 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7480000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 320 | 8229000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1052 | 27301629.64
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 893 | 21579636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 225120 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 58 | 407680 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 68 | 936480 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 960048 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 498240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1221 | 28618180 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2301 | 53225384
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 520 | 11505455 | AGC, Unit1 Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 251040 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 64 | 1528000 | STG Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1190 | 28541090.91 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5415320 | Unit1 Under Maintenance
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 430800 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6807000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3441 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2352 | 54482146.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 354112 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 474258 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 287000 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 193 | 4903636 | Gas Restrction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 209 | 4780508 | Gas Restrction
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 405 | 9225090 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 193730 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 382128 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 476464 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 709536 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 404256 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30840 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1480 | 35459511 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 363472 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 684866 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2539 | 58729407
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 42 | 923345 | Plant availability zero, U-2 Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 422620 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 52434 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 94 | 1973346 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 160422 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1138320 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 170 | 4670487
Eastern Grid Total |  |  |  |  | 17438.042 | 7669.7 | 165559859.37
Western Grid Total |  |  |  |  | 11852.195 | 7362 | 171107424.91
National Grid Total |  |  |  |  | 29290.237 | 15031.7 | 336667284.28
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 13-06-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9940.1 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4544.5 | MW
i) Dhaka area |  |  | 5414.8 |  | MW | i) Khulna area |  |  |  | 1740.5 | MW
ii) Chattogram area |  |  | 1505.3 |  | MW | ii) Barishal area |  |  |  | 429.8 | MW
iii) Cumilla area |  |  | 1383 |  | MW | iii) Rajshahi area |  |  |  | 1429.2 | MW
iv) Mymensingh area |  |  | 1049 |  | MW | iv) Rangpur area |  |  |  | 945 | MW
v) Sylhet area |  |  | 588 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14484.6 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 85 | 19:00 | 133 | Natore | 140 | 22:00
2 | AKSML | 145 | 02:00 | 68 | Hathazari | 92 | 20:00 | 134 | Nawabganj | 54.6 | 19:00
3 | Aftabnagar | 44 | 13:00 | 69 | Hatirjheel | 43 | 13:00 | 135 | Netrakona | 128 | 20:00
4 | Agargaon | 111 | 13:00 | 70 | Ishurdi | 86 | 13:00 | 136 | New | 84.8 | 12:00
5 | Agrabad | 72 | 12:00 | 71 | Jaldhaka | 72 | 22:00 | 137 | Niamatpur | 74 | 23:00
6 | Amnura | 32 | 02:00 | 72 | Jamalpur | 110 | 22:00 | 138 | Noapara | 48 | 20:00
7 | Ashuganj | 94 | 00:00 | 73 | Jashore | 149 | 13:00 | 139 | PHP | 14 | 15:00
8 | BSRM | 197 | 19:30 | 74 | Jhenaidah | 110 | 20:00 | 140 | Pabna | 100 | 20:00
9 | Bagerhat | 88 | 02:00 | 75 | Joydebpur | 156 | 10:00 | 141 | Palashbari | 136 | 01:00
10 | Bajitpur | 96 | 00:00 | 76 | Joypurhat | 70 | 19:30 | 142 | Panchagarh | 57 | 21:00
11 | Bakerganj | 14.8 | 00:00 | 77 | Juldah | 16 | 12:00 | 143 | Patiya | 11.5 | 19:30
12 | Bakulia | 95 | 19:30 | 78 | KSRM | 25 | 21:00 | 144 | Patuakhali | 68.5 | 00:00
13 | Banani | 46 | 13:00 | 79 | Kabirpur | 265 | 18:30 | 145 | Payra | 40 | 00:00
14 | Bangabhaban | 7 | 10:00 | 80 | Kachua | 88 | 05:00 | 146 | Postogola | 62 | 13:00
15 | Barapukuria | 63 | 13:00 | 81 | Kaliganj | 18 | 01:00 | 147 | Pubail | 30 | 12:00
16 | Barguna | 24 | 00:00 | 82 | Kallyanpur | 123 | 23:00 | 148 | Purbachal | 31 | 21:00
17 | Barishal | 115 | 19:00 | 83 | Kalurghat | 38 | 19:00 | 149 | Purbasadipur | 139 | 13:00
18 | Barishal-230 | 104 | 01:00 | 84 | Kamrangirchar | 80 | 13:00 | 150 | Rahanpur | 38 | 04:00
19 | Baroaulia | 53 | 15:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 47 | 10:00
20 | Baroirhat | 76 | 19:00 | 86 | Kasba | 36 | 00:00 | 152 | Rajbari | 77 | 13:00
21 | Bashundhara | 199 | 13:00 | 87 | Kazla | 114 | 13:00 | 153 | Rajendrapur | 114 | 12:00
22 | BashundharaCement | 12 | 17:00 | 88 | Keranigonj | 84 | 19:00 | 154 | Rajshahi | 105 | 22:00
23 | Beanibazar | 76 | 00:00 | 89 | Khagrachori | 30 | 22:00 | 155 | Rajshahi-230 | 110 | 13:00
24 | Benapole | 64 | 19:30 | 90 | Khulna | 64 | 13:00 | 156 | Ramganj | 110 | 22:00
25 | Bhaluka | 164 | 15:00 | 91 | Khulshi | 188 | 20:00 | 157 | Rampur | 58 | 15:00
26 | Bhandaria | 62 | 02:00 | 92 | Kishoreganj | 146 | 01:00 | 158 | Rangamati | 18 | 19:00
27 | Bhangura | 37 | 14:00 | 93 | Kodda | 341 | 18:30 | 159 | Rangpur | 140 | 21:00
28 | Bheramara(GK) | 64 | 14:00 | 94 | Kulaura | 49 | 19:00 | 160 | Ruppur | 2.8 | 10:00
29 | Bhulta | 203 | 11:00 | 95 | Kurigram | 64 | 07:00 | 161 | SSM | 0 | 00:00
30 | Bog-Sherpur | 74 | 02:00 | 96 | Kushtia | 157 | 14:00 | 162 | Saidpur | 101 | 15:00
31 | Bogura | 184 | 23:00 | 97 | Laksam | 36 | 19:00 | 163 | Santhia | 34 | 23:00
32 | Borhanuddin | 88 | 00:00 | 98 | Lakshmipur | 44 | 19:30 | 164 | Satkhira | 138 | 19:30
33 | Brahmanbaria | 127 | 16:00 | 99 | Lalbag | 77 | 13:00 | 165 | Satmasjid | 108 | 13:00
34 | Cantonment | 122 | 13:00 | 100 | Lalmonirhat | 57 | 04:00 | 166 | Savar | 194 | 18:30
35 | Chandina | 23 | 11:00 | 101 | MI_Cement | 15.3 | 09:00 | 167 | SevenRings | 12.21 | 03:00
36 | Chandpur | 80 | 05:00 | 102 | Madanganj | 40 | 11:00 | 168 | ShahCement | 36 | 02:00
37 | Chandraghona | 35 | 19:00 | 103 | Madaripur | 119 | 01:00 | 169 | Shahjadpur | 83 | 13:00
38 | Chapai | 77 | 13:00 | 104 | Madartek | 82 | 23:00 | 170 | Shahjibazar | 127 | 21:00
39 | Charsaidpur | 40 | 04:00 | 105 | Madunaghat | 57 | 19:30 | 171 | Shahmirpur | 52 | 18:30
40 | Chauddagram | 68 | 00:00 | 106 | Magura | 65 | 22:00 | 172 | Shariatpur | 95 | 00:00
41 | Chhatak | 41 | 01:00 | 107 | Mahasthangarh | 88 | 14:00 | 173 | Sherpur | 144 | 21:00
42 | Chowmuhani | 151 | 22:00 | 108 | Maijdee | 44 | 00:00 | 174 | Shikalbaha | 30 | 20:00
43 | Chuadanga | 118 | 19:30 | 109 | Manikganj | 134 | 22:00 | 175 | Shitalakhya | 85.4 | 13:00
44 | Coxsbazar | 142 | 19:00 | 110 | Maniknagar | 75 | 13:00 | 176 | Sholosohor | 53 | 12:00
45 | Cumilla(N) | 113 | 22:00 | 111 | Matarbari | 55 | 22:00 | 177 | Shomvuganj | 18 | 01:00
46 | Cumilla(S) | 180 | 14:00 | 112 | Matuail | 86 | 12:00 | 178 | Shyampur | 158 | 10:00
47 | Daganbhuiyan | 34 | 19:00 | 113 | Metrorail_Motijheel | 20 | 13:00 | 179 | Siddhirganj | 132 | 14:00
48 | Daudkandi | 140 | 22:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 102 | 00:00
49 | DhakaUniversity | 78 | 13:00 | 115 | Millgate | 103 | 15:00 | 181 | Sonargaon | 123 | 18:30
50 | Dhamrai | 126 | 19:00 | 116 | Mirpur | 151 | 12:00 | 182 | Sreemongol | 87 | 22:00
51 | Dhanmondi | 116.6 | 13:00 | 117 | Mirsorai | 34 | 09:00 | 183 | Sreepur | 119 | 18:00
52 | Dohazari | 105 | 19:00 | 118 | Mirzapur | 39 | 21:00 | 184 | Srinagar | 51 | 19:00
53 | Faridpur | 176 | 20:00 | 119 | Mithapukur | 68 | 02:00 | 185 | Sunamganj | 62 | 00:00
54 | Fatullah | 93 | 15:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 112 | 13:00
55 | Fenchuganj | 42 | 00:00 | 121 | Mogbazar | 100.8 | 13:00 | 187 | Sylhet_(South) | 73 | 00:00
56 | Feni | 105 | 22:00 | 122 | Mongla | 50 | 15:00 | 188 | TK | 24 | 21:00
57 | GPH | 24 | 04:00 | 123 | Motijheel | 51 | 13:00 | 189 | Tangail | 164 | 21:00
58 | Ghatail | 86 | 23:00 | 124 | Muktagacha | 35 | 11:00 | 190 | Taraganj | 25 | 14:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 108 | 17:00 | 191 | Tasnim | 38 | 15:00
60 | Ghorashal-230 | 107 | 18:30 | 126 | Muradnagar | 45 | 05:00 | 192 | Thakurgaon | 110 | 20:00
61 | Goalpara | 39 | 00:00 | 127 | Mymensingh | 180 | 13:00 | 193 | Tongi | 159 | 11:00
62 | Gollamari | 112 | 19:00 | 128 | Nabinagar | 96 | 10:00 | 194 | Ullahpara | 41 | 22:00
63 | Gopalganj | 98 | 20:00 | 129 | Naogaon | 142 | 13:00 | 195 | Ullon | 54 | 20:00
64 | Gulshan | 112 | 13:00 | 130 | Narail | 58.5 | 19:30 | 196 | Uttara | 90 | 12:00
65 | Halishahar | 100.5 | 18:00 | 131 | Narinda | 68 | 13:00 | 197 | UttaraNew | 51 | 12:00
66 | HaripurSBU | 134 | 17:00 | 132 | Narshingdi | 167 | 02:00 | 198 | Zigatola | 82 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 13-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14462.9 | 1347 |  | 15870.52
1:00 | 14259.32 | 1056 |  | 15362.84
2:00 | 14113.9 | 1012 |  | 15171.9
3:00 | 13884.9 | 929 |  | 14855.9
4:00 | 13670.4 | 508 |  | 14201.4
5:00 | 13345.2 | 152 |  | 13504.2
6:00 | 12690.61 | 143 |  | 12839.61
7:00 | 12871.54 | 188 |  | 13067.54
8:00 | 12741.2 | 178 |  | 12927.2
9:00 | 12947.14 | 142 |  | 13095.14
10:00 | 13109.92 | 73 |  | 13185.92
11:00 | 13388.89 | 134 |  | 13528.92
12:00 | 13863.2 | 289 |  | 14165.2
13:00 | 14164.45 | 401 |  | 14583.45
14:00 | 14146.6 | 425 |  | 14590.6
15:00 | 14161.97 | 463 |  | 14645.97
16:00 | 13987.02 | 372 |  | 14376.02
17:00 | 13711.05 | 175 |  | 13894.05
18:00 | 13585.18 | 126 |  | 13716.85
19:00 | 14520.7 | 1053 |  | 15620.7
19:30 | 14727.7 | 1249 |  | 16032.7
20:00 | 14914.7 | 1175 |  | 16142.7
21:00 | 15031.7 | 1516 |  | 16615.7
22:00 | 14888.7 | 1221 |  | 16164.7
23:00 | 14829.7 | 1672 |  | 16576.7
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 13-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7127.7 | 7335.2 | 14462.9 | DAILY GENERATION CURVE
00:30 | 7042.41 | 7318.7 | 14361.11
01:00 | 6957.12 | 7302.2 | 14259.32 | 13-06-2026
01:30 | 6903.91 | 7282.7 | 14186.61
02:00 | 6850.7 | 7263.2 | 14113.9
02:30 | 6810.2 | 7189.2 | 13999.4
03:00 | 6769.7 | 7115.2 | 13884.9
03:30 | 6711.95 | 7065.7 | 13777.65
04:00 | 6654.2 | 7016.2 | 13670.4
04:30 | 6524.2 | 6983.6 | 13507.8
05:00 | 6394.2 | 6951 | 13345.2
05:30 | 6162.76 | 6855.145 | 13017.905
06:00 | 5931.32 | 6759.29 | 12690.61
06:30 | 5977 | 6804.075 | 12781.075
07:00 | 6022.68 | 6848.86 | 12871.54
07:30 | 5993.28 | 6813.09 | 12806.37
08:00 | 5963.88 | 6777.32 | 12741.2
08:30 | 5970.855 | 6873.315 | 12844.17
09:00 | 5977.83 | 6969.31 | 12947.14
09:30 | 6076.835 | 6951.695 | 13028.53
10:00 | 6175.84 | 6934.08 | 13109.92
10:30 | 6309.99 | 6939.415 | 13249.405
11:00 | 6444.14 | 6944.75 | 13388.89
11:30 | 6647.04 | 6979.005 | 13626.045
12:00 | 6849.94 | 7013.26 | 13863.2
12:30 | 6939.09 | 7074.735 | 14013.825
13:00 | 7028.24 | 7136.21 | 14164.45
13:30 | 7021.7 | 7133.825 | 14155.525
14:00 | 7015.16 | 7131.44 | 14146.6
14:30 | 7012.395 | 7141.89 | 14154.285
15:00 | 7009.63 | 7152.34 | 14161.97
15:30 | 6975.835 | 7098.66 | 14074.495
16:00 | 6942.04 | 7044.98 | 13987.02
16:30 | 6922.52 | 6926.515 | 13849.035
17:00 | 6903 | 6808.05 | 13711.05
17:30 | 6931.75 | 6716.365 | 13648.115
18:00 | 6960.5 | 6624.68 | 13585.18
18:30 | 7182.6 | 6870.34 | 14052.94
19:00 | 7404.7 | 7116 | 14520.7
19:30 | 7462.7 | 7265 | 14727.7
20:00 | 7590.7 | 7324 | 14914.7
20:30 | 7630.2 | 7343 | 14973.2 |  | Executive Engineer
21:00 | 7669.7 | 7362 | 15031.7 |  | Network Operation Division
21:30 | 7613.7 | 7346.5 | 14960.2
22:00 | 7557.7 | 7331 | 14888.7
22:30 | 7547.7 | 7311.5 | 14859.2
23:00 | 7537.7 | 7292 | 14829.7

## En-Curve
QF-LDC-12
Date | 13-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3122 | 1933 | 892 | 0 | 158 | 1481 | 30 | 4588 | 0 | 716 | 1528.9 | 0 | 0 | 14 | 1347 | DAILY ENERGY CURVE
00:30 | 3122 | 1902.5 | 892.5 | 0 | 155 | 1483.5 | 30 | 4608.5 | 10.21 | 664.5 | 1481.4 | 0 | 0 | 11 | 1201.5 | 13-06-2026
01:00 | 3122 | 1872 | 893 | 0 | 152 | 1486 | 30 | 4629 | 20.42 | 613 | 1433.9 | 0 | 0 | 8 | 1056
01:30 | 3122 | 1904 | 892.5 | 0 | 156 | 1487.5 | 30 | 4604.5 | 10.21 | 588 | 1385.9 | 0 | 0 | 6 | 1034 | Energy Generated | 336.6673 |  | MKWHr
02:00 | 3122 | 1936 | 892 | 0 | 160 | 1489 | 30 | 4580 | 0 | 563 | 1337.9 | 0 | 0 | 4 | 1012 | Energy not Served | 14.75 |  | MKWHr
02:30 | 3115 | 1910 | 892.5 | 0 | 158 | 1486.5 | 30 | 4512.5 | 0 | 563 | 1323.9 | 0 | 0 | 8 | 970.5 | Total Energy Requirement | 351.4173 |  | MKWHr
03:00 | 3108 | 1884 | 893 | 0 | 156 | 1484 | 30 | 4445 | 0 | 563 | 1309.9 | 0 | 0 | 12 | 929
03:30 | 3086.5 | 1839.5 | 893 | 0 | 154 | 1488 | 30 | 4405.5 | 0 | 561 | 1303.65 | 0 | 0 | 16.5 | 718.5
04:00 | 3065 | 1795 | 893 | 0 | 152 | 1492 | 30 | 4366 | 0 | 559 | 1297.4 | 0 | 0 | 21 | 508
04:30 | 3065 | 1765 | 892.5 | 0 | 148 | 1491 | 30 | 4367 | 0 | 529.5 | 1203.3 | 0 | 0 | 16.5 | 330
05:00 | 3065 | 1735 | 892 | 0 | 144 | 1490 | 30 | 4368 | 0 | 500 | 1109.2 | 0 | 0 | 12 | 152
05:30 | 3051 | 1718 | 892.5 | 0 | 144 | 1490.5 | 30 | 4422.5 | 17.305 | 345.5 | 893.1 | 0 | 0 | 13.5 | 147.5
06:00 | 3037 | 1701 | 893 | 0 | 144 | 1491 | 30 | 4477 | 34.61 | 191 | 677 | 0 | 0 | 15 | 143
06:30 | 3055.5 | 1752 | 892.5 | 0 | 144 | 1489 | 30 | 4504 | 75.575 | 204.5 | 618 | 0 | 0 | 16 | 165.5
07:00 | 3074 | 1803 | 892 | 0 | 144 | 1487 | 30 | 4531 | 116.54 | 218 | 559 | 0 | 0 | 17 | 188
07:30 | 3057 | 1792.5 | 892.5 | 0 | 149 | 1482.5 | 30 | 4520 | 140.87 | 192 | 539.5 | 0 | 0 | 10.5 | 183
08:00 | 3040 | 1782 | 893 | 0 | 154 | 1478 | 30 | 4509 | 165.2 | 166 | 520 | 0 | 0 | 4 | 178
08:30 | 3047 | 1754.5 | 892.5 | 0 | 154 | 1466.5 | 30 | 4508.5 | 291.67 | 169 | 525.5 | 0 | 0 | 5 | 160
09:00 | 3054 | 1727 | 892 | 0 | 154 | 1455 | 30 | 4508 | 418.14 | 172 | 531 | 0 | 0 | 6 | 142
09:30 | 3093.5 | 1746 | 892 | 0 | 155 | 1448 | 30 | 4498 | 439.03 | 211 | 504 | 0 | 0 | 12 | 107.5
10:00 | 3133 | 1765 | 892 | 0 | 156 | 1441 | 30 | 4488 | 459.92 | 250 | 477 | 0 | 0 | 18 | 73
10:30 | 3141.5 | 1805 | 892.5 | 0 | 162 | 1462.5 | 30 | 4478 | 467.405 | 245.5 | 554 | 0 | 0 | 11 | 103.5
11:00 | 3150 | 1845 | 893 | 0 | 168 | 1484 | 30 | 4468 | 474.89 | 241 | 631 | 0 | 0 | 4 | 134
11:30 | 3140 | 1830.5 | 892 | 0 | 172 | 1481 | 30 | 4460 | 511.045 | 283 | 824.5 | 0 | 0 | 2 | 211.5
12:00 | 3130 | 1816 | 891 | 0 | 176 | 1478 | 30 | 4452 | 547.2 | 325 | 1018 | 0 | 0 | 0 | 289
12:30 | 3120.5 | 1827 | 892 | 0 | 174 | 1478.5 | 30 | 4471.5 | 558.975 | 333.5 | 1127.85 | 0 | 0 | 0 | 345
13:00 | 3111 | 1838 | 893 | 0 | 172 | 1479 | 30 | 4491 | 570.75 | 342 | 1237.7 | 0 | 0 | 0 | 401
13:30 | 3100.5 | 1808.5 | 892.5 | 0 | 176 | 1473.5 | 30 | 4504.5 | 509.825 | 367 | 1293.2 | 0 | 0 | 0 | 413
14:00 | 3090 | 1779 | 892 | 0 | 180 | 1468 | 30 | 4518 | 448.9 | 392 | 1348.7 | 0 | 0 | 0 | 425
14:30 | 3090.5 | 1803 | 892 | 0 | 173 | 1478.5 | 30 | 4471.5 | 461.585 | 393.5 | 1360.2 | 0 | 0 | 0.5 | 444
15:00 | 3091 | 1827 | 892 | 0 | 166 | 1489 | 30 | 4425 | 474.27 | 395 | 1371.7 | 0 | 0 | 1 | 463
15:30 | 3071.5 | 1830 | 892 | 0 | 155 | 1484.5 | 30 | 4437 | 394.895 | 399 | 1379.6 | 0 | 0 | 1 | 417.5
16:00 | 3052 | 1833 | 892 | 0 | 144 | 1480 | 30 | 4449 | 315.52 | 403 | 1387.5 | 0 | 0 | 1 | 372
16:30 | 3051.5 | 1782.5 | 892.5 | 0 | 147 | 1479.5 | 30 | 4425.5 | 211.935 | 414 | 1410.1 | 0 | 0 | 4.5 | 273.5
17:00 | 3051 | 1732 | 893 | 0 | 150 | 1479 | 30 | 4402 | 108.35 | 425 | 1432.7 | 0 | 0 | 8 | 175
17:30 | 3041.5 | 1703.5 | 892.5 | 0 | 151 | 1425.5 | 30 | 4386.5 | 77.915 | 470.5 | 1458.7 | 0 | 0 | 10.5 | 150.5
18:00 | 3032 | 1675 | 892 | 0 | 152 | 1372 | 30 | 4371 | 47.48 | 516 | 1484.7 | 0 | 0 | 13 | 126
18:30 | 3052.5 | 1791.5 | 892 | 0 | 151 | 1430 | 30 | 4413 | 24.24 | 595.5 | 1662.7 | 0 | 0 | 10.5 | 589.5
19:00 | 3073 | 1908 | 892 | 0 | 150 | 1488 | 30 | 4455 | 1 | 675 | 1840.7 | 0 | 0 | 8 | 1053
19:30 | 2988 | 1778 | 892 | 0 | 156 | 1483 | 30 | 4638 | 0 | 720 | 2036.7 | 0 | 0 | 6 | 1249
20:00 | 3016 | 1853 | 892 | 0 | 156 | 1480 | 30 | 4651 | 0 | 736 | 2092.7 | 0 | 0 | 8 | 1175
20:30 | 2953 | 1917.5 | 892.5 | 0 | 155 | 1480 | 35 | 4684 | 0 | 739 | 2109.2 | 0 | 0 | 8 | 1345.5
21:00 | 2890 | 1982 | 893 | 0 | 154 | 1480 | 40 | 4717 | 0 | 742 | 2125.7 | 0 | 0 | 8 | 1516
21:30 | 2895 | 1994.5 | 892.5 | 0 | 153 | 1476.5 | 40 | 4764 | 0 | 717.5 | 2019.2 | 0 | 0 | 8 | 1368.5
22:00 | 2900 | 2007 | 892 | 0 | 152 | 1473 | 40 | 4811 | 0 | 693 | 1912.7 | 0 | 0 | 8 | 1221
22:30 | 2895.5 | 1990 | 892 | 0 | 154 | 1478 | 39.5 | 4852.5 | 0 | 692.5 | 1857.7 | 0 | 0 | 7.5 | 1446.5
23:00 | 2891 | 1973 | 892 | 0 | 156 | 1483 | 39 | 4894 | 0 | 692 | 1802.7 | 0 | 0 | 7 | 1672
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 13-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 153 | -7 | 560 | 140 | 1778 | 344 | Ishurdi-Ghorashal Ckt-1 | Export | 4021236.36
1:00 | 141 | -11 | 552 | 144 | 1792 | 320
2:00 | 135 | -15 | 560 | 148 | 1760 | 342 |  | Import | 0
3:00 | 125 | -18 | 530 | 116 | 1690 | 332
4:00 | 133 | -12 | 530 | 104 | 1696 | 340 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 146 | -7 | 530 | 88 | 1794 | 346
6:00 | 141 | -8 | 520 | 104 | 1804 | 332 |  | Import | 0
7:00 | 137 | -21 | 510 | 108 | 1858 | 348
8:00 | 151 | -12 | 520 | 130 | 1896 | 370 | Sirajganj-Sreepur Ckt-1 | Export | 3423000
9:00 | 195 | 16 | 630 | 168 | 2114 | 520
10:00 | 215 | 39 | 666 | 166 | 2080 | 582 |  | Import | 0
11:00 | 214 | 44 | 646 | 168 | 2080 | 660
12:00 | 197 | 26 | 612 | 166 | 1946 | 576 | Sirajganj-Sreepur Ckt-2 | Export | 343400
13:00 | 172 | 10 | 580 | 138 | 1882 | 488
14:00 | 181 | 25 | 600 | 164 | 1934 | 506 |  | Import | 0
15:00 | 189 | 28 | 630 | 166 | 1950 | 542
16:00 | 176 | 23 | 590 | 142 | 1902 | 512 | Gopalganj-Aminbazar Ckt-1 | Export | 22880000
17:00 | 181 | 29 | 590 | 134 | 1930 | 520
18:00 | 187 | 39 | 580 | 168 | 1846 | 520 |  | Import | 0
18:30 | 187 | 37 | 590 | 146 | 1876 | 480
19:00 | 181 | 29 | 610 | 154 | 1812 | 434 | Gopalganj-Aminbazar Ckt-2 | Export | 22950000
19:30 | 168 | 18 | 560 | 106 | 1914 | 428
20:00 | 171 | 22 | 570 | 126 | 1904 | 436 |  | Import | 0
21:00 | 161 | 16 | 550 | 112 | 1858 | 434
22:00 | 165 | 17 | 540 | 112 | 1860 | 444 |  | Total Export | 53617636.36
23:00 | 154 | 9 | 552 | 138 | 1786 | 402 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 13-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 05:00 | 360 | 11:00 | Madunaghat | 400 | 04:00 | 390 | 11:00
Amtali | 409 | 03:00 | 402 | 13:00 | Meghnaghat | 385 | 04:00 | 366 | 11:00
Ashuganj | 406 | 4:00 | 385 | 12:00 | Payra | 411 | 04:00 | 405 | 12:00
Bhulta | 400 | 05:00 | 375 | 11:00 | Rahanpur | 400 | 18:30 | 389 | 13:00
Bibiana | 396 | 04:00 | 384 | 11:00 | Rampal | 398 | 05:00 | 381 | 13:00
BIPTC | 403 | 06:00 | 394 | 00:00
Bogura | 383 | 18:30 | 369 | 13:00
Gopalganj | 392 | 04:00 | 377 | 12:00
Kaliakoir | 375 | 03:00 | 350 | 11:00
Korerhat | 400 | 04:00 | 385 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 03:00 | 212 | 12:00 | Jhenaidah | 226 | 18:00 | 201 | 13:00
AKSML | 233 | 01:00 | 226 | 10:00 | Kachua | 228 | 00:00 | 218 | 11:00
Aminbazar | 230 | 05:00 | 213 | 11:00 | Kaliakoir | 232 | 03:00 | 211 | 10:00
Ashuganj | 228 | 03:00 | 219 | 11:00 | Keranigonj | 228 | 04:00 | 211 | 12:00
Ashuganj-400 | 228 | 03:00 | 219 | 11:00 | Khulna(S) | 227 | 18:00 | 210 | 13:00
Baghabari | 229 | 07:00 | 224 | 13:00 | Korerhat | 228 | 00:00 | 218 | 11:00
Barapukuria | 221 | 18:00 | 210 | 22:00 | Madunaghat | 235 | 05:00 | 229 | 10:00
Barapukuria-230 | 221 | 18:00 | 210 | 22:00 | Madunaghat-400 | 236 | 04:00 | 230 | 10:00
Barishal | 231 | 18:30 | 224 | 13:00 | Maniknagar | 228 | 02:00 | 211 | 11:00
Bheramara | 233 | 18:30 | 212 | 13:00 | Meghnaghat | 237 | 02:00 | 223 | 12:00
Bhulta | 230 | 05:00 | 213 | 11:00 | Meghnaghat-400 | 232 | 03:00 | 217 | 11:00
Bibiana | 229 | 03:00 | 224 | 11:00 | Mirsorai | 234 | 03:00 | 223 | 11:00
BIPTC | 235 | 18:30 | 213 | 13:00 | Naogaon | 220 | 17:00 | 201 | 13:00
Bogura | 238 | 18:30 | 228 | 13:00 | Purbasadipur | 219 | 05:00 | 208 | 22:00
Bogura-400 | 238 | 05:00 | 228 | 13:00 | Rajshahi | 231 | 18:00 | 210 | 13:00
Borhanuddin | 233 | 05:00 | 229 | 13:00 | Rampal | 226 | 18:00 | 211 | 13:00
BSRM | 228 | 00:00 | 220 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 227 | 00:00 | 217 | 12:00 | Rampura | 228 | 03:00 | 210 | 12:00
Cumilla(N) | 227 | 18:30 | 218 | 11:00 | Shikalbaha | 235 | 04:00 | 229 | 10:00
Faridpur | 230 | 04:00 | 221 | 12:00 | Shyampur | 230 | 04:00 | 213 | 12:00
Fenchuganj | 232 | 06:00 | 227 | 12:00 | Siddhirganj | 229 | 03:00 | 213 | 10:00
Feni | 227 | 00:00 | 220 | 10:00 | Sirajgonj | 237 | 18:00 | 231 | 12:00
Ghorashal | 230 | 00:00 | 220 | 15:00 | Sreepur | 226 | 05:00 | 216 | 15:00
Ghorashal-230 | 222 | 08:00 | 199 | 11:00 | Tongi | 222 | 07:00 | 200 | 11:00
Gopalganj | 232 | 04:00 | 223 | 13:00
GPH | 232 | 00:00 | 225 | 11:00
Haripur | 230 | 04:00 | 213 | 12:00
Hasnabad | 229 | 03:00 | 211 | 11:00
Hathazari | 231 | 01:00 | 222 | 11:00
Ishurdi | 235 | 18:30 | 215 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 03:00 | 122 | 11:00 | Madunaghat | 136 | 00:00 | 132 | 10:00
Agargaon | 137 | 04:00 | 124 | 11:00 | Magura | 135 | 18:00 | 116 | 13:00
Agrabad | 134 | 00:00 | 131 | 10:00 | Mahasthangarh | 134 | 18:30 | 127 | 22:00
AKS | 133 | 04:00 | 128 | 17:00 | Maijdee | 128 | 00:00 | 122 | 11:00
Aminbazar | 131 | 05:00 | 120 | 11:00 | Manikganj | 133 | 19:00 | 124 | 11:00
Amnura | 134 | 20:00 | 120 | 13:00 | Maniknagar | 135 | 04:00 | 122 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 122 | 14:00 | 111 | 19:00
Ashuganj-230 | 135 | 06:00 | 130 | 13:00 | Matuail | 133 | 06:00 | 121 | 12:00
Bagerhat | 131 | 18:00 | 117 | 13:00 | Metrorail_Motijheel | 135 | 05:00 | 122 | 12:00
Bajitpur | 128 | 06:00 | 120 | 00:00 | Metrorail_Uttara | 136 | 05:00 | 119 | 11:00
Bakerganj | 132 | 07:00 | 128 | 12:00 | Millgate | 137 | 02:00 | 120 | 11:00
Bakulia | 134 | 01:00 | 131 | 10:00 | Mirpur | 130 | 05:00 | 118 | 11:00
Banani | 134 | 05:00 | 121 | 12:00 | Mirzapur | 132 | 01:00 | 122 | 11:00
Bangabhaban | 135 | 03:00 | 122 | 12:00 | Mithapukur | 131 | 10:00 | 125 | 00:00
Barapukuria | 134 | 10:00 | 125 | 22:00 | MI_Cement | 131 | 04:00 | 117 | 11:00
Barguna | 131 | 09:00 | 128 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 18:30 | 127 | 12:00 | Mogbazar | 135 | 03:00 | 122 | 12:00
Barishal-230 | 133 | 07:00 | 128 | 12:00 | Mongla | 131 | 18:00 | 117 | 13:00
Baroaulia | 135 | 00:00 | 130 | 11:00 | Motijheel | 135 | 03:00 | 122 | 12:00
Baroirhat | 133 | 03:00 | 127 | 11:00 | Muktagacha | 126 | 18:30 | 115 | 22:00
Bashundhara | 139 | 04:00 | 118 | 11:00 | Munshiganj | 129 | 05:00 | 120 | 11:00
BashundharaCement | 130 | 01:00 | 121 | 12:00 | Muradnagar | 129 | 00:00 | 121 | 11:00
Beanibazar | 126 | 08:00 | 121 | 00:00 | Mymensingh | 126 | 18:30 | 113 | 13:00
Benapole | 132 | 18:00 | 113 | 13:00 | Nabinagar | 135 | 03:00 | 116 | 11:00
Bhaluka | 128 | 05:00 | 122 | 14:00 | Naogaon | 136 | 18:30 | 121 | 13:00
Bhandaria | 128 | 18:00 | 120 | 01:00 | Narail | 135 | 18:00 | 116 | 13:00
Bhangura | 133 | 06:00 | 125 | 13:00 | Narinda | 135 | 04:00 | 122 | 12:00
Bheramara | 134 | 18:00 | 123 | 13:00 | Narshingdi | 128 | 06:00 | 118 | 12:00
Bheramara(GK) | 134 | 18:30 | 122 | 13:00 | Natore | 134 | 18:30 | 123 | 13:00
Bhulta | 127 | 05:00 | 121 | 11:00 | Nawabganj | 138 | 04:00 | 127 | 11:00
Bog-Sherpur | 135 | 18:30 | 128 | 13:00 | Netrakona | 120 | 21:00 | 111 | 13:00
Bogura | 138 | 18:30 | 132 | 01:00 | New | 136 | 00:00 | 120 | 11:00
Bogura-230 | 138 | 18:30 | 130 | 13:00 | Niamatpur | 131 | 18:00 | 124 | 13:00
Brahmanbaria | 130 | 08:00 | 124 | 14:00 | Noapara | 135 | 18:00 | 119 | 13:00
Cantonment | 137 | 05:00 | 125 | 11:00 | Pabna | 133 | 18:00 | 124 | 13:00
Chandina | 132 | 00:00 | 125 | 11:00 | Palashbari | 129 | 10:00 | 122 | 22:00
Chandpur | 132 | 19:30 | 122 | 11:00 | Panchagarh | 137 | 05:00 | 130 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 135 | 00:00 | 132 | 10:00 | Patiya | 133 | 04:00 | 129 | 19:30
Chapai | 132 | 18:00 | 127 | 13:00 | Patuakhali | 132 | 18:30 | 127 | 11:00
Charsaidpur | 130 | 02:00 | 120 | 12:00 | Payra | 135 | 02:00 | 131 | 13:00
Chauddagram | 131 | 02:00 | 124 | 11:00 | PHP | 132 | 00:00 | 126 | 11:00
Chhatak | 127 | 07:00 | 117 | 01:00 | Postogola | 132 | 04:00 | 120 | 11:00
Chowmuhani | 127 | 00:00 | 122 | 11:00 | Pubail | 128 | 04:00 | 118 | 14:00
Chuadanga | 135 | 18:00 | 114 | 13:00 | Purbachal | 134 | 03:00 | 122 | 11:00
Coxsbazar | 122 | 18:00 | 113 | 19:00 | Purbasadipur | 133 | 18:00 | 126 | 22:00
Cumilla(N) | 132 | 18:30 | 125 | 11:00 | Rahanpur | 132 | 09:00 | 129 | 13:00
Cumilla(S) | 132 | 01:00 | 123 | 12:00 | Rahanpur-400 | 134 | 18:00 | 129 | 13:00
Daganbhuiyan | 130 | 00:00 | 124 | 11:00 | Rahim | 132 | 06:00 | 122 | 12:00
Daudkandi | 127 | 00:00 | 118 | 11:00 | Rajbari | 129 | 03:00 | 123 | 13:00
DhakaUniversity | 134 | 03:00 | 122 | 11:00 | Rajendrapur | 128 | 04:00 | 122 | 12:00
Dhamrai | 135 | 06:00 | 118 | 11:00 | Rajshahi | 132 | 18:00 | 119 | 13:00
Dhanmondi | 135 | 00:00 | 122 | 11:00 | Rajshahi-230 | 133 | 18:30 | 120 | 13:00
Dohazari | 130 | 08:00 | 125 | 19:00 | Ramganj | 128 | 19:30 | 119 | 11:00
Faridpur | 130 | 00:00 | 126 | 12:00 | Rampur | 134 | 04:00 | 130 | 10:00
Fatullah | 138 | 04:00 | 118 | 12:00 | Rampura | 134 | 04:00 | 121 | 12:00
Fenchuganj | 132 | 06:00 | 129 | 00:00 | Rangamati | 134 | 00:00 | 131 | 10:00
Feni | 132 | 03:00 | 125 | 11:00 | Rangpur | 129 | 10:00 | 121 | 20:00
Feni-230 | 132 | 15:00 | 126 | 10:00 | Ruppur | 135 | 18:30 | 124 | 13:00
Ghatail | 125 | 10:00 | 116 | 11:00 | Saidpur | 138 | 03:00 | 125 | 22:00
Ghorashal | 130 | 01:00 | 125 | 15:00 | Santhia | 134 | 18:30 | 126 | 13:00
Goalpara | 136 | 18:00 | 122 | 13:00 | Satkhira | 133 | 18:00 | 117 | 13:00
Gollamari | 135 | 05:00 | 126 | 12:00 | Satmasjid | 136 | 04:00 | 124 | 13:00
Gopalganj | 135 | 04:00 | 122 | 13:00 | Savar | 129 | 05:00 | 117 | 11:00
Gopalganj-400 | 133 | 04:00 | 128 | 13:00 | SevenRings | 130 | 04:00 | 125 | 21:00
Gulshan | 134 | 07:00 | 120 | 12:00 | ShahCement | 130 | 02:00 | 121 | 11:00
Halishahar | 135 | 04:00 | 130 | 19:00 | Shahjadpur | 137 | 04:00 | 130 | 12:00
Haripur | 132 | 05:00 | 122 | 11:00 | Shahjibazar | 130 | 08:00 | 124 | 00:00
HaripurSBU | 132 | 05:00 | 122 | 11:00 | Shahmirpur | 134 | 00:00 | 131 | 09:00
Hasnabad | 132 | 02:00 | 120 | 12:00 | Shariatpur | 130 | 06:00 | 124 | 13:00
Hathazari | 135 | 00:00 | 132 | 11:00 | Sherpur | 123 | 18:30 | 109 | 11:00
Hatirjheel | 134 | 03:00 | 121 | 12:00 | Shikalbaha | 124 | 00:00 | 121 | 12:00
Ishurdi | 136 | 18:00 | 125 | 13:00 | Shikalbaha-230 | 136 | 05:00 | 132 | 10:00
Jaldhaka | 131 | 10:00 | 122 | 22:00 | Shitalakhya | 131 | 04:00 | 117 | 11:00
Jamalpur | 127 | 18:30 | 114 | 11:00 | Sholosohor | 135 | 00:00 | 131 | 10:00
Jashore | 134 | 18:00 | 116 | 13:00 | Shomvuganj | 124 | 05:00 | 116 | 00:00
Jhenaidah | 137 | 18:00 | 119 | 13:00 | Shyampur | 137 | 05:00 | 128 | 13:00
Jhenaidah-230 | 137 | 18:30 | 119 | 13:00 | Shyampur-230 | 138 | 04:00 | 127 | 11:00
Joydebpur | 131 | 07:00 | 117 | 13:00 | Siddhirganj | 133 | 04:00 | 122 | 12:00
Joypurhat | 133 | 18:30 | 124 | 13:00 | Sirajganj | 132 | 20:00 | 125 | 12:00
Juldah | 135 | 00:00 | 131 | 11:00 | Sonargaon | 129 | 00:00 | 120 | 11:00
Kabirpur | 137 | 19:30 | 116 | 11:00 | Sreemongol | 129 | 08:00 | 124 | 00:00
Kachua | 130 | 00:00 | 124 | 11:00 | Sreepur | 132 | 05:00 | 125 | 12:00
Kaliakoir | 138 | 03:00 | 123 | 11:00 | Srinagar | 138 | 05:00 | 126 | 11:00
Kaliganj | 136 | 17:00 | 121 | 13:00 | SSM | 140 | 00:00 | 136 | 08:00
Kallyanpur | 131 | 05:00 | 119 | 12:00 | Sunamganj | 126 | 08:00 | 115 | 00:00
Kalurghat | 136 | 01:00 | 132 | 10:00 | Sylhet | 128 | 08:00 | 124 | 00:00
Kamrangirchar | 139 | 05:00 | 117 | 11:00 | Sylhet_(South) | 127 | 08:00 | 123 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 127 | 18:30 | 117 | 11:00
Kasba | 128 | 00:00 | 121 | 11:00 | Taraganj | 131 | 10:00 | 124 | 22:00
Kazla | 135 | 05:00 | 122 | 12:00 | Tasnim | 130 | 04:00 | 120 | 11:00
Keranigonj | 139 | 04:00 | 128 | 11:00 | Thakurgaon | 137 | 18:00 | 129 | 07:00
Khagrachori | 135 | 05:00 | 130 | 10:00 | TK | 135 | 00:00 | 132 | 09:00
Khulna | 135 | 18:00 | 122 | 13:00 | Tongi | 138 | 07:00 | 124 | 11:00
Khulna(S) | 137 | 18:00 | 123 | 13:00 | Ullahpara | 133 | 18:00 | 125 | 13:00
Khulshi | 133 | 00:00 | 129 | 19:00 | Ullon | 134 | 04:00 | 122 | 12:00
Kishoreganj | 126 | 05:00 | 118 | 13:00 | Uttara | 136 | 05:00 | 118 | 11:00
Kodda | 137 | 19:00 | 125 | 12:00 | UttaraNew | 136 | 05:00 | 119 | 11:00
Korerhat | 134 | 00:00 | 129 | 11:00 | Zigatola | 139 | 05:00 | 128 | 11:00
KSRM | 134 | 00:00 | 131 | 15:00
Kulaura | 131 | 08:00 | 127 | 00:00
Kurigram | 128 | 11:00 | 118 | 22:00
Kushtia | 132 | 18:30 | 118 | 13:00
Laksam | 130 | 00:00 | 124 | 11:00
Lakshmipur | 127 | 00:00 | 122 | 11:00
Lalbag | 137 | 02:00 | 126 | 11:00
Lalmonirhat | 128 | 09:00 | 115 | 22:00
Madanganj | 130 | 01:00 | 121 | 12:00
Madaripur | 132 | 05:00 | 127 | 12:00
Madartek | 133 | 01:00 | 121 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division