## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 15-06-2026 | [28 empty] | Date: | 15-06-2026 | [28 empty] | Date: | 15-06-2026 | [28 empty] | Date: | 15-06-2026 | [28 empty] | Date: | 15-06-2026 | [18 empty] | Date: | 15-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 147 | 81 | 15 | 35 | 54 | 0 | 0 | 0 | 560 | 0 | 0 | 331 | 137 | 0 | 0 | 142 | 19 | 21 | 0 | 520 | 107 | 16 | 50 | 0 | 6 | 50 | 0 | 17 | 12 | 12 | 0 | 75 | 22 | 28 | 1135 | 66 | 0 | 6 | 25.5 | 0 | 218 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 225 | 290 | 220 | 51 | 0 | 207 | 39 | 51 | 0 | 54 | 0 | 19 | 110 | 172 | 52.2 | 0 | 23 | 305 | 0 | 332 | 28 | 0 | 153 | 0 | 25 | 0 | 41 | 28 | 143 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7339.7 | 903 | 0 | 0 | 30 | 42 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 1098 | 69 | 0 | 0 | 1482 | 0 | 32 | 0 | 35 | 35 | 0 | 90 | 14 | 52.2 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 177 | 0 | 180 | 0 | 402 | 0 | 0 | 0 | 40 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 305 | 64 | 220 | 0 | 519 | 1222 | 17 | 7222.2 | 14561.9 | 75.36
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 131 | 81 | 15 | 35 | 35 | 0 | 0 | 0 | 545 | 0 | 0 | 332 | 200 | 0 | 0 | 142 | 19 | 21 | 0 | 500 | 107 | 16 | 29 | 0 | 7 | 50 | 0 | 17 | 12 | 12 | 0 | 70 | 17 | 28 | 1135 | 68 | 0 | 6 | 25.5 | 0 | 217 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 225 | 290 | 220 | 51 | 0 | 201 | 39 | 51 | 0 | 17 | 0 | 19 | 17 | 158 | 16 | 0 | 23 | 300 | 0 | 332 | 28 | 0 | 149 | 0 | 25 | 0 | 41 | 28 | 144 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7086.5 | 929 | 0 | 0 | 29 | 42 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1009 | 69 | 0 | 0 | 1485 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 13 | 49 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 177 | 0 | 180 | 0 | 370 | 0 | 0 | 0 | 40 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 302 | 64 | 220 | 0 | 484 | 1225 | 17 | 6951 | 14037.5 | 75.39
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 131 | 81 | 15 | 35 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 330 | 198 | 0 | 0 | 142 | 19 | 21 | 0 | 535 | 107 | 16 | 24 | 0 | 7 | 0 | 0 | 17 | 12 | 12 | 0 | 67 | 17 | 28 | 1135 | 68 | 0 | 6 | 25.5 | 0 | 218 | 0 | 0 | 0 | 585 | 0 | 13 | 0 | 225 | 290 | 220 | 51 | 0 | 199 | 39 | 0 | 0 | 17 | 0 | 19 | 17 | 162 | 16 | 0 | 23 | 310 | 0 | 332 | 28 | 0 | 148 | 0 | 25 | 0 | 41 | 28 | 142 | 0 | 101 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 6970.5 | 930 | 0 | 0 | 29 | 42 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 991 | 69 | 0 | 0 | 1479 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 177 | 0 | 180 | 0 | 400 | 0 | 0 | 0 | 43 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 303 | 64 | 220 | 0 | 517 | 1226 | 17 | 6962 | 13932.5 | 75.42
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 130 | 81 | 15 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 0 | 330 | 198 | 0 | 0 | 142 | 18.5 | 21 | 0 | 520 | 107 | 16 | 24 | 0 | 12 | 0 | 0 | 17 | 12 | 12 | 0 | 67 | 17 | 28 | 1135 | 66 | 0 | 6 | 25.5 | 0 | 218 | 0 | 0 | 0 | 585 | 0 | 11 | 0 | 225 | 290 | 220 | 51 | 0 | 199 | 39 | 0 | 0 | 17 | 0 | 19 | 17 | 158 | 16 | 0 | 23 | 310 | 0 | 332 | 28 | 0 | 151 | 0 | 8 | 0 | 41 | 28 | 140 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6896 | 930 | 0 | 0 | 29 | 42 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1061 | 69 | 0 | 0 | 1485 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 177 | 0 | 180 | 0 | 380 | 0 | 0 | 0 | 40 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 492 | 1225 | 17 | 6993 | 13889 | 75.45
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 130 | 47 | 15 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 332 | 194 | 0 | 0 | 142 | 18.5 | 21 | 0 | 500 | 97 | 16 | 25 | 0 | 3 | 0 | 0 | 17 | 12 | 12 | 0 | 70 | 17 | 29 | 1135 | 56 | 0 | 6 | 25.5 | 0 | 219 | 0 | 0 | 0 | 580 | 0 | 13 | 0 | 225 | 290 | 220 | 51 | 0 | 199 | 39 | 0 | 0 | 17 | 0 | 19 | 17 | 158 | 16 | 0 | 23 | 305 | 0 | 332 | 28 | 0 | 145 | 0 | 25 | 0 | 41 | 28 | 143 | 0 | 102 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6819 | 929 | 0 | 0 | 29 | 42 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1134 | 69 | 0 | 0 | 1485 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 182 | 0 | 390 | 0 | 0 | 0 | 43 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 475 | 1225 | 17 | 7049 | 13868 | 75.48
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 138 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 295 | 136 | 0 | 0 | 142 | 20 | 21 | 0 | 500 | 92 | 16 | 24 | 0 | 8 | 0 | 0 | 17 | 12 | 12 | 0 | 71 | 17 | 29 | 1135 | 64 | 0 | 6 | 25.5 | 0 | 219 | 0 | 0 | 0 | 580 | 0 | 13 | 0 | 225 | 290 | 220 | 51 | 0 | 207 | 39 | 0 | 0 | 17 | 0 | 19 | 17 | 152 | 16 | 0 | 23 | 310 | 0 | 332 | 28 | 0 | 143 | 0 | 25 | 0 | 41 | 28 | 143 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6730.5 | 929 | 0 | 0 | 29 | 42 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 69 | 0 | 0 | 1450 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 192 | 0 | 377 | 0 | 0 | 0 | 43 | 95 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 306 | 64 | 220 | 0 | 455 | 1225 | 17 | 6993 | 13723.5 | 75.51
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 148 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 490 | 0 | 0 | 302 | 136 | 0 | 2 | 142 | 20 | 21 | 0 | 510 | 89 | 16 | 24 | 0 | 2 | 0 | 0 | 17 | 12 | 12 | 0.08 | 75 | 17 | 29 | 1135 | 63 | 0 | 6 | 25.5 | 0 | 220 | 0 | 0 | 0 | 585 | 2 | 13 | 0 | 225 | 290 | 220 | 51 | 0 | 216 | 20 | 0 | 0 | 17 | 0 | 19 | 17 | 142 | 16 | 8 | 23 | 300 | 0 | 332 | 28 | 0 | 129 | 1 | 23 | 0 | 41 | 28 | 143 | 0 | 102 | 0 | 49 | 0.06 | 48 | 0 | 0 | 0.27 | 0 | 6665.91 | 929 | 0 | 0 | 29 | 42 | 38 | 0 | 0 | 0 | 0 | 0 | 3.92 | 1133 | 69 | 0 | 0 | 1481 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3.81 | 5 | 0 | 0 | 1.05 | 0 | 0 | 190 | 0 | 194 | 0 | 374 | 0 | 0.07 | 0 | 46 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 16 | 268 | 64 | 180 | 0 | 447 | 1225 | 17 | 6912.85 | 13578.76 | 75.54
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 148 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 303 | 135 | 0 | 6 | 105 | 20 | 21 | 0 | 500 | 60 | 16 | 25 | 0 | 2 | 0 | 0 | 0 | 12 | 12 | 0.89 | 75 | 17 | 30 | 1135 | 34 | 0 | 6 | 16 | 0 | 219 | 0 | 0 | 0 | 585 | 5 | 13 | 0 | 240 | 290 | 220 | 51 | 0 | 197 | 20 | 0 | 0 | 17 | 0 | 19 | 17 | 138 | 16 | 9 | 23 | 305 | 0 | 332 | 28 | 0 | 144 | 3 | 23 | 0 | 41 | 30 | 143 | 0 | 101 | 0 | 49 | 0.68 | 48 | 0 | 0.1 | 0.76 | 0 | 6587.43 | 929 | 0 | 0 | 29 | 41 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 1104 | 69 | 0 | 0 | 1485 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 10.7 | 17 | 0 | 0 | 10.05 | 0 | 0 | 194 | 0 | 197 | 0 | 388 | 0 | 0.71 | 0 | 46 | 70 | 1 | 0 | 0 | 0 | 0 | 0.6 | 4 | 0 | 16 | 267 | 64 | 220 | 0 | 476 | 1220 | 17 | 6980.06 | 13567.49 | 75.57
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 147 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 313 | 134 | 0 | 9 | 105 | 20 | 21 | 0 | 525 | 62 | 16 | 24 | 0 | 6 | 0 | 0 | 0 | 12 | 12 | 1.26 | 76 | 17 | 2 | 1135 | 27 | 0 | 6 | 16 | 0 | 217 | 0 | 0 | 0 | 580 | 9 | 13 | 0 | 240 | 290 | 220 | 51 | 0 | 205 | 20 | 0 | 0 | 17 | 0 | 19 | 17 | 148 | 16 | 16 | 23 | 300 | 0 | 332 | 28 | 0 | 147 | 4 | 23 | 0 | 41 | 30 | 144 | 0 | 101 | 0 | 49 | 3.08 | 48 | 0 | 0.1 | 5.84 | 0 | 6624.28 | 930 | 0 | 0 | 0 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 1105 | 69 | 0 | 0 | 1491 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 9.18 | 44 | 0 | 0 | 17.89 | 0 | 0 | 196 | 0 | 200 | 0 | 395 | 0 | 1.59 | 0 | 45 | 70 | 4 | 0 | 0 | 0 | 0 | 3.7 | 20 | 0 | 0 | 273 | 64 | 220 | 0 | 507 | 1180 | 17 | 7006.36 | 13630.64 | 75.6
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 127 | 32 | 15 | 0 | 17 | 0 | 0 | 0 | 520 | 0 | 0 | 290 | 135 | 0 | 20 | 116 | 20 | 21 | 0 | 510 | 87 | 16 | 24 | 0 | 3 | 0 | 0 | 0 | 12 | 12 | 2.62 | 76 | 17 | 2 | 1135 | 36 | 0 | 29 | 20 | 0 | 217 | 0 | 0 | 0 | 585 | 10 | 13 | 0 | 280 | 290 | 220 | 51 | 0 | 186 | 20 | 0 | 0 | 17 | 0 | 19 | 17 | 148 | 16 | 28 | 23 | 305 | 0 | 332 | 28 | 0 | 153 | 1 | 22 | 0 | 41 | 30 | 144 | 0 | 101 | 0 | 49 | 5.1 | 48 | 0 | 0.7 | 11.52 | 0 | 6756.94 | 929 | 0 | 0 | 0 | 33 | 38 | 0 | 0 | 0 | 0 | 0 | 24.99 | 1108 | 20 | 0 | 0 | 1484 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 17.33 | 64 | 0 | 0 | 18.32 | 0 | 0 | 194 | 0 | 198 | 0 | 397 | 0 | 2.42 | 0 | 45 | 55 | 8 | 0 | 0 | 0 | 0 | 4.5 | 50 | 0 | 0 | 277 | 64 | 220 | 0 | 511 | 1180 | 17 | 6999.56 | 13756.5 | 75.62
10:00 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 110 | 32 | 15 | 0 | 17 | 0 | 0 | 0 | 510 | 0 | 17 | 293 | 135 | 0 | 29 | 123 | 20 | 21 | 0 | 490 | 97 | 16 | 24 | 0 | 1 | 0 | 0 | 0 | 12 | 12 | 4.55 | 76 | 17 | 0 | 1135 | 50 | 0 | 45 | 25.5 | 0 | 216 | 0 | 0 | 0 | 583 | 14 | 42 | 0 | 250 | 290 | 220 | 51 | 0 | 187 | 20 | 0 | 0 | 17 | 3 | 19 | 17 | 150 | 16 | 61 | 23 | 305 | 0 | 332 | 28 | 0 | 152 | 1 | 22 | 0 | 41 | 30 | 144 | 0 | 100 | 0 | 49 | 15.99 | 48 | 0 | 1.8 | 10.69 | 0 | 6850.53 | 930 | 0 | 0 | 0 | 32 | 38 | 0 | 0 | 0 | 0 | 0 | 53 | 1128 | 0 | 0 | 0 | 1484 | 0 | 31 | 0 | 0 | 20 | 0 | 0 | 0 | 8 | 41.71 | 88 | 0 | 0 | 12.94 | 0 | 0 | 194 | 0 | 196 | 0 | 395 | 0 | 3.32 | 0 | 45 | 70 | 21 | 0 | 0 | 0 | 0 | 5.6 | 155 | 0 | 0 | 275 | 64 | 220 | 0 | 511 | 1180 | 17 | 7218.57 | 14069.1 | 75.64
11:00 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 24 | 110 | 32 | 15 | 4 | 17 | 0 | 0 | 0 | 520 | 0 | 0 | 309 | 193 | 0 | 30 | 123 | 20 | 21 | 0 | 515 | 96 | 16 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3.18 | 76 | 17 | 2 | 1135 | 49 | 0 | 49 | 25.5 | 0 | 215 | 0 | 0 | 0 | 582 | 11 | 48 | 0 | 250 | 290 | 220 | 51 | 0 | 198 | 20 | 0 | 0 | 17 | 17 | 19 | 17 | 160 | 16 | 25 | 0 | 300 | 0 | 332 | 28 | 0 | 143 | 3 | 22 | 0 | 41 | 30 | 145 | 0 | 101 | 0 | 49 | 20.57 | 48 | 0 | 1.9 | 23.49 | 0 | 7012.64 | 929 | 0 | 0 | 0 | 28 | 38 | 0 | 0 | 0 | 0 | 0 | 92 | 1100 | 0 | 0 | 0 | 1486 | 0 | 31 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 17.49 | 100 | 0 | 0 | 51.48 | 0 | 0 | 193 | 0 | 194 | 0 | 394 | 0 | 5.15 | 0 | 45 | 70 | 15 | 0 | 0 | 0 | 0 | 5.1 | 109 | 0 | 0 | 276 | 64 | 220 | 0 | 513 | 1180 | 36 | 7235.22 | 14247.86 | 75.67
12:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 34 | 109 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 525 | 0 | 0 | 311 | 191 | 0 | 33 | 123 | 19.8 | 21 | 0 | 535 | 100 | 16 | 43 | 0 | 9 | 0 | 0 | 0 | 12 | 12 | 3.24 | 73 | 17 | 2 | 1135 | 48 | 0 | 50 | 25.5 | 0 | 213 | 0 | 0 | 0 | 582 | 15 | 53 | 0 | 250 | 290 | 220 | 51 | 0 | 202 | 20 | 8 | 0 | 17 | 24 | 19 | 17 | 170 | 8 | 20 | 0 | 300 | 0 | 332 | 28 | 0 | 156 | 7 | 0 | 0 | 41 | 30 | 143 | 0 | 101 | 0 | 49 | 16 | 76 | 0 | 2.2 | 41 | 0 | 7169.74 | 929 | 0 | 0 | 0 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 1040 | 0 | 0 | 0 | 1483 | 0 | 39 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 54.39 | 102 | 0 | 0 | 59 | 0 | 0 | 192 | 0 | 194 | 0 | 398 | 0 | 5.32 | 0 | 0 | 70 | 29 | 0 | 0 | 0 | 0 | 6.1 | 79 | 0 | 0 | 281 | 64 | 220 | 0 | 511 | 1180 | 17 | 7066.81 | 14236.55 | 75.7
13:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 34 | 126 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 490 | 0 | 0 | 276 | 194 | 0 | 7 | 136 | 20 | 21 | 0 | 480 | 101 | 16 | 43 | 0 | 11 | 0 | 0 | 0 | 12 | 12 | 4.79 | 65 | 17 | 0 | 1135 | 50 | 0 | 50 | 25.5 | 0 | 213 | 0 | 0 | 0 | 581 | 12 | 53 | 0 | 250 | 290 | 220 | 51 | 0 | 194 | 20 | 34 | 0 | 17 | 17 | 19 | 17 | 172 | 8 | 28 | 0 | 305 | 0 | 342 | 28 | 0 | 151 | 6 | 22 | 0 | 41 | 30 | 145 | 0 | 101 | 0 | 49 | 10.1 | 77 | 0 | 2 | 47.13 | 0 | 7099.52 | 930 | 0 | 0 | 0 | 26 | 38 | 0 | 0 | 0 | 0 | 0 | 32 | 1012 | 0 | 0 | 0 | 1487 | 0 | 39 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 54.67 | 81 | 0 | 0 | 52.83 | 0 | 0 | 189 | 0 | 192 | 0 | 371 | 0 | 4.83 | 0 | 0 | 70 | 28 | 0 | 0 | 0 | 0 | 6.8 | 190 | 0 | 0 | 268 | 62 | 220 | 0 | 488 | 1190 | 17 | 7084.13 | 14183.65 | 75.73
14:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 34 | 128 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 415 | 0 | 0 | 300 | 192 | 0 | 18 | 142 | 20 | 21 | 0 | 495 | 94 | 16 | 42 | 0 | 5 | 0 | 0 | 0 | 12 | 12 | 1.77 | 59 | 17 | 0 | 1135 | 48 | 0 | 50 | 25.5 | 0 | 213 | 0 | 0 | 0 | 580 | 12 | 48 | 0 | 250 | 290 | 220 | 51 | 0 | 202 | 20 | 34 | 0 | 17 | 0 | 19 | 17 | 180 | 8 | 58 | 0 | 300 | 0 | 342 | 28 | 0 | 138 | 11 | 22 | 0 | 41 | 30 | 143 | 0 | 102 | 0 | 49 | 5 | 78 | 0 | 1.6 | 30.74 | 0 | 6972.61 | 928 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69 | 1008 | 0 | 0 | 0 | 1482 | 0 | 39 | 0 | 35 | 35 | 0 | 0 | 11 | 0 | 34.08 | 94 | 0 | 0 | 55.45 | 0 | 0 | 186 | 0 | 192 | 0 | 360 | 0 | 5.12 | 0 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 6.7 | 162 | 0 | 0 | 269 | 62 | 180 | 0 | 434 | 1190 | 17 | 6988.35 | 13960.96 | 75.7
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 34 | 137 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 370 | 0 | 0 | 295 | 196 | 0 | 8 | 142 | 20 | 0 | 0 | 510 | 95 | 16 | 43 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.02 | 59 | 17 | 0 | 1135 | 43 | 0 | 50 | 25.5 | 0 | 213 | 0 | 0 | 0 | 612 | 8 | 46 | 0 | 220 | 290 | 220 | 51 | 0 | 211 | 20 | 34 | 0 | 17 | 0 | 19 | 17 | 182 | 8 | 45 | 0 | 305 | 0 | 316 | 28 | 0 | 145 | 9 | 22 | 0 | 41 | 30 | 145 | 0 | 102 | 0 | 58 | 1.08 | 68 | 0 | 0.8 | 3.79 | 0 | 6841.19 | 929 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 71 | 1003 | 0 | 0 | 0 | 1449 | 0 | 39 | 0 | 35 | 35 | 0 | 0 | 13 | 0 | 20.56 | 31 | 0 | 0 | 18.18 | 0 | 0 | 190 | 0 | 190 | 0 | 379 | 0 | 1.5 | 0 | 0 | 70 | 19 | 0 | 0 | 0 | 0 | 3.1 | 132 | 0 | 0 | 255 | 62 | 220 | 0 | 471 | 1175 | 17 | 6866.34 | 13707.53 | 75.8
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 48 | 149 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 410 | 0 | 0 | 304 | 196 | 0 | 4 | 142 | 20 | 15 | 0 | 520 | 96 | 16 | 44 | 0 | 0 | 0 | 8 | 0 | 12 | 12 | 0.95 | 61 | 17 | 0 | 1135 | 48 | 0 | 50 | 25.5 | 0 | 216 | 0 | 0 | 0 | 612 | 4 | 46 | 0 | 220 | 290 | 220 | 51 | 0 | 204 | 20 | 34 | 0 | 17 | 0 | 19 | 17 | 180 | 8 | 9 | 0 | 300 | 0 | 320 | 28 | 0 | 148 | 5 | 24 | 0 | 41 | 30 | 144 | 0 | 101 | 0 | 58 | 1.04 | 68 | 0 | 0.7 | 1.6 | 0 | 6903.79 | 930 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 1039 | 0 | 0 | 0 | 1432 | 0 | 39 | 0 | 35 | 35 | 0 | 0 | 13 | 0 | 6.33 | 53 | 0 | 0 | 3.26 | 0 | 0 | 190 | 0 | 190 | 0 | 387 | 0 | 0.1 | 0 | 33 | 70 | 15 | 0 | 0 | 0 | 0 | 2.6 | 47 | 0 | 0 | 280 | 62 | 220 | 0 | 493 | 1160 | 17 | 6805.29 | 13709.08 | 75.8
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 54 | 149 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 420 | 0 | 17 | 300 | 137 | 0 | 2 | 142 | 20 | 21 | 0 | 510 | 95 | 16 | 43 | 0 | 0 | 0 | 8 | 0 | 12 | 12 | 0.67 | 65 | 17 | 5 | 1135 | 48 | 0 | 50 | 25.5 | 5 | 216 | 0 | 0 | 0 | 612 | 3 | 46 | 0 | 220 | 290 | 220 | 51 | 0 | 195 | 20 | 34 | 0 | 17 | 4 | 19 | 17 | 172 | 8 | 16 | 7 | 305 | 0 | 307 | 28 | 0 | 142 | 2 | 25 | 0 | 51 | 30 | 146 | 0 | 101 | 0 | 58 | 2.43 | 68 | 0 | 0.3 | 4.49 | 0 | 6879.39 | 929 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 1040 | 0 | 0 | 0 | 1404 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 13 | 0 | 0.98 | 2 | 26 | 0 | 1.83 | 0 | 0 | 180 | 0 | 160 | 0 | 372 | 0 | 0.2 | 0 | 42 | 95 | 8 | 25 | 0 | 0 | 0 | 2.1 | 30 | 0 | 0 | 225 | 62 | 220 | 0 | 451 | 1120 | 17 | 6581.11 | 13460.5 | 75.9
18:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 12 | 72 | 149 | 81 | 15 | 35 | 72 | 0 | 0 | 0 | 330 | 0 | 35 | 301 | 138 | 0 | 1 | 142 | 20 | 21 | 0 | 510 | 95 | 16 | 44 | 0 | 0 | 0 | 12 | 5 | 12 | 12 | 0.22 | 67 | 17 | 8 | 1135 | 53 | 0 | 50 | 25.5 | 34 | 216 | 0 | 0 | 0 | 612 | 1 | 45 | 0 | 220 | 290 | 220 | 51 | 0 | 201 | 20 | 34 | 0 | 57 | 26 | 19 | 17 | 84 | 8 | 4 | 7 | 305 | 0 | 307 | 28 | 0 | 145 | 0 | 25 | 0 | 52 | 30 | 145 | 0 | 101 | 0 | 58 | 0.9 | 67 | 0 | 0 | 1.65 | 0 | 6976.27 | 929 | 0 | 0 | 21 | 20 | 38 | 0 | 0 | 0 | 0 | 32 | 2 | 1040 | 0 | 0 | 0 | 1429 | 0 | 41 | 0 | 35 | 35 | 0 | 0 | 26 | 0 | 0.08 | 0 | 26 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 396 | 0 | 0 | 0 | 31 | 95 | 4 | 31 | 0 | 0 | 0 | 0.6 | 4 | 0 | 0 | 230 | 62 | 220 | 0 | 475 | 1102 | 17 | 6621.68 | 13597.95 | 75.9
19:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 92 | 149 | 81 | 15 | 35 | 108 | 0 | 0 | 0 | 345 | 0 | 35 | 303 | 199 | 0 | 0 | 142 | 20 | 21 | 0 | 510 | 96 | 16 | 79 | 0 | 0 | 50 | 15 | 22 | 12 | 12 | 0 | 69 | 17 | 6 | 1135 | 50 | 0 | 50 | 25.5 | 34 | 216 | 0 | 0 | 0 | 612 | 0 | 46 | 0 | 220 | 290 | 220 | 51 | 0 | 217 | 30 | 40 | 0 | 102 | 29 | 6 | 17 | 124 | 8 | 0 | 16 | 305 | 0 | 307 | 28 | 0 | 148 | 0 | 25 | 0 | 83 | 30 | 142 | 0 | 101 | 1.8 | 68 | 0 | 86 | 0 | 0 | 0 | 0 | 7406.3 | 929 | 0 | 0 | 29 | 53 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1040 | 0 | 0 | 0 | 1449 | 0 | 40 | 0 | 35 | 35 | 0 | 91 | 26 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 192 | 0 | 162 | 0 | 401 | 0 | 0 | 0 | 36 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 498 | 1150 | 17 | 7012 | 14418.3 | 75.9
19:30 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 149 | 149 | 85 | 15 | 35 | 108 | 0 | 0 | 0 | 450 | 0 | 35 | 298 | 138 | 0 | 0 | 142 | 20 | 21 | 0 | 502 | 95 | 16 | 78 | 0 | 0 | 50 | 15 | 54 | 12 | 12 | 0 | 70 | 17 | 7 | 1135 | 51 | 0 | 50 | 25.5 | 34 | 217 | 0 | 0 | 0 | 612 | 0 | 46 | 0 | 220 | 290 | 220 | 51 | 0 | 201 | 30 | 90 | 0 | 104 | 37 | 16 | 17 | 158 | 8 | 0 | 16 | 305 | 0 | 313 | 28 | 0 | 140 | 0 | 23 | 0 | 83 | 30 | 143 | 0 | 101 | 17 | 68 | 0 | 86 | 0 | 0 | 0 | 0 | 7632.5 | 929 | 0 | 0 | 25 | 50 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1046 | 0 | 0 | 0 | 1405 | 0 | 40 | 0 | 35 | 35 | 0 | 91 | 26 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 193 | 0 | 190 | 0 | 387 | 0 | 0 | 0 | 36 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 180 | 0 | 475 | 1222 | 17 | 6991 | 14623.5
20:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 148 | 149 | 97 | 15 | 35 | 108 | 0 | 0 | 0 | 460 | 0 | 55 | 300 | 138 | 0 | 0 | 142 | 19 | 21 | 0 | 510 | 94 | 16 | 78 | 0 | 4 | 50 | 15 | 54 | 12 | 12 | 0 | 71 | 17 | 14 | 1135 | 51 | 0 | 50 | 25.5 | 34 | 217 | 0 | 0 | 0 | 612 | 0 | 48 | 0 | 220 | 290 | 220 | 51 | 0 | 199 | 30 | 85 | 0 | 103 | 37 | 19 | 30 | 156 | 8 | 0 | 16 | 300 | 0 | 313 | 28 | 0 | 143 | 0 | 23 | 0 | 83 | 30 | 144 | 0 | 101 | 17 | 68 | 0 | 87 | 0 | 0 | 0 | 0 | 7701.5 | 929 | 0 | 0 | 25 | 48 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1047 | 0 | 0 | 0 | 1408 | 0 | 40 | 0 | 35 | 35 | 0 | 91 | 28 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 193 | 0 | 190 | 0 | 387 | 0 | 0 | 0 | 40 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 457 | 1222 | 17 | 7021 | 14722.5 | 76
21:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 149 | 149 | 97 | 15 | 35 | 108 | 0 | 0 | 0 | 535 | 0 | 35 | 307 | 199 | 0 | 0 | 142 | 19 | 21 | 0 | 510 | 99 | 16 | 79 | 0 | 8 | 50 | 15 | 54 | 12 | 12 | 0 | 72 | 17 | 18 | 1135 | 51 | 0 | 50 | 25.5 | 34 | 217 | 0 | 0 | 0 | 612 | 0 | 125 | 0 | 280 | 290 | 220 | 51 | 0 | 204 | 30 | 89 | 0 | 103 | 37 | 19 | 52 | 162 | 8 | 0 | 16 | 305 | 0 | 313 | 28 | 0 | 152 | 0 | 23 | 0 | 83 | 30 | 145 | 0 | 101 | 17 | 68 | 0 | 103 | 0 | 0 | 0 | 0 | 8028.5 | 930 | 0 | 0 | 25 | 43 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1042 | 0 | 0 | 0 | 1451 | 0 | 40 | 0 | 35 | 35 | 0 | 91 | 28 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 193 | 0 | 190 | 0 | 404 | 0 | 0 | 0 | 34 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 513 | 1222 | 17 | 7122 | 15150.5 | 76.04
22:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 73 | 149 | 97 | 15 | 35 | 108 | 0 | 0 | 0 | 550 | 0 | 35 | 302 | 135 | 0 | 0 | 142 | 19 | 22 | 0 | 510 | 106 | 16 | 78 | 0 | 4 | 50 | 15 | 54 | 12 | 12 | 0 | 74 | 17 | 21 | 1135 | 51 | 0 | 50 | 25.5 | 34 | 217 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 300 | 290 | 220 | 51 | 0 | 217 | 10 | 72 | 0 | 103 | 37 | 19 | 52 | 162 | 8 | 0 | 16 | 305 | 0 | 324 | 28 | 0 | 152 | 0 | 23 | 0 | 52 | 30 | 143 | 0 | 101 | 17 | 68 | 0 | 117 | 0 | 0 | 0 | 0 | 7901.5 | 929 | 0 | 0 | 25 | 45 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1043 | 0 | 0 | 0 | 1448 | 0 | 40 | 0 | 35 | 35 | 0 | 91 | 28 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 192 | 0 | 190 | 0 | 401 | 0 | 0 | 0 | 37 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 511 | 1222 | 17 | 7118 | 15019.5 | 76.08
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 149 | 97 | 15 | 35 | 108 | 0 | 0 | 0 | 560 | 0 | 35 | 315 | 135 | 0 | 0 | 142 | 19 | 22 | 0 | 540 | 107 | 16 | 79 | 0 | 6 | 50 | 0 | 17 | 12 | 12 | 0 | 74 | 17 | 27 | 1135 | 50 | 0 | 50 | 25.5 | 34 | 217 | 0 | 0 | 0 | 612 | 0 | 43 | 0 | 270 | 290 | 220 | 51 | 0 | 211 | 10 | 69 | 0 | 103 | 10 | 19 | 52 | 166 | 8 | 0 | 8 | 310 | 0 | 335 | 28 | 0 | 153 | 0 | 23 | 0 | 52 | 30 | 85 | 0 | 102 | 17 | 69 | 0 | 117 | 0 | 0 | 0 | 0 | 7621.5 | 929 | 0 | 0 | 25 | 45 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1000 | 0 | 0 | 0 | 1462 | 0 | 40 | 0 | 35 | 35 | 0 | 91 | 28 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 189 | 0 | 191 | 0 | 403 | 0 | 0 | 0 | 38 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 513 | 1222 | 17 | 7092 | 14713.5 | 76.1
Total KWH | 0 | 619200 | 121920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259200 | 50760 | 1061568 | 3289920 | 1309745 | 379361 | 530771 | 799200 | 0 | 0 | 0 | 11858726 | 0 | 270426 | 7455349 | 4230000 | 0 | 174104 | 3333600 | 475200 | 492480 | 0 | 12343181.82 | 2343491 | 386400 | 1076160 | 0 | 105120 | 343708 | 86256 | 358139 | 297600 | 288960 | 24840 | 1682560 | 429891 | 360960 | 27207272.73 | 1242836 | 0 | 832800 | 578853 | 226655 | 5311523 | 0 | 0 | 0 | 14312726 | 103005 | 976873 | 0 | 5880500 | 7377700 | 5454000 | 1262880 | 0 | 5001000 | 618480 | 697920 | 0 | 894720 | 252840 | 461980 | 589380 | 3706560 | 313142 | 401245 | 336960 | 7380000 | 0 | 7996000 | 669000 | 0 | 3539700 | 54351 | 528744 | 0 | 1165440 | 705504 | 3122600 | 0 | 2431460 | 77400 | 1296000 | 77857 | 1586400 | 0 | 11000 | 200470 | 20640 | 171743213.55 | 22447273 | 0 | 0 | 353760 | 749696 | 912000 | 0 | 0 | 0 | 0 | 242928 | 468000 | 25381810 | 594720 | 0 | 0 | 35216626 | 0 | 858984 | 0 | 409824 | 550176 | 0 | 520720 | 213998 | 328507 | 294624 | 645410 | 232595 | 0 | 285600 | 0 | 0 | 4685055 | 0 | 4771436 | 0 | 9394036 | 0 | 29880 | 0 | 762763 | 2100053 | 184202 | 441974 | 0 | 0 | 0 | 48658.8 | 864000 | 3555 | 210528 | 6916000 | 1516000 | 5341160 | 0 | 11810909 | 28900363.64 | 448800 | 169136624.44 | 340879837.99

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 16-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-06-2026 | during | 16-06-2026 | during | 16-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 412 | 412 | 0 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 193 | 199 | 210 | 210 | 170 | 170 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 309 | 307 | 335 | 335 | 310 | 310 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 17 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 110 | 149 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 4 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 19 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 25 | 52.19 | 52.19 | 8 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 97 | 300 | 300 | 33 | 80 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 24 | 149 | 149 | 149 | 35 | 72 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 35 | 105 | 105 | 17 | 34 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 515 | 510 | 584 | 584 | 530 | 530 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 520 | 535 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 123 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2038 | 2398 | 5818.22 | 5792.22 | 2084.06 | 2774.06
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 11 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 49 | 50 | 50 | 50 | 6 | 6 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 76 | 72 | 76 | 76 | 76 | 76 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 0 | 34 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 15 | 8 | 8 | 8 | 8 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 18 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 38 | 79 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.18 | 0 | 4.25 | 0 | 4.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 54 | 54.36 | 54.36 | 17 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 110 | 110 | 17 | 17 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 96 | 99 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 49 | 51 | 163 | 163 | 50 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 582 | 612 | 1224 | 1224 | 612 | 612 | Unit1 Under Maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 8 | 12 | 8 | 12 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1135 | 1135 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2338.68 | 2576.5 | 3944.11 | 3992.86 | 2371.75 | 2605.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 198 | 204 | 221.25 | 221.25 | 205 | 205 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 290 | 350.01 | 350.01 | 290 | 290 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 220 | 220 | 342.01 | 342.01 | 220 | 220 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 250 | 280 | 393 | 393 | 220 | 220 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 30 | 41.65 | 41.65 | 38 | 38 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 48 | 125 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 16 | 23 | 23 | 23 | 23 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 103 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 160 | 162 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 7.33 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 52 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 17 | 37 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 89 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 25 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1348 | 1686 | 2723.27 | 2679.44 | 1554.7 | 1722.7
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-06-2026 | during | 16-06-2026 | during | 16-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 20.57 | 0 | 17 | 0 | 17 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 25 | 25 | Gas shortage
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.9 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 103 | 70 | 90 | 70 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 23.49 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 142.96 | 188 | 480.7 | 446.5 | 219.2 | 202
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 28 | 28 | 28 | 28 | 28 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 143 | 152 | 163 | 163 | 163 | 163 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 145 | 145 | 145 | 145 | 145 | 145 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 83 | 83 | 83 | 41 | 41 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 101 | 102 | 102 | 102 | 102 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 22 | 23 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 332 | 313 | 320 | 320 | 320 | 320 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1145 | 1180 | 1267 | 1267 | 1181 | 1181
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 929 | 930 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 25 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 28 | 43 | 50 | 50 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 105 | 105 | 32 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 92 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1100 | 1042 | 510 | 510 | 1140 | 1140 | U#1 Under Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2187 | 2110 | 2868 | 2778 | 2344 | 2254
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 513 | 513 | 520 | 520 | 520 | 520 | AGC, Unit1 Under Maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 0 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 64 | 63 | 65 | 65 | 65 | 65 | STG Under Maintenance
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1180 | 1222 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 36 | 17 | 150 | 150 | 17 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 276 | 307 | 307 | 307 | 307 | 307 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2289 | 2358 | 2617 | 2616 | 2314 | 2347
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 17.49 | 0 | 54 | 0 | 54 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 31 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 24 | 24 | 24 | 24 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 193 | 193 | 220 | 220 | 200 | 200 | Gas Restrction
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 194 | 190 | 220 | 220 | 200 | 200 | Gas Restrction
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 394 | 404 | 413.79 | 413.79 | 400 | 400 | AGC
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 22 | 22 | 22 | 22 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 0 | 52.2 | 52.2 | 16 | 52 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 91 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 35 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.15 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1486 | 1451 | 1435.88 | 1435.88 | 1356 | 1356 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.48 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2515.12 | 2491 | 2998.47 | 2777.87 | 2548.6 | 2456
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 45 | 34 | 43 | 43 | 40 | 40 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 35 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.1 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 109 | 0 | 159.09 | 0 | 159.09 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 244.1 | 163 | 486.09 | 291 | 385.09 | 190
System Total |  |  |  |  | 28843.2 | 29290.237 | 14247.86 | 15150.5 | 23202.86 | 22640.89 | 15002.4 | 15732.26
Forecast Scenario (16-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14250 |  | 1910 |  | 16246
|  |  |  | 1:00 | 14000 |  | 2170 |  | 16260
|  |  |  | 2:00 | 13950 |  | 2110 |  | 16150
|  |  |  | 3:00 | 13740 |  | 2070 |  | 15900
|  |  |  | 4:00 | 13670 |  | 2040 |  | 15800
|  |  |  | 5:00 | 13550 |  | 1960 |  | 15600
|  |  |  | 6:00 | 13400 |  | 1920 |  | 15400
|  |  |  | 7:00 | 13400 |  | 1630 |  | 15100
|  |  |  | 8:00 | 13350 |  | 1580 |  | 15000
|  |  |  | 9:00 | 13800 |  | 1440 |  | 15300
|  |  |  | 10:00 | 13900 |  | 2074 |  | 15567
|  |  |  | 11:00 | 14170 |  | 1800 |  | 16055
|  |  |  | 12:00 | 14300 |  | 1850 |  | 16237
|  |  |  | 13:00 | 14260 |  | 1900 |  | 16250
|  |  |  | 14:00 | 14160 |  | 1700 |  | 15940
|  |  |  | 15:00 | 14060 |  | 1400 |  | 15526
|  |  |  | 16:00 | 13920 |  | 1050 |  | 15010
|  |  |  | 17:00 | 13930 |  | 1100 |  | 15082
|  |  |  | 18:00 | 14000 |  | 1200 |  | 15257
|  |  |  | 18:30 | 14300 |  | 1300 |  | 15661
|  |  |  | 19:00 | 14490 |  | 1090 |  | 15620
|  |  |  | 19:30 | 14600 |  | 1740 |  | 16420
|  |  |  | 20:00 | 14800 |  | 1230 |  | 16080
|  |  |  | 21:00 | 15150 |  | 1380 |  | 16590
|  |  |  | 22:00 | 14900 |  | 1340 |  | 16300
|  |  |  | 23:00 | 14800 |  | 1780 |  | 16660
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 14640.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16590.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15150.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 320.74 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:50 hrs on 16-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 15-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14247.86 | MW | 11:00 Hr. | Energy Generated |  |  | 340.8798 |  | MKWHr.
| Day Peak Demand |  |  | 15542.8 | MW | 12:00 Hr. | Energy Unserverd |  |  | 30.837 |  | MKWHr.
| Evening Peak Generation |  |  | 15150.5 | MW | 21:00 Hr. | Energy Demand |  |  | 371.7168 |  | MKWHr.
| Evening Peak Demand |  |  | 16930.5 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.7 |  | °C
| Minimum Generation of the Day |  |  | 13460.5 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 892.79 |  | MMCFD
| Maximum Generation of the Day |  |  | 15150.5 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.6121 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 36.8549 | 0 | 12.0257 | 0 | 0 | 0.1741 | 0 | 0 | 49.0547 | Gas | 121.8301 | Gas | 431452864.3194
| Chattogram Zone |  |  | 5.6725 | 41.52 | 8.4917 | 0 | 1.6826 | 0.12784 | 0 | 0.10512 | 57.5998 | Coal | 115.2918 | Coal | 765233272.9409
| Cumilla Zone |  |  | 26.0565 | 0 | 4.0618 | 0 | 0 | 0.40125 | 3.7066 | 0 | 34.2262 | HFO | 35.817 | HFO | 630207526.85
| Mymensingh Zone |  |  | 0 | 0 | 2.9804 | 0 | 0 | 0.28933 | 0 | 0 | 3.2698 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.5384 | 0 | 0 | 0 | 0 | 0.054351 | 0 | 0 | 27.5928 | Hydro | 1.6826 | Hydro | 168256
| Khulna Zone |  |  | 0 | 25.3818 | 1.9411 | 0 | 0 | 0.468 | 23.3593 | 0 | 51.1502 | Solar | 3.8708 | Solar | 60410380.076
| Barishal Zone |  |  | 6.8572 | 47.6273 | 0.65933 | 0 | 0 | 0.003555 | 0 | 0 | 55.1473 | Import | 62.2825 | Import | 364904620.88
| Rajshahi Zone |  |  | 18.8505 | 0 | 3.1148 | 0 | 0 | 1.2555 | 35.2166 | 0 | 58.4375 | Wind | 0.10512 | Wind | 1546315.2
| Rangpur Zone |  |  | 0 | 0.76276 | 2.542 | 0 | 0 | 1.0969 | 0 | 0 | 4.4017
| Total |  |  | 121.8301 | 115.2918 | 35.817 | 0 | 1.6826 | 3.8708 | 62.2825 | 0.10512 | 340.8798
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 431452864.3194 |  | Hydro | 168256
|  |  |  | Coal | 765233272.9409 |  | Solar | 60410380.076
|  |  |  | HFO | 630207526.85 |  | Import | 364904620.88
|  |  |  | HSD | 0 |  | Wind | 1546315.2
[5 empty] | Total: | 225,39,23,236 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.4473 | Peak Hr Flow | 930.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 54801709.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 35.2166 | Peak Hr Flow | 1451.00 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2245 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.7066 | Peak Hr Flow | 162.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2887 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 61.3705 | Peak Hr Flow | 2543.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 250 |  | 5797
|  |  |  | Chattogram |  | 120 |  | 1580
|  |  |  | Cumilla |  | 245 |  | 1613
|  |  |  | Mymensingh |  | 314 |  | 1408
|  |  |  | Sylhet |  | 81 |  | 652
|  |  |  | Khulna |  | 210 |  | 2016
|  |  |  | Barishal |  | 93 |  | 515
|  |  |  | Rajshahi |  | 209 |  | 1602
|  |  |  | Rangpur |  | 181 |  | 1118
|  |  |  | Total |  | 1703 |  | 16301
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 350
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:00 |  | Kushtia 132/33kV S/S 132 KV Bus-B Project Work S/D Due to DWZTGE প্রকল্পের আওতায়
কুষ্টিয়া-মেহেরপুর বে এর কাজের জন্য বাস A থেকে B তে শিফট
|  | 08:48 | Hasnabad 230/132kV S/S AUTO TR-1 LT is restored.
|  | 08:48 | Hasnabad 230/132kV S/S AUTO TR-1 HT is restored.
|  | 09:29 | Haripur 230/132kV S/S EGCB 412MW is restored.
| 11:00 |  | Day Peak Generation is 14247 MW.
|  | 12:48 | Tongi 230/132/33kV S/S Tongi-Tongi 80 MW PS is restored.
| 12:57 | 13:59 | Goalpara- Khulna (C) 132kV Ckt-2 Tripped from Khulna (C) end showing Distance relays Due
to Heavy rsin fall & thundering and from Goalpara 132/33kV end showing Distance relay
relays Due to Thunderstorme
| 14:08 | 14:44 | Barishal(N)-Madaripur 132 kV Ckt-1 Tripped from Barishal 230/132kV end showing REL650
relays.
| 14:28 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Tripped from Ishurdi 230/132kV end showing Distance
protection relay relays.
| 14:46 | 15:01 | Bhandaria 132/33kV S/S Transformer-2 LT Tripped showing 50 O/C DMT relays Due to Bamna | [7 empty] | 28.0MW load
|  |  | pbs 33 kv feeder fault | [7 empty] | interrup.
| 14:46 | 15:01 | Bhandaria 132/33kV S/S Transformer-1 LT Tripped showing 50 o/c DMT trip relays Due to 33 | [7 empty] | 28.0MW load
|  |  | kv Bamna feeder fault | [7 empty] | interrup.
| 15:01 | 17:06 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Maintenance work of source DS of 33 kV | [7 empty] | 45.0MW load
|  |  | Nobogram Feeder by Jhalokathi PBS. | [7 empty] | interrup.
| 15:01 | 17:04 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Maintenance work of source DS of 33 kV | [7 empty] | 45.0MW load
|  |  | Nobogram Feeder by Jhalokathi PBS. | [7 empty] | interrup.
| 15:33 |  | Barapukuria PS unit-1 was synchronized.
| 15:37 | 17:07 | Goalpara- Khulna (C) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to Y phase
current missing DS & CB Goalpara ckt 1
| 17:27 | 18:33 | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to 4 incomer 33kv CT Nut bolt titining
work purpose
| 17:27 | 18:35 | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to T-4 incomer 33kv CT Nut bolt titining
work purpose.
| 21:00 |  | Evening Peak Generation is 15150 MW
| 05:45 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- U1
| 05:46 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- Unit-2 (False sms)
| 05:46 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- Unit-2
| 06:05 | 06:23 | Cumilla(S) 132/33kV S/S TR-4 LT Tripped showing Do relays Due to same as Tr-03 | [7 empty] | 42.0MW load
interrup.
| 06:05 | 06:23 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing REF615, RET650 relays Due to PDB | [7 empty] | 43.0MW load
|  |  | Donaitori feeder fault | [7 empty] | interrup.
| 07:30 |  | Lakshmipur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to 33kV Load Side Redhot Work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 15-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 379361 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 199 | 4230000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 307 | 7455349 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 259200 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 149 | 3289920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 530771 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270426 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 475200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 492480 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 121920 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 97 | 1309745 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1061568 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 35 | 619200 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 799200 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 174104 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 50760 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 510 | 12343181.82 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 535 | 11858726 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3333600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2398 | 49054711.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 578853 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 103005 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 832800 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 72 | 1682560 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5311523 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 226655 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 15 | 86256 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 343708 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 297600 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 360960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 79 | 1076160 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24840 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 386400 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54 | 358139 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 429891 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 288960 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 99 | 2343491 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 51 | 1242836 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14312726 | Unit1 Under Maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 105120 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1135 | 27207272.73 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2576.5 | 57599755.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 204 | 5001000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7377700 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 220 | 5454000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 280 | 5880500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 30 | 618480 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1262880 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 125 | 976873 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 16 | 336960 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 103 | 894720 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 162 | 3706560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 313142 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 461980 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 589380 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 37 | 252840 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 697920 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 401245 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1686 | 34226180
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 77857 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Gas shortage
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 103 | 1586400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1296000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 200470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 20640 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 77400 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 188 | 3269767
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 54351 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 669000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3539700 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 145 | 3122600 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 705504 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1165440 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2431460 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 528744 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7380000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 313 | 7996000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1180 | 27592799
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 930 | 22447273 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 353760 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 43 | 749696 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 594720 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 242928 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 468000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1042 | 25381810 | machine problem
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2110 | 51150187
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 513 | 11810909 | AGC, Unit1 Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 210528 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 63 | 1516000 | STG Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1222 | 28900363.64 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5341160 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 448800 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6916000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3555 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2358 | 55147315.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 294624 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 858984 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 213998 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 193 | 4685055 | Gas Restrction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 190 | 4771436 | Gas Restrction
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 404 | 9394036 | AGC
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 232595 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 328507 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 91 | 520720 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 550176 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 409824 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29880 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1451 | 35216626 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 285600 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 645410 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2491 | 58437471
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 34 | 762763 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 441974 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 48658.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 2100053 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 184202 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 864000 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 163 | 4401650.8
Eastern Grid Total |  |  |  |  | 17438.042 | 8028.5 | 171743213.55
Western Grid Total |  |  |  |  | 11852.195 | 7122 | 169136624.44
National Grid Total |  |  |  |  | 29290.237 | 15150.5 | 340879837.99
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 15-06-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10083.67 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4558 | MW
i) Dhaka area |  |  | 5546.97 |  | MW | i) Khulna area |  |  |  | 1806 | MW
ii) Chattogram area |  |  | 1503.7 |  | MW | ii) Barishal area |  |  |  | 421.6 | MW
iii) Cumilla area |  |  | 1368 |  | MW | iii) Rajshahi area |  |  |  | 1393.4 | MW
iv) Mymensingh area |  |  | 1094 |  | MW | iv) Rangpur area |  |  |  | 937 | MW
v) Sylhet area |  |  | 571 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14641.67 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Hasnabad | 85 | 15:00 | 133 | Natore | 151 | 06:00
2 | AKSML | 135 | 23:00 | 68 | Hathazari | 92 | 20:00 | 134 | Nawabganj | 57.8 | 02:00
3 | Aftabnagar | 46 | 13:00 | 69 | Hatirjheel | 51 | 12:00 | 135 | Netrakona | 132 | 22:00
4 | Agargaon | 133 | 13:00 | 70 | Ishurdi | 82 | 11:00 | 136 | New | 86 | 10:00
5 | Agrabad | 72 | 14:00 | 71 | Jaldhaka | 68 | 21:00 | 137 | Niamatpur | 74 | 21:00
6 | Amnura | 33 | 00:00 | 72 | Jamalpur | 105 | 18:30 | 138 | Noapara | 47 | 06:00
7 | Ashuganj | 90 | 23:00 | 73 | Jashore | 162 | 00:00 | 139 | PHP | 14 | 10:00
8 | BSRM | 205 | 18:30 | 74 | Jhenaidah | 114 | 21:00 | 140 | Pabna | 101 | 01:00
9 | Bagerhat | 87 | 06:00 | 75 | Joydebpur | 156 | 10:00 | 141 | Palashbari | 124 | 19:30
10 | Bajitpur | 87 | 06:00 | 76 | Joypurhat | 64 | 19:00 | 142 | Panchagarh | 69 | 20:00
11 | Bakerganj | 13.6 | 21:00 | 77 | Juldah | 15 | 12:00 | 143 | Patiya | 12 | 23:00
12 | Bakulia | 101 | 19:30 | 78 | KSRM | 27 | 18:30 | 144 | Patuakhali | 61.5 | 15:00
13 | Banani | 62.4 | 13:00 | 79 | Kabirpur | 261 | 18:00 | 145 | Payra | 32 | 23:00
14 | Bangabhaban | 22 | 10:00 | 80 | Kachua | 84 | 06:00 | 146 | Postogola | 64 | 13:00
15 | Barapukuria | 61 | 19:00 | 81 | Kaliganj | 20 | 00:00 | 147 | Pubail | 27 | 21:00
16 | Barguna | 24 | 01:00 | 82 | Kallyanpur | 123 | 13:00 | 148 | Purbachal | 38 | 13:00
17 | Barishal | 109 | 12:00 | 83 | Kalurghat | 40 | 16:00 | 149 | Purbasadipur | 135 | 23:00
18 | Barishal-230 | 98 | 06:00 | 84 | Kamrangirchar | 84 | 13:00 | 150 | Rahanpur | 38 | 06:00
19 | Baroaulia | 70 | 11:00 | 85 | Kaptai | N/A | N/A | 151 | Rahim | 36 | 13:00
20 | Baroirhat | 81 | 19:00 | 86 | Kasba | 32 | 01:00 | 152 | Rajbari | 81 | 06:00
21 | Bashundhara | 212 | 13:00 | 87 | Kazla | 117 | 13:00 | 153 | Rajendrapur | 111 | 06:00
22 | BashundharaCement | 12 | 01:00 | 88 | Keranigonj | 83 | 21:00 | 154 | Rajshahi | 125 | 16:00
23 | Beanibazar | 62 | 19:00 | 89 | Khagrachori | 36 | 20:00 | 155 | Rajshahi-230 | 90 | 16:00
24 | Benapole | 66 | 21:00 | 90 | Khulna | 63 | 12:00 | 156 | Ramganj | 100 | 06:00
25 | Bhaluka | 153 | 21:00 | 91 | Khulshi | 201 | 19:30 | 157 | Rampur | 44 | 19:00
26 | Bhandaria | 61 | 14:00 | 92 | Kishoreganj | 123 | 18:30 | 158 | Rangamati | 19 | 19:00
27 | Bhangura | 36 | 07:00 | 93 | Kodda | 315 | 18:00 | 159 | Rangpur | 140 | 21:00
28 | Bheramara(GK) | 70 | 03:00 | 94 | Kulaura | 53 | 21:00 | 160 | Ruppur | 5 | 10:00
29 | Bhulta | 206 | 07:00 | 95 | Kurigram | 58 | 19:00 | 161 | SSM | 5 | 03:00
30 | Bog-Sherpur | 80 | 06:00 | 96 | Kushtia | 160 | 12:00 | 162 | Saidpur | 104 | 11:00
31 | Bogura | 173 | 20:00 | 97 | Laksam | 36 | 23:00 | 163 | Santhia | 40 | 00:00
32 | Borhanuddin | 84 | 22:00 | 98 | Lakshmipur | 39 | 21:00 | 164 | Satkhira | 141 | 15:00
33 | Brahmanbaria | 120 | 20:00 | 99 | Lalbag | 77 | 12:00 | 165 | Satmasjid | 113 | 13:00
34 | Cantonment | 146 | 13:00 | 100 | Lalmonirhat | 50 | 19:00 | 166 | Savar | 210 | 19:00
35 | Chandina | 30 | 19:00 | 101 | MI_Cement | 9.7 | 21:00 | 167 | SevenRings | 17.6 | 01:00
36 | Chandpur | 72 | 05:00 | 102 | Madanganj | 43 | 11:00 | 168 | ShahCement | 23 | 10:00
37 | Chandraghona | 31 | 23:00 | 103 | Madaripur | 106 | 12:00 | 169 | Shahjadpur | 73 | 06:00
38 | Chapai | 78 | 11:00 | 104 | Madartek | 84 | 23:00 | 170 | Shahjibazar | 116 | 00:00
39 | Charsaidpur | 37 | 01:00 | 105 | Madunaghat | 59 | 19:00 | 171 | Shahmirpur | 50 | 19:00
40 | Chauddagram | 70 | 20:00 | 106 | Magura | 66 | 21:00 | 172 | Shariatpur | 84 | 15:00
41 | Chhatak | 32 | 02:00 | 107 | Mahasthangarh | 75 | 05:00 | 173 | Sherpur | 136 | 19:00
42 | Chowmuhani | 155 | 19:00 | 108 | Maijdee | 37 | 03:00 | 174 | Shikalbaha | 28 | 10:00
43 | Chuadanga | 122 | 04:00 | 109 | Manikganj | 135 | 21:00 | 175 | Shitalakhya | 92.9 | 15:00
44 | Coxsbazar | 134 | 18:30 | 110 | Maniknagar | 82 | 13:00 | 176 | Sholosohor | 48 | 19:00
45 | Cumilla(N) | 115 | 22:00 | 111 | Matarbari | 51 | 19:00 | 177 | Shomvuganj | 18 | 02:00
46 | Cumilla(S) | 181 | 15:00 | 112 | Matuail | 82 | 15:00 | 178 | Shyampur | 170 | 01:00
47 | Daganbhuiyan | 35 | 20:00 | 113 | Metrorail_Motijheel | 22 | 17:00 | 179 | Siddhirganj | 131 | 12:00
48 | Daudkandi | 148 | 21:00 | 114 | Metrorail_Uttara | 0 | 00:00 | 180 | Sirajganj | 112 | 00:00
49 | DhakaUniversity | 98 | 13:00 | 115 | Millgate | 109 | 12:00 | 181 | Sonargaon | 132 | 07:00
50 | Dhamrai | 108 | 23:00 | 116 | Mirpur | 164 | 12:00 | 182 | Sreemongol | 84 | 23:00
51 | Dhanmondi | 133 | 13:00 | 117 | Mirsorai | 35 | 09:00 | 183 | Sreepur | 113 | 06:00
52 | Dohazari | 95 | 19:00 | 118 | Mirzapur | 36 | 06:00 | 184 | Srinagar | 49.7 | 19:00
53 | Faridpur | 192 | 20:00 | 119 | Mithapukur | 64 | 21:00 | 185 | Sunamganj | 54 | 14:00
54 | Fatullah | 94 | 15:00 | 120 | Modern | N/A | N/A | 186 | Sylhet | 126 | 15:00
55 | Fenchuganj | 44 | 21:00 | 121 | Mogbazar | 113.1 | 13:00 | 187 | Sylhet_(South) | 48 | 21:00
56 | Feni | 103 | 22:00 | 122 | Mongla | 43 | 01:00 | 188 | TK | 27.5 | 23:00
57 | GPH | 12 | 07:00 | 123 | Motijheel | 56 | 13:00 | 189 | Tangail | 158 | 21:00
58 | Ghatail | 72 | 17:00 | 124 | Muktagacha | 41 | 12:00 | 190 | Taraganj | 24 | 00:00
59 | Ghorashal | 0 | 00:00 | 125 | Munshiganj | 106 | 06:00 | 191 | Tasnim | 35 | 19:30
60 | Ghorashal-230 | 111 | 21:00 | 126 | Muradnagar | 42 | 02:00 | 192 | Thakurgaon | 102 | 19:30
61 | Goalpara | 42 | 00:00 | 127 | Mymensingh | 189 | 19:00 | 193 | Tongi | 162 | 09:00
62 | Gollamari | 114 | 20:00 | 128 | Nabinagar | 98 | 08:00 | 194 | Ullahpara | 36 | 06:00
63 | Gopalganj | 102.3 | 18:30 | 129 | Naogaon | 133 | 04:00 | 195 | Ullon | 57 | 23:00
64 | Gulshan | 146 | 13:00 | 130 | Narail | 57.5 | 07:00 | 196 | Uttara | 106 | 13:00
65 | Halishahar | 109.5 | 15:00 | 131 | Narinda | 76 | 13:00 | 197 | UttaraNew | 57 | 13:00
66 | HaripurSBU | 135 | 08:00 | 132 | Narshingdi | 186 | 21:00 | 198 | Zigatola | 82 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 15-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14561.9 | 2324 |  | 16990.48
1:00 | 14037.5 | 2347 |  | 16490.5
2:00 | 13932.5 | 2239 |  | 16272.5
3:00 | 13889 | 2098 |  | 16081
4:00 | 13868 | 1983 |  | 15940
5:00 | 13723.5 | 1704 |  | 15504.5
6:00 | 13578.76 | 265 |  | 13855.76
7:00 | 13567.49 | 202 |  | 13778.49
8:00 | 13630.64 | 158 |  | 13795.64
9:00 | 13756.5 | 311 |  | 14081.5
10:00 | 14069.1 | 371 |  | 14457.1
11:00 | 14247.86 | 608 |  | 14882.86
12:00 | 14236.55 | 1250 |  | 15542.8
13:00 | 14183.65 | 1565 |  | 15818.65
14:00 | 13960.96 | 1322 |  | 15341.96
15:00 | 13707.53 | 1373 |  | 15142.53
16:00 | 13709.08 | 999 |  | 14753.08
17:00 | 13460.5 | 712 |  | 14204.5
18:00 | 13597.95 | 675 |  | 14303.33
19:00 | 14418.3 | 1552 |  | 16040.14
19:30 | 14623.5 | 1666 |  | 16364.47
20:00 | 14722.5 | 1569 |  | 16362.11
21:00 | 15150.5 | 1703 |  | 16930.5
22:00 | 15019.5 | 1619 |  | 16711.5
23:00 | 14713.5 | 1888 |  | 16686.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 15-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7339.7 | 7222.2 | 14561.9 | DAILY GENERATION CURVE
00:30 | 7213.1 | 7086.6 | 14299.7
01:00 | 7086.5 | 6951 | 14037.5 | 15-06-2026
01:30 | 7028.5 | 6956.5 | 13985
02:00 | 6970.5 | 6962 | 13932.5
02:30 | 6933.25 | 6977.5 | 13910.75
03:00 | 6896 | 6993 | 13889
03:30 | 6857.5 | 7021 | 13878.5
04:00 | 6819 | 7049 | 13868
04:30 | 6774.75 | 7021 | 13795.75
05:00 | 6730.5 | 6993 | 13723.5
05:30 | 6698.205 | 6952.925 | 13651.13
06:00 | 6665.91 | 6912.85 | 13578.76
06:30 | 6626.67 | 6946.455 | 13573.125
07:00 | 6587.43 | 6980.06 | 13567.49
07:30 | 6605.855 | 6993.21 | 13599.065
08:00 | 6624.28 | 7006.36 | 13630.64
08:30 | 6690.61 | 7002.96 | 13693.57
09:00 | 6756.94 | 6999.56 | 13756.5
09:30 | 6803.735 | 7109.065 | 13912.8
10:00 | 6850.53 | 7218.57 | 14069.1
10:30 | 6931.585 | 7226.895 | 14158.48
11:00 | 7012.64 | 7235.22 | 14247.86
11:30 | 7091.19 | 7151.015 | 14242.205
12:00 | 7169.74 | 7066.81 | 14236.55
12:30 | 7134.63 | 7075.47 | 14210.1
13:00 | 7099.52 | 7084.13 | 14183.65
13:30 | 7036.065 | 7036.24 | 14072.305
14:00 | 6972.61 | 6988.35 | 13960.96
14:30 | 6906.9 | 6927.345 | 13834.245
15:00 | 6841.19 | 6866.34 | 13707.53
15:30 | 6872.49 | 6835.815 | 13708.305
16:00 | 6903.79 | 6805.29 | 13709.08
16:30 | 6891.59 | 6693.2 | 13584.79
17:00 | 6879.39 | 6581.11 | 13460.5
17:30 | 6927.83 | 6601.395 | 13529.225
18:00 | 6976.27 | 6621.68 | 13597.95
18:30 | 7191.285 | 6816.84 | 14008.125
19:00 | 7406.3 | 7012 | 14418.3
19:30 | 7632.5 | 6991 | 14623.5
20:00 | 7701.5 | 7021 | 14722.5
20:30 | 7865 | 7071.5 | 14936.5 |  | Executive Engineer
21:00 | 8028.5 | 7122 | 15150.5 |  | Network Operation Division
21:30 | 7965 | 7120 | 15085
22:00 | 7901.5 | 7118 | 15019.5
22:30 | 7761.5 | 7105 | 14866.5
23:00 | 7621.5 | 7092 | 14713.5

## En-Curve
QF-LDC-12
Date | 15-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3122 | 1962 | 903 | 0 | 172 | 1482 | 75 | 4931 | 0 | 619 | 1289.9 | 0 | 0 | 6 | 2324 | DAILY ENERGY CURVE
00:30 | 3135 | 1940 | 916 | 19 | 165 | 1483.5 | 72.5 | 4869 | 0 | 556.5 | 1136.7 | 0 | 0 | 6.5 | 2335.5 | 15-06-2026
01:00 | 3148 | 1918 | 929 | 38 | 158 | 1485 | 70 | 4807 | 0 | 494 | 983.5 | 0 | 0 | 7 | 2347
01:30 | 3159.5 | 1947.5 | 929.5 | 38 | 160 | 1482 | 68.5 | 4803.5 | 0 | 455 | 934.5 | 0 | 0 | 7 | 2293 | Energy Generated | 340.8798 |  | MKWHr
02:00 | 3171 | 1977 | 930 | 38 | 162 | 1479 | 67 | 4800 | 0 | 416 | 885.5 | 0 | 0 | 7 | 2239 | Energy not Served | 30.837 |  | MKWHr
02:30 | 3160 | 1959.75 | 930 | 38 | 160 | 1482 | 67 | 4822.5 | 0 | 415.5 | 866.5 | 0 | 0 | 9.5 | 2168.5 | Total Energy Requirement | 371.7168 |  | MKWHr
03:00 | 3149 | 1942.5 | 930 | 38 | 158 | 1485 | 67 | 4845 | 0 | 415 | 847.5 | 0 | 0 | 12 | 2098
03:30 | 3158 | 1933.5 | 929.5 | 38 | 158 | 1485 | 68.5 | 4872 | 0 | 406.5 | 822 | 0 | 0 | 7.5 | 2040.5
04:00 | 3167 | 1924.5 | 929 | 38 | 158 | 1485 | 70 | 4899 | 0 | 398 | 796.5 | 0 | 0 | 3 | 1983
04:30 | 3122.5 | 1926.75 | 929 | 38 | 155 | 1467.5 | 70.5 | 4891.5 | 0 | 402 | 787.5 | 0 | 0 | 5.5 | 1843.5
05:00 | 3078 | 1929 | 929 | 38 | 152 | 1450 | 71 | 4884 | 0 | 406 | 778.5 | 0 | 0 | 8 | 1704
05:30 | 3081 | 1871 | 929 | 38 | 147 | 1465.5 | 73 | 4861.5 | 16.13 | 411 | 753 | 0 | 0 | 5 | 984.5
06:00 | 3084 | 1813 | 929 | 38 | 142 | 1481 | 75 | 4839 | 32.26 | 416 | 727.5 | 0 | 0 | 2 | 265
06:30 | 3092.5 | 1843.5 | 929 | 38 | 140 | 1483 | 75 | 4836 | 63.875 | 405.5 | 664.75 | 0 | 0 | 2 | 233.5
07:00 | 3101 | 1874 | 929 | 38 | 138 | 1485 | 75 | 4833 | 95.49 | 395 | 602 | 0 | 0 | 2 | 202
07:30 | 3115 | 1871.5 | 929.5 | 38 | 143 | 1488 | 75.5 | 4829 | 136.065 | 378.5 | 591 | 0 | 0 | 4 | 180
08:00 | 3129 | 1869 | 930 | 38 | 148 | 1491 | 76 | 4825 | 176.64 | 362 | 580 | 0 | 0 | 6 | 158
08:30 | 3127.5 | 1876.5 | 929.5 | 38 | 148 | 1487.5 | 76 | 4833 | 222.57 | 355 | 595.5 | 0 | 0 | 4.5 | 234.5
09:00 | 3126 | 1884 | 929 | 38 | 148 | 1484 | 76 | 4841 | 268.5 | 348 | 611 | 0 | 0 | 3 | 311
09:30 | 3110 | 1867.5 | 929.5 | 38 | 149 | 1484 | 76 | 4849 | 393.55 | 348.5 | 665.75 | 0 | 0 | 2 | 341
10:00 | 3094 | 1851 | 930 | 38 | 150 | 1484 | 76 | 4857 | 518.6 | 349 | 720.5 | 0 | 0 | 1 | 371
10:30 | 3135 | 1862.5 | 929.5 | 38 | 155 | 1485 | 76 | 4844 | 515.98 | 364.5 | 752.5 | 0 | 0 | 0.5 | 489.5
11:00 | 3176 | 1874 | 929 | 38 | 160 | 1486 | 76 | 4831 | 513.36 | 380 | 784.5 | 0 | 0 | 0 | 608
11:30 | 3177.5 | 1881.9 | 929 | 38 | 165 | 1484.5 | 74.5 | 4780 | 494.305 | 393 | 820 | 0 | 0 | 4.5 | 929
12:00 | 3179 | 1889.8 | 929 | 38 | 170 | 1483 | 73 | 4729 | 475.25 | 406 | 855.5 | 0 | 0 | 9 | 1250
12:30 | 3148 | 1854.9 | 929.5 | 38 | 171 | 1485 | 69 | 4701.5 | 521.2 | 419 | 863 | 0 | 0 | 10 | 1407.5
13:00 | 3117 | 1820 | 930 | 38 | 172 | 1487 | 65 | 4674 | 567.15 | 432 | 870.5 | 0 | 0 | 11 | 1565
13:30 | 3124.5 | 1761 | 929 | 38 | 176 | 1484.5 | 62 | 4645 | 578.805 | 393 | 872.5 | 0 | 0 | 8 | 1443.5
14:00 | 3132 | 1702 | 928 | 38 | 180 | 1482 | 59 | 4616 | 590.46 | 354 | 874.5 | 0 | 0 | 5 | 1322
14:30 | 3119.5 | 1702.5 | 928.5 | 38 | 181 | 1465.5 | 59 | 4633.5 | 481.745 | 351 | 871.5 | 0 | 0 | 2.5 | 1347.5
15:00 | 3107 | 1703 | 929 | 38 | 182 | 1449 | 59 | 4651 | 373.03 | 348 | 868.5 | 0 | 0 | 0 | 1373
15:30 | 3114.5 | 1735.5 | 929.5 | 38 | 181 | 1440.5 | 60 | 4701.5 | 270.805 | 358 | 879 | 0 | 0 | 0 | 1186
16:00 | 3122 | 1768 | 930 | 38 | 180 | 1432 | 61 | 4752 | 168.58 | 368 | 889.5 | 0 | 0 | 0 | 999
16:30 | 3053 | 1778.5 | 929.5 | 38 | 176 | 1418 | 63 | 4688.5 | 125.79 | 385 | 929.5 | 0 | 0 | 0 | 855.5
17:00 | 2984 | 1789 | 929 | 38 | 172 | 1404 | 65 | 4625 | 83 | 402 | 969.5 | 0 | 0 | 0 | 712
17:30 | 2969.5 | 1747.5 | 929 | 38 | 128 | 1416.5 | 66 | 4625 | 51.225 | 460 | 1098.5 | 0 | 0 | 0 | 693.5
18:00 | 2955 | 1706 | 929 | 38 | 84 | 1429 | 67 | 4625 | 19.45 | 518 | 1227.5 | 0 | 0 | 0 | 675
18:30 | 3038 | 1723 | 929 | 38 | 104 | 1439 | 68 | 4701.5 | 9.725 | 622.5 | 1335.4 | 0 | 0 | 0 | 1113.5
19:00 | 3121 | 1740 | 929 | 38 | 124 | 1449 | 69 | 4778 | 0 | 727 | 1443.3 | 0 | 0 | 0 | 1552
19:30 | 3062 | 1798 | 929 | 38 | 158 | 1405 | 70 | 4833 | 0 | 720 | 1610.5 | 0 | 0 | 0 | 1666
20:00 | 3063 | 1863 | 929 | 38 | 156 | 1408 | 71 | 4820 | 0 | 720 | 1650.5 | 0 | 0 | 4 | 1569
20:30 | 3138.5 | 1909.5 | 929.5 | 38 | 159 | 1429.5 | 71.5 | 4842.5 | 0 | 717.5 | 1695 | 0 | 0 | 6 | 1636
21:00 | 3214 | 1956 | 930 | 38 | 162 | 1451 | 72 | 4865 | 0 | 715 | 1739.5 | 0 | 0 | 8 | 1703
21:30 | 3188.5 | 1950 | 929.5 | 38 | 162 | 1449.5 | 73 | 4866 | 0 | 707 | 1715.5 | 0 | 0 | 6 | 1661
22:00 | 3163 | 1944 | 929 | 38 | 162 | 1448 | 74 | 4867 | 0 | 699 | 1691.5 | 0 | 0 | 4 | 1619
22:30 | 3128.5 | 1970 | 929 | 38 | 164 | 1455 | 74 | 4847 | 0 | 675 | 1581 | 0 | 0 | 5 | 1753.5
23:00 | 3094 | 1996 | 929 | 38 | 166 | 1462 | 74 | 4827 | 0 | 651 | 1470.5 | 0 | 0 | 6 | 1888
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 15-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 158 | 15 | 524 | 120 | 1770 | 486 | Ishurdi-Ghorashal Ckt-1 | Export | 4243709.09
1:00 | 163 | 12 | 534 | 118 | 1794 | 476
2:00 | 160 | 9 | 542 | 114 | 1752 | 466 |  | Import | 0
3:00 | 151 | 3 | 528 | 114 | 1806 | 456
4:00 | 152 | 12 | 529 | 116 | 1762 | 430 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 154 | 15 | 516 | 98 | 1784 | 430
6:00 | 154 | 15 | 500 | 88 | 1698 | 434 |  | Import | 0
7:00 | 153 | 9 | 508 | 86 | 1734 | 440
8:00 | 175 | 25 | 560 | 112 | 1876 | 520 | Sirajganj-Sreepur Ckt-1 | Export | 3391000
9:00 | 193 | 44 | 590 | 150 | 1906 | 570
10:00 | 206 | 49 | 624 | 164 | 1972 | 614 |  | Import | 0
11:00 | 190 | 35 | 588 | 154 | 1972 | 614
12:00 | 191 | 35 | 608 | 160 | 1856 | 610 | Sirajganj-Sreepur Ckt-2 | Export | 3397000
13:00 | 213 | 53 | 654 | 182 | 1936 | 624
14:00 | 203 | 38 | 620 | 140 | 1942 | 608 |  | Import | 0
15:00 | 182 | 34 | 592 | 120 | 1866 | 572
16:00 | 211 | 52 | 660 | 160 | 2016 | 604 | Gopalganj-Aminbazar Ckt-1 | Export | 21880000
17:00 | 209 | 56 | 610 | 150 | 1904 | 600
18:00 | 194 | 54 | 582 | 160 | 1826 | 564 |  | Import | 0
18:30 | 187 | 49 | 594 | 158 | 1832 | 498
19:00 | 190 | 48 | 574 | 128 | 1884 | 482 | Gopalganj-Aminbazar Ckt-2 | Export | 21890000
19:30 | 161 | 32 | 502 | 92 | 1722 | 432
20:00 | 167 | 35 | 494 | 94 | 1608 | 378 |  | Import | 0
21:00 | 151 | 18 | 486 | 112 | 1608 | 378
22:00 | 148 | 12 | 496 | 112 | 1632 | 348 |  | Total Export | 54801709.09
23:00 | 167 | 24 | 554 | 116 | 1716 | 406 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 15-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 377 | 19:30 | 360 | 12:00 | Madunaghat | 394 | 20:00 | 385 | 11:00
Amtali | 407 | 00:00 | 402 | 11:00 | Meghnaghat | 380 | 20:00 | 366 | 10:00
Ashuganj | 407 | 5:00 | 385 | 13:00 | Payra | 409 | 06:00 | 405 | 08:00
Bhulta | 399 | 05:00 | 376 | 12:00 | Rahanpur | 398 | 18:00 | 389 | 12:00
Bibiana | 394 | 19:30 | 384 | 10:00 | Rampal | 395 | 01:00 | 384 | 10:00
BIPTC | 401 | 06:00 | 389 | 15:00
Bogura | 382 | 18:00 | 371 | 12:00
Gopalganj | 389 | 19:30 | 377 | 12:00
Kaliakoir | 370 | 20:00 | 352 | 11:00
Korerhat | 394 | 19:30 | 380 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 04:00 | 213 | 10:00 | Ishurdi | 234 | 18:30 | 220 | 12:00
AKSML | 231.7 | 19:30 | 221.7 | 10:00 | Jhenaidah | 224 | 18:30 | 208 | 12:00
Aminbazar | 226 | 19:30 | 213 | 11:00 | Kachua | 233 | 19:00 | 215 | 10:00
Ashuganj | 228 | 19:30 | 218 | 13:00 | Kaliakoir | 227 | 19:30 | 212 | 10:00
Ashuganj-400 | 228 | 19:30 | 218 | 13:00 | Keranigonj | 225 | 20:00 | 211 | 13:00
Baghabari | 231 | 18:30 | 222 | 11:00 | Khulna(S) | 224 | 18:30 | 212 | 12:00
Barapukuria | 221 | 05:00 | 212 | 07:00 | Korerhat | 226 | 20:00 | 216 | 10:00
Barapukuria-230 | 221 | 05:00 | 212 | 07:00 | Madunaghat | 231 | 01:00 | 225 | 10:00
Barishal | 231 | 19:30 | 224 | 12:00 | Madunaghat-400 | 232 | 20:00 | 226 | 11:00
Bheramara | 233 | 19:30 | 218 | 12:00 | Maniknagar | 228 | 03:00 | 211 | 12:00
Bhulta | 229 | 05:00 | 213 | 12:00 | Meghnaghat | 235 | 03:00 | 221 | 13:00
Bibiana | 229 | 19:30 | 223 | 12:00 | Meghnaghat-400 | 229 | 04:00 | 217 | 13:00
BIPTC | 236 | 19:30 | 219 | 12:00 | Mirsorai | 230 | 20:00 | 222 | 10:00
Bogura | 237 | 17:00 | 230 | 08:00 | Naogaon | 214 | 17:00 | 204 | 12:00
Bogura-400 | 237 | 18:00 | 229 | 12:00 | Purbasadipur | 219 | 01:00 | 210 | 08:00
Borhanuddin | 234 | 19:30 | 229 | 11:00 | Rajshahi | 232 | 18:30 | 217 | 12:00
BSRM | 226 | 20:00 | 217 | 10:00 | Rampal | 223 | 01:00 | 214 | 11:00
Charfasson | N/A | N/A | N/A | N/A | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 225 | 00:00 | 218 | 10:00 | Rampura | 228 | 05:00 | 210 | 13:00
Cumilla(N) | 226 | 19:30 | 217 | 10:00 | Shikalbaha | 232 | 21:00 | 224 | 10:00
Faridpur | 230 | 19:30 | 219 | 12:00 | Shyampur | 226 | 05:00 | 214 | 10:00
Fenchuganj | 232 | 19:30 | 226 | 13:00 | Siddhirganj | 227 | 19:00 | 213 | 12:00
Feni | 224 | 20:00 | 216 | 10:00 | Sirajgonj | 238 | 19:30 | 230 | 18:00
Ghorashal | 232 | 19:30 | 220 | 08:00 | Sreepur | 224 | 15:00 | 215 | 10:00
Ghorashal-230 | 215 | 19:30 | 197 | 10:00 | Tongi | 222 | 04:00 | 195 | 11:00
Gopalganj | 231 | 19:30 | 223 | 12:00
GPH | 230 | 20:00 | 221 | 10:00
Haripur | 228 | 05:00 | 213 | 13:00
Hasnabad | 225 | 03:00 | 213 | 11:00
Hathazari | 229 | 20:00 | 222 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 03:00 | 120 | 12:00 | Madunaghat | 134 | 19:30 | 130 | 07:00
Agargaon | 134 | 04:00 | 124 | 12:00 | Magura | 133 | 18:00 | 120 | 12:00
Agrabad | 133 | 21:00 | 127 | 10:00 | Mahasthangarh | 133 | 15:00 | 128 | 08:00
AKS | 130 | 20:00 | 126 | 10:00 | Maijdee | 126 | 19:30 | 120 | 10:00
Aminbazar | 129 | 19:30 | 120 | 11:00 | Manikganj | 132 | 19:30 | 122 | 09:00
Amnura | 137 | 19:30 | 125 | 12:00 | Maniknagar | 134 | 04:00 | 121 | 13:00
Ashuganj | 135 | 05:00 | 130 | 13:00 | Matarbari | 122 | 09:00 | 112 | 01:00
Ashuganj-230 | 135 | 05:00 | 130 | 13:00 | Matuail | 132 | 06:00 | 123 | 10:00
Bagerhat | 130 | 01:00 | 117 | 12:00 | Metrorail_Motijheel | 134 | 04:00 | 121 | 13:00
Bajitpur | 129 | 19:30 | 121 | 13:00 | Metrorail_Uttara | 132 | 04:00 | 118 | 12:00
Bakerganj | 131 | 17:00 | 127 | 12:00 | Millgate | 132 | 02:00 | 119 | 10:00
Bakulia | 132 | 20:00 | 128 | 10:00 | Mirpur | 132 | 15:00 | 119 | 11:00
Banani | 134 | 05:00 | 119 | 13:00 | Mirzapur | 131 | 20:00 | 120 | 09:00
Bangabhaban | 134 | 05:00 | 121 | 12:00 | Mithapukur | 130 | 05:00 | 125 | 21:00
Barapukuria | 135 | 04:00 | 125 | 21:00 | MI_Cement | 128 | 03:00 | 118 | 11:00
Barguna | 131 | 17:00 | 127 | 11:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 01:00 | 126 | 12:00 | Mogbazar | 135 | 03:00 | 122 | 13:00
Barishal-230 | 133 | 19:30 | 127 | 12:00 | Mongla | 130 | 01:00 | 117 | 12:00
Baroaulia | 132 | 18:00 | 128 | 11:00 | Motijheel | 134 | 05:00 | 121 | 12:00
Baroirhat | 131 | 19:30 | 126 | 10:00 | Muktagacha | 133 | 23:00 | 114 | 15:00
Bashundhara | 135 | 05:00 | 118 | 12:00 | Munshiganj | 129 | 00:00 | 122 | 10:00
BashundharaCement | 130 | 00:00 | 122 | 12:00 | Muradnagar | 128 | 20:00 | 122 | 10:00
Beanibazar | 126 | 06:00 | 122 | 13:00 | Mymensingh | 126 | 07:00 | 113 | 22:00
Benapole | 129 | 18:00 | 118 | 12:00 | Nabinagar | 129 | 19:30 | 118 | 10:00
Bhaluka | 131 | 07:00 | 122 | 13:00 | Naogaon | 134 | 17:00 | 123 | 12:00
Bhandaria | 130 | 15:00 | 120 | 12:00 | Narail | 134 | 18:30 | 121 | 12:00
Bhangura | 132 | 16:00 | 127 | 11:00 | Narinda | 134 | 04:00 | 121 | 13:00
Bheramara | 134 | 18:00 | 126 | 12:00 | Narshingdi | 129 | 13:00 | 118 | 10:00
Bheramara(GK) | 135 | 19:30 | 126 | 12:00 | Natore | 133 | 18:00 | 127 | 11:00
Bhulta | 128 | 19:30 | 119 | 11:00 | Nawabganj | 135 | 04:00 | 127 | 11:00
Bog-Sherpur | 135 | 17:00 | 128 | 12:00 | Netrakona | 125 | 06:00 | 111 | 13:00
Bogura | 137 | 17:00 | 131 | 08:00 | New | 133 | 20:00 | 121 | 10:00
Bogura-230 | 137 | 17:00 | 131 | 12:00 | Niamatpur | 130 | 17:00 | 125 | 12:00
Brahmanbaria | 128 | 05:00 | 124 | 13:00 | Noapara | 131 | 01:00 | 122 | 12:00
Cantonment | 133 | 03:00 | 124 | 11:00 | Pabna | 133 | 18:00 | 126 | 11:00
Chandina | 131 | 19:30 | 125 | 10:00 | Palashbari | 129 | 05:00 | 122 | 00:00
Chandpur | 132 | 19:30 | 118 | 10:00 | Panchagarh | 138 | 04:00 | 130 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 21:00 | 130 | 10:00 | Patiya | 131 | 00:00 | 126 | 10:00
Chapai | 132 | 16:00 | 125 | 08:00 | Patuakhali | 132 | 19:30 | 127 | 12:00
Charsaidpur | 130 | 03:00 | 122 | 10:00 | Payra | 133 | 16:00 | 130 | 12:00
Chauddagram | 129 | 18:30 | 123 | 12:00 | PHP | 130 | 19:30 | 125 | 10:00
Chhatak | 126 | 05:00 | 118 | 14:00 | Postogola | 130 | 19:30 | 121 | 08:00
Chowmuhani | 127 | 00:00 | 121 | 09:00 | Pubail | 129 | 14:00 | 117 | 10:00
Chuadanga | 134 | 20:00 | 119 | 12:00 | Purbachal | 134 | 03:00 | 120 | 13:00
Coxsbazar | 121 | 09:00 | 113 | 02:00 | Purbasadipur | 135 | 04:00 | 127 | 08:00
Cumilla(N) | 131 | 19:30 | 124 | 10:00 | Rahanpur | 132 | 15:00 | 129 | 11:00
Cumilla(S) | 133 | 18:00 | 121 | 15:00 | Rahanpur-400 | 133 | 17:00 | 130 | 08:00
Daganbhuiyan | 128 | 00:00 | 123 | 08:00 | Rahim | 132 | 05:00 | 123 | 10:00
Daudkandi | 126 | 19:30 | 119 | 10:00 | Rajbari | 129 | 01:00 | 123 | 12:00
DhakaUniversity | 134 | 03:00 | 122 | 12:00 | Rajendrapur | 131 | 15:00 | 123 | 11:00
Dhamrai | 130 | 20:00 | 119 | 10:00 | Rajshahi | 132 | 19:30 | 123 | 12:00
Dhanmondi | 134 | 03:00 | 123 | 10:00 | Rajshahi-230 | 133 | 18:00 | 125 | 11:00
Dohazari | 128 | 00:00 | 122 | 10:00 | Ramganj | 128 | 19:30 | 116 | 08:00
Faridpur | 132 | 01:00 | 126 | 10:00 | Rampur | 132 | 20:00 | 127 | 10:00
Fatullah | 138 | 19:30 | 118 | 11:00 | Rampura | 134 | 04:00 | 121 | 13:00
Fenchuganj | 132 | 09:00 | 129 | 13:00 | Rangamati | 133 | 00:00 | 129 | 10:00
Feni | 130 | 19:30 | 125 | 07:00 | Rangpur | 129 | 01:00 | 122 | 21:00
Feni-230 | 129 | 00:00 | 124 | 10:00 | Ruppur | 135 | 18:00 | 128 | 12:00
Ghatail | 125 | 20:00 | 114 | 08:00 | Saidpur | 133 | 01:00 | 125 | 08:00
Ghorashal | 130 | 20:00 | 120 | 08:00 | Santhia | 134 | 17:00 | 128 | 12:00
Goalpara | 134 | 05:00 | 125 | 12:00 | Satkhira | 128 | 01:00 | 119 | 12:00
Gollamari | 134 | 01:00 | 125 | 11:00 | Satmasjid | 133 | 01:00 | 123 | 13:00
Gopalganj | 133 | 19:30 | 124 | 12:00 | Savar | 128 | 19:30 | 117 | 10:00
Gopalganj-400 | 132 | 01:00 | 127 | 11:00 | SevenRings | 130 | 19:30 | 119 | 10:00
Gulshan | 134 | 05:00 | 120 | 13:00 | ShahCement | 130 | 03:00 | 122 | 10:00
Halishahar | 133 | 20:00 | 127 | 10:00 | Shahjadpur | 136 | 17:00 | 132 | 00:00
Haripur | 132 | 05:00 | 123 | 13:00 | Shahjibazar | 129 | 19:30 | 124 | 13:00
HaripurSBU | 132 | 05:00 | 123 | 11:00 | Shahmirpur | 133 | 04:00 | 127 | 08:00
Hasnabad | 130 | 20:00 | 120 | 12:00 | Shariatpur | 129 | 00:00 | 124 | 11:00
Hathazari | 135 | 00:00 | 130 | 10:00 | Sherpur | 125 | 20:00 | 110 | 01:00
Hatirjheel | 135 | 05:00 | 121 | 13:00 | Shikalbaha | 123 | 02:00 | 118 | 10:00
Ishurdi | 136 | 18:00 | 128 | 12:00 | Shikalbaha-230 | 134 | 21:00 | 129 | 10:00
Jaldhaka | 130 | 04:00 | 123 | 08:00 | Shitalakhya | 128 | 03:00 | 118 | 11:00
Jamalpur | 129 | 20:00 | 113 | 08:00 | Sholosohor | 133 | 00:00 | 129 | 10:00
Jashore | 130 | 18:00 | 120 | 12:00 | Shomvuganj | 123 | 06:00 | 115 | 14:00
Jhenaidah | 135 | 18:30 | 125 | 11:00 | Shyampur | 134 | 05:00 | 127 | 12:00
Jhenaidah-230 | 135 | 18:30 | 124 | 12:00 | Shyampur-230 | 137 | 20:00 | 127 | 12:00
Joydebpur | 130 | 14:00 | 113 | 10:00 | Siddhirganj | 132 | 03:00 | 123 | 11:00
Joypurhat | 131 | 06:00 | 124 | 12:00 | Sirajganj | 132 | 16:00 | 125 | 12:00
Juldah | 133 | 19:30 | 128 | 09:00 | Sonargaon | 129 | 04:00 | 122 | 10:00
Kabirpur | 137 | 20:00 | 115 | 11:00 | Sreemongol | 128 | 19:30 | 125 | 00:00
Kachua | 130 | 20:00 | 122 | 08:00 | Sreepur | 132 | 19:30 | 126 | 09:00
Kaliakoir | 137 | 19:30 | 124 | 10:00 | Srinagar | 135 | 03:00 | 128 | 10:00
Kaliganj | 134 | 18:30 | 123 | 12:00 | SSM | 138 | 22:00 | 132 | 15:00
Kallyanpur | 128 | 19:30 | 120 | 11:00 | Sunamganj | 124 | 07:00 | 116 | 14:00
Kalurghat | 134 | 20:00 | 130 | 10:00 | Sylhet | 127 | 19:30 | 123 | 14:00
Kamrangirchar | 135 | 03:00 | 117 | 11:00 | Sylhet_(South) | 127 | 07:00 | 123 | 14:00
Kaptai | 135 | 1:00 | 133 | 13:00 | Tangail | 127 | 20:00 | 116 | 10:00
Kasba | 127 | 19:30 | 120 | 10:00 | Taraganj | 135 | 04:00 | 123 | 21:00
Kazla | 134 | 06:00 | 121 | 13:00 | Tasnim | 129 | 05:00 | 122 | 10:00
Keranigonj | 136 | 04:00 | 128 | 10:00 | Thakurgaon | 136 | 04:00 | 128 | 21:00
Khagrachori | 132 | 00:00 | 128 | 10:00 | TK | 134 | 00:00 | 129 | 10:00
Khulna | 133 | 04:00 | 124 | 12:00 | Tongi | 137 | 04:00 | 122 | 11:00
Khulna(S) | 134 | 01:00 | 126 | 12:00 | Ullahpara | 133 | 16:00 | 126 | 12:00
Khulshi | 131 | 00:00 | 126 | 10:00 | Ullon | 135 | 05:00 | 120 | 13:00
Kishoreganj | 127 | 06:00 | 119 | 13:00 | Uttara | 133 | 23:00 | 116 | 11:00
Kodda | 137 | 20:00 | 122 | 10:00 | UttaraNew | 132 | 04:00 | 118 | 12:00
Korerhat | 132 | 19:30 | 127 | 10:00 | Zigatola | 136 | 04:00 | 128 | 10:00
KSRM | 133 | 00:00 | 129 | 08:00
Kulaura | 130 | 08:00 | 127 | 16:00
Kurigram | 129 | 01:00 | 119 | 08:00
Kushtia | 134 | 18:30 | 123 | 12:00
Laksam | 129 | 19:30 | 120 | 10:00
Lakshmipur | 125 | 20:00 | 119 | 10:00
Lalbag | 135 | 04:00 | 127 | 11:00
Lalmonirhat | 127 | 11:00 | 117 | 21:00
Madanganj | 130 | 00:00 | 122 | 12:00
Madaripur | 131 | 02:00 | 125 | 12:00
Madartek | 134 | 05:00 | 121 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division