## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-06-2026 | during | 17-06-2026 | during | 17-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 396 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 164 | 0 | 210 | 210 | 210 | 210 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 329 | 335 | 335 | 310 | 310 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 17 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 132 | 127 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 20 | 33 | 33 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 16 | 52.19 | 52.19 | 0 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 32 | 300 | 300 | 33 | 80 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 31 | 53 | 149 | 149 | 35 | 72 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 35 | 105 | 105 | 17 | 34 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 535 | 510 | 584 | 584 | 520 | 520 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 550 | 465 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 123 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2058 | 2356 | 5822.22 | 5792.22 | 2510.06 | 2765.06
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 12 | 0 | 12 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 19 | 50 | 50 | 6 | 6 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 73 | 70 | 76 | 76 | 76 | 76 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 220 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 0 | 34 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 8 | 0 | 0 | 8 | 8 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 17 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 34 | 85 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.69 | 0 | 3.45 | 0 | 3.45 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 54 | 54.36 | 54.36 | 17 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 110 | 110 | 17 | 17 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 0 | 0 | 0 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 92 | 106 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 50 | 85 | 163 | 163 | 50 | 50 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 612 | 1224 | 1224 | 1224 | 1224 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 7 | 0 | 8 | 0 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1135 | 1135 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2324.19 | 2560.5 | 3817.31 | 3884.86 | 2964.95 | 3120.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 211 | 215 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 290 | 350.01 | 350.01 | 290 | 290 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 220 | 220 | 342.01 | 342.01 | 220 | 220 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 260 | 260 | 393 | 393 | 280 | 280 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 0 | 41.65 | 41.65 | 10 | 10 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 50 | 85 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 15 | 22 | 24 | 24 | 24 | 24 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 103 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 160 | 182 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 104 | 114 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 18 | 32 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 89 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 31 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1472.2 | 1690 | 2741.44 | 2680.44 | 1538.25 | 1706.25
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-06-2026 | during | 17-06-2026 | during | 17-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 21.1 | 0 | 15 | 0 | 15 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.3 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 88 | 70 | 90 | 70 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 56 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 18.69 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 146.09 | 173 | 481.7 | 446.5 | 195.2 | 177
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 28 | 0 | 0 | 28 | 28 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 150 | 149 | 163 | 163 | 163 | 163 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 71 | 142 | 145 | 145 | 145 | 145 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 85 | 83 | 83 | 52 | 52 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 100 | 102 | 102 | 102 | 102 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 23 | 23 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 295 | 308 | 350 | 350 | 320 | 320 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1056 | 1170 | 1289 | 1289 | 1192 | 1192
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 927 | 927 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 25 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 24 | 0 | 0 | 0 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 105 | 105 | 32 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 70 | 0 | 98 | 0 | 98 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 510 | 510 | 510 | 510 | 510 | 510 | ps availability is less
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 40 | 40 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1569 | 1532 | 2866 | 2768 | 1762 | 1664
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 500 | 600 | 820 | 820 | 1040 | 1040 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 0 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 63 | 63 | 65 | 65 | 65 | 65 | GT-1 & ST under maint
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1178 | 1212 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2301 | 2435 | 2917 | 2916 | 2834 | 2867
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 39.93 | 0 | 54 | 0 | 54 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 33 | 31 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 13 | 18 | 32 | 32 | 24 | 24 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 191 | 199 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 197 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 399 | 393 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 26 | 26 | 26 | 26 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 25 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 91 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 35 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 35 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.61 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1449 | 1471.89 | 1435.88 | 1435.88 | 1356 | 1356 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 50.21 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 80 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2494.75 | 2493.89 | 3010.47 | 2789.87 | 2549.01 | 2445.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 38 | 40 | 38 | 38 | 40 | 40 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 35 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 10 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 146 | 0 | 154.32 | 0 | 154.32 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 234.6 | 169 | 476.32 | 286 | 380.32 | 190
System Total |  |  |  |  | 28843.2 | 29290.237 | 13655.83 | 14579.39 | 23421.46 | 22852.89 | 15925.79 | 16127.22
Forecast Scenario (17-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14300 |  | 2521.2 |  | 16940
|  |  |  | 1:00 | 14000 |  | 2435.25 |  | 16550
|  |  |  | 2:00 | 13900 |  | 2435.25 |  | 16450
|  |  |  | 3:00 | 13890 |  | 2196.5 |  | 16190
|  |  |  | 4:00 | 13880 |  | 2072.35 |  | 16050
|  |  |  | 5:00 | 13880 |  | 1862.25 |  | 15830
|  |  |  | 6:00 | 14000 |  | 1528 |  | 15600
|  |  |  | 7:00 | 14070 |  | 1260.6 |  | 15390
|  |  |  | 8:00 | 14160 |  | 1060.05 |  | 15270
|  |  |  | 9:00 | 14230 |  | 1279.7 |  | 15570
|  |  |  | 10:00 | 14460 |  | 1327.45 |  | 15850
|  |  |  | 11:00 | 14590 |  | 1251.05 |  | 15900
|  |  |  | 12:00 | 14690 |  | 1547.1 |  | 16310
|  |  |  | 13:00 | 14710 |  | 1671.25 |  | 16460
|  |  |  | 14:00 | 14570 |  | 1871.8 |  | 16530
|  |  |  | 15:00 | 14480 |  | 2101 |  | 16680
|  |  |  | 16:00 | 14320 |  | 1852.7 |  | 16260
|  |  |  | 17:00 | 14330 |  | 1709.45 |  | 16120
|  |  |  | 18:00 | 14600 |  | 1346.55 |  | 16010
|  |  |  | 18:30 | 14590 |  | 1824.05 |  | 16500
|  |  |  | 19:00 | 14750 |  | 2225.15 |  | 17080
|  |  |  | 19:30 | 14760 |  | 2683.55 |  | 17570
|  |  |  | 20:00 | 14800 |  | 2568.95 |  | 17490
|  |  |  | 21:00 | 14950 |  | 2530.75 |  | 17600
|  |  |  | 22:00 | 14860 |  | 2521.2 |  | 17500
|  |  |  | 23:00 | 14820 |  | 2463.9 |  | 17400
Probable Maximum Temperature: |  |  | 35.20°C
Probable Maximum Demand at Day Peak: |  |  | 16310.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2531
Probable Maximum Demand at Evening Peak: |  |  | 17600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14950.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 345.24 MKWHr. |  | 390 | 166 | 354 | 398 | 92 | 412 | 127 | 320 | 272 | 2531
*** This report is generated digitally from Operation Information System (OIS) at 08:16 hrs on 17-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-06-2026 | [28 empty] | Date: | 16-06-2026 | [28 empty] | Date: | 16-06-2026 | [28 empty] | Date: | 16-06-2026 | [28 empty] | Date: | 16-06-2026 | [18 empty] | Date: | 16-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [18 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 149 | 84 | 15 | 35 | 54 | 0 | 0 | 0 | 560 | 0 | 0 | 300 | 136 | 0 | 0 | 142 | 19 | 22 | 0 | 500 | 107 | 16 | 84 | 0 | 8 | 50 | 0 | 17 | 12 | 12 | 0 | 74 | 17 | 28 | 1135 | 48 | 0 | 50 | 25.5 | 0 | 218 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 265 | 290 | 220 | 51 | 0 | 208 | 10 | 62 | 0 | 26 | 0 | 19 | 20 | 170 | 34 | 0 | 15 | 310 | 0 | 339 | 28 | 0 | 153 | 0 | 23 | 0 | 52 | 30 | 95 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7213.5 | 929 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 0 | 0 | 0 | 1473 | 0 | 40 | 0 | 35 | 35 | 0 | 92 | 28 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 189 | 0 | 191 | 0 | 390 | 0 | 0 | 0 | 35 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 512 | 1220 | 17 | 6988 | 14201.5 | 76.16
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 149 | 81 | 15 | 35 | 35 | 0 | 0 | 0 | 555 | 0 | 0 | 296 | 137 | 0 | 0 | 142 | 20 | 22 | 0 | 520 | 106 | 16 | 43 | 0 | 13 | 0 | 0 | 17 | 12 | 12 | 0 | 71 | 17 | 27 | 1135 | 43 | 0 | 50 | 25.5 | 0 | 218 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 265 | 290 | 220 | 51 | 0 | 211 | 10 | 51 | 0 | 17 | 0 | 19 | 93 | 166 | 52.2 | 0 | 15 | 305 | 0 | 339 | 28 | 0 | 151 | 0 | 23 | 0 | 52 | 30 | 96 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7136.7 | 930 | 0 | 0 | 25 | 44 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 0 | 0 | 0 | 1451 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 189 | 0 | 191 | 0 | 399 | 0 | 0 | 0 | 36 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 506 | 1225 | 17 | 6858 | 13994.7 | 76.19
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 149 | 81 | 15 | 35 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 310 | 135 | 0 | 0 | 142 | 21 | 22 | 0 | 520 | 107 | 16 | 31 | 0 | 13 | 0 | 0 | 17 | 12 | 12 | 0 | 64 | 17 | 27 | 1135 | 50 | 0 | 50 | 25.5 | 0 | 218 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 265 | 290 | 220 | 51 | 0 | 210 | 10 | 0 | 0 | 16 | 0 | 19 | 107 | 156 | 52.2 | 0 | 15 | 310 | 0 | 339 | 28 | 0 | 153 | 0 | 23 | 0 | 52 | 30 | 95 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7065.7 | 929 | 0 | 0 | 25 | 44 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 0 | 0 | 0 | 1453 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 192 | 0 | 193 | 0 | 393 | 0 | 0 | 0 | 36 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 509 | 1225 | 17 | 6854 | 13919.7 | 76.22
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 149 | 81 | 15 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 293 | 135 | 0 | 0 | 142 | 21 | 22 | 0 | 500 | 107 | 16 | 32 | 0 | 7 | 0 | 0 | 17 | 12 | 12 | 0 | 61 | 17 | 13 | 1135 | 46 | 0 | 50 | 25.5 | 0 | 218 | 0 | 0 | 0 | 580 | 0 | 11 | 0 | 265 | 290 | 220 | 51 | 0 | 213 | 10 | 0 | 0 | 17 | 0 | 19 | 106 | 150 | 52.2 | 0 | 15 | 305 | 0 | 339 | 28 | 0 | 147 | 0 | 23 | 0 | 53 | 30 | 96 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6906.7 | 929 | 0 | 0 | 25 | 44 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 0 | 0 | 0 | 1446 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 195 | 0 | 193 | 0 | 385 | 0 | 0 | 0 | 36 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 494 | 1225 | 17 | 6829 | 13735.7 | 76.25
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 132 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 294 | 135 | 0 | 0 | 142 | 21 | 22 | 0 | 500 | 107 | 16 | 31 | 0 | 19 | 0 | 0 | 17 | 12 | 12 | 0 | 61 | 17 | 13 | 1135 | 50 | 0 | 50 | 25.5 | 0 | 219 | 0 | 0 | 0 | 580 | 0 | 13 | 0 | 265 | 290 | 220 | 51 | 0 | 218 | 10 | 0 | 0 | 16 | 0 | 19 | 107 | 154 | 52.2 | 0 | 15 | 305 | 0 | 339 | 28 | 0 | 147 | 0 | 23 | 0 | 53 | 30 | 96 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6873.7 | 929 | 0 | 0 | 25 | 43 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 0 | 0 | 0 | 1442 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 193 | 0 | 388 | 0 | 0 | 0 | 36 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 488 | 1225 | 17 | 6792 | 13665.7 | 76.28
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 132 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 300 | 135 | 0 | 0 | 123 | 21 | 22 | 0 | 500 | 106 | 16 | 32 | 0 | 9 | 0 | 0 | 17 | 12 | 12 | 0 | 63 | 17 | 14 | 1135 | 50 | 0 | 50 | 25.5 | 0 | 220 | 0 | 0 | 0 | 580 | 0 | 13 | 0 | 275 | 290 | 220 | 51 | 0 | 216 | 10 | 0 | 0 | 17 | 0 | 19 | 108 | 148 | 52.2 | 0 | 15 | 300 | 0 | 339 | 28 | 0 | 142 | 0 | 22 | 0 | 53 | 30 | 96 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6842.7 | 930 | 0 | 0 | 25 | 43 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 0 | 0 | 0 | 1401 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 198 | 0 | 373 | 0 | 0 | 0 | 36 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 458 | 1225 | 17 | 6706 | 13548.7 | 76.31
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 149 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 300 | 201 | 0 | 0 | 123 | 21 | 22 | 0 | 500 | 107 | 16 | 31 | 0 | 2 | 0 | 0 | 0 | 12 | 12 | 0.09 | 66 | 17 | 14 | 1135 | 53 | 0 | 50 | 17 | 0 | 220 | 0 | 0 | 0 | 580 | 0 | 13 | 0 | 280 | 290 | 220 | 51 | 0 | 217 | 10 | 0 | 0 | 16 | 0 | 19 | 108 | 140 | 52.2 | 1 | 15 | 305 | 0 | 344 | 28 | 0 | 148 | 0 | 22 | 0 | 53 | 30 | 95 | 0 | 101 | 0 | 48 | 0.34 | 48 | 0 | 0 | 2.38 | 0 | 6919.01 | 929 | 0 | 0 | 25 | 43 | 38 | 0 | 0 | 0 | 0 | 0 | 3.38 | 740 | 0 | 0 | 0 | 1430 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0.16 | 0 | 0 | 0 | 0.36 | 0 | 0 | 201 | 0 | 205 | 0 | 399 | 0 | 0.06 | 0 | 36 | 95 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 16 | 307 | 63 | 220 | 0 | 499 | 1225 | 17 | 6543.96 | 13462.97 | 76.34
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 132 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 311 | 198 | 0 | 2 | 123 | 21 | 22 | 0 | 535 | 107 | 16 | 31 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0.54 | 69 | 17 | 19 | 1135 | 50 | 0 | 50 | 17 | 0 | 219 | 0 | 0 | 0 | 580 | 0 | 11 | 0 | 260 | 290 | 220 | 51 | 0 | 213 | 10 | 0 | 0 | 17 | 0 | 17 | 107 | 144 | 52.2 | 9 | 15 | 300 | 0 | 344 | 28 | 0 | 153 | 2 | 22 | 0 | 53 | 30 | 94 | 0 | 101 | 0 | 49 | 0.11 | 48 | 0 | 0.4 | 3.32 | 0 | 6963.57 | 929 | 0 | 0 | 25 | 36 | 38 | 0 | 0 | 0 | 0 | 0 | 18.41 | 510 | 0 | 0 | 0 | 1465 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 6.05 | 21 | 0 | 0 | 3.26 | 0 | 0 | 204 | 0 | 206 | 0 | 404 | 0 | 0.33 | 0 | 42 | 95 | 5 | 0 | 0 | 0 | 0 | 0.9 | 19 | 0 | 16 | 303 | 63 | 220 | 0 | 512 | 1225 | 17 | 6429.95 | 13393.52 | 76.37
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 132 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 307 | 197 | 0 | 15 | 123 | 21 | 22 | 0 | 500 | 107 | 16 | 32 | 0 | 2 | 0 | 0 | 0 | 12 | 12 | 0.48 | 71 | 17 | 2 | 1135 | 48 | 0 | 50 | 21 | 0 | 218 | 0 | 0 | 0 | 580 | 5 | 13 | 0 | 260 | 290 | 220 | 51 | 0 | 214 | 10 | 0 | 0 | 17 | 0 | 17 | 106 | 146 | 52.2 | 9 | 15 | 300 | 0 | 332 | 28 | 0 | 148 | 4 | 22 | 0 | 52 | 30 | 96 | 0 | 101 | 0 | 49 | 2.1 | 48 | 0 | 0.3 | 1.56 | 0 | 6910.64 | 929 | 0 | 0 | 0 | 32 | 38 | 0 | 0 | 0 | 0 | 0 | 48.71 | 510 | 0 | 0 | 0 | 1431 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 18.75 | 38 | 0 | 0 | 7.53 | 0 | 0 | 206 | 0 | 206 | 0 | 384 | 0 | 0.58 | 0 | 36 | 95 | 14 | 0 | 0 | 0 | 0 | 1.5 | 77 | 0 | 16 | 304 | 63 | 220 | 0 | 481 | 1208 | 17 | 6428.07 | 13338.71 | 76.4
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 116 | 32 | 15 | 0 | 17 | 0 | 0 | 0 | 555 | 0 | 0 | 305 | 197 | 0 | 19 | 123 | 20 | 22 | 0 | 510 | 100 | 16 | 29 | 0 | 5 | 0 | 0 | 0 | 12 | 12 | 0.28 | 72 | 17 | 2 | 1135 | 48 | 0 | 50 | 25.5 | 0 | 216 | 0 | 0 | 0 | 582 | 9 | 13 | 0 | 260 | 290 | 220 | 51 | 0 | 214 | 10 | 0 | 0 | 17 | 0 | 17 | 109 | 148 | 52.2 | 16 | 15 | 305 | 0 | 306 | 28 | 0 | 149 | 1 | 22 | 0 | 52 | 30 | 96 | 0 | 101 | 0 | 49 | 6.5 | 48 | 0 | 0.8 | 5.35 | 0 | 6927.63 | 928 | 0 | 0 | 0 | 32 | 38 | 0 | 0 | 0 | 0 | 0 | 71.66 | 510 | 0 | 0 | 0 | 1458 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 31.58 | 65 | 0 | 0 | 16.7 | 0 | 0 | 201 | 0 | 205 | 0 | 404 | 0 | 2.15 | 0 | 36 | 95 | 10 | 0 | 0 | 0 | 0 | 3.6 | 86 | 0 | 16 | 307 | 63 | 220 | 0 | 510 | 1177 | 17 | 6549.69 | 13477.32 | 76.43
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 116 | 32 | 15 | 9 | 17 | 0 | 0 | 0 | 545 | 0 | 17 | 292 | 142 | 0 | 24 | 123 | 20 | 22 | 0 | 500 | 95 | 16 | 31 | 0 | 4 | 0 | 0 | 0 | 12 | 12 | 1.35 | 73 | 17 | 2 | 1135 | 46 | 0 | 50 | 25.5 | 0 | 219 | 0 | 0 | 0 | 580 | 12 | 20 | 0 | 260 | 290 | 220 | 51 | 0 | 208 | 10 | 0 | 0 | 16 | 5 | 17 | 104 | 160 | 52.2 | 42 | 14 | 305 | 0 | 308 | 28 | 0 | 153 | 8 | 23 | 0 | 52 | 30 | 71 | 0 | 101 | 0 | 49 | 12 | 48 | 0 | 1.9 | 22.99 | 0 | 6920.94 | 928 | 0 | 0 | 0 | 28 | 38 | 0 | 0 | 0 | 0 | 0 | 92 | 510 | 0 | 0 | 0 | 1416 | 0 | 33 | 0 | 0 | 20 | 0 | 0 | 13 | 0 | 39.28 | 48 | 0 | 0 | 39.4 | 0 | 0 | 196 | 0 | 203 | 0 | 374 | 0 | 4.45 | 0 | 36 | 35 | 3 | 0 | 0 | 0 | 0 | 4.1 | 136 | 0 | 16 | 301 | 63 | 220 | 0 | 481 | 1180 | 17 | 6474.23 | 13395.17 | 76.46
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 31 | 132 | 32 | 15 | 17 | 17 | 0 | 0 | 0 | 550 | 0 | 17 | 320 | 164 | 0 | 29 | 123 | 20 | 22 | 0 | 535 | 92 | 16 | 34 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.69 | 73 | 17 | 2 | 1135 | 50 | 0 | 50 | 25.5 | 0 | 215 | 0 | 0 | 0 | 580 | 9 | 50 | 0 | 260 | 290 | 220 | 51 | 0 | 211 | 10 | 0 | 0 | 0 | 18 | 0 | 104 | 160 | 52.2 | 31 | 15 | 300 | 0 | 295 | 28 | 0 | 150 | 6 | 23 | 0 | 52 | 30 | 71 | 0 | 101 | 0 | 56 | 21.1 | 48 | 0 | 2.3 | 18.69 | 0 | 7056.48 | 927 | 0 | 0 | 0 | 24 | 38 | 0 | 0 | 0 | 0 | 0 | 70 | 510 | 0 | 0 | 0 | 1449 | 0 | 33 | 0 | 0 | 35 | 0 | 0 | 13 | 0 | 39.93 | 80 | 0 | 0 | 50.21 | 0 | 0 | 191 | 0 | 200 | 0 | 399 | 0 | 4.61 | 0 | 38 | 35 | 10 | 0 | 0 | 0 | 0 | 5.6 | 146 | 0 | 16 | 307 | 63 | 220 | 0 | 500 | 1178 | 17 | 6599.35 | 13655.83 | 76.49
12:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 34 | 129 | 32 | 15 | 17 | 17 | 0 | 0 | 0 | 555 | 0 | 0 | 316 | 139 | 0 | 30 | 123 | 20 | 22 | 0 | 535 | 99 | 16 | 45 | 0 | 11 | 0 | 0 | 0 | 12 | 12 | 0.31 | 73 | 17 | 2 | 1135 | 50 | 0 | 50 | 25.5 | 0 | 215 | 0 | 0 | 0 | 580 | 4 | 53 | 0 | 270 | 290 | 220 | 51 | 0 | 217 | 0 | 6 | 0 | 6 | 18 | 5.5 | 30 | 168 | 52.2 | 49 | 15 | 305 | 0 | 296 | 28 | 0 | 149 | 10 | 23 | 0 | 52 | 30 | 70 | 0 | 101 | 0 | 58 | 20.68 | 67 | 0 | 1.6 | 50.74 | 0 | 7077.53 | 928 | 0 | 0 | 0 | 24 | 38 | 0 | 0 | 0 | 0 | 0 | 53 | 510 | 0 | 0 | 0 | 1440 | 0 | 33 | 0 | 0 | 35 | 0 | 0 | 13 | 0 | 54.19 | 85 | 0 | 0 | 33.45 | 0 | 0 | 191 | 0 | 200 | 0 | 379 | 0 | 5.13 | 0 | 36 | 35 | 14 | 0 | 0 | 0 | 0 | 7.9 | 157 | 0 | 16 | 307 | 63 | 220 | 0 | 480 | 1178 | 17 | 6552.67 | 13630.2 | 76.52
13:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 34 | 127 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 555 | 0 | 0 | 294 | 141 | 0 | 31 | 123 | 20 | 21 | 0 | 510 | 96 | 16 | 50 | 0 | 13 | 0 | 0 | 0 | 12 | 12 | 0.52 | 69 | 17 | 7 | 1135 | 50 | 0 | 50 | 25.5 | 0 | 215 | 0 | 0 | 0 | 580 | 7 | 55 | 0 | 270 | 290 | 220 | 51 | 0 | 215 | 0 | 34 | 0 | 17 | 18 | 5.5 | 20 | 150 | 52.2 | 56 | 15 | 305 | 0 | 296 | 28 | 0 | 148 | 8 | 23 | 0 | 52 | 30 | 140 | 0 | 101 | 0 | 58 | 20 | 66 | 0 | 0.9 | 49.9 | 0 | 7138.52 | 927 | 0 | 0 | 0 | 28 | 38 | 0 | 0 | 0 | 0 | 0 | 90 | 510 | 0 | 0 | 0 | 1420.19 | 0 | 31 | 0 | 0 | 35 | 0 | 0 | 13 | 0 | 51.94 | 95 | 0 | 0 | 28.72 | 0 | 0 | 191 | 0 | 200 | 0 | 375 | 0 | 1.72 | 0 | 39 | 35 | 29 | 0 | 0 | 0 | 0 | 7.3 | 106 | 0 | 16 | 305 | 63 | 220 | 0 | 475 | 1190 | 17 | 6537.87 | 13676.39 | 76.55
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 34 | 126 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 556 | 0 | 0 | 286 | 141 | 0 | 26 | 123 | 20 | 21 | 0 | 485 | 97 | 16 | 50 | 0 | 5 | 0 | 0 | 0 | 12 | 12 | 1.54 | 63 | 17 | 3 | 1135 | 50 | 0 | 19 | 25.5 | 0 | 215 | 0 | 0 | 0 | 580 | 9 | 53 | 0 | 260 | 290 | 220 | 51 | 0 | 216 | 0 | 35 | 0 | 16 | 0 | 5.5 | 17 | 168 | 52.2 | 63 | 15 | 310 | 0 | 296 | 28 | 0 | 147 | 0 | 23 | 0 | 51 | 30 | 142 | 0 | 101 | 0 | 58 | 10 | 66 | 0 | 1.8 | 34.2 | 0 | 7020.74 | 926 | 0 | 0 | 0 | 25 | 38 | 0 | 0 | 0 | 0 | 0 | 83 | 510 | 0 | 0 | 0 | 1436.88 | 0 | 31 | 0 | 35 | 35 | 0 | 0 | 13 | 0 | 47.2 | 85 | 0 | 0 | 18.44 | 0 | 0 | 195 | 0 | 200 | 0 | 398 | 0 | 4.37 | 0 | 41 | 35 | 16 | 0 | 0 | 0 | 0 | 6.7 | 143 | 0.46 | 16 | 307 | 63 | 220 | 0 | 496 | 1210 | 17 | 6652.05 | 13672.79 | 76.58
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 34 | 103 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 557 | 0 | 0 | 300 | 139 | 0 | 6 | 123 | 20 | 21 | 0 | 510 | 101 | 16 | 50 | 0 | 3 | 0 | 8 | 0 | 12 | 12 | 1.32 | 60 | 17 | 2 | 1135 | 51 | 0 | 19 | 25.5 | 0 | 215 | 0 | 0 | 0 | 612 | 7 | 53 | 0 | 260 | 290 | 220 | 51 | 0 | 214 | 0 | 35 | 0 | 17 | 0 | 5.5 | 17 | 166 | 52.2 | 9 | 15 | 305 | 0 | 296 | 28 | 0 | 146 | 2 | 23 | 0 | 51 | 30 | 142 | 0 | 100 | 0 | 58 | 14.61 | 68 | 0 | 1.1 | 33.94 | 0 | 6996.17 | 927 | 0 | 0 | 0 | 24 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 510 | 0 | 0 | 0 | 1431.36 | 0 | 31 | 0 | 35 | 35 | 0 | 0 | 13 | 0 | 37.32 | 71 | 0 | 0 | 39.28 | 0 | 0 | 197 | 0 | 198 | 0 | 376 | 0 | 3.48 | 0 | 40 | 35 | 19 | 0 | 0 | 0 | 0 | 2.5 | 116 | 0.28 | 16 | 307 | 63 | 220 | 0 | 470 | 1222 | 17 | 6504.22 | 13500.39 | 76.61
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 17 | 0 | 34 | 104 | 32 | 15 | 35 | 17 | 0 | 0 | 0 | 555 | 0 | 17 | 294 | 98 | 0 | 14 | 123 | 20 | 21 | 0 | 495 | 106 | 16 | 57 | 0 | 1 | 0 | 8 | 0 | 12 | 0 | 0.48 | 60 | 17 | 3 | 1135 | 51 | 0 | 19 | 25.5 | 0 | 216 | 0 | 0 | 0 | 612 | 4 | 53 | 0 | 260 | 290 | 220 | 51 | 0 | 214 | 0 | 34 | 0 | 17 | 0 | 13 | 17 | 160 | 25 | 3 | 15 | 305 | 0 | 296 | 28 | 0 | 149 | 3 | 0 | 0 | 52 | 30 | 142 | 0 | 100 | 0 | 58 | 5.77 | 68 | 0 | 1.1 | 11.43 | 8 | 6890.28 | 927 | 0 | 0 | 0 | 25 | 38 | 0 | 0 | 0 | 0 | 0 | 6.94 | 510 | 0 | 0 | 0 | 1464.78 | 0 | 31 | 0 | 35 | 35 | 0 | 0 | 15 | 0 | 27.8 | 2 | 0 | 0 | 18.27 | 0 | 0 | 199 | 0 | 197 | 0 | 385 | 0 | 2 | 0 | 40 | 35 | 12 | 25 | 0 | 0 | 0 | 2 | 64 | 0.38 | 16 | 307 | 63 | 220 | 0 | 501 | 1190 | 36 | 6430.17 | 13320.45 | 76.64
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 17 | 0 | 34 | 136 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 550 | 0 | 35 | 294 | 96 | 0 | 10 | 123 | 20 | 21 | 0 | 495 | 107 | 16 | 57 | 0 | 0 | 0 | 8 | 0 | 12 | 0 | 0.07 | 60 | 17 | 6 | 1135 | 50 | 0 | 19 | 25.5 | 5 | 218 | 0 | 0 | 0 | 612 | 2 | 53 | 0 | 260 | 290 | 220 | 51 | 0 | 214 | 0 | 34 | 0 | 39 | 5 | 19 | 26 | 168 | 8 | 2 | 14 | 305 | 0 | 296 | 28 | 0 | 148 | 2 | 0 | 0 | 52 | 30 | 142 | 0 | 100 | 0 | 58 | 4.75 | 68 | 0 | 0.7 | 4.39 | 12 | 6996.41 | 928 | 0 | 0 | 0 | 25 | 38 | 0 | 0 | 0 | 0 | 0 | 10.87 | 510 | 0 | 0 | 0 | 1430.36 | 0 | 31 | 0 | 35 | 35 | 0 | 0 | 15 | 0 | 3.16 | 5 | 0 | 0 | 2.99 | 0 | 0 | 200 | 0 | 197 | 0 | 377 | 0 | 0.3 | 0 | 40 | 35 | 7 | 26 | 0 | 0 | 0 | 2 | 44 | 0.14 | 16 | 294 | 63 | 220 | 0 | 478 | 1175 | 17 | 6260.82 | 13257.23 | 76.67
18:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 17 | 4 | 40 | 126 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 545 | 0 | 35 | 283 | 97 | 0 | 1 | 138 | 19 | 21 | 0 | 485 | 106 | 16 | 61 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0.02 | 63 | 17 | 8 | 1135 | 51 | 0 | 19 | 25.5 | 34 | 219 | 0 | 0 | 0 | 612 | 1 | 61 | 0 | 260 | 290 | 220 | 51 | 0 | 215 | 0 | 34 | 0 | 101 | 27 | 19 | 32 | 158 | 8 | 2 | 14 | 310 | 0 | 296 | 28 | 0 | 136 | 0 | 23 | 0 | 52 | 30 | 142 | 0 | 100 | 0 | 58 | 1.44 | 68 | 0 | 0.2 | 2.05 | 12 | 7223.21 | 927 | 0 | 0 | 0 | 30 | 38 | 0 | 0 | 0 | 0 | 32 | 4 | 510 | 0 | 0 | 0 | 1344.24 | 0 | 31 | 0 | 35 | 35 | 0 | 25 | 8 | 0 | 0 | 10 | 24 | 0 | 0 | 0 | 0 | 199 | 0 | 197 | 0 | 367 | 0 | 0 | 0 | 40 | 95 | 2 | 33 | 0 | 0 | 0 | 0.7 | 12 | 0.02 | 16 | 250 | 63 | 220 | 0 | 421 | 1180 | 17 | 6165.96 | 13389.17 | 76.7
19:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 17 | 17 | 53 | 129 | 32 | 15 | 35 | 108 | 0 | 0 | 0 | 525 | 0 | 35 | 323 | 37 | 0 | 0 | 142 | 19 | 21 | 0 | 540 | 107 | 16 | 66 | 0 | 6 | 50 | 8 | 20 | 0 | 0 | 0 | 66 | 17 | 5 | 1135 | 75 | 0 | 19 | 25.5 | 34 | 218 | 0 | 0 | 0 | 612 | 0 | 138 | 0 | 260 | 290 | 220 | 51 | 0 | 214 | 0 | 55 | 0 | 104 | 27 | 19 | 114 | 180 | 8 | 0 | 21 | 305 | 0 | 296 | 28 | 0 | 146 | 0 | 23 | 0 | 52 | 30 | 142 | 0 | 100 | 1.8 | 68 | 0 | 87 | 0 | 0 | 0 | 0 | 7738.3 | 928 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 510 | 0 | 0 | 0 | 1474.54 | 0 | 31 | 0 | 35 | 35 | 0 | 91 | 15 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 199 | 0 | 197 | 0 | 404 | 0 | 0 | 0 | 40 | 95 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 250 | 63 | 180 | 0 | 520 | 1180 | 17 | 6432.54 | 14170.84 | 76.73
19:30 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 20 | 17 | 53 | 129 | 32 | 15 | 35 | 108 | 0 | 0 | 0 | 540 | 0 | 35 | 329 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 500 | 107 | 16 | 78 | 0 | 0 | 50 | 8 | 54 | 0 | 0 | 0 | 66 | 17 | 2 | 1135 | 110 | 0 | 19 | 25.5 | 34 | 218 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 260 | 290 | 220 | 51 | 0 | 215 | 0 | 90 | 0 | 104 | 27 | 19 | 114 | 182 | 8 | 0 | 21 | 305 | 0 | 296 | 28 | 0 | 149 | 0 | 23 | 0 | 83 | 30 | 143 | 0 | 100 | 17 | 68 | 0 | 87 | 0 | 0 | 0 | 0 | 8009.5 | 927 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 510 | 0 | 0 | 0 | 1468.67 | 0 | 31 | 0 | 35 | 35 | 0 | 91 | 18 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 199 | 0 | 197 | 0 | 382 | 0 | 0 | 0 | 40 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 250 | 63 | 180 | 0 | 538 | 1190 | 17 | 6439.67 | 14449.17
20:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 17 | 17 | 53 | 129 | 32 | 15 | 35 | 108 | 0 | 0 | 0 | 545 | 0 | 35 | 330 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 510 | 107 | 16 | 81 | 0 | 0 | 50 | 8 | 54 | 0 | 0 | 0 | 69 | 17 | 13 | 1135 | 107 | 0 | 19 | 25.5 | 34 | 221 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 260 | 290 | 220 | 51 | 0 | 216 | 0 | 89 | 0 | 103 | 27 | 19 | 114 | 174 | 8 | 0 | 22 | 305 | 0 | 296 | 28 | 0 | 140 | 0 | 23 | 0 | 85 | 30 | 142 | 0 | 100 | 17 | 68 | 0 | 86 | 0 | 0 | 0 | 0 | 7991.5 | 927 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 510 | 0 | 0 | 0 | 1459.7 | 0 | 31 | 0 | 35 | 35 | 0 | 91 | 18 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 199 | 0 | 196 | 0 | 377 | 0 | 0 | 0 | 40 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 291 | 63 | 180 | 0 | 550 | 1190 | 17 | 6473.7 | 14465.2 | 76.76
21:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 17 | 0 | 53 | 127 | 32 | 15 | 35 | 108 | 0 | 0 | 0 | 465 | 0 | 35 | 329 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 510 | 106 | 16 | 85 | 0 | 7 | 50 | 8 | 54 | 0 | 0 | 0 | 70 | 17 | 17 | 1135 | 85 | 0 | 19 | 25.5 | 34 | 220 | 0 | 0 | 0 | 612 | 0 | 85 | 0 | 260 | 290 | 220 | 51 | 0 | 215 | 0 | 89 | 0 | 103 | 32 | 19 | 114 | 182 | 8 | 0 | 22 | 305 | 0 | 308 | 28 | 0 | 149 | 0 | 23 | 0 | 85 | 30 | 142 | 0 | 100 | 17 | 68 | 0 | 88 | 0 | 0 | 0 | 0 | 7949.5 | 927 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 510 | 0 | 0 | 0 | 1471.89 | 0 | 31 | 0 | 35 | 35 | 0 | 91 | 18 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 199 | 0 | 197 | 0 | 393 | 0 | 0 | 0 | 40 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 600 | 1212 | 17 | 6629.89 | 14579.39 | 76.79
22:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 0 | 53 | 113 | 32 | 15 | 35 | 108 | 0 | 0 | 0 | 450 | 0 | 35 | 270 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 510 | 107 | 16 | 85 | 0 | 9 | 50 | 8 | 54 | 0 | 0 | 0 | 71 | 17 | 22 | 1135 | 66 | 0 | 39 | 25.5 | 34 | 220 | 0 | 0 | 0 | 612 | 0 | 11 | 0 | 260 | 290 | 220 | 51 | 0 | 218 | 0 | 72 | 0 | 103 | 37 | 19 | 114 | 186 | 8 | 0 | 22 | 310 | 0 | 308 | 28 | 0 | 152 | 0 | 23 | 0 | 52 | 30 | 142 | 0 | 100 | 17 | 68 | 0 | 88 | 0 | 0 | 0 | 0 | 7774.5 | 927 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 510 | 0 | 0 | 0 | 1476.89 | 0 | 31 | 0 | 35 | 35 | 0 | 91 | 18 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 199 | 0 | 197 | 0 | 403 | 0 | 0 | 0 | 40 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 660 | 1212 | 17 | 6705.89 | 14480.39 | 76.82
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 17 | 0 | 35 | 132 | 32 | 15 | 35 | 108 | 0 | 0 | 0 | 485 | 0 | 35 | 306 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 515 | 107 | 16 | 77 | 0 | 7 | 49 | 8 | 17 | 0 | 0 | 0 | 73 | 17 | 26 | 1135 | 66 | 0 | 50 | 25.5 | 34 | 219 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 0 | 218 | 0 | 69 | 0 | 101 | 12 | 19 | 114 | 186 | 8 | 0 | 23 | 310 | 0 | 308 | 28 | 0 | 145 | 0 | 23 | 0 | 52 | 30 | 141 | 0 | 100 | 17 | 68 | 0 | 88 | 0 | 0 | 0 | 0 | 7699.5 | 927 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 24 | 0 | 516 | 0 | 0 | 0 | 1466.76 | 0 | 31 | 0 | 35 | 35 | 0 | 92 | 18 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 195 | 0 | 197 | 0 | 396 | 0 | 0 | 0 | 39 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 718 | 1222 | 17 | 6750.76 | 14450.26 | 76.85
Total KWH | 0 | 381120 | 70560 | 0 | 0 | 0 | 0 | 0 | 2203200 | 0 | 0 | 241236 | 50760 | 739584 | 3084960 | 935891 | 380945 | 535624 | 806400 | 0 | 0 | 0 | 12984856 | 0 | 270320 | 7403285 | 2927000 | 0 | 202523 | 3232800 | 480600 | 513360 | 0 | 12173636.36 | 2511600 | 396436 | 1206720 | 0 | 143520 | 361028 | 58593 | 335553 | 219840 | 180480 | 9000 | 1610380 | 422364 | 283680 | 27236363.64 | 1363273 | 0 | 928320 | 588679.2 | 226655 | 5033356 | 0 | 0 | 0 | 14285453 | 65475 | 983564 | 0 | 6393000 | 7388600 | 5462000 | 1153032 | 0 | 5257000 | 126288 | 705600 | 0 | 937920 | 241080 | 385140 | 1922040 | 3837120 | 853099 | 291264 | 387952 | 7389000 | 0 | 7685000 | 669000 | 0 | 3558518.18 | 46540 | 524040 | 0 | 1328640 | 713952 | 2635400 | 0 | 2421220 | 76680 | 1329600 | 109803 | 1483200 | 0 | 11300 | 247000 | 33840 | 173672861.38 | 22427636 | 0 | 0 | 285120 | 597248 | 912000 | 0 | 0 | 0 | 0 | 217584 | 566640 | 14792728 | 0 | 0 | 0 | 34009727 | 0 | 763608 | 0 | 406560 | 548352 | 0 | 558432 | 338042 | 0 | 365512 | 609518 | 240270 | 0 | 264336 | 0 | 0 | 4951827 | 0 | 5021127 | 0 | 9452582 | 0 | 28440 | 0 | 893236 | 1836497 | 154059 | 469958 | 0 | 0 | 0 | 47858.16 | 1118880 | 1068 | 401760 | 7113000 | 1502000 | 5365770 | 0 | 12567273 | 29480727.27 | 445200 | 158754575.43 | 332427436.81

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13655.83 | MW | 11:00 Hr. | Energy Generated |  |  | 332.4274 |  | MKWHr.
| Day Peak Demand |  |  | 16012.2 | MW | 12:00 Hr. | Energy Unserverd |  |  | 53.625 |  | MKWHr.
| Evening Peak Generation |  |  | 14579.39 | MW | 21:00 Hr. | Energy Demand |  |  | 386.0524 |  | MKWHr.
| Evening Peak Demand |  |  | 17553.39 | MW | 21:00 Hr. | Maximum Temperature |  |  | 31.5 |  | °C
| Minimum Generation of the Day |  |  | 13257.23 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 901.71 |  | MMCFD
| Maximum Generation of the Day |  |  | 14579.39 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.8051 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.6859 | 0 | 10.7302 | 0 | 0 | 0.20252 | 0 | 0 | 49.6187 | Gas | 123.3861 | Gas | 433175256.3668
| Chattogram Zone |  |  | 5.317 | 41.5218 | 8.7995 | 0 | 1.6104 | 0.074475 | 0 | 0.14352 | 57.4668 | Coal | 106.3688 | Coal | 701159556.5883
| Cumilla Zone |  |  | 26.1651 | 0 | 6.0313 | 0 | 0 | 0.29126 | 3.8371 | 0 | 36.3247 | HFO | 35.5929 | HFO | 691631813.992
| Mymensingh Zone |  |  | 0 | 0 | 2.9233 | 0 | 0 | 0.3681 | 0 | 0 | 3.2914 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.9248 | 0 | 0 | 0 | 0 | 0.04654 | 0 | 0 | 26.9713 | Hydro | 1.6104 | Hydro | 161038
| Khulna Zone |  |  | 0 | 14.7927 | 1.1 | 0 | 0 | 0.56664 | 23.3396 | 0 | 39.799 | Solar | 4.1392 | Solar | 66935624.4132
| Barishal Zone |  |  | 6.8678 | 49.161 | 0.84696 | 0 | 0 | 0.001068 | 0 | 0 | 56.8768 | Import | 61.1865 | Import | 367022663.93
| Rajshahi Zone |  |  | 19.4255 | 0 | 2.8553 | 0 | 0 | 1.2678 | 34.0097 | 0 | 57.5583 | Wind | 0.14352 | Wind | 2111179.2
| Rangpur Zone |  |  | 0 | 0.89324 | 2.3065 | 0 | 0 | 1.3208 | 0 | 0 | 4.5205
| Total |  |  | 123.3861 | 106.3688 | 35.5929 | 0 | 1.6104 | 4.1392 | 61.1865 | 0.14352 | 332.4274
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 433175256.3668 |  | Hydro | 161038
|  |  |  | Coal | 701159556.5883 |  | Solar | 66935624.4132
|  |  |  | HFO | 691631813.992 |  | Import | 367022663.93
|  |  |  | HSD | 0 |  | Wind | 2111179.2
[5 empty] | Total: | 226,21,97,132 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.4276 | Peak Hr Flow | 927.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50316509.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 34.0097 | Peak Hr Flow | 1471.89 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2170 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.8371 | Peak Hr Flow | 182.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2630 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 60.2745 | Peak Hr Flow | 2580.89 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 439 |  | 5839
|  |  |  | Chattogram |  | 186 |  | 1583
|  |  |  | Cumilla |  | 398 |  | 1718
|  |  |  | Mymensingh |  | 448 |  | 1485
|  |  |  | Sylhet |  | 103 |  | 643
|  |  |  | Khulna |  | 464 |  | 2077
|  |  |  | Barishal |  | 142 |  | 583
|  |  |  | Rajshahi |  | 360 |  | 1687
|  |  |  | Rangpur |  | 306 |  | 1172
|  |  |  | Total |  | 2846 |  | 16787
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 350
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:17 | 13:03 | Lakshmipur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to 33kV load side Redhot work.
| 10:11 | 15:10 | Goalpara- Khulna (C) 132kV Ckt-1 Scheduled S/D from Goalpara 132/33kV end Due to y
phase 0 Amp and from Khulna (C) end Due to S/D ordered by ALDC
| 11:45 | 12:53 | Narshingdi 132/33kV S/S T-1 HT Scheduled S/D Due to Tr-1 Transformer shutdown for 33kV | [7 empty] | 25.0MW load
|  |  | bushing B-Phase Oil leakage maintenance work. | [7 empty] | interrup.
| 11:45 | 12:53 | Narshingdi 132/33kV S/S T-1 LT Scheduled S/D Due to Tr-1 Transformer shutdown for 33kV | [7 empty] | 25.0MW load
|  |  | bushing B-Phase Oil leakage maintenance work. | [7 empty] | interrup.
|  | 13:04 | Lakshmipur 132/33kV S/S Transformer-2 LT is restored.
|  | 13:34 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
| 13:49 | 22:55 | Nabinagar 132/33kV S/S T-1 HT Tripped showing PRD relays Due to T-1 PRD Trip due to rain
water entered into the PRD Terminal box
| 13:49 | 22:55 | Nabinagar 132/33kV S/S T-1 LT Tripped showing Intertrip From HV DIFF. relays Due to None
| 15:16 |  | Haripur 412 MW CCPP Synchronized with remarks:- GT
| 17:26 |  | Haripur 412 MW CCPP Synchronized with remarks:- ST
|  | 17:35 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 is restored.
| 19:10 |  | RNPL U-1 synch
| 21:00 |  | Evening peak generation is 14579 MW.
| 23:01 | 00:18 | Chandraghona-Rangamati 132 kV Ckt-1 Forced S/D from Chandraghona 132/33kV end Due to
Y-Phase Line Isolator higg temperature maintenance work
| 00:14 | 01:05 | Ashuganj Network s/s 230 kV Bus coupler CB tripped showing E/F relay.
| 06:00 |  | Minimum generation 13421 MW
| 06:45 | 06:59 | Shahjibazar 132/33kV S/S TR-06 LT Tripped showing None relays Due to Bisic and Lakhai
Feeder Trip
| 06:45 | 06:59 | Shahjibazar 132/33kV S/S TR-06 HT Tripped showing Over current Relay relays Due to Bisic
and Lakhai Feeder Trip
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 396 | 2203200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 380945 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 2927000 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 329 | 7403285 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 241236 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 127 | 3084960 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 535624 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270320 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 480600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 513360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 70560 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 32 | 935891 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 53 | 739584 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 35 | 381120 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 806400 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 202523 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 50760 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 510 | 12173636.36 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 465 | 12984856 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3232800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2356 | 49618660.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 588679.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 65475 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 928320 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1610380 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5033356 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 226655 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 58593 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 361028 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 219840 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 283680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 1206720 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 9000 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 396436 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54 | 335553 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 422364 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 180480 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 106 | 2511600 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 85 | 1363273 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14285453 | Unit1 Under Maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 7 | 143520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1135 | 27236363.64 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2560.5 | 57466768.84
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 215 | 5257000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7388600 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 220 | 5462000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 260 | 6393000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 126288 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1153032 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 85 | 983564 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 22 | 387952 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 103 | 937920 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 182 | 3837120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 853099 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 385140 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1922040 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 32 | 241080 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 705600 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 291264 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1690 | 36324699
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 109803 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Gas shortage
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 88 | 1483200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1329600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 247000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 33840 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 76680 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 173 | 3291423
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 46540 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 669000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3558518.18 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 2635400 | Machine Problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 713952 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1328640 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2421220 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 524040 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7389000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 308 | 7685000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1170 | 26971310.18
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 927 | 22427636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 285120 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 597248 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 217584 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 566640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 510 | 14792728 | U#1 Under Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1532 | 39798956
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 600 | 12567273 | AGC, Unit1 Under Maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 401760 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 63 | 1502000 | STG Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1212 | 29480727.27 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5365770 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 445200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7113000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1068 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2435 | 56876798.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 365512 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 31 | 763608 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 18 | 338042 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 199 | 4951827 | Gas Restrction
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 197 | 5021127 | Gas Restrction
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 393 | 9452582 | AGC
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 240270 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 91 | 558432 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 548352 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 406560 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28440 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1471.89 | 34009727 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 264336 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 609518 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2493.89 | 57558333
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 40 | 893236 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 469958 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47858.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1836497 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 154059 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1118880 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 169 | 4520488.16
Eastern Grid Total |  |  |  |  | 17438.042 | 7949.5 | 173672861.38
Western Grid Total |  |  |  |  | 11852.195 | 6629.89 | 158754575.43
National Grid Total |  |  |  |  | 29290.237 | 14579.39 | 332427436.81
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-06-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9742.19 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4246 | MW
i) Dhaka area |  |  | 5400.19 |  | MW | i) Khulna area |  |  |  | 1612.6 | MW
ii) Chattogram area |  |  | 1445 |  | MW | ii) Barishal area |  |  |  | 440.8 | MW
iii) Cumilla area |  |  | 1320 |  | MW | iii) Rajshahi area |  |  |  | 1326.6 | MW
iv) Mymensingh area |  |  | 1037 |  | MW | iv) Rangpur area |  |  |  | 866 | MW
v) Sylhet area |  |  | 540 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13988.19 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 120 | 18:00 | 133 | Narshingdi | 157 | 20:00 | 199 | Zigatola | 78 | 19:00
2 | AKSML | 142 | 15:00 | 68 | Hasnabad | 84 | 23:00 | 134 | Natore | 121 | 07:00
3 | Aftabnagar | 44 | 00:00 | 69 | Hathazari | 90 | 00:00 | 135 | Nawabganj | 44 | 18:30
4 | Agargaon | 123 | 13:00 | 70 | Hatirjheel | 40 | 11:00 | 136 | Netrakona | 124 | 00:00
5 | Agrabad | 78 | 18:30 | 71 | Ishurdi | 73 | 09:00 | 137 | New | 86 | 12:00
6 | Amnura | 33 | 23:00 | 72 | Jaldhaka | 64 | 05:00 | 138 | Niamatpur | 79 | 22:00
7 | Ashuganj | 98 | 21:00 | 73 | Jamalpur | 110 | 21:00 | 139 | Noapara | 45 | 07:00
8 | BSRM | 194 | 18:00 | 74 | Jashore | 170 | 21:00 | 140 | PHP | 14 | 17:00
9 | Bagerhat | 88 | 04:00 | 75 | Jhenaidah | 102 | 14:00 | 141 | Pabna | 92 | 19:30
10 | Bajitpur | 89 | 02:00 | 76 | Joydebpur | 145 | 18:00 | 142 | Palashbari | 116 | 21:00
11 | Bakerganj | 14.4 | 19:00 | 77 | Joypurhat | 56 | 00:00 | 143 | Panchagarh | 53 | 02:00
12 | Bakulia | 100 | 21:00 | 78 | Juldah | 15 | 00:00 | 144 | Patiya | 11 | 00:00
13 | Banani | 51.6 | 12:00 | 79 | KSRM | 19 | 12:00 | 145 | Patuakhali | 62.5 | 22:00
14 | Bangabhaban | 20 | 10:00 | 80 | Kabirpur | 230 | 20:00 | 146 | Payra | 36 | 04:00
15 | Barapukuria | 57 | 07:00 | 81 | Kachua | 80 | 22:00 | 147 | Postogola | 63 | 23:00
16 | Barguna | 24 | 21:00 | 82 | Kaliganj | 20 | 19:30 | 148 | Pubail | 22 | 05:00
17 | Barishal | 107 | 11:00 | 83 | Kallyanpur | 126 | 19:00 | 149 | Purbachal | 34 | 13:00
18 | Barishal-230 | 96 | 00:00 | 84 | Kalurghat | 39 | 17:00 | 150 | Purbasadipur | 128 | 03:00
19 | Baroaulia | 62 | 23:00 | 85 | Kamrangirchar | 85 | 13:00 | 151 | Rahanpur | 35 | 19:00
20 | Baroirhat | 70 | 19:30 | 86 | Kaptai | N/A | N/A | 152 | Rahim | 27 | 17:00
21 | Bashundhara | 198 | 12:00 | 87 | Kasba | 33 | 21:00 | 153 | Rajbari | 72 | 01:00
22 | BashundharaCement | 12 | 01:00 | 88 | Kazla | 121 | 13:00 | 154 | Rajendrapur | 109 | 14:00
23 | Beanibazar | 84 | 23:00 | 89 | Keranigonj | 77 | 18:30 | 155 | Rajshahi | 109 | 22:00
24 | Benapole | 62 | 02:00 | 90 | Khagrachori | 28 | 00:00 | 156 | Rajshahi-230 | 79 | 20:00
25 | Bhaluka | 141 | 19:00 | 91 | Khulna | 65 | 22:00 | 157 | Ramganj | 100 | 08:00
26 | Bhandaria | 64 | 22:00 | 92 | Khulshi | 186 | 19:00 | 158 | Rampur | 45 | 00:00
27 | Bhangura | 34 | 19:00 | 93 | Kishoreganj | 115 | 06:00 | 159 | Rangamati | 15 | 19:00
28 | Bheramara(GK) | 55 | 00:00 | 94 | Kodda | 276 | 21:00 | 160 | Rangpur | 130 | 22:00
29 | Bhulta | 210 | 18:30 | 95 | Kulaura | 52 | 19:30 | 161 | Ruppur | 4.8 | 11:00
30 | Bog-Sherpur | 70 | 00:00 | 96 | Kurigram | 62 | 06:00 | 162 | SSM | 8 | 23:00
31 | Bogura | 183 | 21:00 | 97 | Kushtia | 146 | 19:30 | 163 | Saidpur | 104 | 09:00
32 | Borhanuddin | 80 | 19:30 | 98 | Laksam | 36 | 00:00 | 164 | Santhia | 32 | 23:00
33 | Brahmanbaria | 110 | 22:00 | 99 | Lakshmipur | 45 | 19:00 | 165 | Satkhira | 142 | 06:00
34 | Cantonment | 136 | 13:00 | 100 | Lalbag | 74 | 20:00 | 166 | Satmasjid | 103 | 19:30
35 | Chandina | 23 | 14:00 | 101 | Lalmonirhat | 50 | 08:00 | 167 | Savar | 216 | 18:30
36 | Chandpur | 72 | 06:00 | 102 | MI_Cement | 14.5 | 13:00 | 168 | SevenRings | 17.77 | 05:00
37 | Chandraghona | 30 | 01:00 | 103 | Madanganj | 42 | 10:00 | 169 | ShahCement | 24 | 15:00
38 | Chapai | 70 | 06:00 | 104 | Madaripur | 99 | 05:00 | 170 | Shahjadpur | 64 | 08:00
39 | Charfasson | 34 | 23:00 | 105 | Madartek | 86 | 23:00 | 171 | Shahjibazar | 128 | 23:00
40 | Charsaidpur | 37 | 19:00 | 106 | Madunaghat | 56 | 02:00 | 172 | Shahmirpur | 50 | 00:00
41 | Chauddagram | 62 | 02:00 | 107 | Magura | 60 | 23:00 | 173 | Shariatpur | 79 | 04:00
42 | Chhatak | 44 | 23:00 | 108 | Mahasthangarh | 73 | 03:00 | 174 | Sherpur | 136 | 19:00
43 | Chowmuhani | 137 | 01:00 | 109 | Maijdee | 35 | 04:00 | 175 | Shikalbaha | 28 | 10:00
44 | Chuadanga | 118 | 00:00 | 110 | Manikganj | 119 | 08:00 | 176 | Shitalakhya | 86.6 | 12:00
45 | Coxsbazar | 136 | 00:00 | 111 | Maniknagar | 76 | 13:00 | 177 | Sholosohor | 45 | 00:00
46 | Cumilla(N) | 114 | 01:00 | 112 | Matarbari | 54 | 01:00 | 178 | Shomvuganj | 22 | 04:00
47 | Cumilla(S) | 186 | 22:00 | 113 | Matuail | 99 | 05:00 | 179 | Shyampur | 154 | 09:00
48 | Daganbhuiyan | 36 | 21:00 | 114 | Metrorail_Motijheel | 30 | 09:00 | 180 | Siddhirganj | 129 | 12:00
49 | Daudkandi | 117 | 08:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Sirajganj | 118 | 19:30
50 | DhakaUniversity | 90 | 13:00 | 116 | Millgate | 110 | 12:00 | 182 | Sonargaon | 118 | 22:00
51 | Dhamrai | 100 | 01:00 | 117 | Mirpur | 153 | 19:00 | 183 | Sreemongol | 86 | 19:00
52 | Dhanmondi | 106 | 12:00 | 118 | Mirsorai | 46 | 14:00 | 184 | Sreepur | 108 | 17:00
53 | Dohazari | 91 | 01:00 | 119 | Mirzapur | 36 | 18:30 | 185 | Srinagar | 44.73 | 23:00
54 | Faridpur | 151 | 00:00 | 120 | Mithapukur | 61 | 22:00 | 186 | Sunamganj | 60 | 23:00
55 | Fatullah | 94 | 12:00 | 121 | Modern | N/A | N/A | 187 | Sylhet | 133 | 23:00
56 | Fenchuganj | 47 | 19:00 | 122 | Mogbazar | 103.4 | 12:00 | 188 | Sylhet_(South) | 57 | 23:00
57 | Feni | 92 | 19:30 | 123 | Mongla | 49 | 12:00 | 189 | TK | 25.5 | 00:00
58 | GPH | 12 | 01:00 | 124 | Motijheel | 52 | 12:00 | 190 | Tangail | 158 | 13:00
59 | Ghatail | 73 | 18:30 | 125 | Muktagacha | 35 | 11:00 | 191 | Taraganj | 22 | 02:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 109 | 21:00 | 192 | Tasnim | 35 | 17:00
61 | Ghorashal-230 | 109 | 09:00 | 127 | Muradnagar | 41 | 19:30 | 193 | Thakurgaon | 101 | 01:00
62 | Goalpara | 39 | 19:30 | 128 | Mymensingh | 179 | 22:00 | 194 | Tongi | 158 | 13:00
63 | Gollamari | 106 | 23:00 | 129 | Nabinagar | 82 | 13:00 | 195 | Ullahpara | 34 | 21:00
64 | Gopalganj | 96 | 07:00 | 130 | Naogaon | 119 | 02:00 | 196 | Ullon | 58 | 23:00
65 | Gulshan | 130 | 13:00 | 131 | Narail | 55 | 07:00 | 197 | Uttara | 97 | 13:00
66 | Halishahar | 103 | 11:00 | 132 | Narinda | 74 | 13:00 | 198 | UttaraNew | 55 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14201.5 | 2298 |  | 16602.91
1:00 | 13994.7 | 2164 |  | 16256.08
2:00 | 13919.7 | 2134 |  | 16149.73
3:00 | 13735.7 | 2065 |  | 15893.63
4:00 | 13665.7 | 2001 |  | 15756.75
5:00 | 13548.7 | 1903 |  | 15537.34
6:00 | 13462.97 | 1761 |  | 15302.97
7:00 | 13393.52 | 1626 |  | 15092.52
8:00 | 13338.71 | 1563 |  | 14971.71
9:00 | 13477.32 | 1722 |  | 15276.32
10:00 | 13395.17 | 2063 |  | 15551.17
11:00 | 13655.83 | 1862 |  | 15601.83
12:00 | 13630.2 | 2279 |  | 16012.2
13:00 | 13676.39 | 2384 |  | 16167.39
14:00 | 13672.79 | 2455 |  | 16237.79
15:00 | 13500.39 | 2761 |  | 16385.39
16:00 | 13320.45 | 2535 |  | 15969.45
17:00 | 13257.23 | 2455 |  | 15822.23
18:00 | 13389.17 | 2226 |  | 15715.17
19:00 | 14170.84 | 2497 |  | 16779.84
19:30 | 14449.17 | 2705 |  | 17276.17
20:00 | 14465.2 | 2611 |  | 17193.2
21:00 | 14579.39 | 2846 |  | 17553.39
22:00 | 14480.39 | 2587 |  | 17183.39
23:00 | 14450.26 | 2827 |  | 17404.26
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7213.5 | 6988 | 14201.5 | DAILY GENERATION CURVE
00:30 | 7175.1 | 6923 | 14098.1
01:00 | 7136.7 | 6858 | 13994.7 | 16-06-2026
01:30 | 7101.2 | 6856 | 13957.2
02:00 | 7065.7 | 6854 | 13919.7
02:30 | 6986.2 | 6841.5 | 13827.7
03:00 | 6906.7 | 6829 | 13735.7
03:30 | 6890.2 | 6810.5 | 13700.7
04:00 | 6873.7 | 6792 | 13665.7
04:30 | 6858.2 | 6749 | 13607.2
05:00 | 6842.7 | 6706 | 13548.7
05:30 | 6880.855 | 6624.98 | 13505.835
06:00 | 6919.01 | 6543.96 | 13462.97
06:30 | 6941.29 | 6486.955 | 13428.245
07:00 | 6963.57 | 6429.95 | 13393.52
07:30 | 6937.105 | 6429.01 | 13366.115
08:00 | 6910.64 | 6428.07 | 13338.71
08:30 | 6919.135 | 6488.88 | 13408.015
09:00 | 6927.63 | 6549.69 | 13477.32
09:30 | 6924.285 | 6511.96 | 13436.245
10:00 | 6920.94 | 6474.23 | 13395.17
10:30 | 6988.71 | 6536.79 | 13525.5
11:00 | 7056.48 | 6599.35 | 13655.83
11:30 | 7067.005 | 6576.01 | 13643.015
12:00 | 7077.53 | 6552.67 | 13630.2
12:30 | 7108.025 | 6545.27 | 13653.295
13:00 | 7138.52 | 6537.87 | 13676.39
13:30 | 7079.63 | 6594.96 | 13674.59
14:00 | 7020.74 | 6652.05 | 13672.79
14:30 | 7008.455 | 6578.135 | 13586.59
15:00 | 6996.17 | 6504.22 | 13500.39
15:30 | 6943.225 | 6467.195 | 13410.42
16:00 | 6890.28 | 6430.17 | 13320.45
16:30 | 6943.345 | 6345.495 | 13288.84
17:00 | 6996.41 | 6260.82 | 13257.23
17:30 | 7109.81 | 6213.39 | 13323.2
18:00 | 7223.21 | 6165.96 | 13389.17
18:30 | 7480.755 | 6299.25 | 13780.005
19:00 | 7738.3 | 6432.54 | 14170.84
19:30 | 8009.5 | 6439.67 | 14449.17
20:00 | 7991.5 | 6473.7 | 14465.2
20:30 | 7970.5 | 6551.795 | 14522.295 |  | Executive Engineer
21:00 | 7949.5 | 6629.89 | 14579.39 |  | Network Operation Division
21:30 | 7862 | 6667.89 | 14529.89
22:00 | 7774.5 | 6705.89 | 14480.39
22:30 | 7737 | 6728.325 | 14465.325
23:00 | 7699.5 | 6750.76 | 14450.26

## En-Curve
QF-LDC-12
Date | 16-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3073 | 1957 | 929 | 38 | 170 | 1473 | 74 | 4801 | 0 | 582 | 1096.5 | 0 | 0 | 8 | 2298 | DAILY ENERGY CURVE
00:30 | 3078 | 1961 | 929.5 | 38 | 168 | 1462 | 72.5 | 4801 | 0 | 524.5 | 1053.1 | 0 | 0 | 10.5 | 2231 | 16-06-2026
01:00 | 3083 | 1965 | 930 | 38 | 166 | 1451 | 71 | 4801 | 0 | 467 | 1009.7 | 0 | 0 | 13 | 2164
01:30 | 3087.5 | 1971.5 | 929.5 | 38 | 161 | 1452 | 67.5 | 4802.5 | 0 | 463.5 | 971.2 | 0 | 0 | 13 | 2149 | Energy Generated | 332.4274 |  | MKWHr
02:00 | 3092 | 1978 | 929 | 38 | 156 | 1453 | 64 | 4804 | 0 | 460 | 932.7 | 0 | 0 | 13 | 2134 | Energy not Served | 53.625 |  | MKWHr
02:30 | 3083 | 1948.5 | 929 | 38 | 153 | 1449.5 | 62.5 | 4780.5 | 0 | 461 | 912.7 | 0 | 0 | 10 | 2099.5 | Total Energy Requirement | 386.0524 |  | MKWHr
03:00 | 3074 | 1919 | 929 | 38 | 150 | 1446 | 61 | 4757 | 0 | 462 | 892.7 | 0 | 0 | 7 | 2065
03:30 | 3080.5 | 1921.5 | 929 | 38 | 152 | 1444 | 61 | 4754 | 0 | 437 | 870.7 | 0 | 0 | 13 | 2033
04:00 | 3087 | 1924 | 929 | 38 | 154 | 1442 | 61 | 4751 | 0 | 412 | 848.7 | 0 | 0 | 19 | 2001
04:30 | 3090.5 | 1916.5 | 929.5 | 38 | 151 | 1421.5 | 62 | 4736 | 0 | 398.5 | 849.7 | 0 | 0 | 14 | 1952
05:00 | 3094 | 1909 | 930 | 38 | 148 | 1401 | 63 | 4721 | 0 | 385 | 850.7 | 0 | 0 | 9 | 1903
05:30 | 3149 | 1917 | 929.5 | 38 | 144 | 1415.5 | 64.5 | 4621.5 | 6.885 | 393 | 821.45 | 0 | 0 | 5.5 | 1832
06:00 | 3204 | 1925 | 929 | 38 | 140 | 1430 | 66 | 4522 | 13.77 | 401 | 792.2 | 0 | 0 | 2 | 1761
06:30 | 3199.5 | 1949 | 929 | 38 | 142 | 1447.5 | 67.5 | 4414.5 | 52.545 | 397.5 | 790.2 | 0 | 0 | 1 | 1693.5
07:00 | 3195 | 1973 | 929 | 38 | 144 | 1465 | 69 | 4307 | 91.32 | 394 | 788.2 | 0 | 0 | 0 | 1626
07:30 | 3178.5 | 1939 | 929 | 38 | 145 | 1448 | 70 | 4280.5 | 167.415 | 379.5 | 790.2 | 0 | 0 | 1 | 1594.5
08:00 | 3162 | 1905 | 929 | 38 | 146 | 1431 | 71 | 4254 | 243.51 | 365 | 792.2 | 0 | 0 | 2 | 1563
08:30 | 3154 | 1915 | 928.5 | 38 | 147 | 1444.5 | 71.5 | 4255.5 | 294.065 | 357 | 799.45 | 0 | 0 | 3.5 | 1642.5
09:00 | 3146 | 1925 | 928 | 38 | 148 | 1458 | 72 | 4257 | 344.62 | 349 | 806.7 | 0 | 0 | 5 | 1722
09:30 | 3080.5 | 1917.5 | 928 | 38 | 154 | 1437 | 72.5 | 4240 | 417.545 | 346.5 | 800.2 | 0 | 0 | 4.5 | 1892.5
10:00 | 3015 | 1910 | 928 | 38 | 160 | 1416 | 73 | 4223 | 490.47 | 344 | 793.7 | 0 | 0 | 4 | 2063
10:30 | 3041.5 | 1917.5 | 927.5 | 38 | 160 | 1432.5 | 73 | 4235.5 | 507.8 | 350.5 | 839.7 | 0 | 0 | 2 | 1962.5
11:00 | 3068 | 1925 | 927 | 38 | 160 | 1449 | 73 | 4248 | 525.13 | 357 | 885.7 | 0 | 0 | 0 | 1862
11:30 | 3046.5 | 1932.25 | 927.5 | 38 | 164 | 1444.5 | 73 | 4237 | 550.565 | 355.5 | 868.7 | 0 | 0 | 5.5 | 2070.5
12:00 | 3025 | 1939.5 | 928 | 38 | 168 | 1440 | 73 | 4226 | 576 | 354 | 851.7 | 0 | 0 | 11 | 2279
12:30 | 3047 | 1928.5 | 927.5 | 38 | 159 | 1430.095 | 71 | 4230 | 579.5 | 354 | 876.7 | 0 | 0 | 12 | 2331.5
13:00 | 3069 | 1917.5 | 927 | 38 | 150 | 1420.19 | 69 | 4234 | 583 | 354 | 901.7 | 0 | 0 | 13 | 2384
13:30 | 3075 | 1905 | 926.5 | 38 | 159 | 1428.535 | 66 | 4256.5 | 566.355 | 352 | 892.7 | 0 | 0 | 9 | 2419.5
14:00 | 3081 | 1892.5 | 926 | 38 | 168 | 1436.88 | 63 | 4279 | 549.71 | 350 | 883.7 | 0 | 0 | 5 | 2455
14:30 | 3074.5 | 1902 | 926.5 | 38 | 167 | 1434.12 | 61.5 | 4287.5 | 461.77 | 342 | 887.7 | 0 | 0 | 4 | 2608
15:00 | 3068 | 1911.5 | 927 | 38 | 166 | 1431.36 | 60 | 4296 | 373.83 | 334 | 891.7 | 0 | 0 | 3 | 2761
15:30 | 3055 | 1897.75 | 927 | 38 | 163 | 1448.07 | 60 | 4295.5 | 276 | 336 | 912.1 | 0 | 0 | 2 | 2648
16:00 | 3042 | 1884 | 927 | 38 | 160 | 1464.78 | 60 | 4295 | 178.17 | 338 | 932.5 | 0 | 0 | 1 | 2535
16:30 | 3047.5 | 1885.5 | 927.5 | 38 | 164 | 1447.57 | 60 | 4269.5 | 139.77 | 353.5 | 955.5 | 0 | 0 | 0.5 | 2495
17:00 | 3053 | 1887 | 928 | 38 | 168 | 1430.36 | 60 | 4244 | 101.37 | 369 | 978.5 | 0 | 0 | 0 | 2455
17:30 | 3100 | 1888 | 927.5 | 38 | 163 | 1387.3 | 61.5 | 4196 | 68.9 | 415.5 | 1077 | 0 | 0 | 0.5 | 2340.5
18:00 | 3147 | 1889 | 927 | 38 | 158 | 1344.24 | 63 | 4148 | 36.43 | 462 | 1175.5 | 0 | 0 | 1 | 2226
18:30 | 3174 | 1887.5 | 927.5 | 38 | 169 | 1409.39 | 64.5 | 4197.5 | 18.215 | 540.5 | 1350.4 | 0 | 0 | 3.5 | 2361.5
19:00 | 3201 | 1886 | 928 | 38 | 180 | 1474.54 | 66 | 4247 | 0 | 619 | 1525.3 | 0 | 0 | 6 | 2497
19:30 | 3302 | 1892 | 927 | 38 | 182 | 1468.67 | 66 | 4275 | 0 | 626 | 1672.5 | 0 | 0 | 0 | 2705
20:00 | 3269 | 1911 | 927 | 38 | 174 | 1459.7 | 69 | 4328 | 0 | 623 | 1666.5 | 0 | 0 | 0 | 2611
20:30 | 3329.5 | 1898 | 927 | 38 | 178 | 1465.795 | 69.5 | 4372 | 0 | 621.5 | 1619.5 | 0 | 0 | 3.5 | 2728.5
21:00 | 3390 | 1885 | 927 | 38 | 182 | 1471.89 | 70 | 4416 | 0 | 620 | 1572.5 | 0 | 0 | 7 | 2846
21:30 | 3370.5 | 1867.5 | 927 | 38 | 184 | 1474.39 | 70.5 | 4446 | 0 | 613.5 | 1530.5 | 0 | 0 | 8 | 2716.5
22:00 | 3351 | 1850 | 927 | 38 | 186 | 1476.89 | 71 | 4476 | 0 | 607 | 1488.5 | 0 | 0 | 9 | 2587
22:30 | 3337 | 1868.5 | 927 | 38 | 186 | 1471.825 | 72 | 4512.5 | 0 | 596 | 1448.5 | 0 | 0 | 8 | 2707
23:00 | 3323 | 1887 | 927 | 38 | 186 | 1466.76 | 73 | 4549 | 0 | 585 | 1408.5 | 0 | 0 | 7 | 2827
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 16-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 186 | 37 | 590 | 128 | 1852 | 454 | Ishurdi-Ghorashal Ckt-1 | Export | 4280509.09
1:00 | 159 | 25 | 520 | 104 | 1722 | 398
2:00 | 155 | 22 | 522 | 110 | 1676 | 396 |  | Import | 0
3:00 | 153 | 22 | 502 | 96 | 1632 | 360
4:00 | 156 | 24 | 514 | 104 | 1636 | 368 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 155 | 25 | 504 | 104 | 1586 | 382
6:00 | 134 | 15 | 468 | 80 | 1268 | 268 |  | Import | 0
7:00 | 135 | 8 | 470 | 64 | 1340 | 260
8:00 | 153 | 20 | 502 | 86 | 1412 | 326 | Sirajganj-Sreepur Ckt-1 | Export | 3666000
9:00 | 194 | 38 | 596 | 102 | 1640 | 400
10:00 | 208 | 49 | 630 | 120 | 1740 | 470 |  | Import | 0
11:00 | 205 | 43 | 648 | 144 | 1698 | 480
12:00 | 211 | 52 | 630 | 130 | 1764 | 526 | Sirajganj-Sreepur Ckt-2 | Export | 3680000
13:00 | 210 | 51 | 618 | 134 | 1802 | 530
14:00 | 212 | 54 | 626 | 130 | 1792 | 524 |  | Import | 0
15:00 | 211 | 51 | 628 | 128 | 1774 | 486
16:00 | 207 | 53 | 610 | 130 | 1782 | 494 | Gopalganj-Aminbazar Ckt-1 | Export | 19320000
17:00 | 199 | 52 | 600 | 130 | 1640 | 476
18:00 | 196 | 51 | 540 | 104 | 1566 | 470 |  | Import | 0
18:30 | 186 | 42 | 550 | 114 | 1506 | 442
19:00 | 196 | 45 | 582 | 134 | 1508 | 416 | Gopalganj-Aminbazar Ckt-2 | Export | 19370000
19:30 | 168 | 35 | 456 | 64 | 1358 | 376
20:00 | 160 | 31 | 456 | 64 | 1380 | 352 |  | Import | 0
21:00 | 164 | 26 | 516 | 102 | 1490 | 368
22:00 | 161 | 21 | 518 | 100 | 1532 | 340 |  | Total Export | 50316509.09
23:00 | 164 | 21 | 556 | 88 | 1596 | 354 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 380 | 06:00 | 368 | 14:00 | Madunaghat | 397 | 20:00 | 389 | 13:00
Amtali | 409 | 19:30 | 405 | 01:00 | Meghnaghat | 383 | 06:00 | 372 | 12:00
Ashuganj | 411 | 6:00 | 395 | 12:00 | Payra | 412 | 19:00 | 406 | 12:00
Bhulta | 402 | 06:00 | 384 | 12:00 | Rahanpur | 401 | 18:00 | 392 | 07:00
Bibiana | 394 | 03:00 | 386 | 14:00 | Rampal | 394 | 00:00 | 384 | 22:00
BIPTC | 400 | 06:00 | 390 | 00:00
Bogura | 384 | 18:00 | 375 | 07:00
Gopalganj | 390 | 19:30 | 381 | 13:00
Kaliakoir | 387 | 22:00 | 358 | 12:00
Korerhat | 398 | 20:00 | 387 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 06:00 | 216 | 12:00 | Ishurdi | 235 | 18:00 | 227 | 07:00
AKSML | 234 | 19:30 | 225 | 12:00 | Jhenaidah | 224 | 10:00 | 215 | 22:00
Aminbazar | 229 | 06:00 | 218 | 13:00 | Kachua | 229 | 19:00 | 220 | 13:00
Ashuganj | 230 | 20:00 | 223 | 12:00 | Kaliakoir | 229 | 06:00 | 217 | 11:00
Ashuganj-400 | 230 | 20:00 | 223 | 12:00 | Keranigonj | 227 | 06:00 | 216 | 12:00
Baghabari | 233 | 04:00 | 227 | 22:00 | Khulna(S) | 224 | 18:00 | 217 | 07:00
Barapukuria | 221 | 18:00 | 212 | 07:00 | Korerhat | 228 | 19:30 | 220 | 12:00
Barapukuria-230 | 221 | 18:00 | 212 | 07:00 | Madunaghat | 233 | 20:00 | 227 | 14:00
Barishal | 233 | 10:00 | 229 | 01:00 | Madunaghat-400 | 234 | 20:00 | 229 | 13:00
Bheramara | 234 | 18:00 | 225 | 22:00 | Maniknagar | 229 | 06:00 | 218 | 12:00
Bhulta | 231 | 06:00 | 218 | 12:00 | Meghnaghat | 236 | 01:00 | 226 | 13:00
Bibiana | 239 | 06:00 | 225 | 14:00 | Meghnaghat-400 | 231 | 03:00 | 222 | 12:00
BIPTC | 236 | 18:00 | 225 | 07:00 | Mirsorai | 232 | 19:30 | 224 | 08:00
Bogura | 239 | 18:00 | 232 | 07:00 | Naogaon | 215 | 18:00 | 208 | 22:00
Bogura-400 | 238 | 18:00 | 231 | 07:00 | Purbasadipur | 219 | 19:00 | 211 | 00:00
Borhanuddin | 238 | 10:00 | 232 | 00:00 | Rajshahi | 233 | 18:00 | 224 | 23:00
BSRM | 228 | 20:00 | 220 | 13:00 | Rampal | 224 | 00:00 | 216 | 07:00
Charfasson | 237 | 18:00 | 234 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 22:00 | 220 | 13:00 | Rampura | 231 | 06:00 | 217 | 13:00
Cumilla(N) | 227 | 05:00 | 221 | 13:00 | Shikalbaha | 233 | 22:00 | 228 | 11:00
Faridpur | 230 | 18:00 | 226 | 12:00 | Shyampur | 229 | 06:00 | 218 | 12:00
Fenchuganj | 232 | 06:00 | 228 | 23:00 | Siddhirganj | 230 | 22:00 | 220 | 12:00
Feni | 228 | 20:00 | 221 | 12:00 | Sirajgonj | 239 | 18:00 | 233 | 11:00
Ghorashal | 230 | 00:00 | 220 | 12:00 | Sreepur | 235 | 20:00 | 218 | 11:00
Ghorashal-230 | 219 | 17:00 | 205 | 12:00 | Tongi | 222 | 04:00 | 202 | 13:00
Gopalganj | 231 | 18:00 | 227 | 11:00
GPH | 232 | 20:00 | 225 | 12:00
Haripur | 231 | 06:00 | 219 | 13:00
Hasnabad | 226 | 01:00 | 217 | 13:00
Hathazari | 230 | 19:00 | 222 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 125 | 12:00 | Madunaghat | 135 | 20:00 | 131 | 12:00
Agargaon | 136 | 06:00 | 127 | 12:00 | Magura | 133 | 10:00 | 126 | 23:00
Agrabad | 133 | 02:00 | 128 | 14:00 | Mahasthangarh | 135 | 18:00 | 129 | 01:00
AKS | 132 | 20:00 | 127 | 14:00 | Maijdee | 128 | 20:00 | 123 | 11:00
Aminbazar | 130 | 05:00 | 124 | 11:00 | Manikganj | 131 | 23:00 | 125 | 14:00
Amnura | 137 | 00:00 | 128 | 22:00 | Maniknagar | 135 | 05:00 | 124 | 13:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 126 | 22:00 | 113 | 00:00
Ashuganj-230 | 136 | 20:00 | 133 | 00:00 | Matuail | 133 | 03:00 | 125 | 13:00
Bagerhat | 128 | 10:00 | 120 | 23:00 | Metrorail_Motijheel | 135 | 06:00 | 122 | 20:00
Bajitpur | 130 | 19:30 | 123 | 02:00 | Metrorail_Uttara | 135 | 04:00 | 123 | 12:00
Bakerganj | 132 | 16:00 | 129 | 02:00 | Millgate | 135 | 05:00 | 124 | 12:00
Bakulia | 135 | 22:00 | 130 | 00:00 | Mirpur | 129 | 04:00 | 120 | 12:00
Banani | 136 | 06:00 | 125 | 13:00 | Mirzapur | 130 | 06:00 | 125 | 14:00
Bangabhaban | 135 | 05:00 | 125 | 13:00 | Mithapukur | 131 | 18:00 | 124 | 07:00
Barapukuria | 134 | 18:00 | 125 | 07:00 | MI_Cement | 130 | 06:00 | 120 | 12:00
Barguna | 132 | 09:00 | 128 | 11:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 00:00 | 130 | 06:00 | Mogbazar | 135 | 03:00 | 127 | 12:00
Barishal-230 | 133 | 10:00 | 130 | 23:00 | Mongla | 129 | 10:00 | 121 | 23:00
Baroaulia | 134 | 20:00 | 130 | 11:00 | Motijheel | 135 | 05:00 | 125 | 13:00
Baroirhat | 132 | 08:00 | 127 | 13:00 | Muktagacha | 129 | 18:00 | 117 | 00:00
Bashundhara | 135 | 03:00 | 123 | 12:00 | Munshiganj | 131 | 04:00 | 125 | 12:00
BashundharaCement | 133 | 22:00 | 126 | 12:00 | Muradnagar | 129 | 06:00 | 124 | 12:00
Beanibazar | 126 | 18:00 | 118 | 23:00 | Mymensingh | 125 | 19:30 | 113 | 01:00
Benapole | 130 | 18:00 | 121 | 23:00 | Nabinagar | 133 | 06:00 | 123 | 12:00
Bhaluka | 132 | 19:30 | 128 | 11:00 | Naogaon | 133 | 18:00 | 125 | 22:00
Bhandaria | 130 | 15:00 | 122 | 22:00 | Narail | 133 | 00:00 | 125 | 23:00
Bhangura | 134 | 18:30 | 131 | 00:00 | Narinda | 135 | 05:00 | 124 | 13:00
Bheramara | 135 | 18:00 | 130 | 07:00 | Narshingdi | 130 | 03:00 | 123 | 12:00
Bheramara(GK) | 135 | 18:00 | 130 | 07:00 | Natore | 134 | 18:00 | 129 | 07:00
Bhulta | 129 | 05:00 | 124 | 12:00 | Nawabganj | 137 | 06:00 | 130 | 12:00
Bog-Sherpur | 136 | 18:00 | 130 | 07:00 | Netrakona | 122 | 07:00 | 117 | 00:00
Bogura | 138 | 18:00 | 132 | 07:00 | New | 136 | 06:00 | 126 | 11:00
Bogura-230 | 138 | 18:00 | 133 | 07:00 | Niamatpur | 131 | 18:00 | 127 | 22:00
Brahmanbaria | 130 | 06:00 | 125 | 23:00 | Noapara | 131 | 00:00 | 125 | 07:00
Cantonment | 135 | 05:00 | 127 | 12:00 | Pabna | 134 | 17:00 | 129 | 07:00
Chandina | 132 | 06:00 | 128 | 12:00 | Palashbari | 131 | 18:00 | 124 | 03:00
Chandpur | 134 | 19:00 | 123 | 02:00 | Panchagarh | 137 | 18:00 | 130 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 135 | 19:00 | 132 | 01:00 | Patiya | 135 | 22:00 | 129 | 11:00
Chapai | 131 | 10:00 | 126 | 05:00 | Patuakhali | 132 | 16:00 | 129 | 22:00
Charsaidpur | 133 | 06:00 | 126 | 13:00 | Payra | 134 | 15:00 | 132 | 08:00
Chauddagram | 131 | 19:30 | 126 | 13:00 | PHP | 131 | 06:00 | 127 | 13:00
Chhatak | 125 | 05:00 | 115 | 23:00 | Postogola | 131 | 04:00 | 123 | 12:00
Chowmuhani | 127 | 18:00 | 123 | 14:00 | Pubail | 128 | 05:00 | 122 | 12:00
Chuadanga | 131 | 18:00 | 123 | 23:00 | Purbachal | 136 | 06:00 | 125 | 12:00
Coxsbazar | 123 | 22:00 | 115 | 00:00 | Purbasadipur | 133 | 19:00 | 128 | 07:00
Cumilla(N) | 131 | 18:00 | 127 | 13:00 | Rahanpur | 134 | 18:00 | 131 | 02:00
Cumilla(S) | 132 | 06:00 | 123 | 19:30 | Rahanpur-400 | 134 | 18:00 | 131 | 07:00
Daganbhuiyan | 130 | 19:30 | 125 | 13:00 | Rahim | 133 | 06:00 | 126 | 13:00
Daudkandi | 129 | 20:00 | 122 | 12:00 | Rajbari | 130 | 18:00 | 127 | 11:00
DhakaUniversity | 136 | 05:00 | 126 | 12:00 | Rajendrapur | 131 | 19:30 | 125 | 11:00
Dhamrai | 134 | 06:00 | 125 | 12:00 | Rajshahi | 132 | 00:00 | 127 | 07:00
Dhanmondi | 136.5 | 06:00 | 125 | 13:00 | Rajshahi-230 | 134 | 18:00 | 129 | 07:00
Dohazari | 130 | 11:00 | 125 | 00:00 | Ramganj | 130 | 19:30 | 120 | 02:00
Faridpur | 131 | 08:00 | 128 | 01:00 | Rampur | 134 | 22:00 | 130 | 11:00
Fatullah | 137 | 06:00 | 120 | 12:00 | Rampura | 136 | 06:00 | 125 | 12:00
Fenchuganj | 132 | 06:00 | 128 | 23:00 | Rangamati | 134 | 19:30 | 131 | 12:00
Feni | 131 | 19:30 | 126 | 11:00 | Rangpur | 129 | 18:00 | 121 | 07:00
Feni-230 | 132 | 20:00 | 127 | 12:00 | Ruppur | 136 | 18:00 | 130 | 22:00
Ghatail | 125 | 23:00 | 116 | 03:00 | Saidpur | 133 | 19:00 | 126 | 03:00
Ghorashal | 129 | 02:00 | 122 | 14:00 | Santhia | 136 | 18:00 | 131 | 06:00
Goalpara | 135 | 18:00 | 128 | 07:00 | Satkhira | 129 | 13:00 | 120 | 07:00
Gollamari | 133 | 00:00 | 128 | 07:00 | Satmasjid | 135 | 06:00 | 127 | 12:00
Gopalganj | 132 | 18:00 | 127 | 07:00 | Savar | 129 | 02:00 | 120 | 12:00
Gopalganj-400 | 132 | 18:00 | 130 | 07:00 | SevenRings | 130 | 06:00 | 123 | 14:00
Gulshan | 135 | 05:00 | 125 | 13:00 | ShahCement | 133 | 06:00 | 126 | 13:00
Halishahar | 135 | 22:00 | 130 | 11:00 | Shahjadpur | 138 | 20:00 | 133 | 22:00
Haripur | 134 | 06:00 | 127 | 12:00 | Shahjibazar | 130 | 20:00 | 124 | 23:00
HaripurSBU | 134 | 06:00 | 127 | 14:00 | Shahmirpur | 135 | 22:00 | 131 | 09:00
Hasnabad | 131 | 03:00 | 123 | 13:00 | Shariatpur | 129 | 10:00 | 127 | 07:00
Hathazari | 135 | 03:00 | 131 | 14:00 | Sherpur | 125 | 18:30 | 111 | 00:00
Hatirjheel | 136 | 04:00 | 126 | 12:00 | Shikalbaha | 124 | 19:30 | 119 | 14:00
Ishurdi | 137 | 18:00 | 132 | 07:00 | Shikalbaha-230 | 136 | 19:30 | 132 | 00:00
Jaldhaka | 129 | 18:00 | 123 | 05:00 | Shitalakhya | 130 | 06:00 | 120 | 12:00
Jamalpur | 131 | 18:30 | 115 | 00:00 | Sholosohor | 135 | 20:00 | 131 | 09:00
Jashore | 131 | 18:00 | 122 | 23:00 | Shomvuganj | 124 | 18:00 | 117 | 02:00
Jhenaidah | 135 | 18:00 | 127 | 23:00 | Shyampur | 135 | 02:00 | 128 | 11:00
Jhenaidah-230 | 134 | 10:00 | 129 | 22:00 | Shyampur-230 | 137 | 03:00 | 130 | 12:00
Joydebpur | 127 | 05:00 | 120 | 15:00 | Siddhirganj | 134 | 04:00 | 127 | 12:00
Joypurhat | 133 | 18:00 | 126 | 07:00 | Sirajganj | 132 | 00:00 | 129 | 07:00
Juldah | 135 | 22:00 | 130 | 16:00 | Sonargaon | 131 | 06:00 | 125 | 11:00
Kabirpur | 135 | 20:00 | 120 | 12:00 | Sreemongol | 129 | 08:00 | 123 | 23:00
Kachua | 131 | 19:00 | 125 | 11:00 | Sreepur | 133 | 19:30 | 128 | 11:00
Kaliakoir | 136 | 06:00 | 124 | 19:00 | Srinagar | 137 | 05:00 | 130 | 12:00
Kaliganj | 134 | 01:00 | 127 | 23:00 | SSM | 140 | 06:00 | 132 | 11:00
Kallyanpur | 128 | 00:00 | 123 | 11:00 | Sunamganj | 122 | 16:00 | 113 | 23:00
Kalurghat | 135 | 06:00 | 131 | 14:00 | Sylhet | 127 | 20:00 | 122 | 23:00
Kamrangirchar | 136 | 04:00 | 119 | 12:00 | Sylhet_(South) | 127 | 08:00 | 122 | 23:00
Kaptai | 137 | 20:00 | 135 | 2:00 | Tangail | 126 | 10:00 | 120 | 01:00
Kasba | 129 | 20:00 | 124 | 12:00 | Taraganj | 130 | 18:00 | 123 | 07:00
Kazla | 135 | 06:00 | 124 | 13:00 | Tasnim | 131 | 03:00 | 125 | 12:00
Keranigonj | 138 | 06:00 | 131 | 12:00 | Thakurgaon | 136 | 19:00 | 129 | 07:00
Khagrachori | 134 | 20:00 | 131 | 00:00 | TK | 134 | 05:00 | 132 | 00:00
Khulna | 133 | 18:00 | 127 | 07:00 | Tongi | 138 | 04:00 | 125 | 13:00
Khulna(S) | 134 | 18:00 | 128 | 07:00 | Ullahpara | 134 | 18:00 | 130 | 07:00
Khulshi | 133 | 22:00 | 128 | 12:00 | Ullon | 136 | 06:00 | 126 | 12:00
Kishoreganj | 128 | 19:30 | 122 | 11:00 | Uttara | 135 | 07:00 | 122 | 12:00
Kodda | 135 | 19:30 | 127 | 12:00 | UttaraNew | 135 | 05:00 | 123 | 12:00
Korerhat | 134 | 20:00 | 130 | 12:00 | Zigatola | 137 | 06:00 | 130 | 12:00
KSRM | 135 | 23:00 | 130 | 10:00
Kulaura | 131 | 06:00 | 126 | 23:00
Kurigram | 128 | 19:00 | 119 | 06:00
Kushtia | 133 | 00:00 | 128 | 07:00
Laksam | 131 | 19:30 | 123 | 14:00
Lakshmipur | 127 | 19:30 | 122 | 14:00
Lalbag | 137 | 04:00 | 130 | 12:00
Lalmonirhat | 126 | 13:00 | 120 | 07:00
Madanganj | 133 | 22:00 | 126 | 12:00
Madaripur | 130 | 00:00 | 128 | 11:00
Madartek | 136 | 06:00 | 126 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division