## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-06-2026 | [28 empty] | Date: | 17-06-2026 | [28 empty] | Date: | 17-06-2026 | [28 empty] | Date: | 17-06-2026 | [28 empty] | Date: | 17-06-2026 | [18 empty] | Date: | 17-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [18 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 17 | 0 | 21 | 142 | 32 | 15 | 35 | 54 | 0 | 0 | 0 | 490 | 0 | 0 | 303 | 0 | 0 | 0 | 86 | 20 | 21 | 0 | 530 | 107 | 16 | 72 | 0 | 11 | 50 | 0 | 17 | 0 | 0 | 0 | 73 | 17 | 28 | 1135 | 66 | 0 | 6 | 25.5 | 0 | 220 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 240 | 290 | 240 | 51 | 0 | 202 | 0 | 49 | 0 | 31 | 0 | 19 | 114 | 182 | 8 | 0 | 23 | 305 | 0 | 307 | 28 | 0 | 151 | 0 | 23 | 0 | 52 | 30 | 142 | 0 | 100 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7328.5 | 844 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 515 | 0 | 0 | 0 | 1472.19 | 0 | 31 | 0 | 35 | 35 | 0 | 92 | 26 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 194 | 0 | 197 | 0 | 386 | 0 | 0 | 0 | 41 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 782 | 1222 | 17 | 6652.19 | 13980.69 | 76.88
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 17 | 142 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 460 | 0 | 0 | 296 | 0 | 0 | 0 | 130 | 20 | 21 | 0 | 510 | 106 | 16 | 48 | 0 | 11 | 50 | 0 | 17 | 0 | 0 | 0 | 74 | 17 | 28 | 1135 | 60 | 0 | 6 | 25.5 | 0 | 220 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 260 | 290 | 280 | 51 | 0 | 197 | 0 | 34 | 0 | 24 | 0 | 19 | 114 | 172 | 8 | 0 | 23 | 300 | 0 | 308 | 28 | 0 | 154 | 0 | 23 | 0 | 53 | 30 | 142 | 0 | 100 | 0 | 58 | 0 | 57 | 0 | 0 | 0 | 0 | 7236.5 | 814 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 516 | 0 | 0 | 0 | 1466.82 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 194 | 0 | 197 | 0 | 382 | 0 | 0 | 0 | 41 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 817 | 1222 | 17 | 6485.82 | 13722.32 | 76.91
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 17 | 141 | 32 | 15 | 35 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 301 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 520 | 107 | 16 | 31 | 0 | 3 | 0 | 0 | 17 | 0 | 0 | 0 | 71 | 17 | 28 | 1135 | 61 | 0 | 6 | 25.5 | 0 | 220 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 240 | 290 | 260 | 51 | 0 | 205 | 0 | 0 | 0 | 17 | 0 | 19 | 17 | 178 | 8 | 0 | 23 | 305 | 0 | 308 | 28 | 0 | 153 | 0 | 23 | 0 | 53 | 30 | 143 | 0 | 100 | 0 | 58 | 0 | 58 | 0 | 0 | 0 | 0 | 7014.5 | 814 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 516 | 0 | 0 | 0 | 1473.05 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 196 | 0 | 197 | 0 | 398 | 0 | 0 | 0 | 42 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 820 | 1222 | 17 | 6514.05 | 13528.55 | 76.91
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 17 | 141 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 305 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 510 | 107 | 16 | 31 | 0 | 7 | 0 | 0 | 17 | 0 | 0 | 0 | 65 | 17 | 21 | 1135 | 61 | 0 | 6 | 25.5 | 0 | 220 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 240 | 290 | 240 | 51 | 0 | 205 | 0 | 0 | 0 | 17 | 0 | 19 | 17 | 164 | 8 | 0 | 23 | 310 | 0 | 308 | 28 | 0 | 154 | 0 | 23 | 0 | 52 | 30 | 141 | 0 | 100 | 0 | 58 | 0 | 58 | 0 | 0 | 0 | 0 | 6929.5 | 915 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 514 | 0 | 0 | 0 | 1465.05 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 26 | 8 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 199 | 0 | 197 | 0 | 401 | 0 | 0 | 0 | 42 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 820 | 1222 | 17 | 6619.05 | 13548.55 | 76.91
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 17 | 142 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 475 | 0 | 0 | 299 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 500 | 94 | 16 | 31 | 0 | 12 | 0 | 0 | 17 | 0 | 0 | 0 | 62 | 17 | 22 | 1135 | 61 | 0 | 6 | 25.5 | 0 | 220 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 240 | 290 | 240 | 51 | 0 | 200 | 0 | 0 | 0 | 17 | 0 | 19 | 17 | 168 | 16 | 0 | 23 | 310 | 0 | 320 | 28 | 0 | 153 | 0 | 23 | 0 | 53 | 30 | 142 | 0 | 100 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6899.5 | 915 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 516 | 0 | 0 | 0 | 1468.64 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 197 | 0 | 384 | 0 | 0 | 0 | 44 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 820 | 1222 | 17 | 6593.64 | 13493.14 | 76.94
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 17 | 142 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 301 | 0 | 0 | 0 | 123 | 20 | 21 | 0 | 520 | 107 | 16 | 32 | 0 | 11 | 0 | 0 | 17 | 0 | 0 | 0 | 62 | 17 | 23 | 1135 | 60 | 0 | 6 | 25.5 | 0 | 221 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 240 | 290 | 240 | 51 | 0 | 202 | 0 | 0 | 0 | 17 | 0 | 19 | 17 | 158 | 52.2 | 0 | 23 | 305 | 0 | 320 | 28 | 0 | 153 | 0 | 23 | 0 | 53 | 30 | 142 | 0 | 100 | 0 | 49 | 0 | 48 | 18 | 0 | 0 | 0 | 6971.7 | 915 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 517 | 0 | 0 | 0 | 1471.67 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 199 | 0 | 393 | 0 | 0 | 0 | 44 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 63 | 220 | 0 | 820 | 1222 | 17 | 6566.67 | 13538.37 | 76.97
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 17 | 130 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 292 | 0 | 0 | 2 | 123 | 19.5 | 21 | 0 | 490 | 106 | 16 | 31 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0.25 | 65 | 17 | 23 | 1135 | 56 | 0 | 6 | 25.5 | 0 | 220 | 0 | 0 | 0 | 612 | 2 | 11 | 0 | 240 | 290 | 240 | 51 | 0 | 195 | 0 | 0 | 0 | 17 | 0 | 19 | 17 | 160 | 52.2 | 1 | 23 | 300 | 0 | 320 | 28 | 0 | 142 | 1 | 23 | 0 | 52 | 30 | 142 | 0 | 100 | 0 | 49 | 0.16 | 48 | 11 | 0 | 0.3 | 0 | 6802.91 | 915 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.44 | 514 | 0 | 0 | 0 | 1489.89 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 18 | 43 | 3.25 | 3 | 0 | 0 | 1.41 | 0 | 0 | 198 | 0 | 201 | 0 | 385 | 0 | 0.12 | 0 | 45 | 35 | 1 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.03 | 16 | 307 | 63 | 220 | 0 | 820 | 1222 | 17 | 6618.34 | 13421.25 | 77
07:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 17 | 123 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 307 | 0 | 0 | 5 | 123 | 19.5 | 21 | 0 | 510 | 107 | 16 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72 | 67 | 17 | 23 | 1135 | 56 | 0 | 6 | 25.5 | 0 | 218 | 0 | 0 | 0 | 612 | 2 | 13 | 0 | 260 | 290 | 260 | 51 | 0 | 216 | 0 | 0 | 0 | 17 | 0 | 19 | 17 | 154 | 52.2 | 10 | 23 | 300 | 0 | 320 | 28 | 0 | 146 | 2 | 23 | 0 | 72 | 30 | 143 | 0 | 100 | 0 | 58 | 0.41 | 57 | 9 | 0 | 1.57 | 0 | 6961.9 | 915 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 514 | 0 | 0 | 0 | 1491.21 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 18 | 43 | 9.14 | 21 | 0 | 0 | 5.58 | 0 | 0 | 195 | 0 | 203 | 0 | 390 | 0 | 0.51 | 0 | 47 | 35 | 3 | 0 | 0 | 0 | 0 | 1.9 | 14 | 0.18 | 16 | 307 | 63 | 220 | 0 | 820 | 1223 | 17 | 6669.52 | 13631.42 | 77.09
08:00 | 0 | 2 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 0 | 17 | 123 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 307 | 0 | 0 | 9 | 123 | 19 | 21 | 0 | 530 | 107 | 16 | 31 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.56 | 70 | 17 | 5 | 1135 | 50 | 0 | 3 | 25.5 | 0 | 218 | 0 | 0 | 0 | 612 | 1 | 13 | 0 | 300 | 290 | 260 | 51 | 0 | 216 | 0 | 0 | 0 | 17 | 0 | 19 | 17 | 162 | 52.2 | 24 | 23 | 305 | 0 | 332 | 28 | 0 | 142 | 3 | 23 | 0 | 83 | 30 | 141 | 0 | 101 | 0 | 58 | 0.03 | 58 | 10 | 0 | 0 | 0 | 7103.29 | 915 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 46 | 510 | 0 | 0 | 0 | 1493.61 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 18 | 52.2 | 17.44 | 39 | 0 | 0 | 10.89 | 0 | 0 | 189 | 0 | 203 | 0 | 385 | 0 | 0.85 | 0 | 46 | 35 | 7 | 0 | 0 | 0 | 0 | 3.6 | 13 | 0.18 | 16 | 307 | 63 | 180 | 0 | 820 | 1212 | 17 | 6670.77 | 13774.06 | 77.12
09:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 17 | 0 | 17 | 136 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 435 | 0 | 0 | 304 | 0 | 0 | 17 | 123 | 19 | 21 | 0 | 500 | 107 | 16 | 31 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2.96 | 72 | 17 | 2 | 1135 | 50 | 0 | 6 | 25.5 | 0 | 217 | 0 | 0 | 0 | 612 | 5 | 13 | 0 | 300 | 290 | 260 | 51 | 0 | 208 | 0 | 0 | 0 | 17 | 0 | 19 | 17 | 162 | 52.2 | 49 | 22 | 310 | 0 | 332 | 28 | 0 | 152 | 3 | 22 | 0 | 83 | 30 | 142 | 0 | 101 | 0 | 58 | 0.6 | 58 | 5 | 0.4 | 2.63 | 0 | 7135.29 | 915 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42 | 510 | 0 | 0 | 0 | 1484.38 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 18 | 52.2 | 32.35 | 44 | 0 | 0 | 17.25 | 0 | 0 | 198 | 0 | 201 | 0 | 386 | 0 | 1.8 | 0 | 45 | 35 | 14 | 0 | 0 | 0 | 0 | 4.9 | 25 | 0.59 | 16 | 307 | 63 | 220 | 0 | 820 | 1185 | 17 | 6724.47 | 13859.76 | 77.15
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 20 | 0 | 19 | 124 | 32 | 15 | 17 | 17 | 0 | 0 | 0 | 420 | 0 | 0 | 295 | 0 | 0 | 19 | 123 | 18.5 | 21 | 0 | 500 | 106 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.67 | 0 | 17 | 2 | 1135 | 38 | 0 | 6 | 25.5 | 0 | 217 | 0 | 0 | 0 | 612 | 7 | 13 | 0 | 250 | 290 | 260 | 51 | 0 | 192 | 0 | 0 | 0 | 17 | 0 | 19 | 17 | 162 | 44 | 35 | 22 | 300 | 0 | 320 | 28 | 0 | 142 | 3 | 23 | 0 | 43 | 30 | 143 | 0 | 101 | 0 | 49 | 6.2 | 48 | 0 | 1 | 7.57 | 0 | 6852.44 | 915 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 64.82 | 510 | 0 | 0 | 0 | 1488.56 | 0 | 32 | 0 | 0 | 20 | 0 | 0 | 21 | 52.2 | 29.77 | 51 | 0 | 0 | 9.08 | 0 | 0 | 200 | 0 | 201 | 0 | 378 | 0 | 1.86 | 0 | 46 | 35 | 23 | 0 | 0 | 0 | 0 | 4.6 | 90 | 0.39 | 16 | 307 | 63 | 220 | 0 | 820 | 1175 | 17 | 6829.28 | 13681.72 | 77.17
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 24.7 | 0 | 17 | 124 | 32 | 0 | 17 | 35 | 0 | 0 | 0 | 425 | 0 | 0 | 316 | 0 | 0 | 22 | 123 | 18.5 | 21 | 0 | 520 | 107 | 16 | 31 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 3.74 | 0 | 17 | 2 | 1135 | 33 | 0 | 6 | 25.5 | 0 | 216 | 0 | 0 | 0 | 612 | 8 | 13 | 0 | 235 | 290 | 260 | 51 | 0 | 198 | 0 | 0 | 0 | 17 | 16 | 19 | 17 | 170 | 16 | 47 | 22 | 305 | 0 | 296 | 28 | 0 | 147 | 1 | 10 | 0 | 43 | 30 | 142 | 0 | 101 | 0 | 49 | 17.8 | 48 | 0 | 1.4 | 19.24 | 0 | 6917.88 | 915 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 93.58 | 510 | 0 | 0 | 0 | 1486.7 | 0 | 31 | 0 | 0 | 35 | 0 | 0 | 14 | 8 | 50.19 | 56 | 0 | 0 | 42.71 | 0 | 0 | 198 | 0 | 193 | 0 | 397 | 0 | 4.08 | 0 | 46 | 0 | 29 | 0 | 0 | 0 | 0 | 7.4 | 128 | 0.14 | 16 | 307 | 63 | 220 | 0 | 820 | 1175 | 17 | 6900.8 | 13818.68 | 77.19
12:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 27.5 | 0 | 17 | 126 | 32 | 15 | 17 | 35 | 0 | 0 | 0 | 455 | 0 | 0 | 295 | 0 | 0 | 24 | 123 | 18 | 21 | 0 | 520 | 107 | 16 | 31 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 4.28 | 0 | 17 | 2 | 1135 | 38 | 0 | 6 | 25.5 | 0 | 215 | 0 | 0 | 0 | 612 | 20 | 35 | 0 | 235 | 290 | 260 | 51 | 0 | 207 | 0 | 1 | 0 | 17 | 18 | 8 | 17 | 172 | 8 | 55 | 22 | 300 | 0 | 296 | 28 | 0 | 150 | 1 | 17 | 0 | 40 | 30 | 141 | 0 | 101 | 0 | 59 | 18.2 | 58 | 0 | 1.8 | 20.72 | 0 | 7013 | 915 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 38.95 | 510 | 0 | 0 | 0 | 1470.41 | 0 | 31 | 0 | 0 | 35 | 0 | 0 | 14 | 8 | 45.98 | 78 | 0 | 0 | 42.75 | 0 | 0 | 194 | 0 | 191 | 0 | 392 | 0 | 4.62 | 0 | 45 | 0 | 29 | 0 | 0 | 0 | 0 | 6 | 142 | 0.44 | 16 | 307 | 63 | 220 | 0 | 820 | 1175 | 35 | 6867.15 | 13880.15 | 77.21
13:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 24 | 0 | 17 | 110 | 32 | 15 | 17 | 35 | 0 | 0 | 0 | 450 | 0 | 0 | 296 | 0 | 0 | 31 | 126 | 18 | 21 | 0 | 520 | 107 | 16 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.36 | 0 | 17 | 8 | 1135 | 40 | 0 | 6 | 25.5 | 0 | 215 | 0 | 0 | 0 | 612 | 8 | 55 | 0 | 235 | 290 | 260 | 51 | 0 | 206 | 0 | 27 | 0 | 17 | 17 | 8 | 17 | 142 | 8 | 67 | 22 | 305 | 0 | 309 | 28 | 0 | 141 | 1 | 17 | 0 | 51 | 30 | 143 | 0 | 102 | 0 | 56 | 21.09 | 58 | 0 | 1.9 | 38.64 | 0 | 7033.49 | 915 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32 | 510 | 0 | 0 | 0 | 1476.72 | 0 | 31 | 0 | 0 | 35 | 0 | 0 | 14 | 8 | 52.34 | 72 | 0 | 0 | 49 | 0 | 0 | 192 | 0 | 192 | 0 | 395 | 0 | 4.49 | 0 | 43 | 0 | 30 | 0 | 0 | 0 | 0 | 7.3 | 113 | 0.68 | 16 | 277 | 63 | 220 | 0 | 820 | 1190 | 17 | 6813.53 | 13847.02 | 77.23
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 0 | 17 | 110 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 430 | 0 | 0 | 301 | 0 | 0 | 29 | 142 | 19 | 21 | 0 | 520 | 107 | 16 | 31 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 4.91 | 0 | 17 | 0 | 1135 | 35 | 0 | 6 | 0 | 0 | 215 | 0 | 0 | 0 | 612 | 12 | 53 | 0 | 235 | 290 | 260 | 51 | 0 | 206 | 0 | 34 | 0 | 17 | 0 | 8 | 17 | 160 | 8 | 57 | 30 | 300 | 0 | 309 | 28 | 0 | 135 | 1 | 17 | 0 | 53 | 30 | 143 | 0 | 102 | 0 | 58 | 20 | 58 | 0 | 1.7 | 29.25 | 0 | 7010.86 | 909 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 64.61 | 510 | 0 | 0 | 0 | 1485.3 | 0 | 31 | 0 | 35 | 35 | 0 | 0 | 14 | 8 | 48.6 | 48 | 0 | 0 | 51.25 | 0 | 0 | 189 | 0 | 193 | 0 | 379 | 0 | 4.72 | 0 | 43 | 0 | 20 | 0 | 0 | 0 | 0 | 6.7 | 166 | 0.07 | 16 | 278 | 63 | 180 | 0 | 920 | 1217 | 17 | 6970.25 | 13981.11 | 77.25
15:00 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 26 | 0 | 17 | 113 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 415 | 0 | 0 | 298 | 0 | 0 | 19 | 142 | 19 | 21 | 0 | 430 | 99 | 16 | 30 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0 | 17 | 2 | 1135 | 35 | 0 | 6 | 1 | 0 | 215 | 0 | 0 | 0 | 584 | 14 | 53 | 0 | 235 | 290 | 260 | 51 | 0 | 196 | 0 | 34 | 0 | 17 | 0 | 19 | 17 | 168 | 8 | 23 | 38 | 300 | 0 | 309 | 28 | 0 | 151 | 5 | 22 | 0 | 52 | 30 | 143 | 0 | 101 | 0 | 49 | 13.5 | 67 | 0 | 1.1 | 19.99 | 0 | 6892.82 | 912 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20.48 | 510 | 0 | 0 | 0 | 1425.86 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 13 | 8 | 40.63 | 55 | 0 | 0 | 29 | 0 | 0 | 189 | 0 | 193 | 0 | 385 | 0 | 1.16 | 0 | 43 | 35 | 17 | 0 | 0 | 0 | 0 | 5.6 | 134 | 0.15 | 16 | 276 | 63 | 220 | 0 | 920 | 1218 | 17 | 6886.88 | 13779.7 | 77.27
16:00 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 33 | 0 | 30 | 128 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 465 | 0 | 17 | 300 | 0 | 0 | 9 | 142 | 19 | 21 | 0 | 430 | 89 | 16 | 36 | 0 | 1 | 0 | 0 | 0 | 10 | 10 | 0.41 | 0 | 17 | 2 | 1135 | 35 | 0 | 6 | 20 | 0 | 216 | 0 | 0 | 0 | 580 | 7 | 53 | 0 | 220 | 290 | 260 | 51 | 0 | 202 | 0 | 34 | 0 | 17 | 5 | 19 | 17 | 158 | 8 | 22 | 31 | 300 | 0 | 309 | 28 | 0 | 139 | 4 | 22 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 49 | 11.66 | 68 | 0 | 0.6 | 18 | 0 | 6999.67 | 911 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14.84 | 510 | 0 | 0 | 0 | 1401.21 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 13 | 8 | 28.05 | 49 | 0 | 0 | 16 | 0 | 0 | 191 | 0 | 193 | 0 | 375 | 0 | 1.77 | 0 | 42 | 70 | 11 | 9 | 0 | 0 | 0 | 3.8 | 59 | 0.22 | 16 | 307 | 63 | 220 | 0 | 882 | 1205 | 17 | 6756.89 | 13756.56 | 77.29
17:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 32 | 0 | 36 | 130 | 32 | 15 | 35 | 35 | 0 | 0 | 0 | 460 | 0 | 35 | 296 | 0 | 0 | 8 | 142 | 19 | 21 | 0 | 400 | 90 | 16 | 38 | 0 | 7 | 0 | 0 | 0 | 12 | 12 | 0.37 | 0 | 23 | 5 | 1135 | 35 | 0 | 6 | 25.5 | 6 | 217 | 0 | 0 | 0 | 580 | 4 | 53 | 0 | 220 | 290 | 260 | 51 | 0 | 202 | 0 | 34 | 0 | 18 | 26 | 19 | 114 | 150 | 8 | 20 | 31 | 295 | 0 | 309 | 28 | 0 | 132 | 3 | 13 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 58 | 4.86 | 58 | 0 | 0.2 | 7.17 | 0 | 7089.1 | 912 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5.21 | 510 | 0 | 0 | 0 | 1297.63 | 0 | 36 | 0 | 35 | 35 | 0 | 0 | 13 | 8 | 11.31 | 31 | 0 | 0 | 13 | 0 | 0 | 193 | 0 | 193 | 0 | 372 | 0 | 1.42 | 0 | 42 | 75 | 6 | 10 | 0 | 0 | 0 | 2.1 | 46 | 0.96 | 16 | 307 | 63 | 180 | 0 | 877 | 1203 | 17 | 6549.63 | 13638.73 | 77.31
18:00 | 0 | 105 | 14 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 36 | 0 | 47 | 130 | 90 | 15 | 35 | 35 | 0 | 0 | 0 | 380 | 0 | 35 | 300 | 0 | 0 | 2 | 142 | 19 | 21 | 0 | 430 | 94 | 32 | 37 | 0 | 0 | 0 | 0 | 1 | 12 | 12 | 0.12 | 0 | 23 | 8 | 1135 | 35 | 0 | 18 | 25.5 | 34 | 218 | 0 | 0 | 0 | 575 | 0 | 53 | 0 | 220 | 290 | 220 | 51 | 0 | 218 | 0 | 35 | 0 | 66 | 26 | 19 | 114 | 156 | 8 | 7 | 31 | 290 | 0 | 309 | 28 | 0 | 132 | 1 | 22 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 58 | 1.17 | 58 | 0 | 0 | 1.94 | 0 | 7195.73 | 912 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 2.71 | 510 | 0 | 0 | 0 | 1235.99 | 0 | 34 | 0 | 35 | 35 | 0 | 40 | 13 | 0 | 3.29 | 11 | 0 | 0 | 3.36 | 0 | 0 | 193 | 0 | 193 | 0 | 376 | 0 | 0.33 | 0 | 42 | 95 | 1 | 35 | 0 | 0 | 0 | 0.6 | 18 | 0.02 | 16 | 307 | 65 | 220 | 0 | 860 | 1203 | 17 | 6530.3 | 13726.03 | 77.33
19:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 36 | 0 | 144 | 130 | 98 | 15 | 35 | 162 | 0 | 0 | 0 | 390 | 0 | 35 | 303 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 500 | 107 | 16 | 42 | 0 | 4 | 50 | 14 | 19 | 25 | 12 | 0 | 0 | 29 | 2 | 1135 | 43 | 0 | 38 | 25.5 | 34 | 219 | 0 | 0 | 0 | 575 | 0 | 53 | 0 | 220 | 290 | 250 | 51 | 0 | 217 | 0 | 41 | 0 | 102 | 31 | 19 | 111 | 172 | 8 | 0 | 38 | 300 | 0 | 308 | 28 | 0 | 142 | 0 | 22 | 0 | 55 | 30 | 142 | 0 | 101 | 1 | 68 | 0 | 86 | 0 | 0 | 0 | 0 | 7812.5 | 912 | 0 | 0 | 19 | 0 | 38 | 0 | 0 | 100 | 0 | 15 | 0 | 510 | 0 | 0 | 0 | 1458.84 | 0 | 38 | 0 | 113 | 65 | 0 | 94 | 20 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 192 | 0 | 192 | 0 | 402 | 0 | 0 | 0 | 42 | 95 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 1000 | 1203 | 17 | 7214.84 | 15027.34 | 77.36
19:30 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 36 | 0 | 149 | 130 | 98 | 15 | 35 | 162 | 0 | 0 | 0 | 386 | 0 | 35 | 275 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 365 | 107 | 16 | 45 | 0 | 7 | 50 | 16 | 54 | 25 | 25 | 0 | 38 | 17 | 5 | 1135 | 83 | 0 | 38 | 25.5 | 34 | 220 | 0 | 0 | 0 | 550 | 0 | 100 | 0 | 220 | 290 | 250 | 51 | 0 | 218 | 0 | 90 | 0 | 115 | 36 | 19 | 105 | 168 | 8 | 0 | 38 | 290 | 0 | 308 | 28 | 0 | 143 | 0 | 22 | 0 | 82 | 30 | 142 | 0 | 101 | 17 | 68 | 0 | 86 | 0 | 0 | 0 | 0 | 7834.5 | 912 | 0 | 0 | 18 | 0 | 38 | 0 | 0 | 102 | 0 | 15 | 0 | 510 | 0 | 0 | 0 | 1460.39 | 0 | 32 | 0 | 113 | 105 | 0 | 94 | 20 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 192 | 0 | 192 | 0 | 361 | 0 | 0 | 0 | 40 | 95 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 180 | 0 | 1000 | 1200 | 17 | 7197.39 | 15031.89 | 77.37
20:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 54 | 6 | 149 | 132 | 98 | 15 | 35 | 162 | 0 | 0 | 0 | 425 | 0 | 35 | 296 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 435 | 107 | 16 | 72 | 0 | 9 | 50 | 24 | 54 | 25 | 25 | 0 | 39 | 17 | 10 | 1135 | 83 | 0 | 38 | 25.5 | 34 | 217 | 0 | 0 | 0 | 580 | 0 | 110 | 0 | 220 | 290 | 250 | 51 | 0 | 221 | 0 | 83 | 0 | 105 | 36 | 19 | 102 | 168 | 8 | 0 | 38 | 295 | 0 | 308 | 28 | 0 | 138 | 0 | 22 | 0 | 84 | 30 | 143 | 0 | 101 | 17 | 68 | 0 | 88 | 0 | 0 | 0 | 0 | 8099.5 | 911 | 0 | 0 | 15 | 0 | 38 | 0 | 0 | 101 | 0 | 15 | 0 | 510 | 0 | 0 | 0 | 1476.01 | 0 | 37 | 0 | 113 | 110 | 0 | 94 | 20 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 192 | 0 | 192 | 0 | 380 | 0 | 0 | 0 | 42 | 95 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 1000 | 1205 | 17 | 7279.01 | 15378.51 | 77.39
21:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 54 | 17 | 149 | 132 | 98 | 15 | 35 | 160 | 0 | 0 | 0 | 480 | 0 | 35 | 300 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 490 | 99 | 16 | 84 | 0 | 6 | 50 | 24 | 54 | 25 | 25 | 0 | 40 | 17 | 19 | 1135 | 86 | 0 | 37 | 25.5 | 34 | 220 | 0 | 0 | 0 | 580 | 0 | 143 | 0 | 220 | 290 | 250 | 26 | 0 | 218 | 0 | 88 | 0 | 103 | 37 | 19 | 108 | 164 | 8 | 0 | 38 | 295 | 0 | 308 | 28 | 0 | 149 | 0 | 22 | 0 | 5 | 0 | 140 | 0 | 101 | 17 | 69 | 0 | 88 | 0 | 0 | 0 | 0 | 8168.5 | 911 | 0 | 0 | 15 | 0 | 38 | 0 | 0 | 100 | 0 | 15 | 0 | 510 | 0 | 0 | 0 | 1461.96 | 0 | 40 | 0 | 113 | 113 | 0 | 94 | 20 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 192 | 0 | 192 | 0 | 393 | 0 | 0 | 0 | 42 | 95 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 1000 | 1205 | 17 | 7292.96 | 15461.46 | 77.39
22:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 17 | 0 | 149 | 132 | 98 | 15 | 35 | 156 | 0 | 0 | 0 | 550 | 0 | 35 | 297 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 470 | 95 | 16 | 85 | 0 | 11 | 50 | 24 | 54 | 25 | 25 | 0 | 40 | 17 | 23 | 1135 | 68 | 0 | 38 | 25.5 | 34 | 220 | 0 | 0 | 0 | 580 | 0 | 82 | 0 | 220 | 290 | 250 | 45 | 0 | 220 | 0 | 87 | 0 | 102 | 36 | 19 | 110 | 164 | 25 | 0 | 38 | 300 | 0 | 308 | 28 | 0 | 150 | 0 | 22 | 0 | 52 | 30 | 142 | 0 | 101 | 17 | 69 | 0 | 87 | 0 | 0 | 0 | 0 | 8210.5 | 818 | 0 | 0 | 15 | 0 | 38 | 0 | 0 | 100 | 0 | 15 | 0 | 510 | 0 | 0 | 0 | 1458.78 | 0 | 40 | 0 | 113 | 113 | 0 | 94 | 20 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 192 | 0 | 192 | 0 | 386 | 0 | 0 | 0 | 42 | 95 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 1000 | 1205 | 17 | 7189.78 | 15400.28 | 77.42
23:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 17 | 0 | 60 | 132 | 32 | 15 | 35 | 90 | 0 | 0 | 0 | 560 | 0 | 35 | 306 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 520 | 96 | 16 | 67 | 0 | 9 | 50 | 24 | 17 | 25 | 25 | 0 | 40 | 17 | 25 | 1135 | 97 | 0 | 38 | 25.5 | 34 | 220 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 220 | 290 | 250 | 51 | 0 | 220 | 0 | 69 | 0 | 104 | 0 | 19 | 108 | 150 | 52.2 | 0 | 39 | 305 | 0 | 308 | 28 | 0 | 152 | 0 | 22 | 0 | 53 | 30 | 144 | 0 | 101 | 17 | 69 | 0 | 88 | 0 | 0 | 0 | 0 | 7945.7 | 818 | 0 | 0 | 15 | 0 | 38 | 0 | 0 | 101 | 0 | 15 | 0 | 510 | 0 | 0 | 0 | 1459.83 | 0 | 40 | 0 | 35 | 59 | 0 | 94 | 20 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 192 | 0 | 193 | 0 | 403 | 0 | 0 | 0 | 43 | 95 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 1000 | 1205 | 17 | 7057.83 | 15003.53 | 77.45
Total KWH | 0 | 1082880 | 210720 | 0 | 0 | 0 | 0 | 0 | 8823600 | 0 | 0 | 441360 | 50760 | 1065744 | 3104160 | 1048800 | 361787 | 531144 | 1084320 | 0 | 0 | 0 | 11059575 | 0 | 269987 | 7343067 | 0 | 0 | 206400 | 3316800 | 472200 | 505800 | 0 | 12011363.64 | 2473964 | 403964 | 1018560 | 0 | 176160 | 349071 | 118744 | 334997 | 157440 | 148800 | 21242 | 1289800 | 450799 | 308640 | 27214545.46 | 1331491 | 0 | 326400 | 554837.4 | 226655 | 5133207 | 0 | 0 | 0 | 14361816 | 76815 | 918327 | 0 | 5807500 | 7367400 | 6190000 | 1221576 | 0 | 5101000 | 0 | 696000 | 0 | 1024800 | 278040 | 448150 | 1242600 | 3915840 | 542098 | 446827 | 666816 | 7314000 | 0 | 7606000 | 669000 | 0 | 3515236.36 | 32091 | 509064 | 0 | 1316160 | 701568 | 3311000 | 0 | 2419280 | 75960 | 1360800 | 110419 | 1490400 | 33600 | 11100 | 187340 | 0 | 175998407.86 | 21560727 | 0 | 0 | 226560 | 0 | 912000 | 0 | 0 | 511352.73 | 0 | 104544 | 506880 | 12385452 | 0 | 0 | 0 | 34815637 | 0 | 811989 | 0 | 697632 | 843840 | 0 | 582768 | 408261 | 320376 | 354544 | 625182 | 207680 | 0 | 308560 | 0 | 0 | 4871400 | 0 | 4936418 | 0 | 9367272 | 0 | 28140 | 0 | 993600 | 1179798 | 202492 | 634358 | 0 | 0 | 0 | 51960.6 | 927360 | 3150 | 400512 | 7309000 | 1523000 | 5380810 | 0 | 21069091 | 29211636.36 | 452400 | 164726382.69 | 340724790.55 | 77.48

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-06-2026 | during | 18-06-2026 | during | 18-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 383 | 372 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 210 | 210 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 295 | 300 | 335 | 335 | 310 | 310 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 27.5 | 54 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 126 | 132 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18 | 19 | 33 | 33 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 34 | 52.19 | 52.19 | 0 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 98 | 300 | 300 | 33 | 80 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 149 | 149 | 149 | 35 | 72 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 105 | 105 | 17 | 34 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 160 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 24 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 520 | 490 | 584 | 584 | 520 | 520 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 455 | 480 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 123 | 142 | 160 | 160 | 140 | 140 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2125.5 | 2658 | 5820.22 | 5792.22 | 2508.06 | 2765.06
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 37 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 0 | 40 | 72 | 72 | 0 | 72 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 220 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 0 | 34 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 32 | 32 | 32 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 25 | 100 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 19 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 31 | 84 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.28 | 0 | 4.36 | 0 | 4.36 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 54 | 54.36 | 54.36 | 17 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 110 | 110 | 17 | 17 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 25 | 100 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 99 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 38 | 86 | 163 | 163 | 50 | 50 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 580 | 1224 | 1224 | 1224 | 1224 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 6 | 12 | 5 | 12 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1135 | 1135 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2229.78 | 2576.5 | 3964.22 | 4009.86 | 2951.86 | 3157.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 207 | 218 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 290 | 350.01 | 350.01 | 290 | 290 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 260 | 250 | 342.01 | 342.01 | 220 | 220 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 235 | 220 | 393 | 393 | 280 | 280 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 10 | 10 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 26 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 35 | 143 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 38 | 40 | 40 | 24 | 24 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 103 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 172 | 164 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 108 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 18 | 37 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 88 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 55 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1396 | 1712 | 2757.44 | 2696.44 | 1582.45 | 1750.45
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-06-2026 | during | 18-06-2026 | during | 18-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 18.2 | 0 | 10 | 0 | 10 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.8 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 88 | 70 | 90 | 70 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 69 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 20.72 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 157.72 | 174 | 476.7 | 446.5 | 190.2 | 177
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 28 | 28 | 28 | 28 | 28 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 150 | 149 | 163 | 163 | 163 | 163 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 141 | 140 | 145 | 145 | 145 | 145 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 0 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 5 | 83 | 83 | 52 | 52 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 101 | 102 | 102 | 102 | 102 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 22 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 296 | 308 | 320 | 320 | 320 | 320 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1104 | 1048 | 1237 | 1237 | 1192 | 1192
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 915 | 911 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 15 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 50 | 50 | Engine Problem
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 32 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 38.95 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 100 | 336 | 336 | 100 | 100 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 510 | 510 | 510 | 510 | 510 | 510 | ps availability is less
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1501.95 | 1589 | 2863 | 2768 | 1857 | 1762
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 820 | 1000 | 1000 | 1000 | 1040 | 1040 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 63 | 65 | 65 | 65 | 65 | 65 | GT-1 & ST under maint
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1175 | 1205 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 17 | 150 | 150 | 17 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.44 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2636.44 | 2830 | 3097 | 3096 | 2850 | 2867
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 45.98 | 0 | 54 | 0 | 54 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 31 | 40 | 32 | 32 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 14 | 20 | 32 | 32 | 24 | 24 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 194 | 192 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 191 | 192 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 392 | 393 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 113 | 113 | 113 | 35 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.62 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1470.41 | 1461.96 | 1435.88 | 1435.88 | 1356 | 1356 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 42.75 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 78 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3519.512 | 2506.76 | 2643.96 | 3001.47 | 2780.87 | 2505.01 | 2411.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 45 | 42 | 43 | 43 | 40 | 40 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 93 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 95 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 142 | 0 | 180.27 | 0 | 180.27 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 222 | 230 | 487.27 | 271 | 351.27 | 170
System Total |  |  |  |  | 28843.2 | 29290.237 | 13880.15 | 15461.46 | 23704.32 | 23097.89 | 15987.85 | 16252.42
Forecast Scenario (18-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14600 |  | 2674 |  | 17400
|  |  |  | 1:00 | 13800 |  | 2931.85 |  | 16870
|  |  |  | 2:00 | 13600 |  | 2845.9 |  | 16580
|  |  |  | 3:00 | 13550 |  | 2645.35 |  | 16320
|  |  |  | 4:00 | 13500 |  | 2530.75 |  | 16150
|  |  |  | 5:00 | 13600 |  | 2225.15 |  | 15930
|  |  |  | 6:00 | 13450 |  | 1833.6 |  | 15370
|  |  |  | 7:00 | 13700 |  | 1518.45 |  | 15290
|  |  |  | 8:00 | 13700 |  | 1518.45 |  | 15290
|  |  |  | 9:00 | 13750 |  | 1623.5 |  | 15450
|  |  |  | 10:00 | 13800 |  | 1528 |  | 15400
|  |  |  | 11:00 | 13850 |  | 1613.95 |  | 15540
|  |  |  | 12:00 | 13900 |  | 2053.25 |  | 16050
|  |  |  | 13:00 | 13900 |  | 2139.2 |  | 16140
|  |  |  | 14:00 | 14000 |  | 2158.3 |  | 16260
|  |  |  | 15:00 | 13800 |  | 2483 |  | 16400
|  |  |  | 16:00 | 13800 |  | 2101 |  | 16000
|  |  |  | 17:00 | 13640 |  | 2158.3 |  | 15900
|  |  |  | 18:00 | 13800 |  | 1910 |  | 15800
|  |  |  | 18:30 | 14400 |  | 1814.5 |  | 16300
|  |  |  | 19:00 | 15030 |  | 1690.35 |  | 16800
|  |  |  | 19:30 | 15040 |  | 2158.3 |  | 17300
|  |  |  | 20:00 | 15380 |  | 1738.1 |  | 17200
|  |  |  | 21:00 | 15460 |  | 2043.7 |  | 17600
|  |  |  | 22:00 | 15400 |  | 1719 |  | 17200
|  |  |  | 23:00 | 15380 |  | 1929.1 |  | 17400
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 16050.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 17600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15460.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 338.39 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:18 hrs on 18-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13880.15 | MW | 12:00 Hr. | Energy Generated |  |  | 340.7248 |  | MKWHr.
| Day Peak Demand |  |  | 16058.15 | MW | 12:00 Hr. | Energy Unserverd |  |  | 50.326 |  | MKWHr.
| Evening Peak Generation |  |  | 15461.46 | MW | 21:00 Hr. | Energy Demand |  |  | 391.0508 |  | MKWHr.
| Evening Peak Demand |  |  | 17328.46 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 13421.25 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 886.55 |  | MMCFD
| Maximum Generation of the Day |  |  | 15461.46 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.7913 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.2156 | 0 | 12.5685 | 0 | 0 | 0.2064 | 0 | 0 | 52.9905 | Gas | 125.2669 | Gas | 431610992.37
| Chattogram Zone |  |  | 5.4418 | 41.5764 | 7.8957 | 0 | 1.2898 | 0.098057 | 0 | 0.17616 | 56.4779 | Coal | 112.5451 | Coal | 740554822.4826
| Cumilla Zone |  |  | 26.1356 | 0 | 5.3687 | 0 | 0 | 0.44683 | 3.9158 | 0 | 35.867 | HFO | 35.6307 | HFO | 693845418.714
| Mymensingh Zone |  |  | 0.0336 | 0 | 2.9272 | 0 | 0 | 0.30886 | 0 | 0 | 3.2696 | HSD | 0.51135 | HSD | 10329325.146
| Sylhet Zone |  |  | 27.3613 | 0 | 0 | 0 | 0 | 0.032091 | 0 | 0 | 27.3934 | Hydro | 1.2898 | Hydro | 128980
| Khulna Zone |  |  | 0 | 12.3855 | 0.3311 | 0.51135 | 0 | 0.50688 | 22.4727 | 0 | 36.2075 | Solar | 4.1005 | Solar | 64733041.352
| Barishal Zone |  |  | 6.9038 | 57.5897 | 0.85291 | 0 | 0 | 0.00315 | 0 | 0 | 65.3496 | Import | 61.2042 | Import | 370184267.79
| Rajshahi Zone |  |  | 19.1751 | 0 | 3.8725 | 0 | 0 | 1.3164 | 34.8156 | 0 | 59.1797 | Wind | 0.17616 | Wind | 2591313.6
| Rangpur Zone |  |  | 0 | 0.9936 | 1.8142 | 0 | 0 | 1.1818 | 0 | 0 | 3.9896
| Total |  |  | 125.2669 | 112.5451 | 35.6307 | 0.51135 | 1.2898 | 4.1005 | 61.2042 | 0.17616 | 340.7248
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 431610992.37 |  | Hydro | 128980
|  |  |  | Coal | 740554822.4826 |  | Solar | 64733041.352
|  |  |  | HFO | 693845418.714 |  | Import | 370184267.79
|  |  |  | HSD | 10329325.146 |  | Wind | 2591313.6
[5 empty] | Total: | 231,39,78,161 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5607 | Peak Hr Flow | 911.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51534618.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 34.8156 | Peak Hr Flow | 1461.96 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2342 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.9158 | Peak Hr Flow | 164.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2797 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 60.2922 | Peak Hr Flow | 2536.96 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 112 |  | 5928
|  |  |  | Chattogram |  | 129 |  | 1629
|  |  |  | Cumilla |  | 214 |  | 1504
|  |  |  | Mymensingh |  | 316 |  | 1373
|  |  |  | Sylhet |  | 20 |  | 594
|  |  |  | Khulna |  | 475 |  | 2216
|  |  |  | Barishal |  | 97 |  | 553
|  |  |  | Rajshahi |  | 229 |  | 1706
|  |  |  | Rangpur |  | 195 |  | 1186
|  |  |  | Total |  | 1787 |  | 16689
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 350
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:43 |  | Gopalganj- Gopalganj(N) 132kV Ckt-2 Scheduled S/D from Gopalganj 132/33kV end Due to
Clamp and Loop Change and from Gopalganj 400/132kVend.
| 10:07 | 15:22 | Ishurdi 230/132kV S/S 230/132 kV T-01 LT Project Work S/D Due to CB 615B testing
| 10:08 | 15:21 | Ishurdi 230/132kV S/S 230/132 kV T-01 HT Project Work S/D Due to CB 615B testing
| 10:40 | 15:48 | BIPTC S/S 20DF23 Scheduled S/D Due to Red hot maintenance of cell
| 10:43 |  | Notun Biddyut- Charfashion-1 Closed.
| 10:44 | 11:15 | Mymensingh RPCL -Mymensingh 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end.
| 11:04 | 11:16 | Candpur- Kachua 132kV Ckt-1 Tripped from Chandpur 132/33kV end showing Distance relay
relays Due to Zone-1 trip
| 11:04 | 11:16 | Candpur- Kachua 132kV Ckt-2 Tripped from Chandpur 132/33kV end showing Distance relay
relays Due to Zone-1 trip
| 11:16 | 11:35 | Mymensingh RPCL -Mymensingh 132kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due
to Relay testing of RPCL end.
|  | 15:10 | Aftabnagar-Rampura 132kV Ckt-1 is restored.
| 15:43 | 19:01 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Tripped showing Over current
relay(51N) O/C B phase Instant. relays Due to 33kv B phase Underground cable fault.
| 15:43 | 19:08 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Tripped showing Over current B phase
instant relays Due to 33kv B phase Underground cable fault.
| 20:15 |  | Ashuganj-Brahmanbaria 132kV Ckt-1 Forced S/D from Brahmanbaria 132/33kV end. | [7 empty] | 80.0MW load
interrup.
Brahmanbaria
132/33kV end
| 20:30 | 23:25 | Ashuganj-Brahmanbaria 132kV Ckt-2 Tripped from Brahmanbaria 132/33kV end showing Main | [7 empty] | 95.0MW load
|  |  | Protection trip relays. | [7 empty] | interrup.
Brahmanbaria
132/33kV end
| 20:30 | 20:56 | Shahjibazar 132/33kV S/S BPDB 60 MW Tripped showing C.B Trip Relay, Busbar Three phase
Over curent Relay relays Due to Voltage down for B.Baria-Ashuganj ckt 02 Faut
| 20:58 |  | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Forced S/D from Brahmanbaria 132/33kV end. | [7 empty] | 10.0MW load
interrup.
Brahmanbaria
132/33kV end
| 20:58 |  | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end. | [7 empty] | 10.0MW load
interrup.
Brahmanbaria
132/33kV end
| 21:00 |  | Evening Peak Generation is 15462 MW.
| 23:27 |  | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end.
| 23:33 |  | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Forced S/D from Brahmanbaria 132/33kV end.
| 02:39 |  | SS Power unit-1 was sync.
| 02:39 |  | SS Power Synchronized with remarks:- U-1
| 04:06 | 04:35 | Kurigram-Lalmonirhat 132kV Ckt-1 Tripped from Kurigram 132/33kV end showing Distance | [7 empty] | 54.0MW load
|  |  | Z-1, relays Due to General Trip, Distance Z-1, | [7 empty] | interrup. Kurigram
132/33kV end
| 04:07 | 04:31 | Kurigram-Rangpur 132kV Ckt-1 Tripped from Rangpur 132/33kV end showing Distance Relay : | [7 empty] | 30.0MW load
|  |  | R phase trip, B phase trip, Zone 1 relays Due to Bad weather | [7 empty] | interrup. Rangpur
132/33kV end
| 04:07 | 04:35 | Lalmonirhat-Rangpur 132 kV Ckt-2 Tripped from Rangpur 132/33kV end showing Distance relay | [7 empty] | 40.0MW load
|  |  | : c phase trip, Z2, Z3 relays Due to Bad weather | [7 empty] | interrup. Rangpur
132/33kV end
| 06:59 |  | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-1 Project Work S/D Due to Jumpering
works
| 06:59 |  | Bogura 400/230kV S/S Bogura - Naogaon 230 kV Ckt-2 Project Work S/D Due to Jumpering
works
| 07:00 |  | Minimum generation 13272 MW
| 07:24 | 07:35 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent protection relay relays.
| 07:40 |  | Korerhat 400/230/132kV S/S ATR-4(7403T) LT Project Work S/D Due to Due to project work
| 07:41 |  | Korerhat 400/230/132kV S/S ATR-4(7403T) HT Project Work S/D Due to Due to project work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 372 | 8823600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 361787 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7343067 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 441360 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 132 | 3104160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 531144 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 269987 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 472200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 505800 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 210720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 98 | 1048800 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1065744 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1082880 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 160 | 1084320 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 206400 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 50760 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 490 | 12011363.64 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 480 | 11059575 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3316800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2658 | 52990467.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 554837.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 76815 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 326400 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 1289800 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 5133207 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 226655 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 118744 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 349071 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 157440 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 19 | 308640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 84 | 1018560 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21242 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 403964 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54 | 334997 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 450799 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 148800 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 99 | 2473964 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 86 | 1331491 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 580 | 14361816 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 176160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1135 | 27214545.46 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 2576.5 | 56477947.86
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 218 | 5101000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7367400 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 250 | 6190000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5807500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 26 | 1221576 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 143 | 918327 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 666816 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 103 | 1024800 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 164 | 3915840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 542098 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 448150 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 108 | 1242600 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 37 | 278040 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 88 | 696000 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 446827 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1712 | 35866974
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 110419 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 33600 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 88 | 1490400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 1360800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 187340 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 75960 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 174 | 3269619
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 32091 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 669000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3515236.36 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 140 | 3311000 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 701568 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 5 | 1316160 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2419280 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 509064 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7314000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 308 | 7606000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1048 | 27393399.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 911 | 21560727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 15 | 226560 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Engine Problem
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 104544 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 506880 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 100 | 511352.73 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 510 | 12385452 | ps availability is less
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1589 | 36207515.73
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1000 | 21069091 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 400512 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 65 | 1523000 | GT-1 & ST under maint
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1205 | 29211636.36 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5380810 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 452400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7309000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3150 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2830 | 65349599.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 354544 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 811989 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 408261 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 192 | 4871400 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 192 | 4936418 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 393 | 9367272 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 207680 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 320376 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 582768 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 843840 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 697632 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28140 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1461.96 | 34815637 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 308560 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 625182 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3519.512 | 2643.96 | 59179699
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 42 | 993600 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 93 | 634358 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 51960.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1179798 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 202492 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 927360 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 230 | 3989568.6
Eastern Grid Total |  |  |  |  | 17438.042 | 8168.5 | 175998407.86
Western Grid Total |  |  |  |  | 11852.195 | 7292.96 | 164726382.69
National Grid Total |  |  |  |  | 29290.237 | 15461.46 | 340724790.55
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-06-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10281.97 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4664.3 | MW
i) Dhaka area |  |  | 5816.17 |  | MW | i) Khulna area |  |  |  | 1740.8 | MW
ii) Chattogram area |  |  | 1544.8 |  | MW | ii) Barishal area |  |  |  | 455.9 | MW
iii) Cumilla area |  |  | 1290 |  | MW | iii) Rajshahi area |  |  |  | 1476.6 | MW
iv) Mymensingh area |  |  | 1057 |  | MW | iv) Rangpur area |  |  |  | 991 | MW
v) Sylhet area |  |  | 574 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14946.27 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 130 | 20:00 | 133 | Narshingdi | 168 | 20:00 | 199 | Zigatola | 84 | 20:00
2 | AKSML | 136.4 | 16:00 | 68 | Hasnabad | 98 | 19:30 | 134 | Natore | 153 | 23:00
3 | Aftabnagar | 46 | 13:00 | 69 | Hathazari | 86 | 21:00 | 135 | Nawabganj | 68.4 | 21:00
4 | Agargaon | 125 | 13:00 | 70 | Hatirjheel | 50 | 12:00 | 136 | Netrakona | 123 | 07:00
5 | Agrabad | 70 | 11:00 | 71 | Ishurdi | 91 | 20:00 | 137 | New | 88 | 12:00
6 | Amnura | 31 | 23:00 | 72 | Jaldhaka | 61 | 22:00 | 138 | Niamatpur | 88 | 23:00
7 | Ashuganj | 92 | 02:00 | 73 | Jamalpur | 106 | 21:00 | 139 | Noapara | 43 | 21:00
8 | BSRM | 201 | 07:00 | 74 | Jashore | 170 | 00:00 | 140 | PHP | 12 | 18:30
9 | Bagerhat | 83 | 01:00 | 75 | Jhenaidah | 112 | 22:00 | 141 | Pabna | 100 | 19:00
10 | Bajitpur | 80 | 05:00 | 76 | Joydebpur | 166 | 19:00 | 142 | Palashbari | 140 | 19:30
11 | Bakerganj | 13.6 | 19:30 | 77 | Joypurhat | 60 | 20:00 | 143 | Panchagarh | 63 | 20:00
12 | Bakulia | 104 | 20:00 | 78 | Juldah | 14.5 | 12:00 | 144 | Patiya | 9.6 | 19:00
13 | Banani | 64 | 12:00 | 79 | KSRM | 29 | 17:00 | 145 | Patuakhali | 62 | 23:00
14 | Bangabhaban | 22 | 10:00 | 80 | Kabirpur | 272 | 18:30 | 146 | Payra | 34 | 22:00
15 | Barapukuria | 63 | 20:00 | 81 | Kachua | 94 | 19:00 | 147 | Postogola | 63 | 00:00
16 | Barguna | 22 | 22:00 | 82 | Kaliganj | 22 | 22:00 | 148 | Pubail | 26 | 13:00
17 | Barishal | 115 | 12:00 | 83 | Kallyanpur | 129 | 20:00 | 149 | Purbachal | 35 | 12:00
18 | Barishal-230 | 112 | 19:00 | 84 | Kalurghat | 42 | 20:00 | 150 | Purbasadipur | 142 | 21:00
19 | Baroaulia | 74 | 14:00 | 85 | Kamrangirchar | 80 | 13:00 | 151 | Rahanpur | 32 | 12:00
20 | Baroirhat | 65 | 00:00 | 86 | Kaptai | N/A | N/A | 152 | Rahim | 34 | 11:00
21 | Bashundhara | 202 | 12:00 | 87 | Kasba | 35 | 15:00 | 153 | Rajbari | 78.5 | 20:00
22 | BashundharaCement | 2 | 15:00 | 88 | Kazla | 121 | 13:00 | 154 | Rajendrapur | 114 | 21:00
23 | Beanibazar | 82 | 00:00 | 89 | Keranigonj | 89 | 21:00 | 155 | Rajshahi | 131 | 21:00
24 | Benapole | 61 | 19:00 | 90 | Khagrachori | 32 | 19:00 | 156 | Rajshahi-230 | 84 | 22:00
25 | Bhaluka | 163 | 19:00 | 91 | Khulna | 65 | 18:30 | 157 | Ramganj | 122 | 19:00
26 | Bhandaria | 58 | 19:00 | 92 | Khulshi | 199 | 20:00 | 158 | Rampur | 44 | 21:00
27 | Bhangura | 38 | 20:00 | 93 | Kishoreganj | 112 | 18:00 | 159 | Rangamati | 16 | 19:30
28 | Bheramara(GK) | 63 | 02:00 | 94 | Kodda | 304 | 21:00 | 160 | Rangpur | 134 | 22:00
29 | Bhulta | 222 | 21:00 | 95 | Kulaura | 51 | 00:00 | 161 | Ruppur | 4.6 | 10:00
30 | Bog-Sherpur | 72 | 06:00 | 96 | Kurigram | 68 | 18:30 | 162 | SSM | 0 | 00:00
31 | Bogura | 197 | 20:00 | 97 | Kushtia | 146 | 21:00 | 163 | Saidpur | 103 | 18:00
32 | Borhanuddin | 81 | 22:00 | 98 | Laksam | 35 | 19:00 | 164 | Santhia | 28 | 00:00
33 | Brahmanbaria | 115 | 19:00 | 99 | Lakshmipur | 46 | 20:00 | 165 | Satkhira | 141 | 07:00
34 | Cantonment | 142 | 12:00 | 100 | Lalbag | 85 | 13:00 | 166 | Satmasjid | 108 | 19:30
35 | Chandina | 22 | 13:00 | 101 | Lalmonirhat | 64 | 21:00 | 167 | Savar | 224 | 19:00
36 | Chandpur | 74 | 20:00 | 102 | MI_Cement | 13.5 | 19:00 | 168 | SevenRings | 6.52 | 02:00
37 | Chandraghona | 34 | 19:30 | 103 | Madanganj | 43 | 20:00 | 169 | ShahCement | 24 | 10:00
38 | Chapai | 69 | 19:30 | 104 | Madaripur | 110 | 22:00 | 170 | Shahjadpur | 72 | 18:00
39 | Charfasson | 33 | 22:00 | 105 | Madartek | 92 | 20:00 | 171 | Shahjibazar | 127 | 22:00
40 | Charsaidpur | 45 | 11:00 | 106 | Madunaghat | 56 | 21:00 | 172 | Shahmirpur | 53 | 23:00
41 | Chauddagram | 70 | 20:00 | 107 | Magura | 62 | 22:00 | 173 | Shariatpur | 83 | 19:00
42 | Chhatak | 43 | 00:00 | 108 | Mahasthangarh | 70 | 04:00 | 174 | Sherpur | 136 | 19:30
43 | Chowmuhani | 161 | 19:00 | 109 | Maijdee | 40 | 23:00 | 175 | Shikalbaha | 30 | 03:00
44 | Chuadanga | 109 | 06:00 | 110 | Manikganj | 153 | 22:00 | 176 | Shitalakhya | 88.9 | 13:00
45 | Coxsbazar | 129 | 07:00 | 111 | Maniknagar | 77 | 13:00 | 177 | Sholosohor | 43 | 21:00
46 | Cumilla(N) | 118 | 19:30 | 112 | Matarbari | 50 | 22:00 | 178 | Shomvuganj | 26 | 20:00
47 | Cumilla(S) | 181 | 00:00 | 113 | Matuail | 84 | 11:00 | 179 | Shyampur | 178 | 12:00
48 | Daganbhuiyan | 38 | 20:00 | 114 | Metrorail_Motijheel | 24 | 12:00 | 180 | Siddhirganj | 139 | 11:00
49 | Daudkandi | 142 | 23:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Sirajganj | 118 | 19:30
50 | DhakaUniversity | 94 | 13:00 | 116 | Millgate | 113 | 15:00 | 182 | Sonargaon | 139 | 22:00
51 | Dhamrai | 112 | 23:00 | 117 | Mirpur | 157 | 19:00 | 183 | Sreemongol | 87 | 00:00
52 | Dhanmondi | 133.4 | 13:00 | 118 | Mirsorai | 57 | 13:00 | 184 | Sreepur | 127 | 22:00
53 | Dohazari | 89 | 21:00 | 119 | Mirzapur | 35 | 07:00 | 185 | Srinagar | 56.4 | 22:00
54 | Faridpur | 160 | 23:00 | 120 | Mithapukur | 70 | 19:00 | 186 | Sunamganj | 63 | 00:00
55 | Fatullah | 98 | 12:00 | 121 | Modern | N/A | N/A | 187 | Sylhet | 125 | 00:00
56 | Fenchuganj | 45 | 00:00 | 122 | Mogbazar | 117.6 | 14:00 | 188 | Sylhet_(South) | 55 | 19:00
57 | Feni | 111 | 19:00 | 123 | Mongla | 48 | 20:00 | 189 | TK | 20 | 00:00
58 | GPH | 11 | 02:00 | 124 | Motijheel | 54 | 12:00 | 190 | Tangail | 160 | 19:30
59 | Ghatail | 74 | 21:00 | 125 | Muktagacha | 34 | 13:00 | 191 | Taraganj | 25 | 22:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 103 | 18:30 | 192 | Tasnim | 42 | 18:00
61 | Ghorashal-230 | 106 | 22:00 | 127 | Muradnagar | 49 | 23:00 | 193 | Thakurgaon | 105 | 19:30
62 | Goalpara | 39 | 00:00 | 128 | Mymensingh | 175 | 07:00 | 194 | Tongi | 158 | 09:00
63 | Gollamari | 104 | 20:00 | 129 | Nabinagar | 100 | 21:00 | 195 | Ullahpara | 36 | 19:30
64 | Gopalganj | 105.4 | 22:00 | 130 | Naogaon | 139 | 23:00 | 196 | Ullon | 58 | 21:00
65 | Gulshan | 134 | 12:00 | 131 | Narail | 54 | 02:00 | 197 | Uttara | 96 | 12:00
66 | Halishahar | 105 | 11:00 | 132 | Narinda | 77 | 13:00 | 198 | UttaraNew | 55 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13980.69 | 3275 |  | 17402.69
1:00 | 13722.32 | 3020 |  | 16878.22
2:00 | 13528.55 | 2928 |  | 16588.31
3:00 | 13548.55 | 2659 |  | 16327.21
4:00 | 13493.14 | 2542 |  | 16149.53
5:00 | 13538.37 | 2296 |  | 15937.69
6:00 | 13421.25 | 1873 |  | 15378.54
7:00 | 13631.42 | 1596 |  | 15299.42
8:00 | 13774.06 | 1453 |  | 15292.45
9:00 | 13859.76 | 1529 |  | 15457.76
10:00 | 13681.72 | 1653 |  | 15408.72
11:00 | 13818.68 | 1654 |  | 15546.68
12:00 | 13880.15 | 2084 |  | 16058.15
13:00 | 13847.02 | 2203 |  | 16149.02
14:00 | 13981.11 | 2185 |  | 16264.44
15:00 | 13779.7 | 2629 |  | 16527.01
16:00 | 13756.56 | 2540 |  | 16410.86
17:00 | 13638.73 | 2368 |  | 16113.29
18:00 | 13726.03 | 1429 |  | 15219.34
19:00 | 15027.34 | 1537 |  | 16633.51
19:30 | 15031.89 | 2056 |  | 17180.41
20:00 | 15378.51 | 1603 |  | 17053.65
21:00 | 15461.46 | 1787 |  | 17328.46
22:00 | 15400.28 | 1624 |  | 17097.28
23:00 | 15003.53 | 1859 |  | 16946.53
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7328.5 | 6652.19 | 13980.69 | DAILY GENERATION CURVE
00:30 | 7282.5 | 6569.005 | 13851.505
01:00 | 7236.5 | 6485.82 | 13722.32 | 17-06-2026
01:30 | 7125.5 | 6499.935 | 13625.435
02:00 | 7014.5 | 6514.05 | 13528.55
02:30 | 6972 | 6566.55 | 13538.55
03:00 | 6929.5 | 6619.05 | 13548.55
03:30 | 6914.5 | 6606.345 | 13520.845
04:00 | 6899.5 | 6593.64 | 13493.14
04:30 | 6935.6 | 6580.155 | 13515.755
05:00 | 6971.7 | 6566.67 | 13538.37
05:30 | 6887.305 | 6592.505 | 13479.81
06:00 | 6802.91 | 6618.34 | 13421.25
06:30 | 6882.405 | 6643.93 | 13526.335
07:00 | 6961.9 | 6669.52 | 13631.42
07:30 | 7032.595 | 6670.145 | 13702.74
08:00 | 7103.29 | 6670.77 | 13774.06
08:30 | 7119.29 | 6697.62 | 13816.91
09:00 | 7135.29 | 6724.47 | 13859.76
09:30 | 6993.865 | 6776.875 | 13770.74
10:00 | 6852.44 | 6829.28 | 13681.72
10:30 | 6885.16 | 6865.04 | 13750.2
11:00 | 6917.88 | 6900.8 | 13818.68
11:30 | 6965.44 | 6883.975 | 13849.415
12:00 | 7013 | 6867.15 | 13880.15
12:30 | 7023.245 | 6840.34 | 13863.585
13:00 | 7033.49 | 6813.53 | 13847.02
13:30 | 7022.175 | 6891.89 | 13914.065
14:00 | 7010.86 | 6970.25 | 13981.11
14:30 | 6951.84 | 6928.565 | 13880.405
15:00 | 6892.82 | 6886.88 | 13779.7
15:30 | 6946.245 | 6821.885 | 13768.13
16:00 | 6999.67 | 6756.89 | 13756.56
16:30 | 7044.385 | 6653.26 | 13697.645
17:00 | 7089.1 | 6549.63 | 13638.73
17:30 | 7142.415 | 6539.965 | 13682.38
18:00 | 7195.73 | 6530.3 | 13726.03
18:30 | 7504.115 | 6872.57 | 14376.685
19:00 | 7812.5 | 7214.84 | 15027.34
19:30 | 7834.5 | 7197.39 | 15031.89
20:00 | 8099.5 | 7279.01 | 15378.51
20:30 | 8134 | 7285.985 | 15419.985 |  | Executive Engineer
21:00 | 8168.5 | 7292.96 | 15461.46 |  | Network Operation Division
21:30 | 8189.5 | 7241.37 | 15430.87
22:00 | 8210.5 | 7189.78 | 15400.28
22:30 | 8078.1 | 7123.805 | 15201.905
23:00 | 7945.7 | 7057.83 | 15003.53

## En-Curve
QF-LDC-12
Date | 17-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3336 | 1910 | 844 | 38 | 182 | 1472.19 | 73 | 4614 | 0 | 516 | 984.5 | 0 | 0 | 11 | 3275 | DAILY ENERGY CURVE
00:30 | 3341.5 | 1884.5 | 829 | 38 | 177 | 1469.505 | 73.5 | 4632 | 0 | 483.5 | 912 | 0 | 0 | 11 | 3147.5 | 17-06-2026
01:00 | 3347 | 1859 | 814 | 38 | 172 | 1466.82 | 74 | 4650 | 0 | 451 | 839.5 | 0 | 0 | 11 | 3020
01:30 | 3343.5 | 1876 | 814 | 38 | 175 | 1469.935 | 72.5 | 4652 | 0 | 431.5 | 746 | 0 | 0 | 7 | 2974 | Energy Generated | 340.7248 |  | MKWHr
02:00 | 3340 | 1893 | 814 | 38 | 178 | 1473.05 | 71 | 4654 | 0 | 412 | 652.5 | 0 | 0 | 3 | 2928 | Energy not Served | 50.326 |  | MKWHr
02:30 | 3332 | 1887 | 864.5 | 38 | 171 | 1469.05 | 68 | 4653 | 0 | 412 | 639 | 0 | 0 | 5 | 2793.5 | Total Energy Requirement | 391.0508 |  | MKWHr
03:00 | 3324 | 1881 | 915 | 38 | 164 | 1465.05 | 65 | 4652 | 0 | 412 | 625.5 | 0 | 0 | 7 | 2659
03:30 | 3316 | 1874 | 915 | 38 | 166 | 1466.845 | 63.5 | 4654 | 0 | 400.5 | 617.5 | 0 | 0 | 9.5 | 2600.5
04:00 | 3308 | 1867 | 915 | 38 | 168 | 1468.64 | 62 | 4656 | 0 | 389 | 609.5 | 0 | 0 | 12 | 2542
04:30 | 3329.5 | 1877.5 | 915 | 38 | 163 | 1470.155 | 62 | 4656.5 | 0 | 375.5 | 617.1 | 0 | 0 | 11.5 | 2419
05:00 | 3351 | 1888 | 915 | 38 | 158 | 1471.67 | 62 | 4657 | 0 | 362 | 624.7 | 0 | 0 | 11 | 2296
05:30 | 3335 | 1829.25 | 915 | 38 | 159 | 1480.78 | 63.5 | 4656 | 11.08 | 356 | 625.7 | 0 | 0 | 10.5 | 2084.5
06:00 | 3319 | 1770.5 | 915 | 38 | 160 | 1489.89 | 65 | 4655 | 22.16 | 350 | 626.7 | 0 | 0 | 10 | 1873
06:30 | 3353.5 | 1797.5 | 915 | 38 | 157 | 1490.55 | 66 | 4656.5 | 62.585 | 347.5 | 637.2 | 0 | 0 | 5 | 1734.5
07:00 | 3388 | 1824.5 | 915 | 38 | 154 | 1491.21 | 67 | 4658 | 103.01 | 345 | 647.7 | 0 | 0 | 0 | 1596
07:30 | 3407 | 1831.25 | 915 | 38 | 158 | 1492.41 | 68.5 | 4650 | 139.28 | 346 | 656.8 | 0 | 0 | 0.5 | 1524.5
08:00 | 3426 | 1838 | 915 | 38 | 162 | 1493.61 | 70 | 4642 | 175.55 | 347 | 665.9 | 0 | 0 | 1 | 1453
08:30 | 3430 | 1836 | 915 | 38 | 162 | 1488.995 | 71 | 4628 | 219.015 | 360 | 667.4 | 0 | 0 | 1.5 | 1491
09:00 | 3434 | 1834 | 915 | 38 | 162 | 1484.38 | 72 | 4614 | 262.48 | 373 | 668.9 | 0 | 0 | 2 | 1529
09:30 | 3381 | 1796.75 | 915 | 38 | 162 | 1486.47 | 36 | 4609.5 | 310.22 | 356 | 678.8 | 0 | 0 | 1 | 1591
10:00 | 3328 | 1759.5 | 915 | 38 | 162 | 1488.56 | 0 | 4605 | 357.96 | 339 | 688.7 | 0 | 0 | 0 | 1653
10:30 | 3330.5 | 1770.5 | 915 | 38 | 166 | 1487.63 | 0 | 4605 | 444.62 | 335 | 650.95 | 0 | 0 | 7 | 1653.5
11:00 | 3333 | 1781.5 | 915 | 38 | 170 | 1486.7 | 0 | 4605 | 531.28 | 331 | 613.2 | 0 | 0 | 14 | 1654
11:30 | 3327 | 1791.75 | 915 | 38 | 171 | 1478.555 | 0 | 4604.5 | 532.01 | 332 | 652.1 | 0 | 0 | 7.5 | 1869
12:00 | 3321 | 1802 | 915 | 38 | 172 | 1470.41 | 0 | 4604 | 532.74 | 333 | 691 | 0 | 0 | 1 | 2084
12:30 | 3316.5 | 1806 | 915 | 38 | 157 | 1473.565 | 0 | 4595.5 | 533.77 | 326.5 | 701.25 | 0 | 0 | 0.5 | 2143.5
13:00 | 3312 | 1810 | 915 | 38 | 142 | 1476.72 | 0 | 4587 | 534.8 | 320 | 711.5 | 0 | 0 | 0 | 2203
13:30 | 3302.5 | 1772 | 912 | 38 | 151 | 1481.01 | 0 | 4651 | 549.805 | 332 | 715.25 | 0 | 0 | 9.5 | 2194
14:00 | 3293 | 1734 | 909 | 38 | 160 | 1485.3 | 0 | 4715 | 564.81 | 344 | 719 | 0 | 0 | 19 | 2185
14:30 | 3303 | 1718 | 910.5 | 38 | 164 | 1455.58 | 0 | 4700.5 | 481.825 | 354.5 | 737 | 0 | 0 | 17.5 | 2407
15:00 | 3313 | 1702 | 912 | 38 | 168 | 1425.86 | 0 | 4686 | 398.84 | 365 | 755 | 0 | 0 | 16 | 2629
15:30 | 3295 | 1721 | 911.5 | 38 | 163 | 1413.535 | 0 | 4673.5 | 327.595 | 400.5 | 816 | 0 | 0 | 8.5 | 2584.5
16:00 | 3277 | 1740 | 911 | 38 | 158 | 1401.21 | 0 | 4661 | 256.35 | 436 | 877 | 0 | 0 | 1 | 2540
16:30 | 3270 | 1693.5 | 911.5 | 38 | 154 | 1349.42 | 0 | 4657.5 | 210.475 | 446.5 | 962.75 | 0 | 0 | 4 | 2454
17:00 | 3263 | 1647 | 912 | 38 | 150 | 1297.63 | 0 | 4654 | 164.6 | 457 | 1048.5 | 0 | 0 | 7 | 2368
17:30 | 3263 | 1645.5 | 912 | 38 | 153 | 1266.81 | 0 | 4643 | 109.07 | 490.5 | 1158 | 0 | 0 | 3.5 | 1898.5
18:00 | 3263 | 1644 | 912 | 38 | 156 | 1235.99 | 0 | 4632 | 53.54 | 524 | 1267.5 | 0 | 0 | 0 | 1429
18:30 | 3304 | 1692.5 | 912 | 38 | 164 | 1347.415 | 0 | 4702 | 26.77 | 615 | 1523 | 50 | 0 | 2 | 1483
19:00 | 3345 | 1741 | 912 | 38 | 172 | 1458.84 | 0 | 4772 | 0 | 706 | 1778.5 | 100 | 0 | 4 | 1537
19:30 | 3222 | 1583 | 912 | 38 | 168 | 1460.39 | 38 | 4742 | 0 | 701 | 2058.5 | 102 | 0 | 7 | 2056
20:00 | 3286 | 1739 | 911 | 38 | 168 | 1476.01 | 39 | 4779 | 0 | 731 | 2101.5 | 101 | 0 | 9 | 1603
20:30 | 3287.5 | 1752 | 911 | 38 | 166 | 1468.985 | 39.5 | 4779 | 0 | 732.5 | 2137.5 | 100.5 | 0 | 7.5 | 1695
21:00 | 3289 | 1765 | 911 | 38 | 164 | 1461.96 | 40 | 4779 | 0 | 734 | 2173.5 | 100 | 0 | 6 | 1787
21:30 | 3302.5 | 1828.5 | 864.5 | 38 | 164 | 1460.37 | 40 | 4779 | 0 | 734 | 2111.5 | 100 | 0 | 8.5 | 1705.5
22:00 | 3316 | 1892 | 818 | 38 | 164 | 1458.78 | 40 | 4779 | 0 | 734 | 2049.5 | 100 | 0 | 11 | 1624
22:30 | 3333.5 | 1930 | 818 | 38 | 157 | 1459.305 | 40 | 4795.5 | 0 | 716.5 | 1803.6 | 100.5 | 0 | 10 | 1741.5
23:00 | 3351 | 1968 | 818 | 38 | 150 | 1459.83 | 40 | 4812 | 0 | 699 | 1557.7 | 101 | 0 | 9 | 1859
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 17-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 175 | 42 | 504 | 90 | 1712 | 388 | Ishurdi-Ghorashal Ckt-1 | Export | 4034618.18
1:00 | 150 | 31 | 492 | 98 | 1606 | 312
2:00 | 145 | 29 | 508 | 96 | 1622 | 338 |  | Import | 0
3:00 | 158 | 19 | 526 | 96 | 1674 | 334
4:00 | 151 | 13 | 530 | 106 | 1618 | 278 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 142 | 10 | 504 | 102 | 1572 | 262
6:00 | 143 | 10 | 516 | 114 | 1586 | 272 |  | Import | 0
7:00 | 146 | 9 | 516 | 118 | 1550 | 244
8:00 | 163 | 29 | 502 | 92 | 1704 | 376 | Sirajganj-Sreepur Ckt-1 | Export | 2866000
9:00 | 194 | 46 | 580 | 124 | 1794 | 410
10:00 | 202 | 52 | 602 | 116 | 1942 | 490 |  | Import | 0
11:00 | 205 | 43 | 618 | 120 | 1932 | 500
12:00 | 200 | 32 | 570 | 108 | 1990 | 518 | Sirajganj-Sreepur Ckt-2 | Export | 2874000
13:00 | 198 | 39 | 570 | 108 | 1912 | 480
14:00 | 203 | 37 | 630 | 144 | 1964 | 466 |  | Import | 0
15:00 | 193 | 31 | 580 | 104 | 1914 | 434
16:00 | 179 | 35 | 520 | 90 | 1840 | 416 | Gopalganj-Aminbazar Ckt-1 | Export | 20860000
17:00 | 170 | 36 | 460 | 78 | 1754 | 400
18:00 | 154 | 37 | 468 | 136 | 1676 | 404 |  | Import | 0
18:30 | 172 | 36 | 580 | 160 | 1706 | 338
19:00 | 183 | 42 | 552 | 136 | 1766 | 354 | Gopalganj-Aminbazar Ckt-2 | Export | 20900000
19:30 | 172 | 35 | 530 | 124 | 1768 | 300
20:00 | 161 | 29 | 510 | 120 | 1712 | 300 |  | Import | 0
21:00 | 162 | 27 | 500 | 118 | 1680 | 306
22:00 | 149 | 19 | 510 | 120 | 1618 | 274 |  | Total Export | 51534618.18
23:00 | 140 | 14 | 460 | 104 | 1600 | 292 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 375 | 04:00 | 357 | 12:00 | Madunaghat | 395 | 01:00 | 383 | 12:00
Amtali | 408 | 00:00 | 402 | 14:00 | Meghnaghat | 381 | 01:00 | 365 | 12:00
Ashuganj | 409 | 1:00 | 389 | 12:00 | Payra | 409 | 01:00 | 403 | 13:00
Bhulta | 401 | 04:00 | 378 | 12:00 | Rahanpur | 400 | 17:00 | 390 | 07:00
Bibiana | 394 | 19:00 | 384 | 12:00 | Rampal | 389 | 00:00 | 375 | 12:00
BIPTC | 401 | 07:00 | 388 | 16:00
Bogura | 384 | 18:00 | 370 | 13:00
Gopalganj | 386 | 01:00 | 371 | 14:00
Kaliakoir | 369 | 19:30 | 348 | 14:00
Korerhat | 395 | 01:00 | 380 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 01:00 | 212 | 12:00 | Ishurdi | 235 | 00:00 | 220 | 12:00
AKSML | 231 | 18:00 | 220 | 11:00 | Jhenaidah | 222 | 00:00 | 207 | 12:00
Aminbazar | 226 | 04:00 | 211 | 12:00 | Kachua | 228 | 19:30 | 215 | 12:00
Ashuganj | 228 | 00:00 | 220 | 12:00 | Kaliakoir | 227 | 19:30 | 212 | 14:00
Ashuganj-400 | 228 | 00:00 | 220 | 12:00 | Keranigonj | 225 | 01:00 | 211 | 12:00
Baghabari | 231 | 00:00 | 222 | 12:00 | Khulna(S) | 222 | 00:00 | 210 | 15:00
Barapukuria | 222 | 00:00 | 210 | 08:00 | Korerhat | 225 | 00:00 | 216 | 11:00
Barapukuria-230 | 222 | 00:00 | 210 | 08:00 | Madunaghat | 231 | 00:00 | 223 | 11:00
Barishal | 230 | 00:00 | 225 | 12:00 | Madunaghat-400 | 233 | 20:00 | 224 | 12:00
Bheramara | 233 | 00:00 | 217 | 12:00 | Maniknagar | 229 | 05:00 | 213 | 12:00
Bhulta | 230 | 02:00 | 215 | 12:00 | Meghnaghat | 236 | 03:00 | 223 | 11:00
Bibiana | 229 | 19:00 | 224 | 11:00 | Meghnaghat-400 | 231 | 00:00 | 218 | 12:00
BIPTC | 235 | 00:00 | 217 | 12:00 | Mirsorai | 230 | 01:00 | 221 | 11:00
Bogura | 238 | 00:00 | 230 | 07:00 | Naogaon | 214 | 00:00 | 204 | 23:00
Bogura-400 | 238 | 00:00 | 230 | 07:00 | Purbasadipur | 219 | 00:00 | 207 | 11:00
Borhanuddin | 233 | 01:00 | 230 | 12:00 | Rajshahi | 235 | 19:30 | 216 | 12:00
BSRM | 226 | 18:00 | 217 | 11:00 | Rampal | 220 | 00:00 | 211 | 14:00
Charfasson | 236 | 00:00 | 230 | 19:30 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 225 | 00:00 | 215 | 12:00 | Rampura | 230 | 02:00 | 213 | 12:00
Cumilla(N) | 227 | 01:00 | 216 | 12:00 | Shikalbaha | 231 | 00:00 | 222 | 14:00
Faridpur | 227 | 00:00 | 220 | 12:00 | Shyampur | 227 | 04:00 | 213 | 12:00
Fenchuganj | 231 | 07:00 | 228 | 00:00 | Siddhirganj | 231 | 04:00 | 216 | 12:00
Feni | 226 | 01:00 | 216 | 11:00 | Sirajgonj | 237 | 00:00 | 232 | 11:00
Ghorashal | 230 | 00:00 | 220 | 10:00 | Sreepur | 224 | 17:00 | 216 | 12:00
Ghorashal-230 | 217 | 01:00 | 200 | 11:00 | Tongi | 217 | 04:00 | 200 | 11:00
Gopalganj | 229 | 00:00 | 222 | 12:00
GPH | 230 | 19:30 | 220 | 13:00
Haripur | 230 | 04:00 | 215 | 12:00
Hasnabad | 225 | 00:00 | 212 | 11:00
Hathazari | 229 | 00:00 | 220 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 01:00 | 123 | 12:00 | Madunaghat | 134 | 00:00 | 129 | 11:00
Agargaon | 135 | 04:00 | 124 | 12:00 | Magura | 131 | 00:00 | 121 | 14:00
Agrabad | 132 | 00:00 | 125 | 11:00 | Mahasthangarh | 134 | 00:00 | 127 | 07:00
AKS | 131 | 19:00 | 124 | 11:00 | Maijdee | 127 | 18:00 | 120 | 11:00
Aminbazar | 129 | 19:30 | 121 | 12:00 | Manikganj | 132 | 18:00 | 124 | 11:00
Amnura | 139 | 19:30 | 125 | 12:00 | Maniknagar | 135 | 07:00 | 123 | 12:00
Ashuganj | 140 | 22:00 | 133 | 06:00 | Matarbari | 126 | 19:00 | 111 | 07:00
Ashuganj-230 | 140 | 22:00 | 133 | 06:00 | Matuail | 133 | 02:00 | 124 | 12:00
Bagerhat | 126 | 10:00 | 116 | 07:00 | Metrorail_Motijheel | 135 | 07:00 | 123 | 12:00
Bajitpur | 128 | 10:00 | 123 | 14:00 | Metrorail_Uttara | 133 | 03:00 | 130 | 06:00
Bakerganj | 131 | 18:00 | 128 | 11:00 | Millgate | 134 | 01:00 | 120 | 11:00
Bakulia | 134 | 00:00 | 125 | 12:00 | Mirpur | 129 | 22:00 | 120 | 11:00
Banani | 135 | 01:00 | 122 | 12:00 | Mirzapur | 132 | 05:00 | 124 | 12:00
Bangabhaban | 135 | 05:00 | 122 | 12:00 | Mithapukur | 132 | 00:00 | 124 | 23:00
Barapukuria | 135 | 00:00 | 125 | 08:00 | MI_Cement | 129 | 05:00 | 116 | 12:00
Barguna | 130 | 00:00 | 127 | 19:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 00:00 | 127 | 19:00 | Mogbazar | 136 | 06:00 | 125 | 12:00
Barishal-230 | 131 | 00:00 | 128 | 23:00 | Mongla | 126 | 01:00 | 117 | 07:00
Baroaulia | 134 | 19:00 | 128 | 09:00 | Motijheel | 135 | 05:00 | 122 | 12:00
Baroirhat | 131 | 01:00 | 125 | 11:00 | Muktagacha | 132 | 07:00 | 116 | 14:00
Bashundhara | 136 | 05:00 | 120 | 11:00 | Munshiganj | 132 | 01:00 | 124 | 12:00
BashundharaCement | 133 | 03:00 | 125 | 11:00 | Muradnagar | 128 | 00:00 | 122 | 11:00
Beanibazar | 125 | 11:00 | 119 | 00:00 | Mymensingh | 130 | 05:00 | 115 | 00:00
Benapole | 126 | 00:00 | 117 | 12:00 | Nabinagar | 130 | 19:30 | 120 | 12:00
Bhaluka | 131 | 05:00 | 123 | 19:00 | Naogaon | 135 | 00:00 | 123 | 06:00
Bhandaria | 127 | 13:00 | 122 | 06:00 | Narail | 132 | 19:30 | 120 | 14:00
Bhangura | 133 | 19:30 | 128 | 11:00 | Narinda | 135 | 07:00 | 123 | 12:00
Bheramara | 134 | 00:00 | 125 | 12:00 | Narshingdi | 128 | 00:00 | 121 | 11:00
Bheramara(GK) | 134 | 00:00 | 126 | 11:00 | Natore | 134 | 19:30 | 126 | 12:00
Bhulta | 128 | 00:00 | 122 | 11:00 | Nawabganj | 136 | 01:00 | 126 | 12:00
Bog-Sherpur | 135 | 00:00 | 129 | 11:00 | Netrakona | 125 | 16:00 | 113 | 07:00
Bogura | 137 | 19:30 | 131 | 08:00 | New | 133 | 02:00 | 120 | 11:00
Bogura-230 | 138 | 00:00 | 132 | 05:00 | Niamatpur | 131 | 17:00 | 125 | 13:00
Brahmanbaria | 129 | 07:00 | 115 | 23:00 | Noapara | 129 | 00:00 | 121 | 07:00
Cantonment | 134 | 04:00 | 123 | 12:00 | Pabna | 132 | 00:00 | 125 | 11:00
Chandina | 131 | 00:00 | 125 | 11:00 | Palashbari | 129 | 00:00 | 122 | 07:00
Chandpur | 132 | 19:30 | 120 | 11:00 | Panchagarh | 139 | 17:00 | 127 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 00:00 | 129 | 10:00 | Patiya | 133 | 01:00 | 125 | 11:00
Chapai | 131 | 00:00 | 129 | 11:00 | Patuakhali | 130 | 01:00 | 127 | 19:00
Charsaidpur | 133 | 00:00 | 124 | 12:00 | Payra | 133 | 01:00 | 131 | 12:00
Chauddagram | 130 | 19:30 | 124 | 11:00 | PHP | 130 | 00:00 | 125 | 11:00
Chhatak | 125 | 10:00 | 116 | 00:00 | Postogola | 130 | 01:00 | 119 | 12:00
Chowmuhani | 126 | 17:00 | 120 | 12:00 | Pubail | 126 | 00:00 | 119 | 14:00
Chuadanga | 129 | 00:00 | 119 | 07:00 | Purbachal | 135 | 01:00 | 122 | 12:00
Coxsbazar | 128 | 23:00 | 112 | 07:00 | Purbasadipur | 132 | 00:00 | 125 | 08:00
Cumilla(N) | 131 | 00:00 | 125 | 11:00 | Rahanpur | 134 | 18:00 | 129 | 05:00
Cumilla(S) | 131 | 01:00 | 123 | 12:00 | Rahanpur-400 | 134 | 17:00 | 130 | 05:00
Daganbhuiyan | 129 | 00:00 | 123 | 11:00 | Rahim | 133 | 01:00 | 125 | 12:00
Daudkandi | 128 | 00:00 | 121 | 12:00 | Rajbari | 128 | 00:00 | 121 | 12:00
DhakaUniversity | 136 | 04:00 | 123 | 12:00 | Rajendrapur | 131 | 17:00 | 124 | 07:00
Dhamrai | 130 | 00:00 | 121 | 12:00 | Rajshahi | 133 | 00:00 | 123 | 12:00
Dhanmondi | 136 | 03:00 | 124 | 12:00 | Rajshahi-230 | 135 | 19:30 | 124 | 12:00
Dohazari | 132 | 19:00 | 122 | 10:00 | Ramganj | 128 | 19:30 | 117 | 10:00
Faridpur | 130 | 00:00 | 126 | 11:00 | Rampur | 133 | 00:00 | 126 | 10:00
Fatullah | 136 | 19:30 | 117 | 12:00 | Rampura | 136 | 04:00 | 123 | 12:00
Fenchuganj | 131 | 06:00 | 128 | 00:00 | Rangamati | 133 | 04:00 | 127 | 11:00
Feni | 129 | 00:00 | 126 | 07:00 | Rangpur | 130 | 00:00 | 121 | 08:00
Feni-230 | 130 | 01:00 | 124 | 11:00 | Ruppur | 136 | 00:00 | 126 | 11:00
Ghatail | 129 | 04:00 | 116 | 14:00 | Saidpur | 132 | 00:00 | 124 | 08:00
Ghorashal | 129 | 00:00 | 122 | 11:00 | Santhia | 134 | 00:00 | 127 | 12:00
Goalpara | 132 | 10:00 | 124 | 14:00 | Satkhira | 128 | 00:00 | 114 | 07:00
Gollamari | 132 | 10:00 | 124 | 7:00 | Satmasjid | 134 | 01:00 | 123 | 11:00
Gopalganj | 129 | 00:00 | 118 | 12:00 | Savar | 131 | 19:30 | 118 | 11:00
Gopalganj-400 | 130 | 00:00 | 125 | 12:00 | SevenRings | 129 | 02:00 | 123 | 11:00
Gulshan | 135 | 04:00 | 123 | 12:00 | ShahCement | 133 | 00:00 | 124 | 12:00
Halishahar | 133 | 01:00 | 125 | 11:00 | Shahjadpur | 135 | 00:00 | 131 | 11:00
Haripur | 134 | 01:00 | 125 | 12:00 | Shahjibazar | 129 | 08:00 | 119 | 21:00
HaripurSBU | 134 | 01:00 | 125 | 12:00 | Shahmirpur | 133 | 00:00 | 127 | 11:00
Hasnabad | 131 | 05:00 | 120 | 11:00 | Shariatpur | 128 | 00:00 | 124 | 11:00
Hathazari | 135 | 22:00 | 129 | 12:00 | Sherpur | 133 | 05:00 | 112 | 00:00
Hatirjheel | 136 | 04:00 | 123 | 12:00 | Shikalbaha | 123 | 00:00 | 117 | 11:00
Ishurdi | 136 | 00:00 | 128 | 11:00 | Shikalbaha-230 | 134 | 00:00 | 127 | 14:00
Jaldhaka | 130 | 00:00 | 122 | 07:00 | Shitalakhya | 129 | 05:00 | 116 | 12:00
Jamalpur | 134 | 05:00 | 117 | 00:00 | Sholosohor | 134 | 01:00 | 126 | 11:00
Jashore | 127 | 00:00 | 118 | 12:00 | Shomvuganj | 125 | 00:00 | 117 | 14:00
Jhenaidah | 134 | 04:00 | 123 | 12:00 | Shyampur | 134 | 00:00 | 125 | 12:00
Jhenaidah-230 | 133 | 00:00 | 122 | 15:00 | Shyampur-230 | 136 | 04:00 | 127 | 12:00
Joydebpur | 124 | 19:30 | 117 | 11:00 | Siddhirganj | 134 | 02:00 | 125 | 12:00
Joypurhat | 132 | 00:00 | 125 | 13:00 | Sirajganj | 131 | 00:00 | 125 | 12:00
Juldah | 134 | 00:00 | 127 | 11:00 | Sonargaon | 132 | 01:00 | 123 | 11:00
Kabirpur | 135 | 18:00 | 118 | 12:00 | Sreemongol | 128 | 08:00 | 122 | 21:00
Kachua | 130 | 18:00 | 122 | 12:00 | Sreepur | 132 | 17:00 | 127 | 07:00
Kaliakoir | 137 | 19:30 | 125 | 12:00 | Srinagar | 136 | 03:00 | 128 | 11:00
Kaliganj | 132 | 00:00 | 122 | 14:00 | SSM | 138 | 17:00 | 130 | 14:00
Kallyanpur | 130 | 19:30 | 120 | 12:00 | Sunamganj | 123 | 10:00 | 113 | 00:00
Kalurghat | 135 | 19:30 | 129 | 11:00 | Sylhet | 126 | 07:00 | 122 | 00:00
Kamrangirchar | 136 | 02:00 | 116 | 11:00 | Sylhet_(South) | 127 | 08:00 | 122 | 00:00
Kaptai | 135 | 1:00 | 131 | 11:00 | Tangail | 129 | 07:00 | 118 | 14:00
Kasba | 129 | 00:00 | 120 | 12:00 | Taraganj | 133 | 00:00 | 122 | 07:00
Kazla | 135 | 05:00 | 122 | 13:00 | Tasnim | 132 | 01:00 | 123 | 11:00
Keranigonj | 137 | 01:00 | 127 | 12:00 | Thakurgaon | 137 | 17:00 | 125 | 11:00
Khagrachori | 132 | 01:00 | 126 | 11:00 | TK | 134 | 00:00 | 129 | 11:00
Khulna | 131 | 19:30 | 123 | 12:00 | Tongi | 135 | 04:00 | 124 | 11:00
Khulna(S) | 132 | 00:00 | 124 | 15:00 | Ullahpara | 133 | 03:00 | 127 | 11:00
Khulshi | 131 | 00:00 | 126 | 10:00 | Ullon | 135 | 02:00 | 123 | 12:00
Kishoreganj | 128 | 10:00 | 121 | 07:00 | Uttara | 133 | 02:00 | 118 | 11:00
Kodda | 136 | 18:30 | 123 | 14:00 | UttaraNew | 133 | 03:00 | 119 | 11:00
Korerhat | 132 | 00:00 | 127 | 11:00 | Zigatola | 137 | 05:00 | 126 | 13:00
KSRM | 133 | 23:00 | 126 | 11:00
Kulaura | 130 | 07:00 | 127 | 00:00
Kurigram | 131 | 01:00 | 120 | 23:00
Kushtia | 133 | 04:00 | 123 | 12:00
Laksam | 129 | 18:00 | 121 | 11:00
Lakshmipur | 126 | 00:00 | 119 | 12:00
Lalbag | 136 | 04:00 | 126 | 12:00
Lalmonirhat | 128 | 00:00 | 119 | 08:00
Madanganj | 133 | 03:00 | 125 | 11:00
Madaripur | 130 | 04:00 | 125 | 12:00
Madartek | 135 | 06:00 | 124 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division