## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 22-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-06-2026 | during | 22-06-2026 | during | 22-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 364 | 288 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 210 | 210 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 318 | 335 | 335 | 335 | 310 | 310 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 129 | 83 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18.5 | 19 | 33 | 33 | 21 | 21 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 42 | 52.19 | 52.19 | 0 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 180 | 300 | 300 | 33 | 80 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 132 | 149 | 149 | 17 | 17 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 105 | 105 | 17 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 102 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 21 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 530 | 535 | 584 | 584 | 520 | 520 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 555 | 550 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 86 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2181.5 | 2595 | 5820.22 | 5792.22 | 2532.06 | 2823.06
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 1 | 0 | 8 | 0 | 8 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 50 | 50 | 6 | 19 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 105 | 89 | 105 | 105 | 105 | 105 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 218 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 86 | 98 | 105 | 105 | 88 | 88 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 37 | 0 | 40 | 56 | 32 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 50 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 5 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 24 | 38 | 108 | 108 | 24 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.75 | 0 | 2.94 | 0 | 4.13 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 21 | 54.36 | 54.36 | 17 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 50 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 106 | 81 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 45 | 0 | 163 | 163 | 50 | 50 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 740 | 676 | 1224 | 1224 | 740 | 740 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 23 | 3 | 15 | 2 | 15 | 2 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1135 | 1135 | 1150 | 1150 | 720 | 1150 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2592.75 | 2533 | 3996.8 | 4063.86 | 2212.63 | 2759.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 211 | 222 | 221.25 | 221.25 | 205.25 | 205.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 290 | 350.01 | 350.01 | 290 | 290 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 220 | 240 | 342.01 | 342.01 | 250 | 250 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 260 | 220 | 393 | 393 | 280 | 280 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 20 | 41.65 | 41.65 | 21 | 21 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 13 | 52 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 0 | 32 | 32 | 24 | 24 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 92 | 96 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 52 | 27 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 146 | 122 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52 | 52 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 75 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 27 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 89 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 19 | 0 | 45 | 0 | 45 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1478.2 | 1558 | 2739.44 | 2688.44 | 1776.25 | 1871.25
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-06-2026 | during | 22-06-2026 | during | 22-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 7.42 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.3 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 47 | 86 | 70 | 90 | 70 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 23.65 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 132.37 | 154 | 486.7 | 446.5 | 200.2 | 177
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 28 | 28 | 28 | 28 | 28 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 153 | 163 | 163 | 163 | 163 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 144 | 142 | 145 | 145 | 145 | 145 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 81 | 84 | 84 | 52 | 52 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 101 | 102 | 102 | 102 | 102 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 22 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 301 | 315 | 350 | 350 | 320 | 320 | plant availability zero
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1142 | 1167 | 1268 | 1268 | 1192 | 1192
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 477 | 476 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 | 25 | 25 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 30 | 30 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 85 | 0 | 105 | 105 | 100 | 100 | -
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 48 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 510 | 740 | 1120 | 1120 | 1150 | 1150 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1158 | 1254 | 3485 | 3415 | 2413 | 2343
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 61 | 51 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 65 | 64 | 65 | 65 | 65 | 65 | GT-1 & ST under maint
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1170 | 1190 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 0 | 150 | 150 | 17 | 35 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.02 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2840.02 | 2832 | 3097 | 3096 | 2904 | 2921
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 19.56 | 0 | 54 | 0 | 54 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 40 | 0 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 10 | 10 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 20 | 0 | 24 | 24 | 24 | 24 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 193 | 178 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 197 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 405 | 408 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 12 | 20 | 20 | 20 | 20 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 0 | 52.2 | 52.2 | 16 | 52 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 42 | 92 | 92 | 50 | 50 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 100 | 100 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 1.26 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1477.74 | 1479.64 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 16.29 | 0 | 59 | 0 | 59 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 58 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2454.85 | 2386.64 | 3027.82 | 2809.12 | 2760.24 | 2612.54
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 40 | 40 | 40 | 40 | 45 | 45 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 35 | 113 | 113 | 100 | 100 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.5 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 95 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 0 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 11 | 0 | 58 | 0 | 58 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 86.5 | 170 | 391 | 302 | 329 | 240
System Total |  |  |  |  | 28843.2 | 29323.517 | 14066.19 | 14649.64 | 24311.98 | 23881.14 | 16319.38 | 16939.35
Forecast Scenario (22-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14410 |  | 2855.45 |  | 17400
|  |  |  | 1:00 | 14160 |  | 2588.05 |  | 16870
|  |  |  | 2:00 | 13970 |  | 2492.55 |  | 16580
|  |  |  | 3:00 | 14010 |  | 2206.05 |  | 16320
|  |  |  | 4:00 | 13950 |  | 2101 |  | 16150
|  |  |  | 5:00 | 13910 |  | 1929.1 |  | 15930
|  |  |  | 6:00 | 13630 |  | 1661.7 |  | 15370
|  |  |  | 7:00 | 13880 |  | 1346.55 |  | 15290
|  |  |  | 8:00 | 13940 |  | 1289.25 |  | 15290
|  |  |  | 9:00 | 14070 |  | 1317.9 |  | 15450
|  |  |  | 10:00 | 14060 |  | 1279.7 |  | 15400
|  |  |  | 11:00 | 14050 |  | 1422.95 |  | 15540
|  |  |  | 12:00 | 13960 |  | 1995.95 |  | 16050
|  |  |  | 13:00 | 14210 |  | 1843.15 |  | 16140
|  |  |  | 14:00 | 14040 |  | 2120.1 |  | 16260
|  |  |  | 15:00 | 13910 |  | 2492.55 |  | 16520
|  |  |  | 16:00 | 13920 |  | 2377.95 |  | 16410
|  |  |  | 17:00 | 14140 |  | 1881.35 |  | 16110
|  |  |  | 18:00 | 14020 |  | 1136.45 |  | 15210
|  |  |  | 18:30 | 14600 |  | 1241.5 |  | 15900
|  |  |  | 19:00 | 15390 |  | 1184.2 |  | 16630
|  |  |  | 19:30 | 15420 |  | 1680.8 |  | 17180
|  |  |  | 20:00 | 15400 |  | 1575.75 |  | 17050
|  |  |  | 21:00 | 15790 |  | 1461.15 |  | 17320
|  |  |  | 22:00 | 15020 |  | 1976.85 |  | 17090
|  |  |  | 23:00 | 14900 |  | 1948.2 |  | 16940
Probable Maximum Temperature: |  |  | 36.40°C
Probable Maximum Demand at Day Peak: |  |  | 16050.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1461
Probable Maximum Demand at Evening Peak: |  |  | 17320.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15790.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 342.74 MKWHr. |  | 450 | 160 | 191 | 170 | 60 | 120 | 50 | 150 | 110 | 1461
*** This report is generated digitally from Operation Information System (OIS) at 09:36 hrs on 22-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 21-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14066.19 | MW | 09:00 Hr. | Energy Generated |  |  | 338.6926 |  | MKWHr.
| Day Peak Demand |  |  | 15930.43 | MW | 12:00 Hr. | Energy Unserverd |  |  | 28.088 |  | MKWHr.
| Evening Peak Generation |  |  | 14649.64 | MW | 21:00 Hr. | Energy Demand |  |  | 366.7806 |  | MKWHr.
| Evening Peak Demand |  |  | 14695.64 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.2 |  | °C
| Minimum Generation of the Day |  |  | 12844.11 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 902.57 |  | MMCFD
| Maximum Generation of the Day |  |  | 15034.74 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 6.8645 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.7127 | 0 | 12.028 | 0 | 0 | 0.12195 | 0 | 0 | 50.8627 | Gas | 124.7435 | Gas | 431952131.29
| Chattogram Zone |  |  | 5.1766 | 43.1255 | 10.5873 | 0 | 2.6692 | 0.071651 | 0 | 0.46992 | 62.1001 | Coal | 117.609 | Coal | 774503636.8593
| Cumilla Zone |  |  | 28.1644 | 0 | 6.5321 | 0 | 0 | 0.31949 | 3.6211 | 0 | 38.6371 | HFO | 39.8474 | HFO | 745807057.98
| Mymensingh Zone |  |  | 0.1248 | 0 | 2.8505 | 0 | 0 | 0.1641 | 0 | 0 | 3.1394 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.054 | 0 | 0 | 0 | 0 | 0.037551 | 0 | 0 | 27.0916 | Hydro | 2.6692 | Hydro | 266924
| Khulna Zone |  |  | 0 | 13.6291 | 0.87322 | 0 | 0 | 0.37008 | 12.304 | 0 | 27.1764 | Solar | 2.1637 | Solar | 32953239.8632
| Barishal Zone |  |  | 6.9104 | 59.891 | 2.4399 | 0 | 0 | 0.002911 | 0 | 0 | 69.2442 | Import | 51.1898 | Import | 332554560.01
| Rajshahi Zone |  |  | 18.6007 | 0 | 2.8071 | 0 | 0 | 0.74008 | 35.2646 | 0 | 57.4125 | Wind | 0.46992 | Wind | 6912523.2
| Rangpur Zone |  |  | 0 | 0.96349 | 1.7293 | 0 | 0 | 0.33593 | 0 | 0 | 3.0287
| Total |  |  | 124.7435 | 117.609 | 39.8474 | 0 | 2.6692 | 2.1637 | 51.1898 | 0.46992 | 338.6926
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 431952131.29 |  | Hydro | 266924
|  |  |  | Coal | 774503636.8593 |  | Solar | 32953239.8632
|  |  |  | HFO | 745807057.98 |  | Import | 332554560.01
|  |  |  | HSD | 0 |  | Wind | 6912523.2
[5 empty] | Total: | 232,49,50,073 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 11.392 | Peak Hr Flow | 476.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47510163.64 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 35.2646 | Peak Hr Flow | 1479.64 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1824 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.6211 | Peak Hr Flow | 122.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2511 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.2778 | Peak Hr Flow | 2077.64 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5376
|  |  |  | Chattogram |  | 0 |  | 1491
|  |  |  | Cumilla |  | 0 |  | 1308
|  |  |  | Mymensingh |  | 0 |  | 1046
|  |  |  | Sylhet |  | 0 |  | 540
|  |  |  | Khulna |  | 34 |  | 1792
|  |  |  | Barishal |  | 0 |  | 502
|  |  |  | Rajshahi |  | 10 |  | 1476
|  |  |  | Rangpur |  | 0 |  | 970
|  |  |  | Total |  | 44 |  | 14501
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 350
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:00 |  | Day Peak Generation is 14067 MW.
| 10:05 | 10:40 | Shahjadpur 132/33kV S/S T-2(415T) LT Forced S/D Due to SD taken by Shahjadpur -01 33Kv | [7 empty] | 8.0MW load
|  |  | feeder for red hot maintenance | [7 empty] | interrup.
|  | 10:39 | Jashore 132/33kV S/S T-1 HT is restored.
|  | 10:40 | Jashore 132/33kV S/S T-1 LT is restored.
| 11:07 | 12:44 | Daganbhuiyan 132/33kV S/S Transformer-2 LT Scheduled S/D Due to HRC fuse change of
auxilary transformer
| 11:07 | 12:43 | Daganbhuiyan 132/33kV S/S Transformer-2 HT Scheduled S/D Due to HRC fuse change of
auxilary transformer
| 11:21 |  | Haripur 412 MW CCPP Tripped with remarks:- ST
|  | 13:11 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 is restored.
|  | 13:11 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 is restored.
| 14:01 |  | Haripur 412 MW CCPP Synchronized with remarks:- STG Sync ( This is False SMS).
| 14:51 | 15:47 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Tripped showing R phase zone 2 relays Due to | [7 empty] | 63.0MW load
|  |  | Power plant trip | [7 empty] | interrup.
| 15:47 | 17:11 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-2 Scheduled S/D
| 15:48 | 17:10 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 Forced S/D
| 16:47 |  | Haripur 412 MW CCPP Synchronized with remarks:- ST
| 16:55 | 18:07 | Aminbazar-Manikgonj PP 132kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing Over | [7 empty] | 120.0MW load
|  |  | Current relays Due to Over load | [7 empty] | interrup. Aminbazar
400/230/132kV end
| 17:05 | 17:24 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Tripped showing P 142 relays Due to PBS Durgapur | [7 empty] | 38.0MW load
|  |  | 33 kv feeder fault. | [7 empty] | interrup.
| 17:11 | 21:06 | Rampura-Ullon-2 132kV Ckt-2 Tripped from Rampura 230/132kV end showing Distance
protection 21/2: Z1 ,CN relays Due to Unknown
| 17:23 |  | Bhandaria- Barishal(N) ckt 1&2 trippedby showing Distance Phase-ABC from Bhandaria end.
| 17:26 |  | Madaripur-Shariatpur 132kV Ckt-1 Tripped from Shariatpur 132/33kV end showing Distance
Relay (Main Protection). Protection Lockout (Backup Protection) relays Due to Distance
Trip (Main Protection Operate). Zcom Trip.
| 17:34 | 18:21 | Keraniganj-Sreenagar 132kV Ckt-1 Tripped from Keranigonj 230/132/33kV end showing | [7 empty] | 1.0MW load
|  |  | Distance Relay. relays Due to Bad weather and thundering. | [7 empty] | interrup.
Keranigonj
230/132/33kV end
| 17:34 | 18:45 | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 Tripped from Keranigonj | [7 empty] | 1.0MW load
|  |  | 230/132/33kV end showing Distance Relay relays Due to Bad weather and thundering. | [7 empty] | interrup.
Keranigonj
230/132/33kV end
| 17:34 | 21:14 | Aggreko-keraniganj 132kV Ckt-1 Tripped from Keranigonj 230/132/33kV end showing Distance
Relay relays Due to Bad weather and thundering.
| 17:35 |  | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end.
| 17:35 |  | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Forced S/D from Brahmanbaria 132/33kV end.
| 17:46 |  | Bhandaria- Barishal(N) ckt 1&2 is Restored.
| 17:53 | 18:36 | Aminbazar-Manikgonj PP 132kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing | [7 empty] | 60.0MW load
|  |  | Distance relays Due to Distance Trip | [7 empty] | interrup. Aminbazar
400/230/132kV end
| 17:56 | 18:24 | Narshingdi 132/33kV S/S T-2 LT Tripped showing Inter trip relays Due to Inter trip | [7 empty] | 45.0MW load
interrup.
| 17:56 | 18:22 | Narshingdi 132/33kV S/S T-2 HT Tripped showing 50 relays Due to Over current | [7 empty] | 45.0MW load
interrup.
| 18:00 | 20:09 | Barishal(N)-Madaripur 132 kV Ckt-2 Tripped from Barishal 230/132kV end showing REL650
relays Due to Stormy weather
| 18:19 | 19:02 | Bhaluka 132/33kV S/S BR Powergen Ckt- 02 Tripped showing R phase zone 2,36.3km relays Due | [7 empty] | 45.0MW load
|  |  | to power plant trip. | [7 empty] | interrup.
| 18:19 | 18:24 | Bhaluka 132/33kV S/S 01. Transformer- 01 LT Tripped showing SPS trip. relays Due to BR | [7 empty] | 60.0MW load
|  |  | Power plant trip. | [7 empty] | interrup.
| 18:19 | 18:24 | Bhaluka 132/33kV S/S 02. Transformer- 02 LT Tripped showing SPS trip. relays Due to BR | [7 empty] | 60.0MW load
|  |  | power plant trip. | [7 empty] | interrup.
| 18:19 | 18:24 | Bhaluka 132/33kV S/S 03. Transformer-03 LT Tripped showing SPS trip. relays Due to BR | [7 empty] | 19.0MW load
|  |  | Power plant trip. | [7 empty] | interrup.
| 18:19 | 19:01 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Tripped showing R phase zone 2,36.7km. relays | [7 empty] | 45.0MW load
|  |  | Due to BR Power plant trip. | [7 empty] | interrup.
| 18:33 | 19:29 | Bogura(New)-Naogaon 132 kV Ckt-1 Tripped from Naogaon 132/33kV end showing Distanec relay
relays Due to Stormy weather
|  | 18:45 | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 is restored.
| 19:32 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
| 20:10 |  | Barishal(N)-Madaripur 132 kV Ckt-2 Scheduled S/D from Barishal 230/132kV end Due to
Tripped line conductor repair work
| 21:00 |  | Evening Peak Generation is 14630 MW.
|  | 23:28 | Maniknagar-Siddhirganj 230kV Ckt-2 is restored.
|  | 23:28 | Maniknagar-Siddhirganj 230kV Ckt-2 is restored.
| 06:00 |  | Minimum generation is 12623 MW.
| 06:21 |  | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Redhot maintenance
| 06:22 |  | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Redhot maintenance
| 07:19 |  | Narail 132/33kV S/S TR2 (413-T) LT Scheduled S/D Due to 33kV N6 Feeder Bus Side Red Hot | [7 empty] | 7.0MW load
|  |  | Maintenance. | [7 empty] | interrup.
| 07:20 |  | Narail 132/33kV S/S TR2 (413-T) HT Scheduled S/D Due to 33kV N6 Feeder Bus Side Red Hot | [7 empty] | 7.0MW load
|  |  | Maintenance. | [7 empty] | interrup.
| 07:51 |  | Hathazari 230/132/33kV S/S MT-03 HT Scheduled S/D Due to Bushing inspection
| 07:51 |  | Hathazari 230/132/33kV S/S MT-03 LT Scheduled S/D Due to Bushing inspection
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 21-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 288 | 7351200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 431010 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7495703 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 258480 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 83 | 2715840 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 425181 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 262414 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 433200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 481680 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 42 | 274560 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 180 | 2034371 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1459296 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 916800 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 102 | 643680 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 121949 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 535 | 11318636.36 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 550 | 11632273 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 86 | 2606400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2595 | 50862673.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 169353 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 50085 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 222240 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 89 | 2669240 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 4868876 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 98 | 2187926 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 728051 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 346428 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 676800 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 307680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 38 | 809280 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21566 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 323673 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 21 | 299790 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 61900 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 880320 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 81 | 2396182 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 1485382 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 676 | 17001816 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 469920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1135 | 26123636.36 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2533 | 62100144.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 222 | 5146000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7437200 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 240 | 5510000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5668000 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 498960 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1234344 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 52 | 1038763 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 461872 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2241650 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 27 | 2405760 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 122 | 3621120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 857669 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 428230 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 75 | 835620 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 226800 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 705600 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 319491 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1558 | 38637079
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 50367 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 124800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 86 | 1464000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1333200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 106130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 53280 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 154 | 3139377
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 37551 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 671000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3419263.64 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 3397000 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 725088 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1318080 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2436570 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 336000 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7365000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 315 | 7386000 | plant availability zero
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1167 | 27091552.64
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 476 | 11392000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 2880 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 870336 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 370080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 740 | 13629094 | Unit1 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1254 | 27176390
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1000 | 23745455 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 51 | 2071488 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 64 | 1546000 | GT-1 & ST under maint
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1190 | 29054545.45 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5364360 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 368400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7091000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2911 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2832 | 69244159.45
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 188800 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 759595 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 29360 | Under Maintenance
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 328271 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 178 | 4728409 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 197 | 4829527 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 408 | 9042763 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 12 | 229939 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 241474 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 42 | 264816 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 532032 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 421632 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 20280 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1479.64 | 35264631 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 218848 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 312150 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2386.64 | 57412527
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 40 | 963491 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 35 | 439641 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 25226.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1289649 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 84624 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 226080 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 170 | 3028711.16
Eastern Grid Total |  |  |  |  | 17438.042 | 8007 | 181830826.36
Western Grid Total |  |  |  |  | 11885.475 | 6642.64 | 156861787.61
National Grid Total |  |  |  |  | 29323.517 | 14649.64 | 338692613.97
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 21-06-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9814.11 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4696.1 | MW
i) Dhaka area |  |  | 5375.51 |  | MW | i) Khulna area |  |  |  | 1758 | MW
ii) Chattogram area |  |  | 1544.6 |  | MW | ii) Barishal area |  |  |  | 501.7 | MW
iii) Cumilla area |  |  | 1308 |  | MW | iii) Rajshahi area |  |  |  | 1466.4 | MW
iv) Mymensingh area |  |  | 1046 |  | MW | iv) Rangpur area |  |  |  | 970 | MW
v) Sylhet area |  |  | 540 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14510.21 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 127 | 06:00 | 133 | Narshingdi | 176 | 21:00 | 199 | Zigatola | 98 | 14:00
2 | AKSML | 125.7 | 10:00 | 68 | Hasnabad | 89 | 21:00 | 134 | Natore | 156 | 20:00
3 | Aftabnagar | 48 | 13:00 | 69 | Hathazari | 98 | 19:30 | 135 | Nawabganj | 61.4 | 01:00
4 | Agargaon | 131 | 13:00 | 70 | Hatirjheel | 54 | 15:00 | 136 | Netrakona | 121 | 22:00
5 | Agrabad | 74 | 17:00 | 71 | Ishurdi | 82 | 16:00 | 137 | New | 58 | 15:00
6 | Amnura | 33 | 00:00 | 72 | Jaldhaka | 74 | 20:00 | 138 | Niamatpur | 78 | 01:00
7 | Ashuganj | 84 | 13:00 | 73 | Jamalpur | 116 | 22:00 | 139 | Noapara | 45 | 10:00
8 | BSRM | 200 | 10:00 | 74 | Jashore | 166 | 00:00 | 140 | PHP | 12 | 12:00
9 | Bagerhat | 87 | 20:00 | 75 | Jhenaidah | 102 | 07:00 | 141 | Pabna | 92 | 07:00
10 | Bajitpur | 85 | 07:00 | 76 | Joydebpur | 170 | 19:00 | 142 | Palashbari | 120 | 22:00
11 | Bakerganj | 15.6 | 21:00 | 77 | Joypurhat | 69 | 22:00 | 143 | Panchagarh | 60 | 19:30
12 | Bakulia | 100 | 19:00 | 78 | Juldah | 19.5 | 01:00 | 144 | Patiya | 11.5 | 19:30
13 | Banani | 69 | 13:00 | 79 | KSRM | 24 | 00:00 | 145 | Patuakhali | 74.1 | 21:00
14 | Bangabhaban | 23 | 11:00 | 80 | Kabirpur | 275 | 19:30 | 146 | Payra | 36 | 04:00
15 | Barapukuria | 68 | 19:30 | 81 | Kachua | 102 | 21:00 | 147 | Postogola | 66 | 00:00
16 | Barguna | 22 | 03:00 | 82 | Kaliganj | 40 | 19:30 | 148 | Pubail | 28 | 09:00
17 | Barishal | 106 | 19:30 | 83 | Kallyanpur | 126 | 15:00 | 149 | Purbachal | 36 | 13:00
18 | Barishal-230 | 100 | 05:00 | 84 | Kalurghat | 43 | 09:00 | 150 | Purbasadipur | 139 | 19:30
19 | Baroaulia | 52 | 13:00 | 85 | Kamrangirchar | 81 | 13:00 | 151 | Rahanpur | 45 | 22:00
20 | Baroirhat | 72 | 22:00 | 86 | Kaptai | N/A | N/A | 152 | Rahim | 48 | 04:00
21 | Bashundhara | 219 | 14:00 | 87 | Kasba | 36 | 02:00 | 153 | Rajbari | 75 | 07:00
22 | BashundharaCement | 1 | 07:00 | 88 | Kazla | 99 | 01:00 | 154 | Rajendrapur | 116 | 19:30
23 | Beanibazar | 70 | 21:00 | 89 | Keranigonj | 87 | 19:30 | 155 | Rajshahi | 108 | 21:00
24 | Benapole | 64 | 19:30 | 90 | Khagrachori | 38 | 19:00 | 156 | Rajshahi-230 | 107 | 16:00
25 | Bhaluka | 140 | 15:00 | 91 | Khulna | 69 | 19:00 | 157 | Ramganj | 98 | 23:00
26 | Bhandaria | 59 | 22:00 | 92 | Khulshi | 192 | 19:00 | 158 | Rampur | 44 | 19:00
27 | Bhangura | 35 | 19:30 | 93 | Kishoreganj | 110 | 22:00 | 159 | Rangamati | 16 | 19:30
28 | Bheramara(GK) | 67 | 21:00 | 94 | Kodda | 356 | 18:30 | 160 | Rangpur | 132 | 20:00
29 | Bhulta | 215 | 09:00 | 95 | Kulaura | 48 | 19:00 | 161 | Ruppur | 4.8 | 10:00
30 | Bog-Sherpur | 78 | 21:00 | 96 | Kurigram | 61 | 20:00 | 162 | SSM | 0 | 00:00
31 | Bogura | 198 | 00:00 | 97 | Kushtia | 153 | 07:00 | 163 | Saidpur | 105 | 19:30
32 | Borhanuddin | 78 | 22:00 | 98 | Laksam | 33 | 19:30 | 164 | Santhia | 32 | 07:00
33 | Brahmanbaria | 127 | 21:00 | 99 | Lakshmipur | 45 | 01:00 | 165 | Satkhira | 142 | 07:00
34 | Cantonment | 144 | 13:00 | 100 | Lalbag | 80 | 13:00 | 166 | Satmasjid | 115 | 15:00
35 | Chandina | 22 | 19:00 | 101 | Lalmonirhat | 56 | 19:00 | 167 | Savar | 192 | 00:00
36 | Chandpur | 86 | 23:00 | 102 | MI_Cement | 13.1 | 13:00 | 168 | SevenRings | 17.8 | 05:00
37 | Chandraghona | 36 | 19:30 | 103 | Madanganj | 48 | 21:00 | 169 | ShahCement | 39 | 08:00
38 | Chapai | 86 | 21:00 | 104 | Madaripur | 124 | 15:00 | 170 | Shahjadpur | 68 | 12:00
39 | Charfasson | 34 | 22:00 | 105 | Madartek | 94 | 16:00 | 171 | Shahjibazar | 117 | 19:00
40 | Charsaidpur | 39 | 00:00 | 106 | Madunaghat | 56 | 19:00 | 172 | Shahmirpur | 53 | 19:00
41 | Chauddagram | 77 | 19:00 | 107 | Magura | 64 | 20:00 | 173 | Shariatpur | 86 | 22:00
42 | Chhatak | 30 | 19:00 | 108 | Mahasthangarh | 75 | 23:00 | 174 | Sherpur | 136 | 21:00
43 | Chowmuhani | 158 | 20:00 | 109 | Maijdee | 42 | 22:00 | 175 | Shikalbaha | 30.5 | 15:00
44 | Chuadanga | 121 | 21:00 | 110 | Manikganj | 128 | 12:00 | 176 | Shitalakhya | 88 | 13:00
45 | Coxsbazar | 137 | 21:00 | 111 | Maniknagar | 82 | 13:00 | 177 | Sholosohor | 49 | 19:00
46 | Cumilla(N) | 121 | 19:00 | 112 | Matarbari | 56 | 19:30 | 178 | Shomvuganj | 34 | 06:00
47 | Cumilla(S) | 174 | 15:00 | 113 | Matuail | 84 | 12:00 | 179 | Shyampur | 166 | 00:00
48 | Daganbhuiyan | 42 | 23:00 | 114 | Metrorail_Motijheel | 20 | 13:00 | 180 | Siddhirganj | 139 | 13:00
49 | Daudkandi | 152 | 20:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Sirajganj | 112 | 00:00
50 | DhakaUniversity | 100 | 13:00 | 116 | Millgate | 150 | 12:00 | 182 | Sonargaon | 134 | 07:00
51 | Dhamrai | 106 | 18:30 | 117 | Mirpur | 167 | 14:00 | 183 | Sreemongol | 74 | 22:00
52 | Dhanmondi | 140.4 | 13:00 | 118 | Mirsorai | 49 | 11:00 | 184 | Sreepur | 121 | 19:30
53 | Dohazari | 96 | 20:00 | 119 | Mirzapur | 44 | 18:30 | 185 | Srinagar | 48 | 00:00
54 | Faridpur | 165 | 06:00 | 120 | Mithapukur | 66 | 22:00 | 186 | Sunamganj | 57 | 21:00
55 | Fatullah | 109 | 10:00 | 121 | Modern | N/A | N/A | 187 | Sylhet | 109 | 00:00
56 | Fenchuganj | 42 | 19:00 | 122 | Mogbazar | 127.8 | 13:00 | 188 | Sylhet_(South) | 46 | 22:00
57 | Feni | 96 | 19:00 | 123 | Mongla | 45 | 09:00 | 189 | TK | 25 | 22:00
58 | GPH | 71 | 00:00 | 124 | Motijheel | 58 | 13:00 | 190 | Tangail | 156 | 23:00
59 | Ghatail | 73 | 15:00 | 125 | Muktagacha | 35 | 04:00 | 191 | Taraganj | 26 | 19:30
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 113 | 19:30 | 192 | Tasnim | 43 | 15:00
61 | Ghorashal-230 | 108 | 07:00 | 127 | Muradnagar | 48 | 18:30 | 193 | Thakurgaon | 115 | 20:00
62 | Goalpara | 42 | 02:00 | 128 | Mymensingh | 171 | 00:00 | 194 | Tongi | 158 | 11:00
63 | Gollamari | 112 | 12:00 | 129 | Nabinagar | 104 | 20:00 | 195 | Ullahpara | 36 | 07:00
64 | Gopalganj | 104 | 07:00 | 130 | Naogaon | 143 | 23:00 | 196 | Ullon | 62 | 00:00
65 | Gulshan | 140 | 13:00 | 131 | Narail | 64.5 | 07:00 | 197 | Uttara | 107 | 13:00
66 | Halishahar | 108 | 15:00 | 132 | Narinda | 80 | 13:00 | 198 | UttaraNew | 57 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 21-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14280.08 | 2709 |  | 17110.99
1:00 | 14158.12 | 2519 |  | 16790.48
2:00 | 13964.28 | 2445 |  | 16519.31
3:00 | 14008.76 | 2261 |  | 16371.51
4:00 | 13946.97 | 2141 |  | 16184.32
5:00 | 13910.21 | 1948 |  | 15945.87
6:00 | 13628.13 | 751 |  | 14413.13
7:00 | 13877.08 | 390 |  | 14285.08
8:00 | 13937.51 | 319 |  | 14270.51
9:00 | 14066.19 | 560 |  | 14651.19
10:00 | 14052.81 | 1072 |  | 15172.81
11:00 | 14040.95 | 1355 |  | 15456.95
12:00 | 13951.43 | 1894 |  | 15930.43
13:00 | 14202.66 | 1858 |  | 16144.66
14:00 | 14035.34 | 1905 |  | 16026.34
15:00 | 13597 | 1901 |  | 15584
16:00 | 13366.17 | 1343 |  | 14769.17
17:00 | 12844.11 | 358 |  | 13218.11
18:00 | 12671.44 | 100 |  | 12775.44
19:00 | 13613.41 | 10 |  | 13623.41
19:30 | 14170 | 47 |  | 14219
20:00 | 14170.96 | 45 |  | 14217.96
21:00 | 14649.64 | 44 |  | 14695.64
22:00 | 14933.73 | 27 |  | 14961.73
23:00 | 15034.74 | 133 |  | 15173.74
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 21-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 121 | 23 | 460 | 116 | 1808 | 456 | Ishurdi-Ghorashal Ckt-1 | Export | 2621163.64
1:00 | 117 | 22 | 450 | 120 | 1804 | 458
2:00 | 120 | 14 | 484 | 120 | 1734 | 410 |  | Import | 0
3:00 | 110 | 9 | 460 | 116 | 1662 | 386
4:00 | 105 | 11 | 418 | 116 | 1604 | 370 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 101 | 10 | 412 | 116 | 1596 | 382
6:00 | 102 | 11 | 408 | 116 | 1474 | 348 |  | Import | 0
7:00 | 104 | 28 | 412 | 124 | 1510 | 380
8:00 | 119 | 35 | 436 | 140 | 1642 | 468 | Sirajganj-Sreepur Ckt-1 | Export | 2641000
9:00 | 142 | 48 | 496 | 168 | 1704 | 492
10:00 | 149 | 49 | 500 | 140 | 1862 | 532 |  | Import | 0
11:00 | 153 | 56 | 522 | 168 | 1804 | 548
12:00 | 154 | 54 | 440 | 124 | 1778 | 540 | Sirajganj-Sreepur Ckt-2 | Export | 2658000
13:00 | 133 | 44 | 440 | 124 | 1696 | 506
14:00 | 145 | 48 | 460 | 114 | 1784 | 518 |  | Import | 0
15:00 | 146 | 49 | 460 | 130 | 1832 | 520
16:00 | 130 | 44 | 390 | 100 | 1844 | 558 | Gopalganj-Aminbazar Ckt-1 | Export | 19780000
17:00 | 108 | 35 | 306 | 76 | 1686 | 568
18:00 | 102 | 17 | 326 | 74 | 1410 | 476 |  | Import | 0
18:30 | 104 | 17 | 310 | 80 | 1350 | 452
19:00 | 83 | 7 | 336 | 122 | 1440 | 346 | Gopalganj-Aminbazar Ckt-2 | Export | 19810000
19:30 | 67 | 3 | 340 | 106 | 1324 | 274
20:00 | 65 | 1 | 332 | 88 | 1488 | 336 |  | Import | 0
21:00 | 66 | 11 | 304 | 102 | 1454 | 332
22:00 | 50 | 1 | 296 | 100 | 1532 | 270 |  | Total Export | 47510163.64
23:00 | 51 | -2 | 310 | 104 | 1558 | 268 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 21-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7735.7 | 6544.38 | 14280.08 | DAILY GENERATION CURVE
00:30 | 7609.45 | 6609.65 | 14219.1
01:00 | 7483.2 | 6674.92 | 14158.12 | 21-06-2026
01:30 | 7425.2 | 6636 | 14061.2
02:00 | 7367.2 | 6597.08 | 13964.28
02:30 | 7401.2 | 6585.32 | 13986.52
03:00 | 7435.2 | 6573.56 | 14008.76
03:30 | 7429.7 | 6548.165 | 13977.865
04:00 | 7424.2 | 6522.77 | 13946.97
04:30 | 7405.7 | 6522.89 | 13928.59
05:00 | 7387.2 | 6523.01 | 13910.21
05:30 | 7296.93 | 6472.24 | 13769.17
06:00 | 7206.66 | 6421.47 | 13628.13
06:30 | 7300.98 | 6451.625 | 13752.605
07:00 | 7395.3 | 6481.78 | 13877.08
07:30 | 7403.57 | 6503.725 | 13907.295
08:00 | 7411.84 | 6525.67 | 13937.51
08:30 | 7469.33 | 6532.52 | 14001.85
09:00 | 7526.82 | 6539.37 | 14066.19
09:30 | 7521.735 | 6537.765 | 14059.5
10:00 | 7516.65 | 6536.16 | 14052.81
10:30 | 7531.38 | 6515.5 | 14046.88
11:00 | 7546.11 | 6494.84 | 14040.95
11:30 | 7495.515 | 6500.675 | 13996.19
12:00 | 7444.92 | 6506.51 | 13951.43
12:30 | 7588.39 | 6488.655 | 14077.045
13:00 | 7731.86 | 6470.8 | 14202.66
13:30 | 7659.175 | 6459.825 | 14119
14:00 | 7586.49 | 6448.85 | 14035.34
14:30 | 7380.965 | 6435.205 | 13816.17
15:00 | 7175.44 | 6421.56 | 13597
15:30 | 7110.165 | 6371.42 | 13481.585
16:00 | 7044.89 | 6321.28 | 13366.17
16:30 | 6969.615 | 6135.525 | 13105.14
17:00 | 6894.34 | 5949.77 | 12844.11
17:30 | 6942.225 | 5815.55 | 12757.775
18:00 | 6990.11 | 5681.33 | 12671.44
18:30 | 7270.055 | 5872.37 | 13142.425
19:00 | 7550 | 6063.41 | 13613.41
19:30 | 7882.36 | 6287.64 | 14170
20:00 | 7736 | 6434.96 | 14170.96
20:30 | 7871.5 | 6538.8 | 14410.3 |  | Executive Engineer
21:00 | 8007 | 6642.64 | 14649.64 |  | Network Operation Division
21:30 | 8098 | 6693.685 | 14791.685
22:00 | 8189 | 6744.73 | 14933.73
22:30 | 8187 | 6797.235 | 14984.235
23:00 | 8185 | 6849.74 | 15034.74

## En-Curve
QF-LDC-12
Date | 21-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3389 | 1697.5 | 381 | 38 | 162 | 1481.18 | 107 | 4658 | 0 | 587 | 1692.4 | 75 | 0 | 12 | 2709 | DAILY ENERGY CURVE
00:30 | 3387 | 1727.25 | 381 | 38 | 158 | 1479.95 | 107.5 | 4658.5 | 0 | 562 | 1570.9 | 137.5 | 0 | 11.5 | 2614 | 21-06-2026
01:00 | 3385 | 1757 | 381 | 38 | 154 | 1478.72 | 108 | 4659 | 0 | 537 | 1449.4 | 200 | 0 | 11 | 2519
01:30 | 3393.5 | 1771.5 | 428.5 | 38 | 160 | 1481.3 | 108 | 4666.5 | 0 | 512.5 | 1391.4 | 100 | 0 | 10 | 2482 | Energy Generated | 338.6926 |  | MKWHr
02:00 | 3402 | 1786 | 476 | 38 | 166 | 1483.88 | 108 | 4674 | 0 | 488 | 1333.4 | 0 | 0 | 9 | 2445 | Energy not Served | 28.088 |  | MKWHr
02:30 | 3409.5 | 1836 | 476 | 38 | 164 | 1484.72 | 108.5 | 4718 | 0 | 478.5 | 1263.3 | 0 | 0 | 10 | 2353 | Total Energy Requirement | 366.7806 |  | MKWHr
03:00 | 3417 | 1886 | 476 | 38 | 162 | 1485.56 | 109 | 4762 | 0 | 469 | 1193.2 | 0 | 0 | 11 | 2261
03:30 | 3381 | 1826 | 476.5 | 38 | 160 | 1483.665 | 109 | 4855 | 0 | 478 | 1160.7 | 0 | 0 | 10 | 2201
04:00 | 3345 | 1766 | 477 | 38 | 158 | 1481.77 | 109 | 4948 | 0 | 487 | 1128.2 | 0 | 0 | 9 | 2141
04:30 | 3337.5 | 1760.5 | 476 | 38 | 152 | 1482.89 | 109 | 4948.5 | 0 | 487 | 1121.7 | 0 | 0 | 15.5 | 2044.5
05:00 | 3330 | 1755 | 475 | 38 | 146 | 1484.01 | 109 | 4949 | 0 | 487 | 1115.2 | 0 | 0 | 22 | 1948
05:30 | 3314.5 | 1720.5 | 475.5 | 38 | 142 | 1486.13 | 107.5 | 4949 | 8.34 | 487 | 1023.7 | 0 | 0 | 17 | 1349.5
06:00 | 3299 | 1686 | 476 | 38 | 138 | 1488.25 | 106 | 4949 | 16.68 | 487 | 932.2 | 0 | 0 | 12 | 751
06:30 | 3355.5 | 1757.5 | 476 | 38 | 140 | 1487.44 | 105 | 4941.5 | 43.465 | 495 | 897.7 | 0 | 0 | 15.5 | 570.5
07:00 | 3412 | 1829 | 476 | 38 | 142 | 1486.63 | 104 | 4934 | 70.25 | 503 | 863.2 | 0 | 0 | 19 | 390
07:30 | 3412.5 | 1865.75 | 476.5 | 38 | 142 | 1486.065 | 105 | 4926.5 | 115.28 | 498 | 802.2 | 0 | 0 | 39.5 | 354.5
08:00 | 3413 | 1902.5 | 477 | 38 | 142 | 1485.5 | 106 | 4919 | 160.31 | 493 | 741.2 | 0 | 0 | 60 | 319
08:30 | 3437.5 | 1923 | 477 | 38 | 144 | 1481.62 | 105.5 | 4910.5 | 198.03 | 500.5 | 744.7 | 0 | 0 | 41.5 | 439.5
09:00 | 3462 | 1943.5 | 477 | 38 | 146 | 1477.74 | 105 | 4902 | 235.75 | 508 | 748.2 | 0 | 0 | 23 | 560
09:30 | 3453.5 | 1919 | 477 | 38 | 147 | 1482.7 | 105.5 | 4903.5 | 254.6 | 478 | 777.2 | 0 | 0 | 23.5 | 816
10:00 | 3445 | 1894.5 | 477 | 38 | 148 | 1487.66 | 106 | 4905 | 273.45 | 448 | 806.2 | 0 | 0 | 24 | 1072
10:30 | 3434 | 1900 | 477 | 38 | 147 | 1488.06 | 106.5 | 4905 | 289.12 | 414 | 828.2 | 0 | 0 | 20 | 1213.5
11:00 | 3423 | 1905.5 | 477 | 38 | 146 | 1488.46 | 107 | 4905 | 304.79 | 380 | 850.2 | 0 | 0 | 16 | 1355
11:30 | 3357.5 | 1891 | 477 | 38 | 152 | 1473.25 | 107 | 4871.5 | 333.34 | 380 | 898.6 | 0 | 0 | 17 | 1624.5
12:00 | 3292 | 1876.5 | 477 | 38 | 158 | 1458.04 | 107 | 4838 | 361.89 | 380 | 947 | 0 | 0 | 18 | 1894
12:30 | 3289.5 | 1919 | 477 | 38 | 158 | 1471.025 | 118.5 | 4840 | 319.77 | 391 | 1038.75 | 0 | 0 | 16.5 | 1876
13:00 | 3287 | 1961.5 | 477 | 38 | 158 | 1484.01 | 130 | 4842 | 277.65 | 402 | 1130.5 | 0 | 0 | 15 | 1858
13:30 | 3265 | 1919 | 477 | 38 | 162 | 1484.185 | 130 | 4847 | 247.815 | 418 | 1118 | 0 | 0 | 13 | 1881.5
14:00 | 3243 | 1876.5 | 477 | 38 | 166 | 1484.36 | 130 | 4852 | 217.98 | 434 | 1105.5 | 0 | 0 | 11 | 1905
14:30 | 3179.5 | 1808.25 | 477 | 38 | 170 | 1488.83 | 130 | 4848.5 | 184.59 | 364 | 1108.5 | 0 | 0 | 19 | 1903
15:00 | 3116 | 1740 | 477 | 38 | 174 | 1493.3 | 130 | 4845 | 151.2 | 294 | 1111.5 | 0 | 0 | 27 | 1901
15:30 | 3073 | 1710.5 | 477 | 38 | 173 | 1486.595 | 130 | 4827 | 109.89 | 283.5 | 1132.6 | 0 | 0 | 40.5 | 1622
16:00 | 3030 | 1681 | 477 | 38 | 172 | 1479.89 | 130 | 4809 | 68.58 | 273 | 1153.7 | 0 | 0 | 54 | 1343
16:30 | 3016.5 | 1566.5 | 476.5 | 38 | 163 | 1457.23 | 130 | 4707.5 | 46.81 | 292.5 | 1174.1 | 0 | 0 | 36.5 | 850.5
17:00 | 3003 | 1452 | 476 | 38 | 154 | 1434.57 | 130 | 4606 | 25.04 | 312 | 1194.5 | 0 | 0 | 19 | 358
17:30 | 3093 | 1468 | 476 | 38 | 155 | 1370.65 | 128 | 4403 | 16.875 | 390.5 | 1204.25 | 0 | 0 | 14.5 | 229
18:00 | 3183 | 1484 | 476 | 38 | 156 | 1306.73 | 126 | 4200 | 8.71 | 469 | 1214 | 0 | 0 | 10 | 100
18:30 | 3258.5 | 1538 | 476 | 38 | 165 | 1336.57 | 124 | 4429 | 4.355 | 483 | 1278 | 0 | 0 | 12 | 55
19:00 | 3334 | 1592 | 476 | 38 | 174 | 1366.41 | 122 | 4658 | 0 | 497 | 1342 | 0 | 0 | 14 | 10
19:30 | 3330 | 1654 | 476 | 38 | 166 | 1464.64 | 120 | 4772 | 0 | 469 | 1666.36 | 0 | 0 | 14 | 47
20:00 | 3360 | 1771 | 476 | 38 | 124 | 1488.96 | 113 | 4886 | 0 | 430 | 1481 | 0 | 0 | 3 | 45
20:30 | 3376 | 1871 | 476 | 38 | 123 | 1484.3 | 101 | 4987 | 0 | 425 | 1526 | 0 | 0 | 3 | 44.5
21:00 | 3392 | 1971 | 476 | 38 | 122 | 1479.64 | 89 | 5088 | 0 | 420 | 1571 | 0 | 0 | 3 | 44
21:30 | 3367.5 | 1900.5 | 476 | 38 | 135 | 1480.185 | 90 | 5162.5 | 0 | 399 | 1732 | 0 | 0 | 11 | 35.5
22:00 | 3343 | 1830 | 476 | 38 | 148 | 1480.73 | 91 | 5237 | 0 | 378 | 1893 | 0 | 0 | 19 | 27
22:30 | 3350.5 | 1852.5 | 476 | 38 | 150 | 1487.735 | 92 | 5277.5 | 0 | 353 | 1887.5 | 0 | 0 | 19.5 | 80
23:00 | 3358 | 1875 | 476 | 38 | 152 | 1494.74 | 93 | 5318 | 0 | 328 | 1882 | 0 | 0 | 20 | 133
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 21-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 380 | 18:00 | 358 | 11:00 | Madunaghat | 398 | 00:00 | 391 | 09:00
Amtali | 410 | 18:00 | 402 | 08:00 | Meghnaghat | 383 | 18:00 | 367 | 13:00
Ashuganj | 392 | 18:30 | 374 | 13:00 | Payra | 411 | 18:00 | 404 | 12:00
Bhulta | 403 | 18:00 | 380 | 11:00 | Rahanpur | 405 | 18:30 | 388 | 23:00
Bibiana | 396 | 18:00 | 386 | 11:00 | Rampal | 396 | 18:00 | 377 | 12:00
BIPTC | 406 | 18:00 | 399 | 22:00
Bogura | 391 | 18:30 | 372 | 13:00
Gopalganj | 392 | 18:30 | 374 | 13:00
Kaliakoir | 372 | 18:00 | 352 | 11:00
Korerhat | 398 | 00:00 | 386 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 18:00 | 217 | 11:00 | Ishurdi | 234 | 18:00 | 222 | 06:00
AKSML | 233.9 | 00:00 | 225 | 09:00 | Jhenaidah | 225 | 18:00 | 210 | 19:30
Aminbazar | 232 | 18:00 | 217 | 11:00 | Kachua | 229 | 00:00 | 221 | 08:00
Ashuganj | 233 | 18:00 | 219 | 13:00 | Kaliakoir | 231 | 18:00 | 215 | 12:00
Ashuganj-400 | 233 | 18:00 | 219 | 13:00 | Keranigonj | 231 | 18:00 | 214 | 13:00
Baghabari | 234 | 18:00 | 224 | 21:00 | Khulna(S) | 224 | 18:00 | 211 | 13:00
Barapukuria | 224 | 18:00 | 209 | 23:00 | Korerhat | 226 | 00:00 | 220 | 08:00
Barapukuria-230 | 224 | 18:00 | 209 | 23:00 | Madunaghat | 233 | 00:00 | 229 | 08:00
Barishal | 230 | 17:00 | 222 | 13:00 | Madunaghat-400 | 235 | 00:00 | 229 | 09:00
Bheramara | 234 | 15:00 | 222 | 06:00 | Maniknagar | 227 | 18:00 | 213 | 13:00
Bhulta | 231 | 18:00 | 216 | 11:00 | Meghnaghat | 236 | 18:00 | 224 | 13:00
Bibiana | 231 | 18:00 | 225 | 09:00 | Meghnaghat-400 | 233 | 18:00 | 219 | 14:00
BIPTC | 235 | 18:00 | 220 | 19:30 | Mirsorai | 231 | 00:00 | 226 | 07:00
Bogura | 242 | 18:00 | 229 | 23:00 | Naogaon | 223 | 00:00 | 205 | 23:00
Bogura-400 | 242 | 18:00 | 230 | 13:00 | Purbasadipur | 221 | 00:00 | 207 | 23:00
Borhanuddin | 233 | 17:00 | 228 | 04:00 | Rajshahi | 232 | 18:00 | 219 | 06:00
BSRM | 228 | 00:00 | 220 | 09:00 | Rampal | 225 | 18:00 | 212 | 12:00
Charfasson | 234 | 16:00 | 226 | 20:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 227 | 01:00 | 220 | 07:00 | Rampura | 229 | 18:00 | 213 | 13:00
Cumilla(N) | 229 | 18:00 | 219 | 11:00 | Shikalbaha | 234 | 00:00 | 229 | 09:00
Faridpur | 226 | 18:00 | 214 | 13:00 | Shyampur | 231 | 18:00 | 216 | 12:00
Fenchuganj | 234 | 18:00 | 229 | 08:00 | Siddhirganj | 230 | 18:00 | 217 | 11:00
Feni | 227 | 00:00 | 220 | 09:00 | Sirajgonj | 241 | 18:00 | 231 | 10:00
Ghorashal | 230 | 01:00 | 220 | 15:00 | Sreepur | 228 | 18:00 | 217 | 11:00
Ghorashal-230 | 220 | 18:00 | 200 | 12:00 | Tongi | 225 | 23:00 | 202 | 11:00
Gopalganj | 225 | 18:00 | 214 | 13:00
GPH | 232 | 00:00 | 225 | 09:00
Haripur | 230 | 18:00 | 217 | 11:00
Hasnabad | 231 | 18:00 | 216 | 12:00
Hathazari | 232 | 00:00 | 225 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 18:00 | 127 | 11:00 | Madunaghat | 135 | 00:00 | 132 | 08:00
Agargaon | 138 | 18:00 | 126 | 11:00 | Magura | 134 | 15:00 | 124 | 07:00
Agrabad | 134 | 00:00 | 130 | 08:00 | Mahasthangarh | 137 | 18:00 | 127 | 23:00
AKS | 131 | 00:00 | 128 | 08:00 | Maijdee | 128 | 18:30 | 123 | 09:00
Aminbazar | 133 | 20:00 | 120 | 02:00 | Manikganj | 133 | 15:00 | 124 | 07:00
Amnura | 137 | 00:00 | 126 | 22:00 | Maniknagar | 133 | 18:30 | 122 | 13:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 123 | 13:00 | 112 | 19:00
Ashuganj-230 | 140 | 18:00 | 133 | 08:00 | Matuail | 132.5 | 18:00 | 125 | 11:00
Bagerhat | 128 | 17:00 | 116 | 19:30 | Metrorail_Motijheel | 133 | 19:00 | 122 | 13:00
Bajitpur | 133 | 17:00 | 122 | 09:00 | Metrorail_Uttara | 134 | 23:00 | 122 | 10:00
Bakerganj | 134 | 17:00 | 127 | 21:00 | Millgate | 135 | 23:00 | 119 | 13:00
Bakulia | 134 | 00:00 | 130 | 02:00 | Mirpur | 133 | 18:00 | 122 | 11:00
Banani | 137 | 18:00 | 126 | 12:00 | Mirzapur | 131 | 19:00 | 124 | 09:00
Bangabhaban | 133 | 22:00 | 123 | 13:00 | Mithapukur | 133 | 18:00 | 123 | 19:30
Barapukuria | 136 | 00:00 | 125 | 21:00 | MI_Cement | 136 | 18:00 | 124 | 11:00
Barguna | 134 | 17:00 | 126 | 23:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 136 | 17:00 | 128 | 19:30 | Mogbazar | 137 | 03:00 | 125 | 13:00
Barishal-230 | 135 | 17:00 | 128 | 07:00 | Mongla | 129 | 17:00 | 117 | 19:30
Baroaulia | 134 | 00:00 | 131 | 07:00 | Motijheel | 133 | 22:00 | 123 | 13:00
Baroirhat | 132 | 00:00 | 127 | 11:00 | Muktagacha | 127 | 12:00 | 117 | 04:00
Bashundhara | 136 | 18:00 | 120 | 12:00 | Munshiganj | 132 | 18:00 | 124 | 11:00
BashundharaCement | 137 | 18:00 | 127 | 13:00 | Muradnagar | 130 | 18:30 | 123 | 11:00
Beanibazar | 128 | 15:00 | 124 | 08:00 | Mymensingh | 127 | 17:00 | 116 | 09:00
Benapole | 131 | 18:00 | 118 | 13:00 | Nabinagar | 130 | 17:00 | 119 | 12:00
Bhaluka | 133 | 17:00 | 123 | 19:00 | Naogaon | 138 | 18:00 | 122 | 23:00
Bhandaria | 135 | 17:00 | 121 | 19:30 | Narail | 136 | 17:00 | 124 | 06:00
Bhangura | 136 | 18:30 | 129 | 08:00 | Narinda | 133 | 18:30 | 122 | 13:00
Bheramara | 135 | 15:00 | 128 | 06:00 | Narshingdi | 133 | 18:00 | 120 | 07:00
Bheramara(GK) | 135 | 18:00 | 128 | 05:00 | Natore | 135 | 18:00 | 126 | 23:00
Bhulta | 130 | 18:00 | 120 | 11:00 | Nawabganj | 141 | 18:00 | 129 | 13:00
Bog-Sherpur | 139 | 18:00 | 129 | 23:00 | Netrakona | 124 | 16:00 | 115 | 08:00
Bogura | 141 | 18:00 | 131 | 22:00 | New | 137 | 22:00 | 119 | 13:00
Bogura-230 | 141 | 18:00 | 131 | 23:00 | Niamatpur | 133 | 18:30 | 125 | 23:00
Brahmanbaria | 133 | 18:30 | 118 | 11:00 | Noapara | 132 | 17:00 | 121 | 19:30
Cantonment | 138 | 18:00 | 127 | 12:00 | Pabna | 134 | 18:00 | 127 | 06:00
Chandina | 132 | 00:00 | 127 | 11:00 | Palashbari | 132 | 18:00 | 121 | 23:00
Chandpur | 135 | 00:00 | 125 | 08:00 | Panchagarh | 139 | 00:00 | 126 | 17:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 135 | 00:00 | 132 | 10:00 | Patiya | 134 | 00:00 | 129 | 07:00
Chapai | 133 | 18:30 | 125 | 06:00 | Patuakhali | 133 | 17:00 | 127 | 21:00
Charsaidpur | 133 | 18:30 | 125 | 11:00 | Payra | 135 | 18:00 | 131 | 07:00
Chauddagram | 131 | 00:00 | 126 | 11:00 | PHP | 131 | 00:00 | 127 | 11:00
Chhatak | 128 | 15:00 | 120 | 23:00 | Postogola | 138 | 18:00 | 126 | 13:00
Chowmuhani | 128 | 18:00 | 123 | 07:00 | Pubail | 128 | 03:00 | 120 | 11:00
Chuadanga | 132 | 17:00 | 120 | 19:30 | Purbachal | 137 | 18:00 | 125 | 13:00
Coxsbazar | 125 | 11:00 | 114 | 19:30 | Purbasadipur | 134 | 00:00 | 125 | 23:00
Cumilla(N) | 132 | 00:00 | 127 | 08:00 | Rahanpur | 135 | 18:30 | 127 | 23:00
Cumilla(S) | 132 | 00:00 | 125 | 14:00 | Rahanpur-400 | 135 | 18:00 | 129 | 23:00
Daganbhuiyan | 130 | 00:00 | 125 | 09:00 | Rahim | 132 | 18:00 | 124 | 13:00
Daudkandi | 128 | 19:00 | 121 | 11:00 | Rajbari | 130 | 18:00 | 121 | 13:00
DhakaUniversity | 137 | 18:00 | 126 | 13:00 | Rajendrapur | 135 | 16:00 | 124 | 03:00
Dhamrai | 132 | 20:00 | 121 | 12:00 | Rajshahi | 131 | 18:00 | 123 | 23:00
Dhanmondi | 138 | 18:00 | 125.5 | 13:00 | Rajshahi-230 | 134 | 18:00 | 125 | 23:00
Dohazari | 130 | 00:00 | 125 | 17:00 | Ramganj | 131 | 00:00 | 122 | 07:00
Faridpur | 131 | 18:00 | 124 | 13:00 | Rampur | 134 | 00:00 | 130 | 10:00
Fatullah | 138 | 18:00 | 125 | 12:00 | Rampura | 137 | 18:00 | 126 | 13:00
Fenchuganj | 133 | 17:00 | 130 | 04:00 | Rangamati | 134 | 00:00 | 131 | 08:00
Feni | 131 | 03:00 | 125 | 09:00 | Rangpur | 130 | 18:00 | 122 | 19:30
Feni-230 | 131 | 00:00 | 126 | 09:00 | Ruppur | 136 | 17:00 | 130 | 05:00
Ghatail | 127 | 19:00 | 116 | 04:00 | Saidpur | 137 | 19:30 | 125 | 21:00
Ghorashal | 131 | 17:00 | 121 | 11:00 | Santhia | 134 | 04:00 | 129 | 06:00
Goalpara | 135 | 18:30 | 123 | 13:00 | Satkhira | 129 | 18:00 | 116 | 19:30
Gollamari | 134 | 17:00 | 125 | 12:00 | Satmasjid | 137 | 18:00 | 125 | 13:00
Gopalganj | 133 | 18:00 | 124 | 12:00 | Savar | 133 | 18:30 | 120 | 12:00
Gopalganj-400 | 134 | 18:00 | 126 | 12:00 | SevenRings | 131 | 18:00 | 120 | 13:00
Gulshan | 137 | 18:00 | 125 | 13:00 | ShahCement | 133 | 18:30 | 125 | 11:00
Halishahar | 135 | 00:00 | 130 | 09:00 | Shahjadpur | 136 | 04:00 | 132 | 22:00
Haripur | 134 | 18:30 | 126 | 11:00 | Shahjibazar | 133 | 18:00 | 126 | 08:00
HaripurSBU | 133 | 19:00 | 128 | 11:00 | Shahmirpur | 136 | 08:00 | 131 | 10:00
Hasnabad | 137 | 18:00 | 125 | 13:00 | Shariatpur | 134 | 18:30 | 124 | 13:00
Hathazari | 136 | 00:00 | 132 | 10:00 | Sherpur | 126 | 12:00 | 110 | 02:00
Hatirjheel | 137 | 18:00 | 126 | 13:00 | Shikalbaha | 124 | 00:00 | 120 | 14:00
Ishurdi | 137 | 18:00 | 130 | 05:00 | Shikalbaha-230 | 136 | 00:00 | 131 | 17:00
Jaldhaka | 131 | 00:00 | 122 | 23:00 | Shitalakhya | 136 | 18:00 | 124 | 11:00
Jamalpur | 129 | 13:00 | 115 | 02:00 | Sholosohor | 135 | 00:00 | 131 | 09:00
Jashore | 131 | 15:00 | 120 | 13:00 | Shomvuganj | 127 | 17:00 | 118 | 07:00
Jhenaidah | 135 | 15:00 | 124 | 19:30 | Shyampur | 137 | 18:00 | 127 | 11:00
Jhenaidah-230 | 135 | 15:00 | 125 | 19:30 | Shyampur-230 | 139 | 18:00 | 129 | 11:00
Joydebpur | 127 | 18:00 | 114 | 13:00 | Siddhirganj | 134 | 18:00 | 126 | 11:00
Joypurhat | 135 | 18:00 | 123 | 22:00 | Sirajganj | 134 | 18:00 | 126 | 13:00
Juldah | 136 | 00:00 | 131 | 10:00 | Sonargaon | 132 | 18:00 | 124 | 11:00
Kabirpur | 139 | 19:00 | 116 | 12:00 | Sreemongol | 132 | 18:00 | 126 | 06:00
Kachua | 132 | 00:00 | 126 | 08:00 | Sreepur | 134 | 17:00 | 126 | 09:00
Kaliakoir | 136 | 18:30 | 126 | 12:00 | Srinagar | 140 | 18:30 | 130 | 11:00
Kaliganj | 135 | 18:00 | 124 | 19:00 | SSM | 138 | 00:00 | 137 | 09:00
Kallyanpur | 132 | 17:00 | 121 | 13:00 | Sunamganj | 127 | 15:00 | 118 | 23:00
Kalurghat | 135 | 00:00 | 132 | 08:00 | Sylhet | 128 | 16:00 | 125 | 09:00
Kamrangirchar | 140 | 18:00 | 119 | 12:00 | Sylhet_(South) | 128 | 14:00 | 125 | 10:00
Kaptai | N/A | N/A | N/A | N/A | Tangail | 127 | 15:00 | 119 | 04:00
Kasba | 130 | 18:30 | 123 | 08:00 | Taraganj | 133 | 18:30 | 125 | 08:00
Kazla | 132 | 06:00 | 122 | 13:00 | Tasnim | 132 | 18:00 | 124 | 11:00
Keranigonj | 141 | 18:00 | 129 | 13:00 | Thakurgaon | 138 | 00:00 | 126 | 17:00
Khagrachori | 132 | 01:00 | 129 | 10:00 | TK | 135 | 00:00 | 132 | 07:00
Khulna | 134 | 18:00 | 124 | 12:00 | Tongi | 138 | 23:00 | 123 | 11:00
Khulna(S) | 134 | 18:00 | 124 | 13:00 | Ullahpara | 136 | 18:30 | 128 | 06:00
Khulshi | 133 | 00:00 | 128 | 17:00 | Ullon | 137 | 18:00 | 126 | 13:00
Kishoreganj | 131 | 17:00 | 120 | 08:00 | Uttara | 138 | 05:00 | 117 | 13:00
Kodda | 137 | 19:30 | 27 | 09:00 | UttaraNew | 134 | 22:00 | 119 | 12:00
Korerhat | 134 | 00:00 | 129 | 10:00 | Zigatola | 141 | 18:00 | 130 | 12:00
KSRM | 135 | 00:00 | 130 | 08:00
Kulaura | 132 | 17:00 | 129 | 03:00
Kurigram | 129 | 18:30 | 119 | 20:00
Kushtia | 134 | 15:00 | 127 | 06:00
Laksam | 132 | 01:00 | 125 | 08:00
Lakshmipur | 127 | 00:00 | 123 | 08:00
Lalbag | 140 | 18:00 | 129 | 12:00
Lalmonirhat | 127 | 10:00 | 117 | 19:30
Madanganj | 134 | 19:00 | 127 | 14:00
Madaripur | 134 | 18:00 | 126 | 13:00
Madartek | 137 | 18:00 | 126 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 21-06-2026 | [28 empty] | Date: | 21-06-2026 | [28 empty] | Date: | 21-06-2026 | [28 empty] | Date: | 21-06-2026 | [28 empty] | Date: | 21-06-2026 | [18 empty] | Date: | 21-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [18 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 41 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 17 | 147 | 97 | 0 | 35 | 54 | 0 | 0 | 0 | 400 | 0 | 0 | 296 | 0 | 0 | 0 | 142 | 20.5 | 21 | 0 | 410 | 107 | 16 | 65 | 0 | 12 | 50 | 35 | 17 | 24 | 60 | 0 | 107 | 110 | 27 | 850 | 85 | 0 | 6 | 8 | 105 | 218 | 0 | 0 | 0 | 740 | 0 | 13 | 0 | 250 | 290 | 220 | 51 | 0 | 218 | 20 | 63 | 94 | 174 | 0 | 19 | 109 | 162 | 52.2 | 0 | 0 | 310 | 0 | 300 | 28 | 0 | 143 | 0 | 24 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 48 | 0 | 48 | 10 | 0 | 0 | 0 | 7735.7 | 381 | 0 | 0 | 15 | 0 | 38 | 0 | 0 | 75 | 0 | 67 | 0 | 510 | 0 | 0 | 0 | 1481.18 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 20 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 197 | 0 | 342 | 0 | 0 | 0 | 39 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 65 | 220 | 0 | 1000 | 1212 | 17 | 6544.38 | 14280.08 | 78.48
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 19 | 146 | 97 | 0 | 35 | 17 | 0 | 0 | 0 | 400 | 0 | 0 | 292 | 0 | 0 | 0 | 142 | 22 | 21 | 0 | 465 | 107 | 16 | 36 | 0 | 11 | 50 | 35 | 17 | 24 | 60 | 0 | 108 | 0 | 27 | 850 | 85 | 0 | 6 | 8 | 105 | 219 | 0 | 0 | 0 | 740 | 0 | 13 | 0 | 230 | 290 | 220 | 51 | 0 | 215 | 20 | 51 | 94 | 176 | 0 | 19 | 109 | 154 | 52.2 | 0 | 22 | 310 | 0 | 300 | 28 | 0 | 145 | 0 | 25 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 49 | 0 | 48 | 11 | 0 | 0 | 0 | 7483.2 | 381 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 200 | 0 | 67 | 0 | 510 | 0 | 0 | 0 | 1478.72 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 20 | 52.2 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 195 | 0 | 197 | 0 | 370 | 0 | 0 | 0 | 42 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 65 | 220 | 0 | 1000 | 1210 | 17 | 6674.92 | 14158.12 | 78.44
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 17 | 147 | 97 | 0 | 35 | 0 | 0 | 0 | 0 | 428 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 22 | 21 | 0 | 475 | 106 | 16 | 31 | 0 | 9 | 0 | 35 | 17 | 24 | 60 | 0 | 108 | 0 | 27 | 860 | 83 | 0 | 6 | 8 | 105 | 218 | 0 | 0 | 0 | 745 | 0 | 13 | 0 | 230 | 290 | 220 | 51 | 0 | 216 | 20 | 0 | 94 | 175 | 0 | 19 | 72 | 166 | 52.2 | 0 | 22 | 310 | 0 | 300 | 28 | 0 | 136 | 0 | 25 | 0 | 52 | 30 | 141 | 0 | 101 | 0 | 49 | 0 | 48 | 12 | 0 | 0 | 0 | 7367.2 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 510 | 0 | 0 | 0 | 1483.88 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 20 | 52.2 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 195 | 0 | 197 | 0 | 392 | 0 | 0 | 0 | 42 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 65 | 220 | 0 | 1000 | 1210 | 17 | 6597.08 | 13964.28 | 78.44
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 17 | 147 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 493 | 0 | 0 | 300 | 0 | 0 | 0 | 123 | 22 | 21 | 0 | 500 | 107 | 16 | 30 | 0 | 11 | 0 | 35 | 17 | 24 | 60 | 0 | 109 | 0 | 28 | 950 | 68 | 0 | 6 | 0 | 105 | 218 | 0 | 0 | 0 | 743 | 0 | 13 | 0 | 230 | 290 | 220 | 51 | 0 | 216 | 20 | 0 | 94 | 175 | 0 | 19 | 17 | 162 | 52.2 | 0 | 22 | 310 | 0 | 300 | 28 | 0 | 145 | 0 | 25 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 49 | 0 | 48 | 12 | 0 | 0 | 0 | 7435.2 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 510 | 0 | 0 | 0 | 1485.56 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 20 | 25 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 196 | 0 | 197 | 0 | 393 | 0 | 0 | 0 | 42 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 65 | 220 | 0 | 1000 | 1210 | 17 | 6573.56 | 14008.76 | 78.44
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 17 | 147 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 0 | 0 | 300 | 0 | 0 | 0 | 123 | 22 | 21 | 0 | 390 | 107 | 16 | 31 | 0 | 9 | 0 | 35 | 17 | 24 | 60 | 0 | 109 | 0 | 29 | 1135 | 68 | 0 | 6 | 0 | 105 | 221 | 0 | 0 | 0 | 742 | 0 | 13 | 0 | 230 | 290 | 220 | 51 | 0 | 218 | 20 | 0 | 94 | 175 | 0 | 19 | 17 | 158 | 52.2 | 0 | 22 | 305 | 0 | 300 | 28 | 0 | 137 | 0 | 25 | 0 | 52 | 30 | 143 | 0 | 101 | 0 | 48 | 0 | 48 | 12 | 0 | 0 | 0 | 7424.2 | 477 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 85 | 0 | 510 | 0 | 0 | 0 | 1481.77 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 20 | 25 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 195 | 0 | 197 | 0 | 326 | 0 | 0 | 0 | 44 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 65 | 220 | 0 | 1000 | 1210 | 17 | 6522.77 | 13946.97 | 78.44
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 17 | 147 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 0 | 0 | 296 | 0 | 0 | 0 | 123 | 22 | 21 | 0 | 385 | 107 | 16 | 32 | 0 | 22 | 0 | 35 | 17 | 24 | 60 | 0 | 109 | 0 | 30 | 1135 | 71 | 0 | 6 | 0 | 105 | 221 | 0 | 0 | 0 | 743 | 0 | 13 | 0 | 230 | 290 | 220 | 51 | 0 | 197 | 20 | 0 | 94 | 175 | 0 | 19 | 17 | 146 | 52.2 | 0 | 22 | 305 | 0 | 300 | 28 | 0 | 133 | 0 | 22 | 0 | 52 | 30 | 143 | 0 | 101 | 0 | 48 | 0 | 48 | 12 | 0 | 0 | 0 | 7387.2 | 475 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 85 | 0 | 510 | 0 | 0 | 0 | 1484.01 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 20 | 8 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 195 | 0 | 197 | 0 | 343 | 0 | 0 | 0 | 44 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 65 | 220 | 0 | 1000 | 1210 | 17 | 6523.01 | 13910.21 | 78.43
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 17 | 147 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 295 | 0 | 0 | 1 | 123 | 0 | 21 | 0 | 385 | 106 | 16 | 31 | 0 | 12 | 0 | 35 | 0 | 24 | 24 | 0.15 | 106 | 0 | 32 | 1135 | 55 | 0 | 6 | 0 | 101 | 221 | 0 | 0 | 0 | 745 | 0 | 11 | 0 | 230 | 290 | 220 | 51 | 0 | 195 | 20 | 0 | 94 | 174 | 0 | 19 | 17 | 138 | 52.2 | 1 | 22 | 310 | 0 | 302 | 28 | 0 | 124 | 0 | 22 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 48 | 0.4 | 48 | 12 | 0.1 | 1.81 | 0 | 7206.66 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 85 | 3 | 510 | 0 | 0 | 0 | 1488.25 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 2.73 | 4 | 15 | 0 | 1.27 | 0 | 0 | 195 | 0 | 197 | 0 | 331 | 0 | 0.2 | 0 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.02 | 110 | 307 | 65 | 220 | 0 | 1000 | 1210 | 17 | 6421.47 | 13628.13 | 78.43
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 17 | 148 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 442 | 0 | 0 | 303 | 0 | 0 | 5 | 138 | 21 | 21 | 0 | 500 | 107 | 16 | 31 | 0 | 19 | 0 | 35 | 0 | 24 | 24 | 0.9 | 104 | 0 | 30 | 1135 | 31 | 0 | 6 | 0 | 88 | 220 | 0 | 0 | 0 | 740 | 1 | 13 | 0 | 230 | 290 | 220 | 51 | 0 | 202 | 20 | 0 | 94 | 177 | 0 | 19 | 17 | 142 | 52.2 | 2 | 22 | 305 | 0 | 302 | 28 | 0 | 146 | 2 | 22 | 0 | 52 | 30 | 144 | 0 | 101 | 0 | 48 | 3.25 | 48 | 12 | 0.3 | 5.65 | 0 | 7395.3 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 85 | 12 | 510 | 0 | 0 | 0 | 1486.63 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 8.34 | 19 | 15 | 0 | 9.28 | 0 | 0 | 195 | 0 | 197 | 0 | 403 | 0 | 0.88 | 0 | 42 | 35 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0 | 0.05 | 72 | 307 | 65 | 220 | 0 | 1000 | 1200 | 17 | 6481.78 | 13877.08 | 78.43
08:00 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 17 | 129 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 0 | 0 | 303 | 0 | 0 | 6 | 142 | 19.5 | 21 | 0 | 525 | 107 | 16 | 24 | 0 | 60 | 0 | 35 | 0 | 24 | 24 | 1.42 | 106 | 0 | 10 | 1135 | 31 | 0 | 6 | 0 | 89 | 218 | 0 | 0 | 0 | 740 | 1 | 13 | 0 | 230 | 290 | 220 | 51 | 0 | 203 | 20 | 0 | 94 | 74 | 0 | 13 | 17 | 142 | 52.2 | 15 | 22 | 310 | 0 | 301 | 28 | 0 | 152 | 4 | 22 | 0 | 52 | 30 | 144 | 0 | 101 | 0 | 48 | 4.25 | 47 | 5 | 0.3 | 11.17 | 0 | 7411.84 | 477 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 85 | 44 | 510 | 0 | 0 | 0 | 1485.5 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 15.93 | 31 | 16 | 0 | 12.8 | 0 | 0 | 194 | 0 | 201 | 0 | 403 | 0 | 1.22 | 0 | 42 | 35 | 1 | 0 | 0 | 0 | 0 | 0.2 | 11 | 0.02 | 60 | 307 | 65 | 220 | 0 | 1000 | 1185 | 17 | 6525.67 | 13937.51 | 78.4
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 17 | 129 | 32 | 0 | 0 | 17 | 0 | 0 | 0 | 555 | 0 | 0 | 318 | 0 | 0 | 21 | 142 | 18.5 | 21 | 0 | 530 | 106 | 16 | 24 | 0 | 23 | 0 | 37 | 0 | 24 | 24 | 1.75 | 105 | 0 | 4 | 1135 | 45 | 0 | 6 | 0 | 86 | 215 | 0 | 0 | 0 | 740 | 1 | 13 | 0 | 260 | 290 | 220 | 51 | 0 | 211 | 20 | 0 | 92 | 52 | 0 | 13 | 17 | 146 | 52.2 | 19 | 22 | 305 | 0 | 301 | 28 | 0 | 152 | 7 | 22 | 0 | 52 | 30 | 144 | 0 | 101 | 0 | 49 | 7.42 | 47 | 5 | 0.3 | 23.65 | 0 | 7526.82 | 477 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 85 | 48 | 510 | 0 | 0 | 0 | 1477.74 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 19.56 | 58 | 16 | 0 | 16.29 | 0 | 0 | 193 | 0 | 200 | 0 | 405 | 0 | 1.26 | 0 | 40 | 35 | 0 | 0 | 0 | 0 | 0 | 0.5 | 11 | 0.02 | 61 | 307 | 65 | 220 | 0 | 1000 | 1170 | 17 | 6539.37 | 14066.19 | 78.42
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 0 | 17 | 130 | 32 | 0 | 0 | 17 | 0 | 0 | 0 | 555 | 0 | 0 | 298 | 0 | 0 | 18 | 123 | 18.5 | 21 | 0 | 480 | 107 | 16 | 24 | 0 | 24 | 0 | 30 | 0 | 24 | 24 | 1.55 | 106 | 0 | 2 | 1135 | 100 | 0 | 6 | 0 | 88 | 218 | 0 | 0 | 0 | 740 | 1 | 13 | 0 | 280 | 290 | 220 | 51 | 0 | 200 | 20 | 0 | 92 | 52 | 1 | 13 | 17 | 148 | 52.2 | 26 | 22 | 310 | 0 | 296 | 28 | 0 | 151 | 4 | 22 | 0 | 51 | 30 | 144 | 0 | 101 | 0 | 49 | 11.21 | 47 | 5 | 1.7 | 14.49 | 0 | 7516.65 | 477 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 72 | 510 | 0 | 0 | 0 | 1487.66 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 26.17 | 61 | 16 | 0 | 17.13 | 0 | 0 | 193 | 0 | 194 | 0 | 390 | 0 | 1.37 | 0 | 43 | 35 | 8 | 0 | 0 | 0 | 0 | 1.8 | 8 | 0.03 | 60 | 307 | 65 | 220 | 0 | 1000 | 1170 | 17 | 6536.16 | 14052.81 | 78.4
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 0 | 17 | 128 | 37 | 4 | 17 | 17 | 0 | 0 | 0 | 550 | 0 | 0 | 298 | 0 | 0 | 22 | 123 | 18.5 | 21 | 0 | 500 | 104 | 16 | 22 | 0 | 16 | 0 | 30 | 0 | 24 | 24 | 1.42 | 107 | 0 | 2 | 1135 | 81 | 0 | 6 | 0 | 88 | 218 | 0 | 0 | 0 | 740 | 1 | 35 | 0 | 250 | 290 | 220 | 51 | 0 | 204 | 20 | 0 | 92 | 52 | 18 | 13 | 17 | 146 | 52.2 | 37 | 22 | 310 | 0 | 296 | 28 | 0 | 147 | 4 | 22 | 0 | 51 | 30 | 144 | 0 | 101 | 0 | 49 | 12.6 | 47 | 5 | 0.9 | 18.49 | 0 | 7546.11 | 477 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 63 | 510 | 0 | 0 | 0 | 1488.46 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 28.49 | 73 | 0 | 0 | 12.16 | 0 | 0 | 195 | 0 | 191 | 0 | 400 | 0 | 1.22 | 0 | 43 | 35 | 9 | 3 | 0 | 0 | 0 | 3.2 | 17 | 0.31 | 60 | 307 | 65 | 220 | 0 | 1000 | 1170 | 17 | 6494.84 | 14040.95 | 78.4
12:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 0 | 0 | 39 | 126 | 38 | 15 | 17 | 17 | 0 | 0 | 0 | 545 | 0 | 0 | 320 | 0 | 0 | 20 | 123 | 18.5 | 21 | 0 | 480 | 107 | 16 | 22 | 0 | 18 | 0 | 30 | 0 | 24 | 24 | 2.94 | 107 | 0 | 2 | 1135 | 88 | 0 | 6 | 5 | 88 | 215 | 0 | 0 | 0 | 675 | 14 | 53 | 0 | 220 | 290 | 220 | 51 | 0 | 208 | 20 | 4 | 92 | 51 | 17 | 13 | 17 | 158 | 43 | 46 | 24 | 305 | 0 | 290 | 28 | 0 | 148 | 2 | 22 | 0 | 51 | 30 | 143 | 0 | 101 | 0 | 58 | 5.4 | 70 | 5 | 1.5 | 11.58 | 0 | 7444.92 | 477 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83 | 510 | 0 | 0 | 0 | 1458.04 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 38.57 | 70 | 0 | 0 | 30.82 | 0 | 0 | 192 | 0 | 191 | 0 | 392 | 0 | 2.71 | 0 | 41 | 35 | 16 | 3 | 0 | 0 | 0 | 4.6 | 12 | 0.77 | 73 | 307 | 64 | 220 | 0 | 1000 | 1170 | 17 | 6506.51 | 13951.43 | 78.41
13:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 17 | 0 | 64 | 125 | 48 | 15 | 35 | 17 | 0 | 0 | 0 | 550 | 0 | 0 | 320 | 0 | 0 | 29 | 134 | 18.5 | 21 | 0 | 550 | 107 | 16 | 24 | 0 | 15 | 0 | 32 | 0 | 24 | 24 | 1.99 | 130 | 0 | 6 | 1135 | 105 | 0 | 6 | 25.5 | 88 | 215 | 0 | 0 | 0 | 670 | 14 | 55 | 0 | 220 | 290 | 220 | 51 | 0 | 208 | 20 | 31 | 91 | 57 | 17 | 19 | 17 | 158 | 43 | 67 | 30 | 305 | 0 | 284 | 28 | 0 | 148 | 7 | 21 | 0 | 52 | 30 | 143 | 0 | 102 | 0 | 58 | 5.6 | 75 | 5 | 1.4 | 6.87 | 0 | 7731.86 | 477 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13 | 510 | 0 | 0 | 0 | 1484.01 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 40.82 | 10 | 0 | 0 | 37.22 | 0 | 0 | 192 | 0 | 191 | 0 | 397 | 0 | 3.37 | 0 | 40 | 35 | 18 | 0 | 0 | 0 | 0 | 4.2 | 18 | 0.18 | 110 | 307 | 64 | 220 | 0 | 1000 | 1180 | 17 | 6470.8 | 14202.66 | 78.41
14:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 17 | 0 | 66 | 127 | 48 | 15 | 35 | 17 | 0 | 0 | 0 | 530 | 0 | 0 | 300 | 0 | 0 | 5 | 123 | 18.5 | 21 | 0 | 500 | 106 | 16 | 28 | 0 | 11 | 0 | 45 | 0 | 24 | 24 | 2.64 | 130 | 0 | 10 | 1135 | 100 | 0 | 6 | 25.5 | 88 | 215 | 0 | 0 | 0 | 670 | 10 | 53 | 0 | 220 | 290 | 220 | 51 | 0 | 208 | 20 | 34 | 91 | 58 | 0 | 19 | 17 | 166 | 43 | 58 | 30 | 310 | 0 | 284 | 28 | 0 | 146 | 2 | 0 | 0 | 51 | 30 | 144 | 0 | 101 | 0 | 57 | 2.25 | 66 | 5 | 0.6 | 0 | 0 | 7586.49 | 477 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13 | 510 | 0 | 0 | 0 | 1484.36 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 31.73 | 2 | 0 | 0 | 29.68 | 0 | 0 | 192 | 0 | 191 | 0 | 370 | 0 | 2.27 | 0 | 40 | 35 | 12 | 0 | 0 | 0 | 0 | 4.4 | 42 | 0.41 | 110 | 307 | 64 | 220 | 0 | 1000 | 1190 | 17 | 6448.85 | 14035.34 | 78.4
15:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 17 | 0 | 69 | 128 | 48 | 15 | 35 | 17 | 0 | 0 | 0 | 500 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 19 | 21 | 0 | 400 | 107 | 16 | 31 | 0 | 27 | 0 | 31 | 0 | 24 | 24 | 3.94 | 130 | 0 | 0 | 1135 | 103 | 0 | 6 | 25.5 | 88 | 214 | 0 | 0 | 0 | 673 | 6 | 53 | 0 | 220 | 290 | 220 | 51 | 0 | 208 | 20 | 34 | 91 | 50 | 0 | 19 | 17 | 174 | 43 | 22 | 22 | 305 | 0 | 284 | 28 | 0 | 146 | 1 | 8 | 0 | 51 | 30 | 143 | 0 | 101 | 0 | 57 | 0.5 | 67 | 5 | 0.5 | 0 | 0 | 7175.44 | 477 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 510 | 0 | 0 | 0 | 1493.3 | 0 | 44 | 0 | 0 | 3 | 0 | 0 | 26 | 0 | 0.07 | 1 | 0 | 0 | 24.39 | 0 | 0 | 192 | 0 | 190 | 0 | 358 | 0 | 2.23 | 0 | 40 | 35 | 11 | 0 | 0 | 0 | 0 | 3.2 | 63 | 0.37 | 110 | 307 | 64 | 220 | 0 | 1000 | 1180 | 17 | 6421.56 | 13597 | 78.4
16:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 17 | 0 | 69 | 110 | 48 | 26 | 35 | 17 | 0 | 0 | 0 | 415 | 0 | 0 | 322 | 0 | 0 | 0 | 2 | 19 | 21 | 0 | 430 | 107 | 16 | 31 | 0 | 54 | 0 | 31 | 0 | 24 | 24 | 2.29 | 130 | 0 | 0 | 1135 | 102 | 0 | 6 | 25.5 | 87 | 216 | 0 | 0 | 0 | 678 | 5 | 53 | 0 | 220 | 290 | 220 | 51 | 0 | 213 | 20 | 34 | 91 | 50 | 0 | 19 | 17 | 172 | 52.2 | 20 | 22 | 300 | 0 | 293 | 28 | 0 | 138 | 0 | 17 | 0 | 51 | 30 | 140 | 0 | 101 | 0 | 57 | 0.4 | 67 | 5 | 0.4 | 0.1 | 0 | 7044.89 | 477 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 510 | 0 | 0 | 0 | 1479.89 | 0 | 45 | 0 | 0 | 35 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 1.91 | 0 | 0 | 192 | 0 | 184 | 0 | 376 | 0 | 0.16 | 0 | 40 | 35 | 9 | 0 | 0 | 0 | 0 | 2.2 | 22 | 0.12 | 102 | 276 | 64 | 220 | 0 | 1000 | 1170 | 17 | 6321.28 | 13366.17 | 78.4
17:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0 | 69 | 30 | 48 | 29 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 35 | 292 | 0 | 0 | 0 | 80 | 0 | 21 | 0 | 380 | 107 | 16 | 31 | 0 | 19 | 0 | 60 | 0 | 50 | 24 | 0.66 | 130 | 0 | 0 | 1135 | 105 | 0 | 6 | 25.5 | 71 | 216 | 0 | 0 | 0 | 675 | 1 | 55 | 0 | 220 | 290 | 220 | 51 | 0 | 213 | 20 | 34 | 91 | 97 | 24 | 19 | 17 | 154 | 8 | 10 | 27 | 295 | 0 | 315 | 28 | 0 | 127 | 0 | 8 | 0 | 51 | 30 | 143 | 0 | 101 | 0 | 58 | 0.13 | 67 | 5 | 0 | 0.05 | 0 | 6894.34 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.5 | 500 | 0 | 0 | 0 | 1434.57 | 0 | 42 | 0 | 0 | 35 | 10 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 150 | 0 | 333 | 0 | 0 | 0 | 40 | 35 | 3 | 30 | 0 | 0 | 0 | 1.7 | 6 | 0 | 101 | 249 | 64 | 180 | 0 | 852 | 1155 | 17 | 5949.77 | 12844.11 | 78.39
18:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 78 | 30 | 48 | 24 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 35 | 288 | 0 | 0 | 0 | 86 | 0 | 21 | 0 | 380 | 60 | 16 | 36 | 0 | 10 | 0 | 54 | 17 | 12 | 25 | 0.11 | 126 | 0 | 0 | 1000 | 92 | 0 | 10 | 8 | 74 | 217 | 0 | 0 | 0 | 674 | 1 | 50 | 0 | 220 | 290 | 220 | 51 | 0 | 170 | 20 | 33 | 92 | 125 | 27 | 19 | 16 | 156 | 8 | 1 | 22 | 300 | 0 | 315 | 28 | 0 | 127 | 0 | 8 | 0 | 53 | 30 | 143 | 0 | 101 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 0 | 6990.11 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 1 | 442 | 0 | 0 | 0 | 1306.73 | 0 | 47 | 0 | 35 | 35 | 10 | 60 | 20 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 150 | 0 | 150 | 0 | 325 | 0 | 0 | 0 | 40 | 95 | 1 | 33 | 0 | 0 | 0 | 0.6 | 4 | 0 | 80 | 192 | 64 | 180 | 0 | 752 | 1100 | 17 | 5681.33 | 12671.44 | 78.36
19:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 10 | 0 | 130 | 96 | 50 | 35 | 17 | 45 | 0 | 0 | 0 | 320 | 0 | 35 | 333 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 480 | 60 | 16 | 39 | 0 | 14 | 50 | 54 | 48 | 36 | 46 | 0 | 122 | 0 | 0 | 1135 | 30 | 0 | 19 | 8 | 87 | 216 | 0 | 0 | 0 | 674 | 0 | 55 | 0 | 220 | 290 | 220 | 51 | 0 | 220 | 20 | 43 | 97 | 111 | 26 | 8 | 17 | 174 | 8 | 0 | 22 | 300 | 0 | 315 | 28 | 0 | 132 | 0 | 8 | 0 | 53 | 30 | 141 | 0 | 101 | 0 | 68 | 0 | 86 | 0 | 0 | 0 | 0 | 7550 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 415 | 0 | 0 | 0 | 1366.41 | 0 | 0 | 0 | 35 | 35 | 10 | 91 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 180 | 0 | 160 | 0 | 365 | 0 | 0 | 0 | 40 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 64 | 220 | 0 | 1000 | 1120 | 17 | 6063.41 | 28 | 78.36
19:30 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 35 | 0 | 132 | 96 | 150 | 48 | 35 | 108 | 0 | 0 | 0 | 400 | 0 | 35 | 332 | 0 | 0 | 0 | 2 | 20 | 21 | 0 | 460 | 60 | 16 | 39 | 0 | 14 | 50 | 24 | 54.36 | 36 | 50 | 0 | 120 | 0 | 3 | 1135 | 34 | 0 | 19 | 8 | 87 | 218 | 0 | 0 | 0 | 674 | 0 | 80 | 0 | 220 | 290 | 220 | 51 | 0 | 222 | 20 | 89 | 97 | 112 | 27 | 8 | 17 | 166 | 8 | 0 | 22 | 300 | 0 | 315 | 28 | 0 | 142 | 0 | 17 | 0 | 52 | 30 | 141 | 0 | 101 | 0 | 68 | 0 | 86 | 0 | 0 | 0 | 0 | 7882.36 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 464 | 0 | 0 | 0 | 1464.64 | 0 | 0 | 0 | 35 | 35 | 10 | 91 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 180 | 0 | 190 | 0 | 371 | 0 | 0 | 0 | 40 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 279 | 64 | 180 | 0 | 1000 | 1180 | 17 | 6287.64 | 13613.41 | 78.34
20:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 35 | 0 | 132 | 96 | 195 | 45 | 35 | 72 | 0 | 0 | 0 | 425 | 0 | 17 | 335 | 0 | 0 | 0 | 36 | 20 | 21 | 0 | 470 | 60 | 0 | 39 | 0 | 3 | 50 | 0 | 17 | 36 | 50 | 0 | 113 | 0 | 10 | 1135 | 0 | 0 | 19 | 0 | 87 | 218 | 0 | 0 | 0 | 674 | 0 | 45 | 0 | 220 | 290 | 220 | 51 | 0 | 222 | 20 | 85 | 97 | 65 | 27 | 19 | 17 | 124 | 8 | 0 | 22 | 295 | 0 | 315 | 28 | 0 | 142 | 0 | 17 | 0 | 81 | 30 | 140 | 0 | 101 | 0 | 68 | 0 | 86 | 0 | 0 | 0 | 0 | 7736 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 580 | 0 | 0 | 0 | 1488.96 | 0 | 0 | 0 | 35 | 35 | 10 | 42 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 178 | 0 | 190 | 0 | 383 | 0 | 0 | 0 | 40 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 275 | 64 | 220 | 0 | 1000 | 1182 | 17 | 6434.96 | 14170 | 78.32
21:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 35 | 0 | 132 | 83 | 180 | 30 | 17 | 102 | 0 | 0 | 0 | 550 | 0 | 35 | 335 | 0 | 0 | 0 | 86 | 19 | 21 | 0 | 535 | 81 | 0 | 38 | 0 | 3 | 50 | 0 | 21 | 50 | 50 | 0 | 89 | 0 | 5 | 1135 | 0 | 0 | 19 | 0 | 98 | 218 | 0 | 0 | 0 | 676 | 0 | 52 | 0 | 220 | 290 | 240 | 51 | 0 | 222 | 20 | 89 | 96 | 27 | 27 | 19 | 75 | 122 | 8 | 0 | 0 | 300 | 0 | 315 | 28 | 0 | 153 | 0 | 17 | 0 | 81 | 30 | 142 | 0 | 101 | 0 | 68 | 0 | 86 | 0 | 0 | 0 | 0 | 8007 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 0 | 0 | 0 | 1479.64 | 0 | 0 | 0 | 35 | 35 | 0 | 42 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 178 | 0 | 197 | 0 | 408 | 0 | 0 | 0 | 40 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 307 | 64 | 220 | 0 | 1000 | 1190 | 0 | 6642.64 | 14170.96 | 78.32
22:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 35 | 0 | 132 | 95 | 278 | 55 | 20 | 100 | 0 | 0 | 0 | 545 | 0 | 35 | 335 | 0 | 0 | 0 | 86 | 19 | 21 | 0 | 450 | 94 | 0 | 56 | 0 | 19 | 50 | 0 | 35 | 50 | 50 | 0 | 91 | 0 | 0 | 1135 | 0 | 0 | 19 | 0 | 88 | 219 | 0 | 0 | 0 | 675 | 0 | 100 | 0 | 220 | 290 | 240 | 51 | 0 | 216 | 20 | 72 | 96 | 65 | 27 | 19 | 107 | 148 | 8 | 0 | 0 | 295 | 0 | 308 | 28 | 0 | 141 | 0 | 17 | 0 | 52 | 30 | 142 | 0 | 100 | 17 | 68 | 0 | 88 | 0 | 0 | 0 | 0 | 8189 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 0 | 0 | 0 | 1480.73 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 197 | 0 | 368 | 0 | 0 | 0 | 40 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 307 | 64 | 220 | 0 | 1000 | 1210 | 0 | 6744.73 | 14649.64 | 78.3
23:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 35 | 0 | 132 | 45 | 278 | 55 | 35 | 102 | 0 | 0 | 0 | 545 | 0 | 35 | 335 | 0 | 0 | 0 | 86 | 19 | 21 | 0 | 490 | 92 | 0 | 55 | 0 | 20 | 50 | 0 | 35 | 50 | 50 | 0 | 93 | 0 | 2 | 1135 | 0 | 0 | 19 | 0 | 89 | 221 | 0 | 0 | 0 | 675 | 0 | 100 | 0 | 220 | 290 | 240 | 51 | 0 | 207 | 20 | 70 | 96 | 63 | 0 | 19 | 107 | 152 | 8 | 0 | 0 | 295 | 0 | 314 | 28 | 0 | 143 | 0 | 17 | 0 | 53 | 30 | 142 | 0 | 101 | 17 | 68 | 0 | 88 | 0 | 0 | 0 | 0 | 8185 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 0 | 0 | 0 | 1494.74 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 194 | 0 | 384 | 0 | 0 | 0 | 41 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 307 | 64 | 220 | 0 | 1000 | 1220 | 0 | 6849.74 | 14933.73 | 78.27
Total KWH | 0 | 916800 | 274560 | 0 | 0 | 0 | 0 | 0 | 7351200 | 0 | 0 | 258480 | 0 | 1459296 | 2715840 | 2034371 | 431010 | 425181 | 643680 | 0 | 0 | 0 | 11632273 | 0 | 262414 | 7495703 | 0 | 0 | 121949 | 2606400 | 433200 | 481680 | 0 | 11318636.36 | 2396182 | 323673 | 809280 | 0 | 469920 | 346428 | 728051 | 299790 | 676800 | 880320 | 21566 | 2669240 | 61900 | 307680 | 26123636.36 | 1485382 | 0 | 222240 | 169353 | 2187926 | 4868876 | 0 | 0 | 0 | 17001816 | 50085 | 1038763 | 0 | 5668000 | 7437200 | 5510000 | 1234344 | 0 | 5146000 | 498960 | 705600 | 2241650 | 2405760 | 226800 | 428230 | 835620 | 3621120 | 857669 | 319491 | 461872 | 7365000 | 0 | 7386000 | 671000 | 0 | 3419263.64 | 37551 | 336000 | 0 | 1318080 | 725088 | 3397000 | 0 | 2436570 | 53280 | 1333200 | 50367 | 1464000 | 124800 | 7600 | 106130 | 0 | 181830826.36 | 11392000 | 0 | 0 | 2880 | 0 | 912000 | 0 | 0 | 0 | 0 | 870336 | 370080 | 13629094 | 0 | 0 | 0 | 35264631 | 0 | 759595 | 0 | 421632 | 532032 | 29360 | 264816 | 328271 | 241474 | 188800 | 312150 | 229939 | 0 | 218848 | 0 | 0 | 4728409 | 0 | 4829527 | 0 | 9042763 | 0 | 20280 | 0 | 963491 | 1289649 | 84624 | 439641 | 0 | 0 | 0 | 25226.16 | 226080 | 2911 | 2071488 | 7091000 | 1546000 | 5364360 | 0 | 23745455 | 29054545.45 | 368400 | 156861787.61 | 338692613.97 | 78.26