## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-06-2026 | [28 empty] | Date: | 22-06-2026 | [28 empty] | Date: | 22-06-2026 | [28 empty] | Date: | 22-06-2026 | [28 empty] | Date: | 22-06-2026 | [18 empty] | Date: | 22-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 35 | 0 | 133 | 45 | 278 | 55 | 35 | 108 | 0 | 0 | 0 | 545 | 0 | 35 | 335 | 0 | 0 | 0 | 100 | 20 | 21 | 0 | 475 | 94 | 16 | 52 | 0 | 24 | 34 | 0 | 37 | 24 | 25 | 0 | 95 | 0 | 2 | 1135 | 5 | 0 | 6 | 0 | 34 | 220 | 0 | 0 | 0 | 676 | 0 | 100 | 0 | 220 | 290 | 220 | 51 | 0 | 217 | 20 | 63 | 96 | 77 | 0 | 19 | 34 | 160 | 8 | 0 | 0 | 295 | 0 | 327 | 28 | 0 | 147 | 0 | 17 | 0 | 53 | 30 | 142 | 0 | 101 | 17 | 49 | 0 | 49 | 0 | 0 | 0 | 0 | 8000 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 0 | 0 | 0 | 1491.66 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 190 | 0 | 371 | 0 | 0 | 0 | 40 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 307 | 64 | 220 | 0 | 1000 | 1220 | 17 | 6867.66 | 14867.66 | 78.21
01:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 133 | 15 | 278 | 55 | 35 | 54 | 0 | 0 | 0 | 476 | 0 | 0 | 300 | 0 | 0 | 0 | 130 | 20 | 21 | 0 | 445 | 92 | 16 | 37 | 0 | 47 | 34 | 0 | 35 | 24 | 25 | 0 | 95 | 0 | 2 | 1135 | 104 | 0 | 6 | 11 | 34 | 221 | 0 | 0 | 0 | 676 | 0 | 102 | 0 | 230 | 290 | 220 | 51 | 0 | 201 | 0 | 51 | 97 | 164 | 0 | 19 | 17 | 146 | 8 | 0 | 0 | 295 | 0 | 327 | 28 | 0 | 143 | 0 | 17 | 0 | 53 | 30 | 143 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7835 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 1420.99 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 189 | 0 | 352 | 0 | 0 | 0 | 40 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 275 | 64 | 220 | 0 | 889 | 1175 | 17 | 6534.99 | 14369.99 | 78.18
02:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 50 | 15 | 278 | 40 | 35 | 0 | 0 | 0 | 0 | 476 | 0 | 0 | 294 | 0 | 0 | 0 | 105 | 20 | 21 | 0 | 475 | 94 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 24 | 25 | 0 | 95 | 0 | 5 | 1135 | 136 | 0 | 6 | 17 | 34 | 221 | 0 | 0 | 0 | 676 | 0 | 40 | 0 | 250 | 290 | 220 | 51 | 0 | 197 | 0 | 0 | 97 | 120 | 0 | 19 | 17 | 154 | 8 | 0 | 0 | 300 | 0 | 327 | 28 | 0 | 141 | 0 | 17 | 0 | 53 | 30 | 144 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7457 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 0 | 0 | 0 | 1366.39 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 187 | 0 | 357 | 0 | 0 | 0 | 40 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 261 | 64 | 220 | 0 | 893 | 1100 | 17 | 6429.39 | 13886.39 | 78.15
03:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 19 | 15 | 180 | 30 | 0 | 0 | 0 | 0 | 0 | 477 | 0 | 0 | 298 | 0 | 0 | 0 | 68 | 20 | 21 | 0 | 485 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 25 | 0 | 99 | 0 | 23 | 1135 | 32 | 0 | 6 | 0 | 34 | 221 | 0 | 0 | 0 | 676 | 0 | 33 | 0 | 250 | 290 | 220 | 51 | 0 | 199 | 0 | 0 | 97 | 114 | 0 | 19 | 17 | 146 | 8 | 0 | 0 | 295 | 0 | 327 | 28 | 0 | 145 | 0 | 17 | 0 | 53 | 30 | 144 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7107 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1395.49 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 187 | 0 | 377 | 0 | 0 | 0 | 41 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 200 | 64 | 220 | 0 | 948 | 1070 | 17 | 6513.49 | 13620.49 | 78.12
04:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 17 | 15 | 48 | 45 | 0 | 0 | 0 | 0 | 0 | 475 | 0 | 0 | 300 | 0 | 0 | 0 | 68 | 20 | 21 | 0 | 490 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 25 | 0 | 99 | 0 | 23 | 1135 | 0 | 0 | 6 | 0 | 34 | 220 | 0 | 0 | 0 | 676 | 0 | 30 | 0 | 250 | 290 | 250 | 51 | 0 | 200 | 0 | 0 | 97 | 0 | 0 | 19 | 0 | 150 | 0 | 0 | 0 | 295 | 0 | 327 | 28 | 0 | 142 | 0 | 17 | 0 | 53 | 30 | 144 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6740 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 0 | 0 | 1402.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 187 | 0 | 369 | 0 | 0 | 0 | 40 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 64 | 220 | 0 | 958 | 1070 | 0 | 6374.79 | 13114.79 | 78
05:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475 | 0 | 0 | 298 | 0 | 0 | 0 | 51 | 20 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 21 | 1135 | 0 | 0 | 0 | 0 | 34 | 220 | 0 | 0 | 0 | 676 | 0 | 0 | 0 | 250 | 290 | 250 | 51 | 0 | 197 | 0 | 0 | 96 | 0 | 0 | 19 | 0 | 134 | 0 | 0 | 0 | 290 | 0 | 327 | 28 | 0 | 143 | 0 | 17 | 0 | 53 | 30 | 141 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6497 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 0 | 0 | 1400.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 187 | 0 | 355 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 64 | 220 | 0 | 940 | 1084 | 0 | 6284.57 | 12781.57 | 78
06:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 298 | 0 | 0 | 1 | 51 | 20 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0.17 | 95 | 0 | 23 | 1135 | 0 | 0 | 0 | 0 | 105 | 220 | 0 | 0 | 0 | 676 | 0 | 0 | 0 | 250 | 290 | 250 | 51 | 0 | 198 | 0 | 0 | 96 | 0 | 0 | 19 | 0 | 124 | 0 | 0 | 0 | 290 | 0 | 327 | 28 | 0 | 130 | 1 | 17 | 0 | 53 | 30 | 143 | 0 | 101 | 0 | 49 | 0.38 | 48 | 10 | 0.1 | 0.75 | 0 | 6499.4 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.69 | 1110 | 0 | 0 | 0 | 1297.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.11 | 0 | 0 | 0 | 2.18 | 0 | 0 | 175 | 0 | 191 | 0 | 339 | 0 | 0.23 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 4 | 0.02 | 0 | 200 | 64 | 220 | 0 | 889 | 1075 | 0 | 6123.98 | 12623.38 | 78
07:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475 | 0 | 0 | 298 | 0 | 0 | 3 | 51 | 20 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0.93 | 93 | 0 | 23 | 1135 | 0 | 0 | 0 | 0 | 105 | 219 | 0 | 0 | 0 | 676 | 1 | 0 | 0 | 250 | 290 | 250 | 51 | 0 | 200 | 0 | 0 | 96 | 0 | 0 | 19 | 0 | 126 | 0 | 7 | 0 | 290 | 0 | 327 | 28 | 0 | 143 | 2 | 17 | 0 | 53 | 30 | 143 | 0 | 101 | 0 | 49 | 2.2 | 48 | 10 | 0.4 | 4.94 | 0 | 6618.47 | 477 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.69 | 1110 | 0 | 0 | 0 | 1274.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.98 | 8 | 0 | 0 | 7.11 | 0 | 0 | 184 | 0 | 194 | 0 | 381 | 0 | 0.86 | 0 | 40 | 0 | 1 | 0 | 0 | 0 | 0 | 0.1 | 30 | 0.02 | 0 | 200 | 64 | 220 | 0 | 865 | 1050 | 0 | 6155.95 | 12774.42 | 78
08:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 475 | 0 | 0 | 300 | 0 | 0 | 8 | 68 | 20 | 21 | 0 | 480 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 1.36 | 91 | 0 | 3 | 1135 | 0 | 0 | 0 | 0 | 105 | 219 | 0 | 0 | 0 | 675 | 1 | 0 | 0 | 250 | 290 | 250 | 51 | 0 | 221 | 0 | 0 | 94 | 0 | 0 | 19 | 0 | 144 | 0 | 10 | 0 | 295 | 0 | 327 | 28 | 0 | 143 | 5 | 17 | 0 | 52 | 30 | 143 | 0 | 101 | 0 | 49 | 9 | 48 | 5 | 0.4 | 10.59 | 0 | 6666.35 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18.22 | 1120 | 0 | 0 | 0 | 1247.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.54 | 30 | 0 | 0 | 14.36 | 0 | 0 | 195 | 0 | 197 | 0 | 387 | 0 | 0.98 | 0 | 41 | 0 | 3 | 0 | 0 | 0 | 0 | 0.1 | 17 | 0.02 | 0 | 200 | 64 | 220 | 0 | 850 | 1010 | 0 | 6140.12 | 12806.47 | 77.98
09:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 17 | 15 | 32 | 30 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 0 | 300 | 0 | 0 | 9 | 79 | 19 | 21 | 0 | 500 | 3 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 12 | 2 | 91 | 0 | 2 | 1135 | 0 | 0 | 1 | 0 | 105 | 217 | 0 | 0 | 0 | 673 | 2 | 10 | 0 | 280 | 290 | 250 | 51 | 0 | 200 | 0 | 0 | 94 | 0 | 0 | 19 | 17 | 148 | 0 | 14 | 0 | 295 | 0 | 332 | 28 | 0 | 146 | 5 | 17 | 0 | 52 | 30 | 143 | 0 | 101 | 0 | 49 | 9.1 | 48 | 5 | 0.5 | 17.42 | 0 | 6836.02 | 476 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25.75 | 1120 | 0 | 0 | 0 | 1277.71 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 26.29 | 40 | 0 | 0 | 18.28 | 0 | 0 | 195 | 0 | 197 | 0 | 386 | 0 | 1.89 | 0 | 41 | 0 | 2 | 0 | 0 | 0 | 0 | 0.6 | 39 | 0.02 | 0 | 200 | 64 | 220 | 0 | 929 | 1000 | 0 | 6298.54 | 13134.56 | 77.96
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 17 | 15 | 48 | 30 | 17 | 17 | 0 | 0 | 0 | 480 | 0 | 0 | 302 | 0 | 0 | 14 | 86 | 19 | 21 | 0 | 510 | 15 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 12 | 4.69 | 91 | 0 | 2 | 1135 | 0 | 0 | 6 | 0 | 105 | 218 | 0 | 0 | 0 | 676 | 0 | 26 | 0 | 280 | 290 | 250 | 43 | 0 | 201 | 0 | 0 | 93 | 0 | 1 | 19 | 17 | 154 | 8 | 15 | 0 | 295 | 0 | 332 | 28 | 0 | 148 | 5 | 17 | 0 | 52 | 30 | 144 | 0 | 101 | 0 | 49 | 12.3 | 48 | 5 | 0.6 | 28.82 | 0 | 6904.41 | 490 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 33 | 1120 | 0 | 0 | 0 | 1291.69 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 41.22 | 81 | 0 | 0 | 44.58 | 0 | 0 | 197 | 0 | 201 | 0 | 370 | 0 | 4.48 | 0 | 42 | 0 | 17 | 0 | 0 | 0 | 0 | 0.4 | 46 | 0.02 | 0 | 200 | 64 | 220 | 0 | 937 | 1005 | 0 | 6463.39 | 13367.8 | 77.94
11:00 | 0 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 17 | 15 | 48 | 30 | 17 | 17 | 0 | 0 | 0 | 475 | 0 | 0 | 302 | 0 | 0 | 23 | 86 | 18.5 | 21 | 0 | 525 | 43 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 24 | 1.25 | 93 | 0 | 2 | 1135 | 2 | 0 | 6 | 0 | 105 | 218 | 0 | 0 | 0 | 720 | 1 | 65 | 0 | 300 | 290 | 250 | 43 | 0 | 200 | 0 | 0 | 92 | 5 | 17 | 19 | 34 | 154 | 8 | 17 | 0 | 300 | 0 | 332 | 28 | 0 | 148 | 3 | 17 | 0 | 53 | 30 | 144 | 0 | 101 | 0 | 49 | 8.9 | 48 | 0 | 2.1 | 27.32 | 0 | 7132.07 | 502 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24 | 1120 | 0 | 0 | 0 | 1321.14 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 46.2 | 78 | 0 | 0 | 21.73 | 0 | 0 | 207 | 0 | 197 | 0 | 400 | 0 | 2.52 | 0 | 42 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 25 | 0.02 | 0 | 211 | 64 | 220 | 0 | 991 | 995 | 0 | 6544.61 | 13676.68 | 77.93
12:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 36 | 15 | 48 | 42 | 17 | 17 | 0 | 0 | 0 | 480 | 0 | 0 | 313 | 0 | 0 | 27 | 86 | 18.5 | 21 | 0 | 540 | 65 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 24 | 24 | 1.61 | 95 | 0 | 2 | 1135 | 23 | 0 | 6 | 0 | 105 | 216 | 0 | 0 | 0 | 720 | 5 | 88 | 0 | 250 | 290 | 250 | 43 | 0 | 210 | 0 | 2 | 93 | 42 | 18 | 19 | 70 | 150 | 8 | 29 | 0 | 295 | 0 | 321 | 28 | 0 | 148 | 3 | 17 | 0 | 53 | 30 | 142 | 0 | 101 | 0 | 58 | 20 | 67 | 0 | 1.8 | 38.09 | 0 | 7357 | 502 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 51 | 1060 | 0 | 0 | 0 | 1486.95 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 26.47 | 71 | 0 | 0 | 18.93 | 0 | 0 | 207 | 0 | 196 | 0 | 397 | 0 | 2.16 | 0 | 43 | 35 | 16 | 0 | 0 | 0 | 0 | 2.3 | 53 | 0.05 | 0 | 248 | 64 | 220 | 0 | 984 | 1050 | 0 | 6814.86 | 14171.86 | 77.92
13:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 51 | 15 | 130 | 48 | 35 | 17 | 0 | 0 | 0 | 505 | 0 | 0 | 297 | 0 | 0 | 19 | 114 | 14.5 | 21 | 0 | 450 | 87 | 16 | 25 | 0 | 7 | 0 | 0 | 0 | 24 | 24 | 0.93 | 95 | 0 | 2 | 1135 | 75 | 0 | 6 | 7 | 105 | 218 | 0 | 0 | 0 | 720 | 9 | 102 | 0 | 210 | 290 | 230 | 43 | 0 | 200 | 0 | 31 | 92 | 127 | 18 | 19 | 17 | 152 | 8 | 40 | 23 | 300 | 0 | 319 | 28 | 0 | 144 | 3 | 17 | 0 | 52 | 30 | 141 | 0 | 101 | 11 | 48 | 13 | 67 | 0 | 0.8 | 30.41 | 0 | 7558.64 | 503 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 1000 | 0 | 0 | 0 | 1481.69 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 6 | 16 | 22.54 | 70 | 0 | 0 | 20.32 | 0 | 0 | 206 | 0 | 196 | 0 | 356 | 0 | 1.88 | 0 | 43 | 70 | 18 | 0 | 0 | 0 | 0 | 6.6 | 72 | 0.05 | 0 | 307 | 64 | 220 | 0 | 936 | 1115 | 0 | 6857.08 | 14415.72 | 77.91
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 100 | 15 | 210 | 48 | 35 | 17 | 0 | 0 | 0 | 500 | 0 | 0 | 300 | 0 | 0 | 22 | 123 | 18.5 | 21 | 0 | 490 | 70 | 16 | 45 | 0 | 2 | 0 | 22 | 0 | 24 | 24 | 1.7 | 97 | 0 | 2 | 1135 | 54 | 0 | 6 | 25.5 | 105 | 216 | 0 | 0 | 0 | 720 | 2 | 51 | 0 | 210 | 290 | 230 | 43 | 0 | 215 | 0 | 34 | 92 | 139 | 0 | 19 | 17 | 160 | 8 | 30 | 23 | 295 | 0 | 317 | 28 | 0 | 144 | 7 | 12 | 0 | 52 | 30 | 142 | 0 | 101 | 17 | 48 | 4.8 | 67 | 0 | 0 | 34.54 | 0 | 7709.04 | 503 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44 | 1000 | 0 | 0 | 0 | 1483.69 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 6 | 16 | 45.57 | 61 | 0 | 0 | 26.22 | 0 | 0 | 205 | 0 | 196 | 0 | 379 | 0 | 2.37 | 0 | 43 | 70 | 8 | 0 | 0 | 0 | 0 | 4.7 | 74 | 0.05 | 0 | 278 | 64 | 220 | 0 | 946 | 1095 | 0 | 6878.6 | 14587.64 | 77.9
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 133 | 15 | 210 | 48 | 35 | 35 | 0 | 0 | 0 | 500 | 0 | 0 | 301 | 0 | 0 | 21 | 123 | 18.5 | 21 | 0 | 490 | 76 | 16 | 48 | 0 | 1 | 0 | 30 | 17 | 24 | 24 | 1.62 | 97 | 0 | 0 | 1135 | 64 | 0 | 6 | 25.5 | 97 | 213 | 0 | 0 | 0 | 720 | 2 | 20 | 0 | 230 | 290 | 230 | 51 | 0 | 215 | 0 | 33 | 92 | 144 | 0 | 19 | 17 | 144 | 8 | 19 | 22 | 300 | 0 | 320 | 28 | 0 | 150 | 5 | 17 | 0 | 52 | 30 | 143 | 0 | 101 | 17 | 48 | 2.11 | 67 | 0 | 0.5 | 24.22 | 0 | 7777.45 | 503 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 73 | 1000 | 0 | 0 | 0 | 1485.83 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 31.25 | 57 | 0 | 0 | 10.04 | 0 | 0 | 201 | 0 | 193 | 0 | 389 | 0 | 1.21 | 0 | 42 | 70 | 18 | 0 | 0 | 0 | 0 | 1 | 53 | 0.49 | 0 | 274 | 64 | 220 | 0 | 993 | 1110 | 0 | 6945.82 | 14723.27 | 77.89
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 133 | 15 | 210 | 48 | 35 | 35 | 0 | 0 | 0 | 500 | 0 | 5 | 298 | 0 | 0 | 14 | 123 | 18.5 | 21 | 0 | 460 | 89 | 16 | 54 | 0 | 0 | 0 | 40 | 17 | 24 | 24 | 0.45 | 99 | 0 | 0 | 1135 | 79 | 0 | 6 | 25.5 | 87 | 214 | 0 | 0 | 0 | 720 | 3 | 20 | 0 | 220 | 290 | 230 | 51 | 0 | 212 | 0 | 34 | 92 | 143 | 0 | 19 | 17 | 140 | 8 | 41 | 22 | 295 | 0 | 318 | 28 | 0 | 149 | 5 | 17 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 48 | 0.65 | 68 | 0 | 0.5 | 1.54 | 0 | 7725.14 | 513 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 1000 | 0 | 0 | 0 | 1494.87 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 16.75 | 51 | 0 | 0 | 7.92 | 0 | 0 | 193 | 0 | 190 | 0 | 366 | 0 | 0.96 | 0 | 42 | 70 | 4 | 0 | 0 | 0 | 0 | 1.5 | 60 | 0.26 | 0 | 278 | 64 | 220 | 0 | 979 | 1150 | 0 | 6854.26 | 14579.4 | 77.89
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 133 | 15 | 95 | 48 | 35 | 35 | 0 | 0 | 0 | 495 | 0 | 17 | 300 | 0 | 0 | 4 | 123 | 18.5 | 21 | 0 | 520 | 30 | 16 | 46 | 0 | 1 | 0 | 58 | 17 | 24 | 24 | 0.39 | 99 | 0 | 6 | 1135 | 33 | 0 | 6 | 25.5 | 51 | 215 | 0 | 0 | 0 | 720 | 2 | 20 | 0 | 220 | 290 | 230 | 51 | 0 | 214 | 0 | 34 | 92 | 90 | 0 | 19 | 17 | 146 | 8 | 21 | 22 | 295 | 0 | 318 | 28 | 0 | 135 | 2 | 22 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 48 | 1 | 68 | 0 | 0.4 | 0.22 | 0 | 7445.01 | 584 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 1000 | 0 | 0 | 0 | 1479.3 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 12.07 | 27 | 0 | 0 | 9.53 | 0 | 0 | 192 | 0 | 190 | 0 | 383 | 0 | 0.98 | 0 | 42 | 70 | 8 | 33 | 0 | 0 | 0 | 1.9 | 15 | 0.18 | 0 | 277 | 64 | 220 | 0 | 915 | 1100 | 0 | 6775.96 | 14220.97 | 77.88
18:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 15.5 | 0 | 133 | 15 | 95 | 40 | 35 | 35 | 0 | 0 | 0 | 500 | 0 | 17 | 308 | 0 | 0 | 2 | 123 | 18.5 | 21 | 0 | 525 | 30 | 16 | 55 | 0 | 2 | 0 | 58 | 17 | 24 | 24 | 0.32 | 97 | 0 | 9 | 1135 | 29 | 0 | 10 | 25.5 | 51 | 215 | 0 | 0 | 0 | 720 | 1 | 20 | 0 | 220 | 290 | 230 | 51 | 0 | 214 | 0 | 34 | 92 | 67 | 0 | 19 | 17 | 140 | 8 | 3 | 22 | 300 | 0 | 318 | 28 | 0 | 145 | 1 | 17 | 0 | 52 | 30 | 143 | 0 | 100 | 0 | 48 | 0.48 | 101 | 0 | 0.2 | 0.55 | 0 | 7489.05 | 656 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 830 | 0 | 0 | 0 | 1482.45 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 3.23 | 6 | 0 | 0 | 4.38 | 0 | 0 | 192 | 0 | 189 | 0 | 386 | 0 | 0.24 | 0 | 41 | 70 | 1 | 33 | 0 | 0 | 0 | 0.6 | 17 | 0.06 | 0 | 307 | 64 | 220 | 0 | 1000 | 1060 | 0 | 6689.96 | 14179.01 | 77.88
19:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 35 | 0 | 133 | 105 | 280 | 55 | 35 | 108 | 0 | 0 | 0 | 505 | 0 | 55 | 319 | 0 | 0 | 0 | 135 | 18 | 21 | 0 | 557 | 35 | 16 | 63 | 0 | 3 | 38 | 66 | 54.36 | 50 | 50 | 0 | 95 | 0 | 10 | 1135 | 37 | 0 | 19 | 25.5 | 70 | 216 | 0 | 0 | 0 | 745 | 0 | 60 | 0 | 220 | 290 | 250 | 51 | 0 | 215 | 0 | 38 | 92 | 85 | 0 | 19 | 17 | 154 | 8 | 0 | 22 | 300 | 0 | 318 | 28 | 0 | 146 | 0 | 17 | 0 | 80 | 30 | 142 | 0 | 101 | 0 | 48 | 0 | 178 | 0 | 0 | 0 | 0 | 8390.86 | 767 | 0 | 0 | 22 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 506 | 0 | 0 | 0 | 1483.21 | 0 | 0 | 0 | 35 | 35 | 12 | 101 | 25 | 52 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 193 | 0 | 193 | 0 | 402 | 0 | 0 | 0 | 43 | 92 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 64 | 220 | 0 | 1000 | 1190 | 54 | 6963.21 | 15354.07 | 77.87
19:30 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 35 | 0 | 133 | 130 | 295 | 55 | 35 | 108 | 0 | 0 | 0 | 495 | 0 | 55 | 295 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 435 | 85 | 16 | 77 | 0 | 5 | 50 | 66 | 54.36 | 50 | 50 | 0 | 95 | 0 | 2 | 1135 | 100 | 0 | 19 | 25.5 | 85 | 218 | 0 | 0 | 0 | 775 | 0 | 130 | 0 | 220 | 290 | 230 | 51 | 0 | 214 | 0 | 90 | 93 | 172 | 28 | 19 | 17 | 154 | 8 | 0 | 23 | 300 | 0 | 308 | 28 | 0 | 146 | 0 | 17 | 0 | 80 | 30 | 141 | 0 | 101 | 0 | 48 | 0 | 178 | 0 | 0 | 0 | 0 | 8637.86 | 832 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 508 | 0 | 0 | 0 | 1484.25 | 0 | 0 | 0 | 35 | 35 | 12 | 101 | 26 | 52 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 193 | 0 | 192 | 0 | 344 | 0 | 0 | 0 | 43 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 307 | 64 | 220 | 0 | 1000 | 1220 | 90 | 7085.25 | 15723.11
20:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 35 | 0 | 133 | 131 | 293 | 55 | 35 | 108 | 0 | 0 | 0 | 480 | 0 | 55 | 305 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 470 | 94 | 16 | 77 | 0 | 8 | 50 | 66 | 54.36 | 50 | 50 | 0 | 91 | 0 | 7 | 1135 | 132 | 0 | 19 | 25.5 | 87 | 217 | 0 | 0 | 0 | 800 | 0 | 128 | 0 | 220 | 290 | 230 | 51 | 0 | 213 | 0 | 79 | 93 | 176 | 22 | 19 | 17 | 140 | 8 | 0 | 22 | 295 | 0 | 308 | 28 | 0 | 138 | 0 | 17 | 0 | 81 | 30 | 143 | 0 | 101 | 0 | 48 | 0 | 196 | 0 | 0 | 0 | 0 | 8729.86 | 830 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 510 | 0 | 0 | 0 | 1473.58 | 0 | 0 | 0 | 35 | 35 | 12 | 101 | 27 | 52 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 193 | 0 | 192 | 0 | 380 | 0 | 0 | 0 | 42 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 64 | 220 | 0 | 1000 | 1220 | 90 | 7116.58 | 15846.44 | 77.87
21:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 0 | 133 | 147 | 293 | 55 | 35 | 108 | 0 | 0 | 0 | 510 | 0 | 35 | 302 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 520 | 99 | 16 | 77 | 0 | 8 | 50 | 66 | 54.36 | 50 | 50 | 0 | 91 | 0 | 14 | 1135 | 137 | 0 | 19 | 25.5 | 88 | 217 | 0 | 0 | 0 | 802 | 0 | 68 | 0 | 220 | 290 | 230 | 51 | 0 | 208 | 0 | 89 | 94 | 185 | 27 | 19 | 17 | 168 | 8 | 0 | 22 | 300 | 0 | 308 | 28 | 0 | 154 | 0 | 22 | 0 | 81 | 30 | 143 | 0 | 101 | 0 | 48 | 0 | 196 | 0 | 0 | 0 | 0 | 8856.86 | 930 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 510 | 0 | 0 | 0 | 1485.55 | 0 | 48 | 0 | 35 | 35 | 12 | 101 | 25 | 52 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 193 | 0 | 190 | 0 | 403 | 0 | 0 | 0 | 42 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 64 | 220 | 0 | 1000 | 1222 | 90 | 7297.55 | 16154.41 | 77.86
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 35 | 0 | 133 | 147 | 293 | 55 | 35 | 108 | 0 | 0 | 0 | 495 | 0 | 35 | 300 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 420 | 92 | 16 | 77 | 0 | 7 | 50 | 66 | 54.36 | 50 | 50 | 0 | 91 | 0 | 24 | 1135 | 144 | 0 | 19 | 25.5 | 87 | 217 | 0 | 0 | 0 | 802 | 0 | 20 | 0 | 220 | 290 | 230 | 51 | 0 | 208 | 0 | 87 | 94 | 176 | 27 | 19 | 17 | 162 | 8 | 0 | 22 | 300 | 0 | 308 | 28 | 0 | 136 | 0 | 22 | 0 | 81 | 30 | 143 | 0 | 101 | 0 | 48 | 0 | 112 | 0 | 0 | 0 | 0 | 8556.86 | 930 | 0 | 0 | 20 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 0 | 1486.13 | 0 | 41 | 0 | 35 | 35 | 0 | 101 | 25 | 8 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 193 | 0 | 190 | 0 | 368 | 0 | 0 | 0 | 42 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 64 | 220 | 0 | 1000 | 1222 | 72 | 7162.13 | 15718.99 | 77.86
23:00 | 0 | 35 | 42 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 0 | 133 | 16 | 113 | 55 | 35 | 108 | 0 | 0 | 0 | 510 | 0 | 35 | 320 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 550 | 99 | 16 | 63 | 0 | 2 | 50 | 66 | 18 | 50 | 50 | 0 | 91 | 0 | 26 | 1135 | 132 | 0 | 19 | 25.5 | 64 | 217 | 0 | 0 | 0 | 751 | 0 | 20 | 0 | 230 | 290 | 230 | 51 | 0 | 208 | 0 | 70 | 94 | 188 | 11 | 19 | 17 | 180 | 0 | 0 | 22 | 295 | 0 | 308 | 28 | 0 | 152 | 0 | 21 | 0 | 81 | 30 | 143 | 0 | 101 | 6 | 48 | 0 | 111 | 0 | 0 | 0 | 0 | 8367.5 | 930 | 0 | 0 | 20 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 495 | 0 | 0 | 0 | 1495.34 | 0 | 47 | 0 | 35 | 35 | 0 | 102 | 26 | 8 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 192 | 0 | 193 | 0 | 407 | 0 | 0 | 0 | 42 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 64 | 220 | 0 | 1000 | 1222 | 54 | 7187.34 | 15554.84 | 77.85
Total KWH | 0 | 1248000 | 134400 | 0 | 0 | 0 | 0 | 0 | 8456400 | 0 | 0 | 229320 | 0 | 1876896 | 832320 | 3277375 | 976746 | 533052 | 878400 | 0 | 0 | 0 | 11835989 | 0 | 270716 | 7288703 | 0 | 0 | 169364 | 2618400 | 471000 | 508320 | 0 | 11618636.36 | 1408855 | 205745 | 771840 | 0 | 189600 | 314400 | 559973 | 342303 | 525120 | 602880 | 15883 | 2274380 | 15890 | 217440 | 27229090.91 | 1455273 | 0 | 196800 | 313405.2 | 1865091 | 5159694 | 0 | 0 | 0 | 17149089 | 30510 | 948436 | 0 | 5822000 | 7458100 | 5784000 | 1191232 | 0 | 5082000 | 3456 | 708480 | 2237264 | 2272320 | 167160 | 473860 | 406980 | 3579840 | 137890 | 248191 | 250944 | 7156000 | 0 | 7810000 | 667000 | 0 | 3470073 | 43809 | 507840 | 0 | 1403520 | 709056 | 3161000 | 0 | 2422710 | 77040 | 1179600 | 82818 | 1905600 | 21120 | 7550 | 225660 | 0 | 181689848.47 | 14182545 | 0 | 0 | 106560 | 0 | 912000 | 0 | 0 | 0 | 0 | 76320 | 373680 | 21949089 | 0 | 0 | 0 | 34049371 | 0 | 190609 | 0 | 469920 | 661536 | 32283 | 556912 | 138810 | 251928 | 263872 | 571320 | 87436 | 0 | 267888 | 0 | 0 | 4775118 | 0 | 4874564 | 0 | 9201672 | 0 | 25800 | 0 | 963490 | 1182571 | 95447 | 407193 | 0 | 0 | 0 | 20907.72 | 540000 | 3529 | 934464 | 6196000 | 1535000 | 5440790 | 0 | 22916363 | 26893090.91 | 429600 | 161577678.63 | 343267527.1

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-06-2026 | during | 23-06-2026 | during | 23-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 360 | 370 | 412 | 412 | 380 | 380 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 42 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 313 | 302 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 147 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18.5 | 20 | 33 | 33 | 21 | 21 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 8 | 52.19 | 52.19 | 0 | 42 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 48 | 293 | 300 | 300 | 48 | 128 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 36 | 133 | 149 | 149 | 70 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105 | 17 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 540 | 520 | 584 | 584 | 520 | 520 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 480 | 510 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 86 | 142 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2045.5 | 2751 | 5818.22 | 5792.22 | 2361.06 | 2749.06
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 5 | 0 | 4 | 0 | 4 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 50 | 50 | 6 | 19 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 95 | 91 | 100 | 100 | 100 | 100 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 88 | 105 | 105 | 88 | 88 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 66 | 40 | 56 | 40 | 56 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 50 | 100 | 100 | 25 | 50 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 14 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 77 | 108 | 108 | 30 | 80 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.61 | 0 | 2.94 | 0 | 2.94 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 54.36 | 54.36 | 54.36 | 0 | 35 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 50 | 100 | 100 | 25 | 50 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 65 | 99 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 23 | 137 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 720 | 802 | 1224 | 1224 | 740 | 740 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 5 | 8 | 18 | 1 | 18 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1135 | 1135 | 1150 | 1150 | 1135 | 1135 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2426.61 | 2998.86 | 3990.8 | 4057.86 | 2714.44 | 2929.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 210 | 208 | 221.25 | 221.25 | 205.25 | 205.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 290 | 350.01 | 350.01 | 290 | 290 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 250 | 230 | 342.01 | 342.01 | 250 | 250 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 250 | 220 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 21 | 21 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 88 | 68 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 22 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 93 | 94 | 163 | 163 | 0 | 0 | Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 42 | 185 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 150 | 168 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 8 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 17 | 114 | 114 | 17 | 17 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 18 | 27 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 2 | 89 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 29 | 0 | 45 | 0 | 45 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1562 | 1696 | 2739.44 | 2688.44 | 1596.25 | 1691.25
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-06-2026 | during | 23-06-2026 | during | 23-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 20 | 0 | 10 | 0 | 10 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.8 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 67 | 196 | 70 | 90 | 70 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 48 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 38.09 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 184.89 | 244 | 470.7 | 446.5 | 184.2 | 177
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 28 | 28 | 28 | 28 | 28 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 148 | 154 | 163 | 163 | 163 | 163 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 142 | 143 | 145 | 145 | 145 | 145 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 53 | 81 | 81 | 81 | 52 | 52 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 101 | 102 | 102 | 102 | 102 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 22 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 321 | 308 | 350 | 350 | 320 | 320 | plant availability zero
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1138 | 1167 | 1313 | 1313 | 1192 | 1192
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 502 | 930 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 25 | 25 | 25 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 30 | 30 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 51 | 0 | 79 | 0 | 79 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1060 | 510 | 510 | 510 | 510 | 510 | Unit1 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1651 | 1518 | 2554 | 2475 | 1697 | 1618
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 984 | 1000 | 1000 | 1000 | 1000 | 1000 | Plant availability less
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 110 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 64 | 64 | 65 | 65 | 65 | 65 | GT-1 & ST under maint
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1050 | 1222 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 90 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 248 | 307 | 307 | 307 | 307 | 307 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.05 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2566.05 | 3013 | 3097 | 3096 | 2904 | 2903
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 26.47 | 0 | 54 | 0 | 54 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 12 | 32 | 32 | 10 | 10 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 207 | 193 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 190 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 397 | 403 | 413.79 | 413.79 | 372.41 | 372.41 | AGC
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 16 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 101 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 2.16 | 0 | 5.7 | 0 | 5.7 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1486.95 | 1485.55 | 1469.13 | 1469.13 | 1389 | 1389 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 18.93 | 0 | 52 | 0 | 52 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 71 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2448.51 | 2595.55 | 3039.82 | 2828.12 | 2578.31 | 2528.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 43 | 42 | 40 | 40 | 45 | 45 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.3 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 95 | 115 | 115 | 35 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 53 | 0 | 170 | 0 | 170 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 149.3 | 171 | 500 | 302 | 298 | 195
System Total |  |  |  |  | 28843.2 | 29323.517 | 14171.86 | 16154.41 | 23522.98 | 22999.14 | 15525.26 | 15983.42
Forecast Scenario (23-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15760 |  | 620.75 |  | 16410
|  |  |  | 1:00 | 15665 |  | 339.025 |  | 16020
|  |  |  | 2:00 | 14670 |  | 945.45 |  | 15660
|  |  |  | 3:00 | 14350 |  | 916.8 |  | 15310
|  |  |  | 4:00 | 14250 |  | 764 |  | 15050
|  |  |  | 5:00 | 14040 |  | 639.85 |  | 14710
|  |  |  | 6:00 | 13680 |  | 305.6 |  | 14000
|  |  |  | 7:00 | 13640 |  | 343.8 |  | 14000
|  |  |  | 8:00 | 13770 |  | 286.5 |  | 14070
|  |  |  | 9:00 | 13880 |  | 257.85 |  | 14150
|  |  |  | 10:00 | 14350 |  | 305.6 |  | 14670
|  |  |  | 11:00 | 14400 |  | 286.5 |  | 14700
|  |  |  | 12:00 | 14500 |  | 296.05 |  | 14810
|  |  |  | 13:00 | 14600 |  | 410.65 |  | 15030
|  |  |  | 14:00 | 14600 |  | 410.65 |  | 15030
|  |  |  | 15:00 | 14650 |  | 477.5 |  | 15150
|  |  |  | 16:00 | 14400 |  | 506.15 |  | 14930
|  |  |  | 17:00 | 14300 |  | 248.3 |  | 14560
|  |  |  | 18:00 | 14300 |  | 210.1 |  | 14520
|  |  |  | 18:30 | 14900 |  | 286.5 |  | 15200
|  |  |  | 19:00 | 15100 |  | 639.85 |  | 15770
|  |  |  | 19:30 | 15500 |  | 764 |  | 16300
|  |  |  | 20:00 | 15800 |  | 811.75 |  | 16650
|  |  |  | 21:00 | 16100 |  | 735.35 |  | 16870
|  |  |  | 22:00 | 15700 |  | 200.55 |  | 15910
|  |  |  | 23:00 | 15400 |  | 334.25 |  | 15750
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 14810.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16870.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 342.68999 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:11 hrs on 23-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14171.86 | MW | 12:00 Hr. | Energy Generated |  |  | 343.2675 |  | MKWHr.
| Day Peak Demand |  |  | 14610.86 | MW | 12:00 Hr. | Energy Unserverd |  |  | 7.257 |  | MKWHr.
| Evening Peak Generation |  |  | 16154.41 | MW | 21:00 Hr. | Energy Demand |  |  | 350.5245 |  | MKWHr.
| Evening Peak Demand |  |  | 16854.11 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.8 |  | °C
| Minimum Generation of the Day |  |  | 12623.38 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 907.35 |  | MMCFD
| Maximum Generation of the Day |  |  | 16154.41 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.6151 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.179 | 0 | 12.8756 | 0 | 0 | 0.16936 | 0 | 0 | 53.224 | Gas | 126.7636 | Gas | 437084201.6512
| Chattogram Zone |  |  | 5.3771 | 44.3782 | 8.5776 | 0 | 2.2744 | 0.046393 | 0 | 0.1896 | 60.8433 | Coal | 123.2962 | Coal | 816663901.8826
| Cumilla Zone |  |  | 28.0519 | 0 | 4.8922 | 0 | 0 | 0.24819 | 3.5798 | 0 | 36.7722 | HFO | 35.0338 | HFO | 632836198.362
| Mymensingh Zone |  |  | 0.02112 | 0 | 3.1622 | 0 | 0 | 0.31603 | 0 | 0 | 3.4994 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.3072 | 0 | 0 | 0 | 0 | 0.043809 | 0 | 0 | 27.351 | Hydro | 2.2744 | Hydro | 227438
| Khulna Zone |  |  | 0 | 21.9491 | 0.18288 | 0 | 0 | 0.37368 | 15.0945 | 0 | 37.6002 | Solar | 2.9862 | Solar | 47087758.5144
| Barishal Zone |  |  | 6.9758 | 56.0055 | 1.3641 | 0 | 0 | 0.003529 | 0 | 0 | 64.3488 | Import | 52.7238 | Import | 334044072.21
| Rajshahi Zone |  |  | 18.8514 | 0 | 2.3894 | 0 | 0 | 1.1289 | 34.0494 | 0 | 56.419 | Wind | 0.1896 | Wind | 2789016
| Rangpur Zone |  |  | 0 | 0.96349 | 1.5898 | 0 | 0 | 0.65635 | 0 | 0 | 3.2096
| Total |  |  | 126.7636 | 123.2962 | 35.0338 | 0 | 2.2744 | 2.9862 | 52.7238 | 0.1896 | 343.2675
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 437084201.6512 |  | Hydro | 227438
|  |  |  | Coal | 816663901.8826 |  | Solar | 47087758.5144
|  |  |  | HFO | 632836198.362 |  | Import | 334044072.21
|  |  |  | HSD | 0 |  | Wind | 2789016
[5 empty] | Total: | 227,07,32,586 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 14.1825 | Peak Hr Flow | 930.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 48775454.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 34.0494 | Peak Hr Flow | 1485.55 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2035 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.5798 | Peak Hr Flow | 168.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2614 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.8118 | Peak Hr Flow | 2583.55 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 88 |  | 5861
|  |  |  | Chattogram |  | 0 |  | 1526
|  |  |  | Cumilla |  | 110 |  | 1579
|  |  |  | Mymensingh |  | 241 |  | 1380
|  |  |  | Sylhet |  | 0 |  | 627
|  |  |  | Khulna |  | 31 |  | 1897
|  |  |  | Barishal |  | 0 |  | 528
|  |  |  | Rajshahi |  | 0 |  | 1641
|  |  |  | Rangpur |  | 26 |  | 1002
|  |  |  | Total |  | 496 |  | 16041
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 350
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:09 | Dhamrai 132/33kV S/S Transformer-1 HT is restored.
|  | 08:10 | Dhamrai 132/33kV S/S Transformer-1 LT is restored.
|  | 08:39 | Barishal(N)-Madaripur 132 kV Ckt-2 is restored.
|  | 08:48 | Narail 132/33kV S/S TR2 (413-T) HT is restored.
|  | 08:48 | Hathazari 230/132/33kV S/S MT-03 HT is restored.
|  | 08:48 | Hathazari 230/132/33kV S/S MT-03 LT is restored.
|  | 08:49 | Narail 132/33kV S/S TR2 (413-T) LT is restored.
| 09:07 | 10:26 | Srinagar 132/33kV S/S Tr-01 LT Scheduled S/D Due to 33 kv bus -01 shutdown for PBS red | [7 empty] | 20.0MW load
|  |  | hot maintenance. | [7 empty] | interrup.
| 09:08 | 10:24 | Srinagar 132/33kV S/S Tr-01 HT Scheduled S/D Due to 33 kv bus -01 shutdown for PBS red | [7 empty] | 20.0MW load
|  |  | hot maintenance. | [7 empty] | interrup.
| 09:19 | 10:17 | Srinagar 132/33kV S/S 33 kV bus Scheduled S/D Due to 33 kv bus -01 shutdown for PBS red | [7 empty] | 20.0MW load
|  |  | hot maintenance. | [7 empty] | interrup.
| 09:20 | 09:59 | Shahjadpur 132/33kV S/S T-2(415T) HT Forced S/D Due to Maintenance | [7 empty] | 9.0MW load
interrup.
| 09:20 | 14:58 | Shyampur-Shyampur(New) 132kV Ckt-1 Scheduled S/D from Shyampur 230/132kV end Due to Short
span jumper opening between Shy-1 & Fat-1 circuit. and from Shyampur 132/33kV end Due to
working for circuit-1
| 09:33 |  | Fatullah-Shyampur(New) 132 kV Ckt-1 Forced S/D from Fatullah 132/33kV end Due to By NLDC
| 10:22 | 12:34 | Chhatak 132/33kV S/S T-1 LT Scheduled S/D Due to Shutdown for 33KV T-1 Bus section red | [7 empty] | 12.0MW load
|  |  | hot maintenance. | [7 empty] | interrup.
| 10:22 | 12:34 | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to Shutdown for 33KV T-1 Bus section red | [7 empty] | 12.0MW load
|  |  | hot maintenance. | [7 empty] | interrup.
| 10:23 | 14:26 | Khulna(S)-PDB 330MW CCPP 230kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to
Maintenance Work at power Plant end.
| 11:20 | 11:30 | Hathazari 230/132/33kV S/S MT-03 HT Scheduled S/D Due to Bushing Measurement
|  | 14:44 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 is restored.
|  | 14:44 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 is restored.
| 15:44 | 17:27 | Daganbhuiyan 132/33kV S/S Transformer-1 HT Forced S/D Due to shutdown for Red Hot
Maintenance
| 15:47 | 17:30 | Daganbhuiyan 132/33kV S/S Transformer-1 LT Forced S/D Due to shutdown for Red Hot | [7 empty] | 14.0MW load
|  |  | Maintenance | [7 empty] | interrup.
| 16:06 | 17:07 | Fenchuganj 230/132/33kV S/S TR-01 HT Scheduled S/D Due to PDB Feeder maintenance | [7 empty] | 11.0MW load
interrup.
| 16:23 | 16:45 | Chapai 132/33kV S/S T-4 (435T) HT Forced S/D Due to Nest Remove | [7 empty] | 8.0MW load
interrup.
| 19:02 |  | Satiya-64 MW Solar132 KV-2 syn.
| 06:26 |  | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Red-hot Maintenance
| 06:26 |  | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Red-hot Maintenance
| 07:00 |  | Minimum Generation is 13639 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 370 | 8456400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 976746 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 302 | 7288703 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 229320 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 147 | 832320 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 533052 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270716 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 471000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 508320 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 134400 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 293 | 3277375 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 1876896 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 1248000 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 878400 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 169364 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 520 | 11618636.36 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 510 | 11835989 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 2618400 | Engine Problem
Dhaka Area Total |  |  |  |  | 6668.974 | 2751 | 53224037.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 313405.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 30510 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 196800 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 91 | 2274380 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5159694 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 88 | 1865091 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 66 | 559973 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 314400 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 525120 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 14 | 217440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 77 | 771840 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 15883 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 205745 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 342303 | Liquid fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 15890 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 602880 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 99 | 1408855 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 137 | 1455273 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 802 | 17149089 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 189600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1135 | 27229090.91 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2998.86 | 60843262.11
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 208 | 5082000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7458100 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 230 | 5784000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5822000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 3456 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1191232 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 68 | 948436 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 22 | 250944 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 94 | 2237264 | Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 185 | 2272320 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 168 | 3579840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 137890 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 473860 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 406980 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 167160 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 708480 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 248191 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1696 | 36772153
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 82818 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 21120 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 196 | 1905600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 48 | 1179600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 225660 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 77040 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 244 | 3499388
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 43809 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 667000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3470073 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 143 | 3161000 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 709056 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1403520 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2422710 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 507840 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7156000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 308 | 7810000 | plant availability zero
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1167 | 27351008
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 930 | 14182545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 106560 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 76320 | -
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 373680 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 510 | 21949089 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1518 | 37600194
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1000 | 22916363 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 934464 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 64 | 1535000 | GT-1 & ST under maint
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1222 | 26893090.91 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5440790 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 90 | 429600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6196000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3529 | -
Barishal Area Total |  |  |  |  | 3481.04 | 3013 | 64348836.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 263872 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 190609 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 12 | 32283 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 138810 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 193 | 4775118 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 190 | 4874564 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 403 | 9201672 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 16 | 87436 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52 | 251928 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 101 | 556912 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 661536 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 469920 | Fuel shortage due to BPDB's payment delay
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 25800 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1485.55 | 34049371 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 267888 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 571320 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2595.55 | 56419039
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 42 | 963490 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 407193 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 20907.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1182571 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 95447 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 540000 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 171 | 3209608.72
Eastern Grid Total |  |  |  |  | 17438.042 | 8856.86 | 181689848.47
Western Grid Total |  |  |  |  | 11885.475 | 7297.55 | 161577678.63
National Grid Total |  |  |  |  | 29323.517 | 16154.41 | 343267527.1
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-06-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10590.39 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5010.6 | MW
i) Dhaka area |  |  | 5772.89 |  | MW | i) Khulna area |  |  |  | 1866.5 | MW
ii) Chattogram area |  |  | 1582.5 |  | MW | ii) Barishal area |  |  |  | 527.5 | MW
iii) Cumilla area |  |  | 1469 |  | MW | iii) Rajshahi area |  |  |  | 1640.6 | MW
iv) Mymensingh area |  |  | 1139 |  | MW | iv) Rangpur area |  |  |  | 976 | MW
v) Sylhet area |  |  | 627 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15600.99 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 140 | 10:00 | 133 | Narshingdi | 179 | 23:00 | 199 | Zigatola | 92 | 15:00
2 | AKSML | 127.7 | 01:00 | 68 | Hasnabad | 95 | 19:00 | 134 | Natore | 161 | 19:30
3 | Aftabnagar | 44 | 13:00 | 69 | Hathazari | 90 | 18:30 | 135 | Nawabganj | 62.8 | 22:00
4 | Agargaon | 118 | 13:00 | 70 | Hatirjheel | 47 | 12:00 | 136 | Netrakona | 114 | 00:00
5 | Agrabad | 74 | 15:00 | 71 | Ishurdi | 84 | 20:00 | 137 | New | 52 | 12:00
6 | Amnura | 32 | 23:00 | 72 | Jaldhaka | 70 | 00:00 | 138 | Niamatpur | 88 | 22:00
7 | Ashuganj | 82 | 16:00 | 73 | Jamalpur | 128 | 21:00 | 139 | Noapara | 54 | 20:00
8 | BSRM | 203 | 01:00 | 74 | Jashore | 155 | 19:30 | 140 | PHP | 13 | 18:00
9 | Bagerhat | 87 | 19:00 | 75 | Jhenaidah | 105 | 19:30 | 141 | Pabna | 101 | 21:00
10 | Bajitpur | 102 | 19:00 | 76 | Joydebpur | 154 | 10:00 | 142 | Palashbari | 124 | 20:00
11 | Bakerganj | 16.2 | 22:00 | 77 | Joypurhat | 67 | 22:00 | 143 | Panchagarh | 67 | 19:30
12 | Bakulia | 98 | 19:00 | 78 | Juldah | 18 | 10:00 | 144 | Patiya | 11 | 19:30
13 | Banani | 65 | 13:00 | 79 | KSRM | 16 | 12:00 | 145 | Patuakhali | 74 | 22:00
14 | Bangabhaban | 20 | 10:00 | 80 | Kabirpur | 276 | 18:30 | 146 | Payra | 36 | 21:00
15 | Barapukuria | 66 | 00:00 | 81 | Kachua | 96 | 19:00 | 147 | Postogola | 62 | 13:00
16 | Barguna | 22 | 00:00 | 82 | Kaliganj | 38 | 20:00 | 148 | Pubail | 36 | 19:00
17 | Barishal | 109 | 12:00 | 83 | Kallyanpur | 123 | 19:00 | 149 | Purbachal | 31 | 13:00
18 | Barishal-230 | 108 | 19:30 | 84 | Kalurghat | 40 | 15:00 | 150 | Purbasadipur | 140 | 19:30
19 | Baroaulia | 51 | 16:00 | 85 | Kamrangirchar | 79 | 12:00 | 151 | Rahanpur | 46 | 22:00
20 | Baroirhat | 74 | 19:00 | 86 | Kaptai | N/A | N/A | 152 | Rahim | 44 | 15:00
21 | Bashundhara | 205 | 19:30 | 87 | Kasba | 38 | 20:00 | 153 | Rajbari | 90 | 20:00
22 | BashundharaCement | 1 | 00:00 | 88 | Kazla | 120 | 13:00 | 154 | Rajendrapur | 112 | 11:00
23 | Beanibazar | 78 | 19:00 | 89 | Keranigonj | 87 | 13:00 | 155 | Rajshahi | 122 | 23:00
24 | Benapole | 63 | 02:00 | 90 | Khagrachori | 34 | 21:00 | 156 | Rajshahi-230 | 106 | 21:00
25 | Bhaluka | 178 | 19:00 | 91 | Khulna | 66 | 20:00 | 157 | Ramganj | 114 | 19:00
26 | Bhandaria | 60 | 22:00 | 92 | Khulshi | 192 | 19:30 | 158 | Rampur | 44 | 00:00
27 | Bhangura | 41 | 20:00 | 93 | Kishoreganj | 112 | 18:30 | 159 | Rangamati | 18 | 19:30
28 | Bheramara(GK) | 72 | 21:00 | 94 | Kodda | 293 | 19:30 | 160 | Rangpur | 137 | 20:00
29 | Bhulta | 217 | 21:00 | 95 | Kulaura | 51 | 21:00 | 161 | Ruppur | 4.8 | 11:00
30 | Bog-Sherpur | 84 | 22:00 | 96 | Kurigram | 64 | 20:00 | 162 | SSM | 4 | 23:00
31 | Bogura | 180 | 21:00 | 97 | Kushtia | 170 | 19:30 | 163 | Saidpur | 106 | 20:00
32 | Borhanuddin | 81 | 21:00 | 98 | Laksam | 34 | 22:00 | 164 | Santhia | 34 | 22:00
33 | Brahmanbaria | 127 | 19:00 | 99 | Lakshmipur | 45 | 21:00 | 165 | Satkhira | 139 | 21:00
34 | Cantonment | 146 | 14:00 | 100 | Lalbag | 79 | 19:30 | 166 | Satmasjid | 108 | 19:30
35 | Chandina | 40 | 20:00 | 101 | Lalmonirhat | 58 | 20:00 | 167 | Savar | 218 | 19:00
36 | Chandpur | 86 | 20:00 | 102 | MI_Cement | 8.7 | 03:00 | 168 | SevenRings | 18.62 | 11:00
37 | Chandraghona | 34 | 19:00 | 103 | Madanganj | 52 | 09:00 | 169 | ShahCement | 34 | 18:00
38 | Chapai | 84 | 21:00 | 104 | Madaripur | 108 | 20:00 | 170 | Shahjadpur | 78 | 20:00
39 | Charfasson | 34 | 00:00 | 105 | Madartek | 82 | 23:00 | 171 | Shahjibazar | 134 | 21:00
40 | Charsaidpur | 41 | 15:00 | 106 | Madunaghat | 56 | 19:30 | 172 | Shahmirpur | 52 | 01:00
41 | Chauddagram | 76 | 20:00 | 107 | Magura | 70 | 20:00 | 173 | Shariatpur | 95 | 22:00
42 | Chhatak | 39 | 22:00 | 108 | Mahasthangarh | 81 | 22:00 | 174 | Sherpur | 160 | 19:30
43 | Chowmuhani | 157 | 23:00 | 109 | Maijdee | 42 | 00:00 | 175 | Shikalbaha | 28.5 | 00:00
44 | Chuadanga | 113 | 19:30 | 110 | Manikganj | 146 | 21:00 | 176 | Shitalakhya | 81.6 | 16:00
45 | Coxsbazar | 141 | 18:30 | 111 | Maniknagar | 80 | 13:00 | 177 | Sholosohor | 48 | 15:00
46 | Cumilla(N) | 116 | 20:00 | 112 | Matarbari | 56 | 21:00 | 178 | Shomvuganj | 40 | 19:00
47 | Cumilla(S) | 183 | 23:00 | 113 | Matuail | 80 | 12:00 | 179 | Shyampur | 160 | 06:00
48 | Daganbhuiyan | 42 | 19:00 | 114 | Metrorail_Motijheel | 18 | 18:30 | 180 | Siddhirganj | 130 | 12:00
49 | Daudkandi | 149 | 20:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Sirajganj | 116 | 20:00
50 | DhakaUniversity | 94 | 13:00 | 116 | Millgate | 141 | 12:00 | 182 | Sonargaon | 140 | 22:00
51 | Dhamrai | 122 | 19:00 | 117 | Mirpur | 159 | 19:30 | 183 | Sreemongol | 87 | 22:00
52 | Dhanmondi | 126.7 | 13:00 | 118 | Mirsorai | 47 | 09:00 | 184 | Sreepur | 136 | 19:00
53 | Dohazari | 112 | 21:00 | 119 | Mirzapur | 42 | 21:00 | 185 | Srinagar | 50.91 | 22:00
54 | Faridpur | 171 | 22:00 | 120 | Mithapukur | 68 | 20:00 | 186 | Sunamganj | 62 | 23:00
55 | Fatullah | 108 | 12:00 | 121 | Modern | N/A | N/A | 187 | Sylhet | 125 | 14:00
56 | Fenchuganj | 42 | 23:00 | 122 | Mogbazar | 95.7 | 16:00 | 188 | Sylhet_(South) | 48 | 22:00
57 | Feni | 103 | 19:00 | 123 | Mongla | 41 | 11:00 | 189 | TK | 25 | 00:00
58 | GPH | 76 | 17:00 | 124 | Motijheel | 53 | 13:00 | 190 | Tangail | 196 | 20:00
59 | Ghatail | 90 | 21:00 | 125 | Muktagacha | 36 | 12:00 | 191 | Taraganj | 28 | 19:30
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 119 | 22:00 | 192 | Tasnim | 36 | 16:00
61 | Ghorashal-230 | 101 | 21:00 | 127 | Muradnagar | 51 | 20:00 | 193 | Thakurgaon | 111 | 20:00
62 | Goalpara | 42 | 13:00 | 128 | Mymensingh | 154 | 23:00 | 194 | Tongi | 161 | 11:00
63 | Gollamari | 114 | 21:00 | 129 | Nabinagar | 100 | 10:00 | 195 | Ullahpara | 42 | 19:30
64 | Gopalganj | 118 | 19:30 | 130 | Naogaon | 152 | 21:00 | 196 | Ullon | 57 | 21:00
65 | Gulshan | 126 | 13:00 | 131 | Narail | 62 | 20:00 | 197 | Uttara | 95 | 13:00
66 | Halishahar | 108.5 | 10:00 | 132 | Narinda | 76 | 13:00 | 198 | UttaraNew | 54 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14867.66 | 174 |  | 15049.49
1:00 | 14369.99 | 197 |  | 14575.86
2:00 | 13886.39 | 213 |  | 14108.98
3:00 | 13620.49 | 192 |  | 13821.13
4:00 | 13114.79 | 186 |  | 13309.16
5:00 | 12781.57 | 176 |  | 12965.49
6:00 | 12623.38 | 171 |  | 12802.08
7:00 | 12774.42 | 223 |  | 13007.42
8:00 | 12806.47 | 197 |  | 13012.47
9:00 | 13134.56 | 201 |  | 13344.56
10:00 | 13367.8 | 278 |  | 13658.8
11:00 | 13676.68 | 346 |  | 14038.68
12:00 | 14171.86 | 420 |  | 14610.86
13:00 | 14415.72 | 405 |  | 14838.72
14:00 | 14587.64 | 236 |  | 14834.64
15:00 | 14723.27 | 221 |  | 14954.27
16:00 | 14579.4 | 148 |  | 14734.4
17:00 | 14220.97 | 138 |  | 14364.97
18:00 | 14179.01 | 140 |  | 14325.01
19:00 | 15354.07 | 213 |  | 15577.07
19:30 | 15723.11 | 1082 |  | 16854.11
20:00 | 15846.44 | 414 |  | 16279.44
21:00 | 16154.41 | 496 |  | 16672.41
22:00 | 15718.99 | 636 |  | 16383.61
23:00 | 15554.84 | 1236 |  | 16846.46
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8000 | 6867.66 | 14867.66 | DAILY GENERATION CURVE
00:30 | 7917.5 | 6701.325 | 14618.825
01:00 | 7835 | 6534.99 | 14369.99 | 22-06-2026
01:30 | 7646 | 6482.19 | 14128.19
02:00 | 7457 | 6429.39 | 13886.39
02:30 | 7282 | 6471.44 | 13753.44
03:00 | 7107 | 6513.49 | 13620.49
03:30 | 6923.5 | 6444.14 | 13367.64
04:00 | 6740 | 6374.79 | 13114.79
04:30 | 6618.5 | 6329.68 | 12948.18
05:00 | 6497 | 6284.57 | 12781.57
05:30 | 6498.2 | 6204.275 | 12702.475
06:00 | 6499.4 | 6123.98 | 12623.38
06:30 | 6558.935 | 6139.965 | 12698.9
07:00 | 6618.47 | 6155.95 | 12774.42
07:30 | 6642.41 | 6148.035 | 12790.445
08:00 | 6666.35 | 6140.12 | 12806.47
08:30 | 6751.185 | 6219.33 | 12970.515
09:00 | 6836.02 | 6298.54 | 13134.56
09:30 | 6870.215 | 6380.965 | 13251.18
10:00 | 6904.41 | 6463.39 | 13367.8
10:30 | 7018.24 | 6504 | 13522.24
11:00 | 7132.07 | 6544.61 | 13676.68
11:30 | 7244.535 | 6679.735 | 13924.27
12:00 | 7357 | 6814.86 | 14171.86
12:30 | 7457.82 | 6835.97 | 14293.79
13:00 | 7558.64 | 6857.08 | 14415.72
13:30 | 7633.84 | 6867.84 | 14501.68
14:00 | 7709.04 | 6878.6 | 14587.64
14:30 | 7743.245 | 6912.21 | 14655.455
15:00 | 7777.45 | 6945.82 | 14723.27
15:30 | 7751.295 | 6900.04 | 14651.335
16:00 | 7725.14 | 6854.26 | 14579.4
16:30 | 7585.075 | 6815.11 | 14400.185
17:00 | 7445.01 | 6775.96 | 14220.97
17:30 | 7467.03 | 6732.96 | 14199.99
18:00 | 7489.05 | 6689.96 | 14179.01
18:30 | 7939.955 | 6826.585 | 14766.54
19:00 | 8390.86 | 6963.21 | 15354.07
19:30 | 8637.86 | 7085.25 | 15723.11
20:00 | 8729.86 | 7116.58 | 15846.44
20:30 | 8793.36 | 7207.065 | 16000.425 |  | Executive Engineer
21:00 | 8856.86 | 7297.55 | 16154.41 |  | Network Operation Division
21:30 | 8706.86 | 7229.84 | 15936.7
22:00 | 8556.86 | 7162.13 | 15718.99
22:30 | 8462.18 | 7174.735 | 15636.915
23:00 | 8367.5 | 7187.34 | 15554.84

## En-Curve
QF-LDC-12
Date | 22-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3367 | 1865 | 476 | 38 | 160 | 1491.66 | 95 | 5338 | 0 | 326 | 1687 | 0 | 0 | 24 | 174 | DAILY ENERGY CURVE
00:30 | 3339 | 1813.5 | 476 | 38 | 153 | 1456.325 | 95 | 5239 | 0 | 305 | 1668.5 | 0 | 0 | 35.5 | 185.5 | 22-06-2026
01:00 | 3311 | 1762 | 476 | 38 | 146 | 1420.99 | 95 | 5140 | 0 | 284 | 1650 | 0 | 0 | 47 | 197
01:30 | 3318 | 1780 | 476 | 38 | 150 | 1393.69 | 95 | 5137.5 | 0 | 254.5 | 1462 | 0 | 0 | 23.5 | 205 | Energy Generated | 343.2675 |  | MKWHr
02:00 | 3325 | 1798 | 476 | 38 | 154 | 1366.39 | 95 | 5135 | 0 | 225 | 1274 | 0 | 0 | 0 | 213 | Energy not Served | 7.257 |  | MKWHr
02:30 | 3337 | 1812 | 476 | 38 | 150 | 1380.94 | 97 | 5152.5 | 0 | 206.5 | 1103.5 | 0 | 0 | 0 | 202.5 | Total Energy Requirement | 350.5245 |  | MKWHr
03:00 | 3349 | 1826 | 476 | 38 | 146 | 1395.49 | 99 | 5170 | 0 | 188 | 933 | 0 | 0 | 0 | 192
03:30 | 3360.5 | 1826 | 476 | 38 | 148 | 1399.14 | 99 | 5177 | 0 | 188 | 652.5 | 0 | 0 | 3.5 | 189
04:00 | 3372 | 1826 | 476 | 38 | 150 | 1402.79 | 99 | 5184 | 0 | 188 | 372 | 0 | 0 | 7 | 186
04:30 | 3360.5 | 1803 | 476 | 38 | 142 | 1401.68 | 99 | 5182 | 0 | 179.5 | 260 | 0 | 0 | 6.5 | 181
05:00 | 3349 | 1780 | 476 | 38 | 134 | 1400.57 | 99 | 5180 | 0 | 171 | 148 | 0 | 0 | 6 | 176
05:30 | 3344.5 | 1747 | 476 | 38 | 129 | 1349.11 | 97 | 5152.5 | 6.365 | 171 | 183.5 | 0 | 0 | 8.5 | 173.5
06:00 | 3340 | 1714 | 476 | 38 | 124 | 1297.65 | 95 | 5125 | 12.73 | 171 | 219 | 0 | 0 | 11 | 171
06:30 | 3357.5 | 1773 | 476.5 | 38 | 125 | 1285.92 | 94 | 5100.5 | 46.48 | 171 | 219 | 0 | 0 | 12 | 197
07:00 | 3375 | 1832 | 477 | 38 | 126 | 1274.19 | 93 | 5076 | 80.23 | 171 | 219 | 0 | 0 | 13 | 223
07:30 | 3388 | 1814 | 476.5 | 38 | 135 | 1261.045 | 92 | 5053.5 | 109.9 | 179.5 | 231.5 | 0 | 0 | 11.5 | 210
08:00 | 3401 | 1796 | 476 | 38 | 144 | 1247.9 | 91 | 5031 | 139.57 | 188 | 244 | 0 | 0 | 10 | 197
08:30 | 3416 | 1809 | 476 | 38 | 146 | 1262.805 | 91 | 5064.5 | 176.21 | 193.5 | 284.5 | 0 | 0 | 13 | 199
09:00 | 3431 | 1822 | 476 | 38 | 148 | 1277.71 | 91 | 5098 | 212.85 | 199 | 325 | 0 | 0 | 16 | 201
09:30 | 3444.5 | 1824 | 483 | 38 | 151 | 1284.7 | 91 | 5106.5 | 280.48 | 150 | 380.5 | 0 | 0 | 17.5 | 239.5
10:00 | 3458 | 1826 | 490 | 38 | 154 | 1291.69 | 91 | 5115 | 348.11 | 101 | 436 | 0 | 0 | 19 | 278
10:30 | 3487 | 1833.75 | 496 | 38 | 154 | 1306.415 | 92 | 5164.5 | 316.575 | 110.5 | 509 | 0 | 0 | 14.5 | 312
11:00 | 3516 | 1841.5 | 502 | 38 | 154 | 1321.14 | 93 | 5214 | 285.04 | 120 | 582 | 0 | 0 | 10 | 346
11:30 | 3492 | 1849 | 502 | 38 | 152 | 1404.045 | 94 | 5227 | 325.725 | 123 | 710 | 0 | 0 | 7.5 | 383
12:00 | 3468 | 1856.5 | 502 | 38 | 150 | 1486.95 | 95 | 5240 | 366.41 | 126 | 838 | 0 | 0 | 5 | 420
12:30 | 3400 | 1822 | 502.5 | 38 | 151 | 1484.32 | 95 | 5248 | 355.97 | 154.5 | 1036.5 | 0 | 0 | 6 | 412.5
13:00 | 3332 | 1787.5 | 503 | 38 | 152 | 1481.69 | 95 | 5256 | 345.53 | 183 | 1235 | 0 | 0 | 7 | 405
13:30 | 3352 | 1802 | 503 | 38 | 156 | 1482.69 | 96 | 5236.5 | 356.74 | 198.5 | 1275.75 | 0 | 0 | 4.5 | 320.5
14:00 | 3372 | 1816.5 | 503 | 38 | 160 | 1483.69 | 97 | 5217 | 367.95 | 214 | 1316.5 | 0 | 0 | 2 | 236
14:30 | 3389 | 1827.5 | 503 | 38 | 152 | 1484.76 | 97 | 5245.5 | 344.195 | 230.5 | 1342.5 | 0 | 0 | 1.5 | 228.5
15:00 | 3406 | 1838.5 | 503 | 38 | 144 | 1485.83 | 97 | 5274 | 320.44 | 247 | 1368.5 | 0 | 0 | 1 | 221
15:30 | 3379.5 | 1820.5 | 508 | 38 | 142 | 1490.35 | 98 | 5289 | 278.485 | 232 | 1375 | 0 | 0 | 0.5 | 184.5
16:00 | 3353 | 1802.5 | 513 | 38 | 140 | 1494.87 | 99 | 5304 | 236.53 | 217 | 1381.5 | 0 | 0 | 0 | 148
16:30 | 3352.5 | 1828.5 | 548.5 | 38 | 143 | 1487.085 | 99 | 5246.5 | 185.1 | 226 | 1245.5 | 0 | 0 | 0.5 | 143
17:00 | 3352 | 1854.5 | 584 | 38 | 146 | 1479.3 | 99 | 5189 | 133.67 | 235 | 1109.5 | 0 | 0 | 1 | 138
17:30 | 3365 | 1866 | 620 | 38 | 143 | 1480.875 | 98 | 5141 | 88.865 | 235 | 1122.75 | 0 | 0 | 1.5 | 139
18:00 | 3378 | 1877.5 | 656 | 38 | 140 | 1482.45 | 97 | 5093 | 44.06 | 235 | 1136 | 0 | 0 | 2 | 140
18:30 | 3409.5 | 1910.75 | 711.5 | 38 | 147 | 1482.83 | 96 | 5009.5 | 22.03 | 408.5 | 1528.43 | 0 | 0 | 2.5 | 176.5
19:00 | 3441 | 1944 | 767 | 38 | 154 | 1483.21 | 95 | 4926 | 0 | 582 | 1920.86 | 0 | 0 | 3 | 213
19:30 | 3296 | 1806 | 832 | 38 | 154 | 1484.25 | 95 | 4988 | 0 | 635 | 2389.86 | 0 | 0 | 5 | 1082
20:00 | 3357 | 1819 | 830 | 38 | 140 | 1473.58 | 91 | 5014 | 0 | 632 | 2443.86 | 0 | 0 | 8 | 414
20:30 | 3374 | 1875.5 | 880 | 38 | 154 | 1479.565 | 91 | 5016 | 0 | 663 | 2421.36 | 0 | 0 | 8 | 455
21:00 | 3391 | 1932 | 930 | 38 | 168 | 1485.55 | 91 | 5018 | 0 | 694 | 2398.86 | 0 | 0 | 8 | 496
21:30 | 3361 | 1870 | 930 | 38 | 165 | 1485.84 | 91 | 5018 | 0 | 674.5 | 2295.86 | 0 | 0 | 7.5 | 566
22:00 | 3331 | 1808 | 930 | 38 | 162 | 1486.13 | 91 | 5018 | 0 | 655 | 2192.86 | 0 | 0 | 7 | 636
22:30 | 3378 | 1886.5 | 930 | 38 | 171 | 1490.735 | 91 | 4985 | 0 | 619.5 | 2042.68 | 0 | 0 | 4.5 | 936
23:00 | 3425 | 1965 | 930 | 38 | 180 | 1495.34 | 91 | 4952 | 0 | 584 | 1892.5 | 0 | 0 | 2 | 1236
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 22-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 46 | -3 | 306 | 100 | 1570 | 262 | Ishurdi-Ghorashal Ckt-1 | Export | 2793454.54
1:00 | 43 | 0 | 272 | 86 | 1434 | 316
2:00 | 48 | 3 | 300 | 100 | 1488 | 326 |  | Import | 0
3:00 | 81 | 16 | 350 | 112 | 1642 | 388
4:00 | 85 | 19 | 362 | 110 | 1656 | 388 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 89 | 21 | 364 | 110 | 1672 | 392
6:00 | 88 | 23 | 338 | 114 | 1598 | 412 |  | Import | 0
7:00 | 87 | 24 | 356 | 128 | 1574 | 402
8:00 | 106 | 32 | 380 | 124 | 1632 | 476 | Sirajganj-Sreepur Ckt-1 | Export | 2384000
9:00 | 137 | 47 | 428 | 126 | 1822 | 550
10:00 | 158 | 54 | 500 | 146 | 1900 | 586 |  | Import | 0
11:00 | 153 | 52 | 478 | 142 | 1946 | 592
12:00 | 144 | 42 | 498 | 158 | 1854 | 584 | Sirajganj-Sreepur Ckt-2 | Export | 2378000
13:00 | 136 | 37 | 490 | 156 | 1830 | 562
14:00 | 135 | 34 | 520 | 172 | 1828 | 544 |  | Import | 0
15:00 | 143 | 45 | 536 | 190 | 1914 | 608
16:00 | 141 | 43 | 518 | 170 | 1932 | 602 | Gopalganj-Aminbazar Ckt-1 | Export | 20590000
17:00 | 160 | 48 | 536 | 180 | 1918 | 642
18:00 | 152 | 39 | 540 | 164 | 1726 | 524 |  | Import | 0
18:30 | 155 | 38 | 540 | 154 | 1754 | 454
19:00 | 143 | 20 | 478 | 132 | 1664 | 404 | Gopalganj-Aminbazar Ckt-2 | Export | 20630000
19:30 | 106 | 8 | 374 | 86 | 1476 | 308
20:00 | 104 | 6 | 372 | 96 | 1450 | 308 |  | Import | 0
21:00 | 117 | -1 | 440 | 130 | 1478 | 300
22:00 | 109 | -11 | 420 | 106 | 1482 | 260 |  | Total Export | 48775454.54
23:00 | 134 | 5 | 470 | 134 | 1604 | 352 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 01:00 | 362 | 12:00 | Madunaghat | 395 | 01:00 | 389 | 12:00
Amtali | 408 | 06:00 | 402 | 23:00 | Meghnaghat | 383 | 01:00 | 367 | 12:00
Ashuganj | 410 | 5:00 | 388 | 16:00 | Payra | 410 | 07:00 | 404 | 22:00
Bhulta | 402 | 05:00 | 379 | 12:00 | Rahanpur | 400 | 08:00 | 385 | 21:00
Bibiana | 396 | 01:00 | 386 | 12:00 | Rampal | 395 | 05:00 | 375 | 21:00
BIPTC | 405 | 04:00 | 393 | 23:00
Bogura | 383 | 08:00 | 366 | 21:00
Gopalganj | 390 | 06:00 | 376 | 21:00
Kaliakoir | 373 | 00:00 | 351 | 15:00
Korerhat | 395 | 01:00 | 385 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 02:00 | 219 | 12:00 | Ishurdi | 235 | 08:00 | 215 | 22:00
AKSML | 230 | 00:00 | 223 | 12:00 | Jhenaidah | 225 | 08:00 | 201 | 22:00
Aminbazar | 233 | 04:00 | 219 | 12:00 | Kachua | 227 | 19:30 | 219 | 11:00
Ashuganj | 229 | 04:00 | 220 | 14:00 | Kaliakoir | 234 | 02:00 | 217 | 12:00
Ashuganj-400 | 229 | 04:00 | 220 | 14:00 | Keranigonj | 231 | 01:00 | 217 | 12:00
Baghabari | 232 | 05:00 | 219 | 22:00 | Khulna(S) | 224 | 08:00 | 205 | 21:00
Barapukuria | 220 | 17:00 | 204 | 20:00 | Korerhat | 227 | 19:30 | 200 | 13:00
Barapukuria-230 | 220 | 17:00 | 204 | 20:00 | Madunaghat | 232 | 19:00 | 226 | 11:00
Barishal | 226 | 02:00 | 220 | 12:00 | Madunaghat-400 | 232 | 01:00 | 228 | 11:00
Bheramara | 235 | 05:00 | 213 | 22:00 | Maniknagar | 229 | 02:00 | 215 | 16:00
Bhulta | 231 | 06:00 | 215 | 12:00 | Meghnaghat | 237 | 01:00 | 225 | 12:00
Bibiana | 231 | 07:00 | 224 | 16:00 | Meghnaghat-400 | 233 | 05:00 | 220 | 12:00
BIPTC | 236 | 08:00 | 213 | 22:00 | Mirsorai | 231 | 01:00 | 224 | 11:00
Bogura | 236 | 06:00 | 225 | 21:00 | Naogaon | 223 | 10:00 | 199 | 21:00
Bogura-400 | 236 | 06:00 | 226 | 21:00 | Purbasadipur | 219 | 15:00 | 204 | 20:00
Borhanuddin | 230 | 02:00 | 226 | 15:00 | Rajshahi | 231 | 07:00 | 211 | 22:00
BSRM | 225 | 06:00 | 220 | 11:00 | Rampal | 223 | 05:00 | 207 | 22:00
Charfasson | 231 | 08:00 | 225 | 22:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 226 | 19:30 | 219 | 11:00 | Rampura | 230 | 06:00 | 213 | 16:00
Cumilla(N) | 227 | 05:00 | 218 | 15:00 | Shikalbaha | 232 | 19:00 | 226 | 09:00
Faridpur | 222 | 06:00 | 212 | 22:00 | Shyampur | 232 | 06:00 | 217 | 16:00
Fenchuganj | 232 | 06:00 | 227 | 15:00 | Siddhirganj | 233 | 05:00 | 219 | 13:00
Feni | 224 | 00:00 | 219 | 11:00 | Sirajgonj | 238 | 08:00 | 230 | 21:00
Ghorashal | 232 | 08:00 | 220 | 16:00 | Sreepur | 224 | 01:00 | 214 | 21:00
Ghorashal-230 | 222 | 02:00 | 201 | 12:00 | Tongi | 228 | 04:00 | 205 | 11:00
Gopalganj | 222 | 02:00 | 214 | 22:00
GPH | 228 | 00:00 | 224 | 11:00
Haripur | 231 | 06:00 | 217 | 16:00
Hasnabad | 232 | 05:00 | 217 | 12:00
Hathazari | 229 | 03:00 | 223 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 04:00 | 126 | 12:00 | Madunaghat | 134 | 02:00 | 130 | 11:00
Agargaon | 138 | 00:00 | 127 | 12:00 | Magura | 135 | 08:00 | 116 | 22:00
Agrabad | 133 | 19:30 | 128 | 08:00 | Mahasthangarh | 133 | 09:00 | 124 | 20:00
AKS | 131 | 19:00 | 126 | 12:00 | Maijdee | 125 | 01:00 | 123 | 04:00
Aminbazar | 133 | 00:00 | 124 | 12:00 | Manikganj | 132 | 01:00 | 123 | 11:00
Amnura | 133 | 05:00 | 125 | 21:00 | Maniknagar | 135 | 03:00 | 125 | 13:00
Ashuganj | 137 | 05:00 | 130 | 15:00 | Matarbari | 118 | 06:00 | 108 | 19:00
Ashuganj-230 | 137 | 05:00 | 130 | 15:00 | Matuail | 134 | 04:00 | 124 | 16:00
Bagerhat | 127 | 08:00 | 110 | 22:00 | Metrorail_Motijheel | 135 | 03:00 | 123 | 12:00
Bajitpur | 127 | 01:00 | 121 | 13:00 | Metrorail_Uttara | 136 | 01:00 | 120 | 15:00
Bakerganj | 130 | 05:00 | 126 | 12:00 | Millgate | 138 | 01:00 | 121 | 12:00
Bakulia | 134 | 19:30 | 128 | 12:00 | Mirpur | 133 | 00:00 | 123 | 12:00
Banani | 138 | 05:00 | 125 | 13:00 | Mirzapur | 131 | 02:00 | 122 | 15:00
Bangabhaban | 135 | 04:00 | 124 | 13:00 | Mithapukur | 131 | 17:00 | 120 | 20:00
Barapukuria | 134 | 17:00 | 121 | 20:00 | MI_Cement | 137 | 05:00 | 125 | 15:00
Barguna | 130 | 07:00 | 126 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 19:30 | 125 | 12:00 | Mogbazar | 139 | 03:00 | 127 | 12:00
Barishal-230 | 131 | 02:00 | 126 | 12:00 | Mongla | 129 | 08:00 | 113 | 22:00
Baroaulia | 134 | 22:00 | 129 | 12:00 | Motijheel | 135 | 04:00 | 124 | 13:00
Baroirhat | 130 | 00:00 | 127 | 11:00 | Muktagacha | 129 | 18:30 | 116 | 15:00
Bashundhara | 138 | 01:00 | 121 | 12:00 | Munshiganj | 132 | 00:00 | 123 | 12:00
BashundharaCement | 134 | 07:00 | 125 | 12:00 | Muradnagar | 130 | 16:00 | 122 | 15:00
Beanibazar | 127 | 06:00 | 120 | 23:00 | Mymensingh | 129 | 18:30 | 114 | 14:00
Benapole | 129 | 09:00 | 112 | 22:00 | Nabinagar | 134 | 07:00 | 120 | 15:00
Bhaluka | 129 | 03:00 | 122 | 15:00 | Naogaon | 134 | 10:00 | 120 | 21:00
Bhandaria | 125 | 05:00 | 120 | 12:00 | Narail | 135 | 08:00 | 117 | 21:00
Bhangura | 133 | 04:00 | 125 | 21:00 | Narinda | 135 | 03:00 | 125 | 13:00
Bheramara | 136 | 08:00 | 122 | 22:00 | Narshingdi | 127 | 19:30 | 118 | 12:00
Bheramara(GK) | 135 | 05:00 | 122 | 22:00 | Natore | 133 | 04:00 | 122 | 22:00
Bhulta | 129 | 05:00 | 120 | 12:00 | Nawabganj | 139 | 01:00 | 129 | 15:00
Bog-Sherpur | 134 | 06:00 | 126 | 22:00 | Netrakona | 123 | 19:30 | 111 | 23:00
Bogura | 136 | 10:00 | 128 | 22:00 | New | 138 | 01:00 | 123 | 12:00
Bogura-230 | 136 | 06:00 | 129 | 21:00 | Niamatpur | 131 | 08:00 | 123 | 21:00
Brahmanbaria | 129 | 19:30 | 117 | 12:00 | Noapara | 131 | 05:00 | 117 | 22:00
Cantonment | 138 | 00:00 | 126 | 15:00 | Pabna | 133 | 04:00 | 122 | 22:00
Chandina | 131 | 06:00 | 125 | 15:00 | Palashbari | 129 | 17:00 | 118 | 20:00
Chandpur | 132 | 19:30 | 125 | 04:00 | Panchagarh | 134 | 13:00 | 125 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 01:00 | 131 | 11:00 | Patiya | 132 | 19:30 | 127 | 11:00
Chapai | 132 | 10:00 | 125 | 22:00 | Patuakhali | 131 | 19:30 | 126 | 12:00
Charsaidpur | 133 | 04:00 | 124 | 12:00 | Payra | 134 | 02:00 | 130 | 12:00
Chauddagram | 129 | 06:00 | 124 | 15:00 | PHP | 130 | 06:00 | 126 | 15:00
Chhatak | 125 | 05:00 | 116 | 23:00 | Postogola | 138 | 04:00 | 128 | 12:00
Chowmuhani | 127 | 19:30 | 123 | 12:00 | Pubail | 127 | 01:00 | 117 | 12:00
Chuadanga | 132 | 08:00 | 113 | 22:00 | Purbachal | 138 | 04:00 | 125 | 16:00
Coxsbazar | 120 | 18:00 | 112 | 23:00 | Purbasadipur | 132 | 13:00 | 123 | 20:00
Cumilla(N) | 131 | 05:00 | 126 | 11:00 | Rahanpur | 133 | 06:00 | 128 | 20:00
Cumilla(S) | 131 | 05:00 | 123 | 23:00 | Rahanpur-400 | 134 | 08:00 | 128 | 21:00
Daganbhuiyan | 127 | 00:00 | 125 | 11:00 | Rahim | 134 | 04:00 | 125 | 16:00
Daudkandi | 126 | 04:00 | 120 | 12:00 | Rajbari | 127 | 06:00 | 119 | 21:00
DhakaUniversity | 138 | 04:00 | 126 | 12:00 | Rajendrapur | 129 | 19:30 | 122 | 15:00
Dhamrai | 134 | 05:00 | 122 | 12:00 | Rajshahi | 131 | 06:00 | 120 | 22:00
Dhanmondi | 138.6 | 05:00 | 125 | 12:00 | Rajshahi-230 | 133 | 06:00 | 121 | 22:00
Dohazari | 128 | 19:30 | 123 | 19:00 | Ramganj | 128 | 19:30 | 121 | 08:00
Faridpur | 128 | 06:00 | 123 | 21:00 | Rampur | 132 | 20:00 | 127 | 12:00
Fatullah | 138 | 02:00 | 126 | 15:00 | Rampura | 138 | 04:00 | 126 | 12:00
Fenchuganj | 132 | 02:00 | 128 | 19:00 | Rangamati | 133 | 19:30 | 130 | 11:00
Feni | 128 | 00:00 | 125 | 15:00 | Rangpur | 129 | 17:00 | 116 | 20:00
Feni-230 | 129 | 00:00 | 126 | 09:00 | Ruppur | 136 | 04:00 | 124 | 22:00
Ghatail | 125 | 05:00 | 115 | 15:00 | Saidpur | 132 | 17:00 | 121 | 20:00
Ghorashal | 130 | 02:00 | 122 | 12:00 | Santhia | 135 | 07:00 | 124 | 22:00
Goalpara | 134 | 08:00 | 121 | 22:00 | Satkhira | 128 | 08:00 | 111 | 22:00
Gollamari | 133 | 05:00 | 120 | 22:00 | Satmasjid | 137 | 00:00 | 127 | 12:00
Gopalganj | 130 | 06:00 | 120 | 22:00 | Savar | 131 | 00:00 | 122 | 12:00
Gopalganj-400 | 131 | 02:00 | 126 | 21:00 | SevenRings | 131 | 01:00 | 121 | 11:00
Gulshan | 137 | 04:00 | 126 | 12:00 | ShahCement | 133 | 05:00 | 124 | 12:00
Halishahar | 133 | 19:30 | 128 | 11:00 | Shahjadpur | 137 | 03:00 | 129 | 22:00
Haripur | 134 | 03:00 | 125 | 16:00 | Shahjibazar | 131 | 06:00 | 124 | 15:00
HaripurSBU | 134 | 03:00 | 125 | 16:00 | Shahmirpur | 134 | 22:00 | 128 | 11:00
Hasnabad | 138 | 03:00 | 128 | 12:00 | Shariatpur | 130 | 06:00 | 123 | 21:00
Hathazari | 135 | 19:00 | 130 | 11:00 | Sherpur | 130 | 18:30 | 114 | 01:00
Hatirjheel | 138 | 03:00 | 126 | 16:00 | Shikalbaha | 123 | 19:30 | 118 | 11:00
Ishurdi | 137 | 08:00 | 125 | 22:00 | Shikalbaha-230 | 135 | 19:00 | 130 | 09:00
Jaldhaka | 130 | 13:00 | 119 | 20:00 | Shitalakhya | 137 | 05:00 | 125 | 15:00
Jamalpur | 131 | 18:30 | 117 | 01:00 | Sholosohor | 133 | 20:00 | 128 | 12:00
Jashore | 130 | 08:00 | 113 | 22:00 | Shomvuganj | 128 | 17:00 | 117 | 21:00
Jhenaidah | 134 | 09:00 | 118 | 22:00 | Shyampur | 138 | 07:00 | 129 | 12:00
Jhenaidah-230 | 135 | 06:00 | 119 | 22:00 | Shyampur-230 | 139 | 06:00 | 130 | 12:00
Joydebpur | 125 | 05:00 | 113 | 17:00 | Siddhirganj | 134 | 03:00 | 126 | 11:00
Joypurhat | 134 | 11:00 | 122 | 21:00 | Sirajganj | 131 | 04:00 | 122 | 21:00
Juldah | 134 | 19:00 | 129 | 11:00 | Sonargaon | 131 | 07:00 | 123 | 12:00
Kabirpur | 135 | 00:00 | 118 | 11:00 | Sreemongol | 130 | 04:00 | 123 | 15:00
Kachua | 129 | 22:00 | 125 | 11:00 | Sreepur | 131 | 01:00 | 124 | 21:00
Kaliakoir | 139 | 02:00 | 126 | 15:00 | Srinagar | 140 | 05:00 | 130 | 15:00
Kaliganj | 134 | 04:00 | 118 | 22:00 | SSM | 138 | 00:00 | 128 | 11:00
Kallyanpur | 133 | 04:00 | 123 | 15:00 | Sunamganj | 123 | 05:00 | 114 | 19:00
Kalurghat | 134 | 19:30 | 130 | 11:00 | Sylhet | 128 | 05:00 | 123 | 19:00
Kamrangirchar | 140 | 01:00 | 121 | 12:00 | Sylhet_(South) | 128 | 06:00 | 122 | 23:00
Kaptai | 136 | 1:00 | 134 | 11:00 | Tangail | 127 | 05:00 | 117 | 15:00
Kasba | 128 | 06:00 | 121 | 16:00 | Taraganj | 131 | 13:00 | 120 | 20:00
Kazla | 135 | 04:00 | 124 | 13:00 | Tasnim | 132 | 04:00 | 123 | 12:00
Keranigonj | 141 | 06:00 | 130 | 16:00 | Thakurgaon | 134 | 13:00 | 124 | 20:00
Khagrachori | 131 | 01:00 | 129 | 11:00 | TK | 134 | 01:00 | 130 | 11:00
Khulna | 133 | 08:00 | 119 | 22:00 | Tongi | 141 | 04:00 | 125 | 11:00
Khulna(S) | 134 | 08:00 | 121 | 22:00 | Ullahpara | 133 | 05:00 | 124 | 21:00
Khulshi | 131 | 22:00 | 127 | 11:00 | Ullon | 138 | 04:00 | 125 | 12:00
Kishoreganj | 127 | 19:30 | 119 | 14:00 | Uttara | 137 | 02:00 | 119 | 12:00
Kodda | 137 | 00:00 | 122 | 11:00 | UttaraNew | 136 | 01:00 | 120 | 12:00
Korerhat | 133 | 01:00 | 129 | 11:00 | Zigatola | 141 | 01:00 | 130 | 16:00
KSRM | 133 | 18:30 | 129 | 10:00
Kulaura | 131 | 08:00 | 126 | 19:00
Kurigram | 130 | 17:00 | 113 | 20:00
Kushtia | 134 | 05:00 | 120 | 22:00
Laksam | 128 | 01:00 | 125 | 04:00
Lakshmipur | 124 | 01:00 | 122 | 15:00
Lalbag | 140 | 04:00 | 130 | 12:00
Lalmonirhat | 128 | 17:00 | 114 | 20:00
Madanganj | 134 | 07:00 | 125 | 12:00
Madaripur | 130 | 05:00 | 125 | 15:00
Madartek | 138 | 05:00 | 125 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division