## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-06-2026 | during | 28-06-2026 | during | 28-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 378 | 375 | 412 | 412 | 380 | 380 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 296 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 15 | 149.36 | 149.36 | 132 | 132 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 20 | 33 | 33 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 17 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 25 | 52.19 | 52.19 | 0 | 0 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 81 | 146 | 300 | 300 | 48 | 128 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 132 | 149 | 149 | 70 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 23 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 490 | 480 | 584 | 584 | 526 | 526 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 555 | 370 | 583 | 583 | 525 | 525 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 142 | 160 | 160 | 142 | 142 | Engine Problem
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2027 | 2357 | 5822.22 | 5792.22 | 2314 | 2585
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 6 | 50 | 50 | 6 | 19 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 89 | 92 | 100 | 100 | 100 | 100 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 30 | 55 | 40 | 56 | 40 | 56 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 33 | 0 | 51 | 0 | 51 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 38 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 5 | 10 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 18 | 48 | 108 | 108 | 30 | 80 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.33 | 0 | 2.04 | 0 | 2.04 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 54.36 | 54.36 | 54.36 | 0 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 110 | 110 | 17 | 17 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 38 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 720 | 1100 | 1224 | 1224 | 720 | 720 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 7 | 14 | 20 | 18 | 20 | 18 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 520 | 1135 | 1150 | 1150 | 1135 | 1135 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1795.33 | 2953.86 | 3840.9 | 3911.86 | 2463.54 | 2703.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 201 | 214 | 221.25 | 221.25 | 205.25 | 205.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 290 | 350.01 | 350.01 | 290 | 290 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 290 | 240 | 342.01 | 342.01 | 230 | 230 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 220 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 10 | 41.65 | 41.65 | 42 | 42 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 26 | 55 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 50 | 163 | 163 | 142 | 142 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 104 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 172 | 154 | 84 | 76 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 8 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 17 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 18 | 27 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 6 | 88 | 115 | 115 | 34 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 76 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1475 | 1522 | 2744.44 | 2686.44 | 1589.25 | 1925.45
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-06-2026 | during | 28-06-2026 | during | 28-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 21.3 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.1 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 67 | 97 | 70 | 90 | 70 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 58 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.01 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 190.41 | 172 | 486.4 | 446.5 | 199.9 | 177
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 28 | 28 | 28 | 28 | 28 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 151 | 148 | 163 | 163 | 163 | 163 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 142 | 143 | 145 | 145 | 145 | 145 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 82 | 83 | 83 | 53 | 53 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 100 | 102 | 102 | 102 | 102 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 285 | 319 | 320 | 320 | 320 | 320 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1132 | 1177 | 1257 | 1257 | 1173 | 1173
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 891 | 798 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 23 | 35 | 50 | 50 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 39.85 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 27 | 151 | 336 | 336 | 100 | 100 | Fuel shortage
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 392 | 450 | 450 | 450 | 560 | 560 | U-2 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1410.85 | 1487 | 2811 | 2726 | 1798 | 1713
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 1000 | 1000 | 1050 | 1050 | 1050 | 1050 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 48 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 62 | 65 | 65 | 65 | 65 | 65 | GT-1 & ST under maint
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1160 | 1165 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 272 | 284 | 307 | 307 | 287 | 287 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.31 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2747.31 | 2799 | 3147 | 3146 | 2840 | 2839
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 55.69 | 0 | 54 | 0 | 54 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 47 | 47 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 10 | 32 | 32 | 10 | 10 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 12 | 25 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 10 | 166 | 214 | 214 | 200 | 200 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 179 | 50 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 178 | 165 | 220 | 220 | 182 | 182 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 377 | 377 | 413.79 | 413.79 | 372.41 | 372.41 | AGC
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 83 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.24 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1479.54 | 1476.39 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 49.7 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2446.17 | 2484.39 | 3270.72 | 3050.12 | 2510.14 | 2451.54
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 35 | 37 | 40 | 40 | 46 | 46 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 175 | 180 | 200 | 200 | 200 | 200 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.3 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 95 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 167 | 0 | 110.6 | 0 | 110.6 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 501.3 | 346 | 648.6 | 502 | 521.6 | 410
System Total |  |  |  |  | 28843.2 | 29323.517 | 13725.37 | 15298.25 | 24028.28 | 23518.14 | 15409.43 | 15977.49
Forecast Scenario (28-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14780 |  | 2502.1 |  | 17400
|  |  |  | 1:00 | 14220 |  | 2530.75 |  | 16870
|  |  |  | 2:00 | 14110 |  | 2358.85 |  | 16580
|  |  |  | 3:00 | 14030 |  | 2186.95 |  | 16320
|  |  |  | 4:00 | 13990 |  | 2062.8 |  | 16150
|  |  |  | 5:00 | 13570 |  | 2253.8 |  | 15930
|  |  |  | 6:00 | 13270 |  | 2005.5 |  | 15370
|  |  |  | 7:00 | 13640 |  | 1575.75 |  | 15290
|  |  |  | 8:00 | 13710 |  | 1508.9 |  | 15290
|  |  |  | 9:00 | 13690 |  | 1680.8 |  | 15450
|  |  |  | 10:00 | 13360 |  | 1948.2 |  | 15400
|  |  |  | 11:00 | 13760 |  | 1699.9 |  | 15540
|  |  |  | 12:00 | 14200 |  | 1766.75 |  | 16050
|  |  |  | 13:00 | 14340 |  | 1719 |  | 16140
|  |  |  | 14:00 | 14330 |  | 1843.15 |  | 16260
|  |  |  | 15:00 | 14240 |  | 2177.4 |  | 16520
|  |  |  | 16:00 | 14230 |  | 2081.9 |  | 16410
|  |  |  | 17:00 | 14220 |  | 1804.95 |  | 16110
|  |  |  | 18:00 | 15100 |  | 668.5 |  | 15800
|  |  |  | 18:30 | 15200 |  | 668.5 |  | 15900
|  |  |  | 19:00 | 15230 |  | 1976.85 |  | 17300
|  |  |  | 19:30 | 15340 |  | 2444.8 |  | 17900
|  |  |  | 20:00 | 15410 |  | 2397.05 |  | 17920
|  |  |  | 21:00 | 15650 |  | 2053.25 |  | 17800
|  |  |  | 22:00 | 15360 |  | 2139.2 |  | 17600
|  |  |  | 23:00 | 15270 |  | 2034.15 |  | 17400
Probable Maximum Temperature: |  |  | 36.80°C
Probable Maximum Demand at Day Peak: |  |  | 16050.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2397
Probable Maximum Demand at Evening Peak: |  |  | 17920.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15650.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 343.71 MKWHr. |  | 500 | 160 | 300 | 377 | 180 | 280 | 140 | 270 | 190 | 2397
*** This report is generated digitally from Operation Information System (OIS) at 10:13 hrs on 28-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13725.37 | MW | 12:00 Hr. | Energy Generated |  |  | 340.1896 |  | MKWHr.
| Day Peak Demand |  |  | 14831.37 | MW | 12:00 Hr. | Energy Unserverd |  |  | 42.784 |  | MKWHr.
| Evening Peak Generation |  |  | 15298.25 | MW | 21:00 Hr. | Energy Demand |  |  | 382.9736 |  | MKWHr.
| Evening Peak Demand |  |  | 18301.25 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.4 |  | °C
| Minimum Generation of the Day |  |  | 13201.11 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 905.31 |  | MMCFD
| Maximum Generation of the Day |  |  | 15348.44 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 6.3833 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.8309 | 0 | 9.2833 | 0 | 0 | 0.21202 | 0 | 0 | 50.3262 | Gas | 127.6191 | Gas | 441453946.9695
| Chattogram Zone |  |  | 5.502 | 35.66 | 6.4611 | 0 | 2.133 | 0.14257 | 0 | 0.2424 | 50.1411 | Coal | 114.9338 | Coal | 762247972.588
| Cumilla Zone |  |  | 28.4156 | 0 | 3.1122 | 0 | 0 | 0.40062 | 3.9427 | 0 | 35.8711 | HFO | 28.4987 | HFO | 501981149.128
| Mymensingh Zone |  |  | 0.14304 | 0 | 2.9042 | 0 | 0 | 0.44985 | 0 | 0 | 3.4971 | HSD | 0.68573 | HSD | 13851685.4
| Sylhet Zone |  |  | 26.9731 | 0 | 0 | 0 | 0 | 0.065072 | 0 | 0 | 27.0382 | Hydro | 2.133 | Hydro | 213302
| Khulna Zone |  |  | 0 | 16.4 | 0.76179 | 0.68573 | 0 | 0.66816 | 21.9775 | 0 | 40.4931 | Solar | 4.7457 | Solar | 75436001.5312
| Barishal Zone |  |  | 6.7742 | 57.4267 | 1.1666 | 0 | 0 | 0.003955 | 0 | 0 | 65.3715 | Import | 61.3311 | Import | 372790435.39
| Rajshahi Zone |  |  | 18.9803 | 0 | 2.1407 | 0 | 0 | 1.5948 | 35.4109 | 0 | 58.1267 | Wind | 0.2424 | Wind | 3565704
| Rangpur Zone |  |  | 0 | 5.4471 | 2.6688 | 0 | 0 | 1.2086 | 0 | 0 | 9.3245
| Total |  |  | 127.6191 | 114.9338 | 28.4987 | 0.68573 | 2.133 | 4.7457 | 61.3311 | 0.2424 | 340.1896
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 441453946.9695 |  | Hydro | 213302
|  |  |  | Coal | 762247972.588 |  | Solar | 75436001.5312
|  |  |  | HFO | 501981149.128 |  | Import | 372790435.39
|  |  |  | HSD | 13851685.4 |  | Wind | 3565704
[5 empty] | Total: | 217,15,40,197 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.0655 | Peak Hr Flow | 798.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51918000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 35.4109 | Peak Hr Flow | 1476.39 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2193 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.9427 | Peak Hr Flow | 154.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 3010 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 60.4191 | Peak Hr Flow | 2428.39 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 538 |  | 6313
|  |  |  | Chattogram |  | 162 |  | 1588
|  |  |  | Cumilla |  | 343 |  | 1712
|  |  |  | Mymensingh |  | 519 |  | 1550
|  |  |  | Sylhet |  | 247 |  | 784
|  |  |  | Khulna |  | 375 |  | 2081
|  |  |  | Barishal |  | 142 |  | 570
|  |  |  | Rajshahi |  | 352 |  | 1891
|  |  |  | Rangpur |  | 196 |  | 1136
|  |  |  | Total |  | 2874 |  | 17625
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Tangail Palli Power Gen 22 MW |  |  | 22
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 72
|  |  |  | Total Unavailable Capacity |  |  |  | 372
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:11 | 10:34 | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to 33 KV PDB Salauddin Feeder | [7 empty] | 25.0MW load
|  |  | Maintenance Work | [7 empty] | interrup.
| 08:11 | 10:34 | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to 33 KV PDB Salauddin Feeder | [7 empty] | 25.0MW load
|  |  | Maintenance Work | [7 empty] | interrup.
|  | 08:20 | Chandpur 132/33kV S/S 402T (T-01) HT is restored.
|  | 08:20 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
|  | 08:20 | Chandpur 132/33kV S/S 33 kV T-1 Section is restored.
| 08:20 |  | Chandpur 132/33kV S/S 422T(T-5) LT Scheduled S/D
| 08:57 | 19:32 | Korerhat 400/230/132kV S/S ATR-3(7103T) LT Project Work S/D Due to Project work
| 08:59 | 19:30 | Korerhat 400/230/132kV S/S ATR-4(7403T) HT Project Work S/D Due to Project work
| 09:15 | 10:56 | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to 33 kv Jhallokati Wzpdco feeder | [7 empty] | 40.0MW load
|  |  | red hot maintenance Work | [7 empty] | interrup.
| 09:16 | 10:54 | Barishal 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to 33 kv Jhalokati wzpdco feeder | [7 empty] | 40.0MW load
|  |  | red hot maintenance work. | [7 empty] | interrup.
| 09:30 | 10:49 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Scheduled S/D Due to Project Work
|  | 09:33 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 is restored.
| 09:56 | 12:20 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Tripped showing REF 615 relays Due to BPDB | [7 empty] | 10.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 10:00 |  | Rampal 1320 MW (BIFPCL) unit-2 was forced shutdown due to a problem with boiler feed
water pump.
| 10:03 | 16:25 | Madunaghat 132/33kV S/S TR-2(517T) LT Forced S/D Due to 33 kV grounding recovery and high
temperature maintenance.
| 10:04 | 16:27 | Madunaghat 132/33kV S/S TR-2(517T) HT Forced S/D Due to 33 kV grounding recovery and high
temperature maintenance.
| 10:12 | 18:18 | BIPTC S/S Baharampur-4 Scheduled S/D Due to Shutdown is taken by baharampur end.
| 10:55 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
| 10:55 |  | Sirajganj unit-1 GT was sync.
| 12:00 |  | Day Peak Generation: 13,726 MW.
| 12:44 | 18:56 | Joypurhat-Naogaon 132kV Ckt-1 Scheduled S/D from Joypurhat 132/33kV end Due to S/D taken
at Noagaon ss end
| 14:12 | 21:16 | Joypurhat 132/33kV S/S Patnitola Ckt.-1 Scheduled S/D Due to Poject Work
| 14:13 | 21:17 | Joypurhat 132/33kV S/S Patnitola Ckt.-2 Scheduled S/D Due to Poject Work
|  | 15:00 | Bhulta 132/33kV S/S GT2 HT is restored.
| 15:31 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 15:55 | 16:13 | Cox'sbazar-Dohazari 132 kV Ckt-2 Tripped from Coxsbazar 132/33kV end showing Distance
relays. and from Dohazari 132/33kV end showing General trip, R phase trip, Zone-01 trip
relays.
|  | 17:28 | Jhenaidah 230/132kV S/S 230 kV Bus is restored.
|  | 18:04 | Jhenaidah-Khulna 230kV Ckt-1 is restored.
|  | 19:30 | Korerhat 400/230/132kV S/S ATR-4(7403T) HT is restored.
| 20:56 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- ST
| 21:10 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- GT
| 21:14 | 21:19 | Sylhet_(South) 132/33kV S/S Trafo-2 LT Tripped showing BCPU relay. relays Due to 33 kv | [7 empty] | 41.0MW load
|  |  | Moglabazar feeder breaker insulator crack. and 33 kv gotatikor feeder fault. | [7 empty] | interrup.
| 21:14 | 21:19 | Sylhet_(South) 132/33kV S/S Trafo-1 LT Tripped showing BCPU relay. relays Due to 33 kv | [7 empty] | 41.0MW load
|  |  | Moglabazar feeder breaker insulator crack. and 33 kv gotatikor feeder fault. | [7 empty] | interrup.
|  | 21:15 | Gopalganj 132/33kV S/S Gallamari-1 is restored.
|  | 21:15 | Gopalganj 132/33kV S/S Gallamari-2 is restored.
| 21:15 | 21:25 | Chattak-Sylhet 132 kV Ckt-2 Tripped from Sylhet 132/33kV end showing Distance relays Due | [7 empty] | 40.0MW load
|  |  | to Distance protection Operated | [7 empty] | interrup. Sylhet
132/33kV end
|  | 21:16 | Gallamari- Khulna (S) 132kV Ckt-1 is restored.
|  | 21:16 | Gallamari- Khulna (S) 132kV Ckt-2 is restored.
| 21:20 | 21:48 | Sylhet_(South) 132/33kV S/S Trafo-2 LT Forced S/D Due to 33 kv Moglabazar feeder breaker | [7 empty] | 41.0MW load
|  |  | insulator crack. and 33 kv gotatikor feeder fault. | [7 empty] | interrup.
| 21:20 | 21:47 | Sylhet_(South) 132/33kV S/S Trafo-1 LT Forced S/D Due to 33 kv Moglabazar feeder breaker | [7 empty] | 41.0MW load
|  |  | insulator crack. and 33 kv gotatikor feeder fault. | [7 empty] | interrup.
| 03:00 |  | Minimum Generation: 13712 MW.
| 06:05 |  | Shyampur 230/132kV S/S 230 kV APR (D04) Scheduled S/D Due to NLDC Requirements
| 07:05 | 07:24 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to Due to PBS 33KV bus coupler bypass | [7 empty] | 100.0MW load
|  |  | under T2. | [7 empty] | interrup.
|  | 07:30 | Sonargaon 132/33kV S/S Tr-1 HT is restored.
|  | 07:42 | Sonargaon 132/33kV S/S Tr-1 LT is restored.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 375 | 9000000 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1273060 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 296 | 7284312 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 219960 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 15 | 223680 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 531735 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270277 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 501600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 17 | 374040 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 50880 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 146 | 2639815 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1398240 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 172800 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1048320 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 212025 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 110520 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 480 | 11730454.55 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 370 | 11940455 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 1344000 | Engine Problem
Dhaka Area Total |  |  |  |  | 6668.974 | 2357 | 50326173.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 156709.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 118800 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 151200 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 92 | 2133020 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5136741 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 12545 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 55 | 900432 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 230132 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 298560 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 365280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 48 | 732480 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23766 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 381382 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 331689 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 424000 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 288960 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2553000 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | Under Maintenance
55 | SS Power |  | IPP | 2*660 | 1224 | 1100 | 19063634 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 14 | 242400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1135 | 16596363.64 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 2953.86 | 50141094.44
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 214 | 5064000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7412500 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 240 | 6700000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5677000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 47952 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1226600 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 55 | 953454 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 96320 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1922741 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 104 | 1128000 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 154 | 3942720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 364780 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 232680 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 88 | 701760 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 400618 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1522 | 35871125
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 138772 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 143040 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 97 | 1512000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 1284000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 296130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 32640 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 75600 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 172 | 3497132
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 65072 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 670000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 148 | 3492654.55 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 143 | 3267000 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 707520 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1320000 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2403950 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 345024 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7592000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 319 | 7175000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1177 | 27038220.55
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 798 | 21065455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 35 | 720896 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 40896 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 668160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 151 | 685727 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 450 | 16399997 | U#2 under shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1487 | 40493131
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1000 | 22509090 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 751391 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 65 | 1526000 | GT-1 & ST under maint
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1165 | 28219636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5248230 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 415200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 284 | 6698000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3955 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2799 | 65371502.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 399656 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 47 | 178090 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 10 | 36119 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 403635 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 166 | 1256636 | Minor Inspection
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 50 | 3871764 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 165 | 4487927 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 377 | 9363927 | AGC
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 49458 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 83 | 483488 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 549984 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 439968 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 36420 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1476.39 | 35410909 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 375728 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 783030 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2484.39 | 58126739
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 37 | 853091 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4594000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 375120 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 33925.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 2293643 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 190437 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 984240 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 346 | 9324456.56
Eastern Grid Total |  |  |  |  | 17438.042 | 8181.86 | 166873745.54
Western Grid Total |  |  |  |  | 11885.475 | 7116.39 | 173315828.92
National Grid Total |  |  |  |  | 29323.517 | 15298.25 | 340189574.46
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-06-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10185.72 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4613.4 | MW
i) Dhaka area |  |  | 5775.42 |  | MW | i) Khulna area |  |  |  | 1706.4 | MW
ii) Chattogram area |  |  | 1473.3 |  | MW | ii) Barishal area |  |  |  | 427.6 | MW
iii) Cumilla area |  |  | 1369 |  | MW | iii) Rajshahi area |  |  |  | 1539.4 | MW
iv) Mymensingh area |  |  | 1031 |  | MW | iv) Rangpur area |  |  |  | 940 | MW
v) Sylhet area |  |  | 537 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14799.12 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 145 | 11:00 | 133 | Narshingdi | 182 | 07:00 | 199 | UttaraNew | 61 | 23:00
2 | AKSML | 116 | 15:00 | 68 | Hasnabad | 97 | 18:30 | 134 | Natore | 140 | 07:00 | 200 | Zigatola | 100 | 15:00
3 | Aftabnagar | 48 | 13:00 | 69 | Hathazari | 83 | 00:00 | 135 | Nawabganj | 70.8 | 19:00
4 | Agargaon | 121 | 00:00 | 70 | Hatirjheel | 42 | 13:00 | 136 | Netrakona | 108 | 23:00
5 | Agrabad | 54 | 18:30 | 71 | Ishurdi | 77 | 19:30 | 137 | New | 78 | 15:00
6 | Amnura | 32 | 00:00 | 72 | Jaldhaka | 71 | 23:00 | 138 | Niamatpur | 82 | 00:00
7 | Ashuganj | 97 | 23:00 | 73 | Jamalpur | 98 | 22:00 | 139 | Noapara | 45 | 07:00
8 | BSRM | 174 | 05:00 | 74 | Jashore | 173 | 21:00 | 140 | PHP | 14 | 12:00
9 | Bagerhat | 86 | 19:30 | 75 | Jhenaidah | 98 | 21:00 | 141 | Pabna | 99 | 21:00
10 | Bajitpur | 82 | 06:00 | 76 | Joydebpur | 140 | 09:00 | 142 | Palashbari | 144 | 00:00
11 | Bakerganj | 15.8 | 00:00 | 77 | Joypurhat | 58 | 00:00 | 143 | Panchagarh | 77 | 19:30
12 | Bakulia | 103 | 20:00 | 78 | Juldah | 19.5 | 10:00 | 144 | Patiya | 11 | 00:00
13 | Banani | 60 | 12:00 | 79 | KSRM | 20 | 06:00 | 145 | Patuakhali | 73.8 | 00:00
14 | Bangabhaban | 8 | 11:00 | 80 | Kabirpur | 207 | 20:00 | 146 | Payra | 38 | 00:00
15 | Barapukuria | 64 | 13:00 | 81 | Kachua | 90 | 06:00 | 147 | Postogola | 68 | 23:00
16 | Barguna | 28 | 19:00 | 82 | Kaliganj | 38 | 21:00 | 148 | Pubail | 36 | 07:00
17 | Barishal | 104 | 00:00 | 83 | Kallyanpur | 135 | 00:00 | 149 | Purbachal | 32 | 14:00
18 | Barishal-230 | 110 | 00:00 | 84 | Kalurghat | 39 | 20:00 | 150 | Purbasadipur | 140 | 13:00
19 | Baroaulia | 55 | 13:00 | 85 | Kamrangirchar | 81 | 12:00 | 151 | Rahanpur | 41 | 05:00
20 | Baroirhat | 67 | 22:00 | 86 | Kaptai | N/A | N/A | 152 | Rahim | 33 | 11:00
21 | Bashundhara | 219 | 19:30 | 87 | Kasba | 34 | 04:00 | 153 | Rajbari | 90 | 00:00
22 | BashundharaCement | 1 | 11:00 | 88 | Kazla | 123 | 16:00 | 154 | Rajendrapur | 114 | 08:00
23 | Beanibazar | 66 | 05:00 | 89 | Keranigonj | 93 | 19:00 | 155 | Rajshahi | 150 | 13:00
24 | Benapole | 62 | 12:00 | 90 | Khagrachori | 36 | 19:30 | 156 | Rajshahi-230 | 102 | 13:00
25 | Bhaluka | 127 | 21:00 | 91 | Khulna | 58 | 12:00 | 157 | Ramganj | 102 | 00:00
26 | Bhandaria | 62 | 00:00 | 92 | Khulshi | 200 | 22:00 | 158 | Rampur | 42 | 21:00
27 | Bhangura | 46 | 19:30 | 93 | Kishoreganj | 123 | 18:30 | 159 | Rangamati | 15 | 11:00
28 | Bheramara(GK) | 63 | 01:00 | 94 | Kodda | 295 | 21:00 | 160 | Rangpur | 126 | 00:00
29 | Bhulta | 232 | 19:30 | 95 | Kulaura | 51 | 00:00 | 161 | Ruppur | 3 | 14:00
30 | Bog-Sherpur | 68 | 04:00 | 96 | Kurigram | 73 | 07:00 | 162 | SSM | 0 | 00:00
31 | Bogura | 202 | 22:00 | 97 | Kushtia | 156 | 18:30 | 163 | Saidpur | 107 | 22:00
32 | Borhanuddin | 82 | 00:00 | 98 | Laksam | 36 | 19:00 | 164 | Santhia | 44 | 19:30
33 | Brahmanbaria | 124 | 22:00 | 99 | Lakshmipur | 43 | 23:00 | 165 | Satkhira | 149 | 00:00
34 | Cantonment | 140 | 13:00 | 100 | Lalbag | 78 | 19:00 | 166 | Satmasjid | 115 | 19:30
35 | Chandina | 38 | 21:00 | 101 | Lalmonirhat | 64 | 05:00 | 167 | Savar | 224 | 18:30
36 | Chandpur | 76 | 09:00 | 102 | MI_Cement | 14.2 | 08:00 | 168 | SevenRings | 15.38 | 11:00
37 | Chandraghona | 35 | 23:00 | 103 | Madanganj | 50 | 22:00 | 169 | ShahCement | 28 | 16:00
38 | Chapai | 81 | 07:00 | 104 | Madaripur | 122 | 00:00 | 170 | Shahjadpur | 76 | 18:30
39 | Charfasson | 40 | 00:00 | 105 | Madartek | 94 | 23:00 | 171 | Shahjibazar | 122 | 00:00
40 | Charsaidpur | 41 | 16:00 | 106 | Madunaghat | 55 | 19:30 | 172 | Shahmirpur | 47 | 22:00
41 | Chauddagram | 65 | 00:00 | 107 | Magura | 62 | 06:00 | 173 | Shariatpur | 99 | 01:00
42 | Chhatak | 32 | 00:00 | 108 | Mahasthangarh | 74 | 06:00 | 174 | Sherpur | 126 | 22:00
43 | Chowmuhani | 157 | 22:00 | 109 | Maijdee | 38 | 05:00 | 175 | Shikalbaha | 30 | 21:00
44 | Chuadanga | 132 | 12:00 | 110 | Manikganj | 118 | 13:00 | 176 | Shitalakhya | 84.6 | 16:00
45 | Coxsbazar | 138 | 00:00 | 111 | Maniknagar | 80 | 23:00 | 177 | Sholosohor | 44 | 19:00
46 | Cumilla(N) | 119 | 19:00 | 112 | Matarbari | 50 | 04:00 | 178 | Shomvuganj | 28 | 21:00
47 | Cumilla(S) | 193 | 16:00 | 113 | Matuail | 78 | 12:00 | 179 | Shyampur | 190 | 13:00
48 | Daganbhuiyan | 36 | 20:00 | 114 | Metrorail_Motijheel | 22 | 10:00 | 180 | Siddhirganj | 142 | 15:00
49 | Daudkandi | 143 | 08:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Sirajganj | 128 | 21:00
50 | DhakaUniversity | 86 | 13:00 | 116 | Millgate | 138 | 15:00 | 182 | Sitakunda | 21 | 21:00
51 | Dhamrai | 93 | 20:00 | 117 | Mirpur | 170 | 19:30 | 183 | Sonargaon | 101 | 16:00
52 | Dhanmondi | 121.5 | 13:00 | 118 | Mirsorai | 43 | 13:00 | 184 | Sreemongol | 70 | 04:00
53 | Dohazari | 92 | 01:00 | 119 | Mirzapur | 35 | 19:00 | 185 | Sreepur | 129 | 18:30
54 | Faridpur | 184 | 00:00 | 120 | Mithapukur | 72 | 08:00 | 186 | Srinagar | 57.97 | 19:00
55 | Fatullah | 107 | 10:00 | 121 | Modern | N/A | N/A | 187 | Sunamganj | 47 | 23:00
56 | Fenchuganj | 43 | 21:00 | 122 | Mogbazar | 105.4 | 12:00 | 188 | Sylhet | 127 | 22:00
57 | Feni | 100 | 00:00 | 123 | Mongla | 42 | 19:30 | 189 | Sylhet_(South) | 64 | 18:00
58 | GPH | 4 | 15:00 | 124 | Motijheel | 52 | 13:00 | 190 | TK | 25 | 01:00
59 | Ghatail | 72 | 21:00 | 125 | Muktagacha | 41 | 14:00 | 191 | Tangail | 170 | 22:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 112 | 07:00 | 192 | Taraganj | 25 | 13:00
61 | Ghorashal-230 | 118 | 18:30 | 127 | Muradnagar | 45 | 06:00 | 193 | Tasnim | 38 | 18:00
62 | Goalpara | 39 | 03:00 | 128 | Mymensingh | 181 | 22:00 | 194 | Thakurgaon | 93 | 00:00
63 | Gollamari | 124 | 00:00 | 129 | Nabinagar | 126 | 11:00 | 195 | Tongi | 147 | 11:00
64 | Gopalganj | 123.4 | 00:00 | 130 | Naogaon | 140 | 14:00 | 196 | Ullahpara | 38 | 14:00
65 | Gulshan | 116 | 13:00 | 131 | Narail | 63 | 22:00 | 197 | Ullon | 65 | 23:00
66 | Halishahar | 107 | 16:00 | 132 | Narinda | 76 | 13:00 | 198 | Uttara | 106 | 16:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14749.76 | 2275 |  | 17127.14
1:00 | 14331.75 | 2284 |  | 16718.75
2:00 | 14156.73 | 2277 |  | 16535.73
3:00 | 13951.42 | 2156 |  | 16204.42
4:00 | 13893.95 | 2050 |  | 16035.95
5:00 | 13818.62 | 1989 |  | 15897.62
6:00 | 13469.79 | 1651 |  | 15195.09
7:00 | 13598.5 | 861 |  | 14498.5
8:00 | 13586.07 | 655 |  | 14270.55
9:00 | 13201.11 | 643 |  | 13873.05
10:00 | 13286.22 | 548 |  | 13858.88
11:00 | 13278.25 | 789 |  | 14102.76
12:00 | 13725.37 | 1058 |  | 14831.37
13:00 | 13791.69 | 1308 |  | 15158.69
14:00 | 13738.03 | 1739 |  | 15555.03
15:00 | 13955.67 | 2069 |  | 16117.67
16:00 | 13811.88 | 2054 |  | 15957.88
17:00 | 13940.96 | 2048 |  | 16080.96
18:00 | 13966.9 | 1808 |  | 15855.9
19:00 | 14964.92 | 2127 |  | 17187.64
19:30 | 15022.96 | 2630 |  | 17770.96
20:00 | 14922.19 | 2685 |  | 17728.19
21:00 | 15298.25 | 2874 |  | 18301.25
22:00 | 15348.44 | 2386 |  | 17841.44
23:00 | 15268.26 | 2450 |  | 17828.26
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 27-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 162 | 16 | 520 | 92 | 1946 | 342 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 139 | 2 | 510 | 90 | 2016 | 354
2:00 | 134 | 10 | 556 | 94 | 2040 | 358 |  | Import | 0
3:00 | 134 | 14 | 554 | 104 | 2048 | 360
4:00 | 136 | 5 | 558 | 88 | 2072 | 356 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 147 | 11 | 566 | 112 | 2120 | 400
6:00 | 158 | 18 | 586 | 118 | 2120 | 400 |  | Import | 0
7:00 | 154 | 12 | 596 | 124 | 2090 | 430
8:00 | 187 | 33 | 640 | 140 | 2118 | 578 | Sirajganj-Sreepur Ckt-1 | Export | 3525000
9:00 | 218 | 56 | 666 | 148 | 2088 | 610
10:00 | 219 | 52 | 712 | 164 | 1972 | 566 |  | Import | 0
11:00 | 217 | 48 | 696 | 162 | 1960 | 544
12:00 | 197 | 39 | 640 | 154 | 1970 | 500 | Sirajganj-Sreepur Ckt-2 | Export | 3533000
13:00 | 216 | 57 | 688 | 164 | 2106 | 560
14:00 | 193 | 45 | 622 | 154 | 1970 | 528 |  | Import | 0
15:00 | 202 | 56 | 656 | 172 | 1934 | 512
16:00 | 187 | 43 | 620 | 150 | 1856 | 514 | Gopalganj-Aminbazar Ckt-1 | Export | 22410000
17:00 | 180 | 37 | 634 | 174 | 1852 | 496
18:00 | 176 | 36 | 616 | 136 | 1780 | 482 |  | Import | 0
18:30 | 188 | 52 | 630 | 180 | 1800 | 526
19:00 | 180 | 45 | 600 | 154 | 1736 | 516 | Gopalganj-Aminbazar Ckt-2 | Export | 22450000
19:30 | 162 | 35 | 550 | 120 | 1690 | 508
20:00 | 155 | 38 | 500 | 108 | 1610 | 478 |  | Import | 0
21:00 | 131 | 37 | 462 | 158 | 1600 | 472
22:00 | 131 | 33 | 460 | 162 | 1470 | 424 |  | Total Export | 51918000
23:00 | 124 | 30 | 434 | 156 | 1484 | 434 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6996 | 7753.76 | 14749.76 | DAILY GENERATION CURVE
00:30 | 6888.5 | 7652.255 | 14540.755
01:00 | 6781 | 7550.75 | 14331.75 | 27-06-2026
01:30 | 6723.5 | 7520.74 | 14244.24
02:00 | 6666 | 7490.73 | 14156.73
02:30 | 6571 | 7483.075 | 14054.075
03:00 | 6476 | 7475.42 | 13951.42
03:30 | 6432.5 | 7490.185 | 13922.685
04:00 | 6389 | 7504.95 | 13893.95
04:30 | 6344 | 7512.285 | 13856.285
05:00 | 6299 | 7519.62 | 13818.62
05:30 | 6212.46 | 7431.745 | 13644.205
06:00 | 6125.92 | 7343.87 | 13469.79
06:30 | 6134.395 | 7399.75 | 13534.145
07:00 | 6142.87 | 7455.63 | 13598.5
07:30 | 6162.615 | 7429.67 | 13592.285
08:00 | 6182.36 | 7403.71 | 13586.07
08:30 | 6188.94 | 7204.65 | 13393.59
09:00 | 6195.52 | 7005.59 | 13201.11
09:30 | 6334.71 | 6908.955 | 13243.665
10:00 | 6473.9 | 6812.32 | 13286.22
10:30 | 6459.84 | 6822.395 | 13282.235
11:00 | 6445.78 | 6832.47 | 13278.25
11:30 | 6532.76 | 6969.05 | 13501.81
12:00 | 6619.74 | 7105.63 | 13725.37
12:30 | 6641.63 | 7116.9 | 13758.53
13:00 | 6663.52 | 7128.17 | 13791.69
13:30 | 6697.29 | 7067.57 | 13764.86
14:00 | 6731.06 | 7006.97 | 13738.03
14:30 | 6814.57 | 7032.28 | 13846.85
15:00 | 6898.08 | 7057.59 | 13955.67
15:30 | 6883.74 | 7000.035 | 13883.775
16:00 | 6869.4 | 6942.48 | 13811.88
16:30 | 6971.285 | 6905.135 | 13876.42
17:00 | 7073.17 | 6867.79 | 13940.96
17:30 | 7143.905 | 6810.025 | 13953.93
18:00 | 7214.64 | 6752.26 | 13966.9
18:30 | 7535.57 | 6930.34 | 14465.91
19:00 | 7856.5 | 7108.42 | 14964.92
19:30 | 7950.86 | 7072.1 | 15022.96
20:00 | 7974.86 | 6947.33 | 14922.19
20:30 | 8078.36 | 7031.86 | 15110.22 |  | Executive Engineer
21:00 | 8181.86 | 7116.39 | 15298.25 |  | Network Operation Division
21:30 | 8215.18 | 7108.165 | 15323.345
22:00 | 8248.5 | 7099.94 | 15348.44
22:30 | 8272 | 7036.35 | 15308.35
23:00 | 8295.5 | 6972.76 | 15268.26

## En-Curve
QF-LDC-12
Date | 27-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3375 | 1900 | 902 | 38 | 168 | 1482.76 | 87 | 5175 | 0 | 302 | 1314 | 0 | 0 | 6 | 2275 | DAILY ENERGY CURVE
00:30 | 3381 | 1909.5 | 902 | 38 | 167 | 1479.255 | 87 | 5106.5 | 0 | 248 | 1215.5 | 0 | 0 | 7 | 2279.5 | 27-06-2026
01:00 | 3387 | 1919 | 902 | 38 | 166 | 1475.75 | 87 | 5038 | 0 | 194 | 1117 | 0 | 0 | 8 | 2284
01:30 | 3435.5 | 1938 | 863 | 38 | 165 | 1479.24 | 87 | 5042.5 | 0 | 173.5 | 1016 | 0 | 0 | 6.5 | 2280.5 | Energy Generated | 340.1896 |  | MKWHr
02:00 | 3484 | 1957 | 824 | 38 | 164 | 1482.73 | 87 | 5047 | 0 | 153 | 915 | 0 | 0 | 5 | 2277 | Energy not Served | 42.784 |  | MKWHr
02:30 | 3486 | 1964.5 | 824 | 38 | 160 | 1483.075 | 88 | 5019 | 0 | 143 | 843 | 0 | 0 | 5.5 | 2216.5 | Total Energy Requirement | 382.9736 |  | MKWHr
03:00 | 3488 | 1972 | 824 | 38 | 156 | 1483.42 | 89 | 4991 | 0 | 133 | 771 | 0 | 0 | 6 | 2156
03:30 | 3474 | 1941.5 | 857 | 38 | 156 | 1487.185 | 89 | 4985.5 | 0 | 137.5 | 749 | 0 | 0 | 8 | 2103
04:00 | 3460 | 1911 | 890 | 38 | 156 | 1490.95 | 89 | 4980 | 0 | 142 | 727 | 0 | 0 | 10 | 2050
04:30 | 3468 | 1902.5 | 890 | 38 | 153 | 1486.285 | 89 | 4962 | 0 | 142 | 717.5 | 0 | 0 | 8 | 2019.5
05:00 | 3476 | 1894 | 890 | 38 | 150 | 1481.62 | 89 | 4944 | 0 | 142 | 708 | 0 | 0 | 6 | 1989
05:30 | 3445 | 1811 | 890 | 38 | 141 | 1483.19 | 90 | 4860.5 | 16.015 | 142 | 719 | 0 | 0 | 8.5 | 1820
06:00 | 3414 | 1728 | 890 | 38 | 132 | 1484.76 | 91 | 4777 | 32.03 | 142 | 730 | 0 | 0 | 11 | 1651
06:30 | 3439 | 1709 | 890 | 38 | 137 | 1484.965 | 91 | 4767.5 | 81.68 | 150 | 738 | 0 | 0 | 8 | 1256
07:00 | 3464 | 1690 | 890 | 38 | 142 | 1485.17 | 91 | 4758 | 131.33 | 158 | 746 | 0 | 0 | 5 | 861
07:30 | 3446 | 1697.5 | 890 | 38 | 149 | 1486.365 | 91 | 4720 | 210.42 | 147.5 | 713.5 | 0 | 0 | 3 | 758
08:00 | 3428 | 1705 | 890 | 38 | 156 | 1487.56 | 91 | 4682 | 289.51 | 137 | 681 | 0 | 0 | 1 | 655
08:30 | 3413 | 1712.25 | 889.5 | 38 | 159 | 1453.225 | 91 | 4490.5 | 338.615 | 135 | 673 | 0 | 0 | 0.5 | 649
09:00 | 3398 | 1719.5 | 889 | 38 | 162 | 1418.89 | 91 | 4299 | 387.72 | 133 | 665 | 0 | 0 | 0 | 643
09:30 | 3426 | 1822 | 889.5 | 38 | 160 | 1415.835 | 92 | 4189 | 465.33 | 122.5 | 623.5 | 0 | 0 | 0 | 595.5
10:00 | 3454 | 1924.5 | 890 | 38 | 158 | 1412.78 | 93 | 4079 | 542.94 | 112 | 582 | 0 | 0 | 0 | 548
10:30 | 3442.5 | 1925 | 890 | 38 | 163 | 1418.175 | 91 | 4024.5 | 572.06 | 104 | 614 | 0 | 0 | 0 | 668.5
11:00 | 3431 | 1925.5 | 890 | 38 | 168 | 1423.57 | 89 | 3970 | 601.18 | 96 | 646 | 0 | 0 | 0 | 789
11:30 | 3411 | 1918.25 | 890.5 | 38 | 170 | 1451.555 | 89 | 4122 | 617.505 | 89 | 688 | 13.5 | 0 | 3.5 | 923.5
12:00 | 3391 | 1911 | 891 | 38 | 172 | 1479.54 | 89 | 4274 | 633.83 | 82 | 730 | 27 | 0 | 7 | 1058
12:30 | 3360.5 | 1914 | 890.5 | 38 | 174 | 1474.26 | 89 | 4339.5 | 622.27 | 85.5 | 752.5 | 13.5 | 0 | 5 | 1183
13:00 | 3330 | 1917 | 890 | 38 | 176 | 1468.98 | 89 | 4405 | 610.71 | 89 | 775 | 0 | 0 | 3 | 1308
13:30 | 3319 | 1877.75 | 890 | 38 | 174 | 1479.145 | 86 | 4447.5 | 568.465 | 99 | 763 | 16 | 0 | 7 | 1523.5
14:00 | 3308 | 1838.5 | 890 | 38 | 172 | 1489.31 | 83 | 4490 | 526.22 | 109 | 751 | 32 | 0 | 11 | 1739
14:30 | 3330 | 1904.5 | 890 | 38 | 176 | 1487.715 | 84 | 4493.5 | 511.135 | 115 | 767.5 | 31 | 0 | 18.5 | 1904
15:00 | 3352 | 1970.5 | 890 | 38 | 180 | 1486.12 | 85 | 4497 | 496.05 | 121 | 784 | 30 | 0 | 26 | 2069
15:30 | 3355 | 1932 | 890 | 38 | 186 | 1484.645 | 86 | 4521.5 | 397.63 | 132 | 804 | 30 | 0 | 27 | 2061.5
16:00 | 3358 | 1893.5 | 890 | 38 | 192 | 1483.17 | 87 | 4546 | 299.21 | 143 | 824 | 30 | 0 | 28 | 2054
16:30 | 3377.5 | 1895 | 890 | 38 | 183 | 1479.515 | 88 | 4622.5 | 228.905 | 149 | 869 | 33 | 0 | 23 | 2051
17:00 | 3397 | 1896.5 | 890 | 38 | 174 | 1475.86 | 89 | 4699 | 158.6 | 155 | 914 | 36 | 0 | 18 | 2048
17:30 | 3367.5 | 1812.25 | 890 | 38 | 170 | 1472.27 | 89 | 4695.5 | 101.91 | 187.5 | 1041 | 69 | 0 | 20 | 1928
18:00 | 3338 | 1728 | 890 | 38 | 166 | 1468.68 | 89 | 4692 | 45.22 | 220 | 1168 | 102 | 0 | 22 | 1808
18:30 | 3468.5 | 1758.5 | 890 | 38 | 179 | 1474.05 | 89 | 4803 | 22.61 | 335 | 1326.25 | 66 | 0 | 16 | 1967.5
19:00 | 3599 | 1789 | 890 | 38 | 192 | 1479.42 | 89 | 4914 | 0 | 450 | 1484.5 | 30 | 0 | 10 | 2127
19:30 | 3486 | 1731 | 892 | 38 | 158 | 1476.1 | 91 | 4904 | 0 | 446 | 1690.86 | 100 | 0 | 10 | 2630
20:00 | 3471 | 1633 | 892 | 38 | 152 | 1476.33 | 91 | 4846 | 0 | 466 | 1692.86 | 150 | 0 | 14 | 2685
20:30 | 3413 | 1688.5 | 845 | 38 | 153 | 1476.36 | 91.5 | 5098.5 | 0 | 484 | 1657.86 | 150.5 | 0 | 14 | 2779.5
21:00 | 3355 | 1744 | 798 | 38 | 154 | 1476.39 | 92 | 5351 | 0 | 502 | 1622.86 | 151 | 0 | 14 | 2874
21:30 | 3328 | 1762.5 | 798 | 38 | 160 | 1482.165 | 92 | 5437 | 0 | 476.5 | 1585.18 | 151 | 0 | 13 | 2630
22:00 | 3301 | 1781 | 798 | 38 | 166 | 1487.94 | 92 | 5523 | 0 | 451 | 1547.5 | 151 | 0 | 12 | 2386
22:30 | 3314 | 1823 | 798 | 38 | 171 | 1485.85 | 91.5 | 5543 | 0 | 440.5 | 1518.5 | 75.5 | 0 | 9.5 | 2418
23:00 | 3327 | 1865 | 798 | 38 | 176 | 1483.76 | 91 | 5563 | 0 | 430 | 1489.5 | 0 | 0 | 7 | 2450
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 27-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 372 | 09:00 | 361 | 13:00 | Madunaghat | 395 | 00:00 | 386 | 23:00
Amtali | 408 | 09:00 | 401 | 13:00 | Meghnaghat | 379 | 06:00 | 367 | 19:00
Ashuganj | 366 | 06:00 | 352 | 14:00 | Payra | 410 | 09:00 | 404 | 13:00
Bhulta | 400 | 04:00 | 381 | 17:00 | Rahanpur | 400 | 09:00 | 390 | 23:00
Bibiana | 392 | 05:00 | 386 | 13:00 | Rampal | 395 | 09:00 | 375 | 23:00
BIPTC | 399 | 06:00 | 389 | 12:00
Bogura | 384 | 09:00 | 372 | 23:00
Gopalganj | 386 | 09:00 | 375 | 13:00
Kaliakoir | 366 | 06:00 | 352 | 14:00
Korerhat | 393 | 00:00 | 383 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 03:00 | 217 | 15:00 | Ishurdi | 234 | 09:00 | 222 | 12:00
AKSML | 230 | 00:00 | 224 | 22:00 | Jhenaidah | 228 | 09:00 | 210 | 12:00
Aminbazar | 229 | 03:00 | 219 | 13:00 | Kachua | 225 | 09:00 | 218 | 22:00
Ashuganj | 228 | 06:00 | 220 | 22:00 | Kaliakoir | 228 | 03:00 | 216 | 15:00
Ashuganj-400 | 228 | 06:00 | 220 | 22:00 | Keranigonj | 228 | 06:00 | 217 | 13:00
Baghabari | 231 | 09:00 | 224 | 00:00 | Khulna(S) | 226 | 09:00 | 211 | 23:00
Barapukuria | 224 | 09:00 | 217 | 22:00 | Korerhat | 225 | 09:00 | 217 | 23:00
Barapukuria-230 | 224 | 09:00 | 217 | 22:00 | Madunaghat | 232 | 01:00 | 226 | 22:00
Barishal | 224 | 09:00 | 218 | 00:00 | Madunaghat-400 | 232 | 01:00 | 227 | 23:00
Bheramara | 233 | 09:00 | 221 | 07:00 | Maniknagar | 227 | 05:00 | 217 | 15:00
Bhulta | 229 | 03:00 | 217 | 17:00 | Meghnaghat | 235 | 05:00 | 231 | 13:00
Bibiana | 228 | 09:00 | 223 | 23:00 | Meghnaghat-400 | 230 | 02:00 | 221 | 17:00
BIPTC | 236 | 09:00 | 220 | 17:00 | Mirsorai | 229 | 01:00 | 221 | 22:00
Bogura | 238 | 09:00 | 230 | 23:00 | Naogaon | 226 | 09:00 | 207 | 14:00
Bogura-400 | 238 | 09:00 | 231 | 23:00 | Purbasadipur | 223 | 09:00 | 213 | 22:00
Borhanuddin | 229 | 10:00 | 223 | 00:00 | Rajshahi | 232 | 09:00 | 219 | 12:00
BSRM | 227 | 18:30 | 219 | 21:00 | Rampal | 225 | 09:00 | 211 | 23:00
Charfasson | 231 | 09:00 | 225 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 225 | 01:00 | 218 | 22:00 | Rampura | 228 | 06:00 | 215 | 17:00
Cumilla(N) | 225 | 00:00 | 219 | 21:00 | Shikalbaha | 231 | 02:00 | 225 | 21:00
Faridpur | 220 | 09:00 | 211 | 00:00 | Shyampur | 228 | 06:00 | 218 | 13:00
Fenchuganj | 232 | 05:00 | 225 | 23:00 | Siddhirganj | 233 | 11:00 | 220 | 13:00
Feni | 224 | 01:00 | 217 | 22:00 | Sirajgonj | 237 | 09:00 | 232 | 23:00
Ghorashal | 230 | 00:00 | 220 | 15:00 | Sreepur | 222 | 03:00 | 216 | 11:00
Ghorashal-230 | 217 | 01:00 | 201 | 17:00 | Tongi | 220 | 04:00 | 200 | 15:00
Gopalganj | 221 | 09:00 | 213 | 00:00
GPH | 230 | 01:00 | 223 | 22:00
Haripur | 229 | 03:00 | 219 | 17:00
Hasnabad | 229 | 06:00 | 218 | 12:00
Hathazari | 229 | 00:00 | 223 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 02:00 | 127 | 17:00 | Madunaghat | 134 | 00:00 | 131 | 21:00
Agargaon | 135 | 04:00 | 125 | 15:00 | Magura | 132 | 10:00 | 110 | 07:00
Agrabad | 132 | 00:00 | 128 | 21:00 | Mahasthangarh | 134 | 09:00 | 128 | 04:00
AKS | 131 | 09:00 | 127 | 21:00 | Maijdee | 126 | 01:00 | 122 | 21:00
Aminbazar | 130 | 00:00 | 123 | 13:00 | Manikganj | 128 | 06:00 | 122 | 10:00
Amnura | 133 | 09:00 | 125 | 12:00 | Maniknagar | 134 | 03:00 | 125 | 17:00
Ashuganj | 135 | 00:00 | 130 | 22:00 | Matarbari | 120 | 10:00 | 112 | 04:00
Ashuganj-230 | 135 | 00:00 | 130 | 22:00 | Matuail | 133 | 01:00 | 127 | 16:00
Bagerhat | 131 | 09:00 | 118 | 00:00 | Metrorail_Motijheel | 134 | 03:00 | 125 | 17:00
Bajitpur | 125 | 09:00 | 118 | 18:30 | Metrorail_Uttara | 132 | 02:00 | 119 | 15:00
Bakerganj | 130 | 09:00 | 125 | 00:00 | Millgate | 134 | 04:00 | 121 | 12:00
Bakulia | 133 | 09:00 | 129 | 21:00 | Mirpur | 130 | 06:00 | 122 | 13:00
Banani | 136 | 03:00 | 126 | 17:00 | Mirzapur | 131 | 20:00 | 123 | 22:00
Bangabhaban | 133 | 04:00 | 125 | 15:00 | Mithapukur | 131 | 09:00 | 126 | 23:00
Barapukuria | 136 | 09:00 | 128 | 22:00 | MI_Cement | 134 | 05:00 | 125 | 17:00
Barguna | 129 | 09:00 | 124 | 19:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 130 | 09:00 | 125 | 00:00 | Mogbazar | 137 | 01:00 | 128 | 13:00
Barishal-230 | 130 | 10:00 | 125 | 00:00 | Mongla | 130 | 09:00 | 118 | 23:00
Baroaulia | 134 | 12:00 | 130 | 20:00 | Motijheel | 133 | 04:00 | 125 | 15:00
Baroirhat | 130 | 07:00 | 125 | 22:00 | Muktagacha | 130 | 20:00 | 116 | 00:00
Bashundhara | 137 | 05:00 | 120 | 15:00 | Munshiganj | 132 | 02:00 | 126 | 17:00
BashundharaCement | 133 | 01:00 | 128 | 15:00 | Muradnagar | 128 | 01:00 | 122 | 22:00
Beanibazar | 127 | 10:00 | 122 | 23:00 | Mymensingh | 128 | 18:00 | 110 | 22:00
Benapole | 132 | 09:00 | 118 | 23:00 | Nabinagar | 129 | 00:00 | 121 | 11:00
Bhaluka | 123 | 20:00 | 118 | 11:00 | Naogaon | 136 | 09:00 | 125 | 00:00
Bhandaria | 127 | 19:00 | 115 | 00:00 | Narail | 132 | 10:00 | 107 | 07:00
Bhangura | 131 | 09:00 | 125 | 00:00 | Narinda | 134 | 03:00 | 125 | 17:00
Bheramara | 134 | 10:00 | 125 | 07:00 | Narshingdi | 129 | 10:00 | 121 | 17:00
Bheramara(GK) | 134 | 09:00 | 126 | 07:00 | Natore | 134 | 09:00 | 126 | 07:00
Bhulta | 128 | 00:00 | 122 | 17:00 | Nawabganj | 137 | 06:00 | 129 | 19:00
Bog-Sherpur | 135 | 09:00 | 129 | 23:00 | Netrakona | 117 | 09:00 | 108 | 22:00
Bogura | 137 | 09:00 | 132 | 01:00 | New | 134 | 04:00 | 122 | 16:00
Bogura-230 | 138 | 09:00 | 132 | 23:00 | Niamatpur | 131 | 09:00 | 126 | 00:00
Brahmanbaria | 129 | 09:00 | 124 | 22:00 | Noapara | 134 | 09:00 | 122 | 23:00
Cantonment | 134 | 03:00 | 126 | 13:00 | Pabna | 133 | 09:00 | 126 | 07:00
Chandina | 130 | 00:00 | 125 | 21:00 | Palashbari | 131 | 10:00 | 123 | 22:00
Chandpur | 131 | 00:00 | 125 | 02:00 | Panchagarh | 138 | 02:00 | 131 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 00:00 | 131 | 22:00 | Patiya | 133 | 16:00 | 127 | 22:00
Chapai | 132 | 19:00 | 127 | 05:00 | Patuakhali | 129 | 20:00 | 125 | 00:00
Charsaidpur | 134 | 05:00 | 126 | 17:00 | Payra | 133 | 10:00 | 131 | 00:00
Chauddagram | 129 | 09:00 | 124 | 21:00 | PHP | 129 | 00:00 | 125 | 22:00
Chhatak | 126 | 12:00 | 118 | 23:00 | Postogola | 136 | 06:00 | 128 | 12:00
Chowmuhani | 126 | 01:00 | 123 | 07:00 | Pubail | 124 | 00:00 | 117 | 15:00
Chuadanga | 135 | 09:00 | 119 | 12:00 | Purbachal | 137 | 05:00 | 127 | 13:00
Coxsbazar | 122 | 15:00 | 111 | 11:00 | Purbasadipur | 134 | 02:00 | 129 | 22:00
Cumilla(N) | 129 | 00:00 | 126 | 19:00 | Rahanpur | 133 | 09:00 | 130 | 01:00
Cumilla(S) | 130 | 05:00 | 121 | 13:00 | Rahanpur-400 | 134 | 09:00 | 130 | 23:00
Daganbhuiyan | 128 | 01:00 | 124 | 19:00 | Rahim | 133 | 02:00 | 127 | 18:30
Daudkandi | 127 | 00:00 | 120 | 22:00 | Rajbari | 126 | 09:00 | 118 | 00:00
DhakaUniversity | 136 | 01:00 | 127 | 14:00 | Rajendrapur | 123 | 02:00 | 118 | 11:00
Dhamrai | 130 | 01:00 | 123 | 11:00 | Rajshahi | 131 | 09:00 | 123 | 12:00
Dhanmondi | 138 | 06:00 | 127 | 17:00 | Rajshahi-230 | 157 | 01:00 | 125 | 12:00
Dohazari | 128 | 12:00 | 124 | 02:00 | Ramganj | 126 | 00:00 | 122 | 06:00
Faridpur | 129 | 09:00 | 122 | 15:00 | Rampur | 132 | 00:00 | 128 | 21:00
Fatullah | 136 | 02:00 | 126 | 13:00 | Rampura | 137 | 06:00 | 127 | 17:00
Fenchuganj | 132 | 09:00 | 127 | 23:00 | Rangamati | 134 | 10:00 | 130 | 21:00
Feni | 129 | 17:00 | 124 | 23:00 | Rangpur | 130 | 02:00 | 122 | 09:00
Feni-230 | 128 | 00:00 | 124 | 22:00 | Ruppur | 135 | 09:00 | 128 | 07:00
Ghatail | 125 | 18:00 | 114 | 22:00 | Saidpur | 133 | 06:00 | 127 | 22:00
Ghorashal | 129 | 09:00 | 121 | 15:00 | Santhia | 133 | 09:00 | 128 | 00:00
Goalpara | 135 | 09:00 | 125 | 23:00 | Satkhira | 130 | 09:00 | 116 | 00:00
Gollamari | 136 | 09:00 | 124 | 23:00 | Satmasjid | 134 | 03:00 | 125 | 13:00
Gopalganj | 128 | 09:00 | 123 | 00:00 | Savar | 129 | 00:00 | 121 | 17:00
Gopalganj-400 | 130 | 09:00 | 126 | 00:00 | SevenRings | 127 | 01:00 | 120 | 15:00
Gulshan | 136 | 05:00 | 127 | 15:00 | ShahCement | 134 | 05:00 | 126 | 17:00
Halishahar | 133 | 06:00 | 120 | 23:00 | Shahjadpur | 136 | 09:00 | 132 | 00:00
Haripur | 134 | 02:00 | 128 | 15:00 | Shahjibazar | 130 | 09:00 | 123 | 23:00
HaripurSBU | 134 | 03:00 | 128 | 17:00 | Shahmirpur | 133 | 00:00 | 129 | 22:00
Hasnabad | 134 | 00:00 | 128 | 13:00 | Shariatpur | 129 | 09:00 | 121 | 00:00
Hathazari | 134 | 00:00 | 131 | 22:00 | Sherpur | 129 | 20:00 | 113 | 00:00
Hatirjheel | 137 | 06:00 | 127 | 17:00 | Shikalbaha | 122 | 00:00 | 119 | 23:00
Ishurdi | 136 | 09:00 | 129 | 07:00 | Shikalbaha-230 | 133 | 02:00 | 130 | 21:00
Jaldhaka | 130 | 02:00 | 124 | 23:00 | Shitalakhya | 134 | 05:00 | 125.5 | 15:00
Jamalpur | 131 | 20:00 | 116 | 02:00 | Sholosohor | 133 | 00:00 | 129 | 21:00
Jashore | 134 | 09:00 | 119 | 23:00 | Shomvuganj | 119 | 00:00 | 114 | 19:00
Jhenaidah | 140 | 09:00 | 110 | 07:00 | Shyampur | 136 | 02:00 | 127 | 13:00
Jhenaidah-230 | 139 | 09:00 | 125 | 23:00 | Shyampur-230 | 136 | 00:00 | 129 | 13:00
Joydebpur | 123 | 04:00 | 112 | 01:00 | Siddhirganj | 134 | 03:00 | 127 | 17:00
Joypurhat | 135 | 09:00 | 125 | 14:00 | Sirajganj | 132 | 09:00 | 126 | 21:00
Juldah | 133 | 00:00 | 129 | 23:00 | Sitakunda | 133 | 00:00 | 130 | 21:00
Kabirpur | 133 | 20:00 | 116 | 15:00 | Sonargaon | 132 | 02:00 | 126 | 16:00
Kachua | 128 | 00:00 | 125 | 07:00 | Sreemongol | 128 | 09:00 | 123 | 22:00
Kaliakoir | 135 | 03:00 | 128 | 12:00 | Sreepur | 125 | 20:00 | 121 | 08:00
Kaliganj | 138 | 09:00 | 124 | 23:00 | Srinagar | 137 | 05:00 | 129 | 19:00
Kallyanpur | 130 | 06:00 | 122 | 13:00 | SSM | 138 | 01:00 | 136 | 00:00
Kalurghat | 134 | 00:00 | 131 | 21:00 | Sunamganj | 123 | 13:00 | 116 | 23:00
Kamrangirchar | 137 | 02:00 | 120 | 17:00 | Sylhet | 127 | 09:00 | 123 | 23:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet_(South) | 127 | 09:00 | 122 | 23:00
Kasba | 127 | 01:00 | 122 | 21:00 | Tangail | 127 | 10:00 | 118 | 22:00
Kazla | 133 | 03:00 | 125 | 16:00 | Taraganj | 132 | 10:00 | 119 | 02:00
Keranigonj | 138 | 04:00 | 130 | 19:00 | Tasnim | 132 | 05:00 | 126 | 16:00
Khagrachori | 134 | 09:00 | 128 | 21:00 | Thakurgaon | 138 | 02:00 | 130 | 22:00
Khulna | 133 | 09:00 | 123 | 23:00 | TK | 134 | 09:00 | 131 | 00:00
Khulna(S) | 137 | 09:00 | 125 | 10:00 | Tongi | 135 | 01:00 | 122 | 15:00
Khulshi | 131 | 00:00 | 128 | 13:00 | Ullahpara | 133 | 09:00 | 127 | 00:00
Kishoreganj | 124 | 02:00 | 117 | 18:30 | Ullon | 136 | 05:00 | 127 | 13:00
Kodda | 132 | 20:00 | 122 | 11:00 | Uttara | 132 | 03:00 | 118 | 15:00
Korerhat | 132 | 00:00 | 127 | 23:00 | UttaraNew | 132 | 02:00 | 119 | 15:00
KSRM | 133 | 02:00 | 129 | 21:00 | Zigatola | 137 | 03:00 | 131 | 13:00
Kulaura | 130 | 09:00 | 126 | 23:00
Kurigram | 130 | 10:00 | 122 | 22:00
Kushtia | 133 | 10:00 | 117 | 07:00
Laksam | 128 | 00:00 | 124 | 19:00
Lakshmipur | 125 | 00:00 | 121 | 22:00
Lalbag | 138 | 06:00 | 129 | 19:00
Lalmonirhat | 131 | 10:00 | 122 | 02:00
Madanganj | 133 | 01:00 | 128 | 15:00
Madaripur | 130 | 07:00 | 125 | 00:00
Madartek | 136 | 04:00 | 127 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-06-2026 | [28 empty] | Date: | 27-06-2026 | [28 empty] | Date: | 27-06-2026 | [28 empty] | Date: | 27-06-2026 | [28 empty] | Date: | 27-06-2026 | [18 empty] | Date: | 27-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [18 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 40 | 16 | 146 | 47 | 35 | 35 | 0 | 0 | 0 | 500 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 21 | 21 | 0 | 520 | 105 | 16 | 49 | 0 | 6 | 33 | 45 | 18 | 12 | 12 | 0 | 87 | 17 | 14 | 640 | 0 | 0 | 6 | 8 | 0 | 216 | 0 | 0 | 0 | 720 | 0 | 147 | 0 | 250 | 290 | 220 | 51 | 0 | 198 | 0 | 34 | 93 | 190 | 0 | 19 | 0 | 168 | 0 | 0 | 15 | 315 | 0 | 308 | 28 | 0 | 149 | 0 | 17 | 0 | 53 | 30 | 145 | 0 | 101 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 6996 | 902 | 0 | 0 | 0 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 0 | 0 | 0 | 1482.76 | 0 | 0 | 0 | 35 | 35 | 0 | 93 | 25 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 172 | 0 | 169 | 0 | 414 | 0 | 0 | 176 | 34 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 306 | 64 | 220 | 0 | 991 | 1202 | 54 | 7753.76 | 14749.76 | 77.09
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 17 | 16 | 146 | 49 | 35 | 35 | 0 | 0 | 0 | 510 | 0 | 0 | 297 | 0 | 0 | 0 | 17 | 21 | 21 | 0 | 520 | 106 | 16 | 28 | 0 | 8 | 33 | 37 | 18 | 12 | 12 | 0 | 87 | 17 | 20 | 500 | 0 | 0 | 6 | 8 | 0 | 216 | 0 | 0 | 0 | 720 | 0 | 128 | 0 | 250 | 290 | 230 | 51 | 0 | 197 | 0 | 34 | 93 | 160 | 0 | 19 | 0 | 166 | 0 | 0 | 8 | 315 | 0 | 308 | 28 | 0 | 152 | 0 | 17 | 0 | 53 | 30 | 142 | 0 | 101 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 6781 | 902 | 0 | 0 | 0 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1106 | 0 | 0 | 0 | 1475.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 172 | 0 | 170 | 0 | 414 | 0 | 0 | 179 | 38 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 305 | 64 | 220 | 0 | 990 | 1200 | 17 | 7550.75 | 14331.75 | 77.07
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 17 | 16 | 146 | 55 | 35 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 307 | 0 | 0 | 0 | 17 | 21 | 21 | 0 | 515 | 107 | 16 | 26 | 0 | 5 | 0 | 29 | 18 | 12 | 12 | 0 | 87 | 17 | 28 | 500 | 0 | 0 | 6 | 8 | 0 | 217 | 0 | 0 | 0 | 720 | 0 | 115 | 0 | 280 | 290 | 270 | 51 | 0 | 202 | 0 | 0 | 93 | 34 | 0 | 19 | 0 | 164 | 0 | 0 | 8 | 315 | 0 | 308 | 28 | 0 | 152 | 0 | 17 | 0 | 53 | 30 | 142 | 0 | 100 | 0 | 49 | 0 | 48 | 11 | 0 | 0 | 0 | 6666 | 824 | 0 | 0 | 0 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 0 | 0 | 1482.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 172 | 0 | 172 | 0 | 414 | 0 | 0 | 178 | 38 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 306 | 64 | 220 | 0 | 997 | 1200 | 17 | 7490.73 | 14156.73 | 77.05
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 17 | 16 | 146 | 55 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 21 | 21 | 0 | 520 | 106 | 16 | 24 | 0 | 6 | 0 | 29 | 18 | 12 | 12 | 0 | 89 | 17 | 40 | 440 | 0 | 0 | 6 | 0 | 0 | 217 | 0 | 0 | 0 | 720 | 0 | 35 | 0 | 270 | 290 | 290 | 51 | 0 | 196 | 0 | 0 | 94 | 17 | 0 | 19 | 0 | 156 | 0 | 0 | 8 | 310 | 0 | 308 | 28 | 0 | 150 | 0 | 17 | 0 | 53 | 30 | 143 | 0 | 102 | 0 | 48 | 0 | 48 | 20 | 0 | 0 | 0 | 6476 | 824 | 0 | 0 | 0 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 1483.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 172 | 0 | 414 | 0 | 0 | 181 | 38 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 304 | 64 | 220 | 0 | 998 | 1200 | 17 | 7475.42 | 13951.42 | 77.04
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 17 | 16 | 146 | 55 | 0 | 0 | 0 | 0 | 0 | 515 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 21 | 21 | 0 | 495 | 107 | 16 | 24 | 0 | 10 | 0 | 30 | 18 | 12 | 12 | 0 | 89 | 17 | 40 | 440 | 0 | 0 | 6 | 0 | 0 | 218 | 0 | 0 | 0 | 720 | 0 | 25 | 0 | 250 | 290 | 290 | 51 | 0 | 194 | 0 | 0 | 94 | 16 | 0 | 19 | 0 | 156 | 0 | 0 | 16 | 310 | 0 | 308 | 28 | 0 | 149 | 0 | 17 | 0 | 53 | 30 | 142 | 0 | 100 | 0 | 48 | 0 | 48 | 18 | 0 | 0 | 0 | 6389 | 890 | 0 | 0 | 0 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 1490.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 172 | 0 | 414 | 0 | 0 | 182 | 38 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 306 | 65 | 220 | 0 | 982 | 1202 | 17 | 7504.95 | 13893.95 | 77.03
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 17 | 16 | 81 | 55 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 21 | 21 | 0 | 485 | 107 | 16 | 25 | 0 | 6 | 0 | 30 | 18 | 12 | 12 | 0 | 89 | 17 | 42 | 440 | 0 | 0 | 6 | 0 | 0 | 218 | 0 | 0 | 0 | 720 | 0 | 26 | 0 | 230 | 290 | 290 | 51 | 0 | 207 | 0 | 0 | 95 | 17 | 0 | 19 | 0 | 150 | 0 | 0 | 16 | 310 | 0 | 308 | 28 | 0 | 150 | 0 | 17 | 0 | 53 | 30 | 142 | 0 | 102 | 0 | 48 | 0 | 48 | 18 | 0 | 0 | 0 | 6299 | 890 | 0 | 0 | 0 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 0 | 0 | 1481.62 | 0 | 0 | 0 | 35 | 8 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 181 | 0 | 414 | 0 | 0 | 182 | 35 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 65 | 220 | 0 | 948 | 1200 | 17 | 7519.62 | 13818.62 | 77.02
06:00 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 17 | 16 | 81 | 55 | 0 | 0 | 0 | 0 | 0 | 465 | 0 | 0 | 298 | 0 | 0 | 2 | 17 | 21 | 21 | 0 | 410 | 106 | 16 | 24 | 0 | 11 | 0 | 30 | 0 | 12 | 12 | 0.11 | 91 | 17 | 40 | 440 | 0 | 0 | 6 | 0 | 0 | 218 | 0 | 0 | 0 | 720 | 0 | 26 | 0 | 230 | 290 | 290 | 51 | 0 | 214 | 0 | 0 | 95 | 17 | 0 | 19 | 0 | 132 | 0 | 2 | 15 | 315 | 0 | 308 | 28 | 0 | 136 | 0 | 17 | 0 | 53 | 30 | 142 | 0 | 101 | 0 | 48 | 0.44 | 48 | 18 | 0.1 | 1.27 | 0 | 6125.92 | 890 | 0 | 0 | 0 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 1113 | 0 | 0 | 0 | 1484.76 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 25 | 0 | 3.06 | 5 | 0 | 0 | 2.33 | 0 | 0 | 183 | 0 | 182 | 0 | 370 | 0 | 0.28 | 180 | 35 | 95 | 2 | 0 | 0 | 0 | 0 | 0.4 | 7 | 0.04 | 48 | 276 | 65 | 180 | 0 | 818 | 1195 | 17 | 7343.87 | 13469.79 | 77.01
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 17 | 16 | 81 | 55 | 0 | 0 | 0 | 0 | 0 | 445 | 0 | 0 | 301 | 0 | 0 | 7 | 17 | 21 | 0 | 0 | 420 | 107 | 16 | 24 | 0 | 5 | 0 | 30 | 0 | 12 | 12 | 0.6 | 91 | 17 | 35 | 440 | 0 | 0 | 6 | 0 | 0 | 219 | 0 | 0 | 0 | 720 | 5 | 26 | 0 | 230 | 290 | 290 | 51 | 0 | 215 | 0 | 0 | 94 | 17 | 0 | 19 | 0 | 142 | 0 | 15 | 15 | 315 | 0 | 308 | 28 | 0 | 134 | 2 | 17 | 0 | 53 | 30 | 144 | 0 | 101 | 0 | 48 | 2.4 | 48 | 18 | 0.3 | 6.57 | 0 | 6142.87 | 890 | 0 | 0 | 0 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 1112 | 0 | 0 | 0 | 1485.17 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 25 | 0 | 10.35 | 18 | 0 | 0 | 11.33 | 0 | 0 | 186 | 0 | 184 | 0 | 414 | 0 | 0.81 | 175 | 35 | 95 | 1 | 0 | 0 | 0 | 0 | 0.8 | 24 | 0.17 | 48 | 276 | 65 | 180 | 0 | 810 | 1190 | 17 | 7455.63 | 13598.5 | 76.99
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 17 | 16 | 81 | 55 | 0 | 0 | 0 | 0 | 0 | 445 | 0 | 0 | 302 | 0 | 0 | 14 | 17 | 21 | 0 | 0 | 460 | 106 | 16 | 25 | 0 | 1 | 0 | 30 | 0 | 12 | 12 | 1.53 | 91 | 17 | 12 | 440 | 0 | 0 | 6 | 0 | 0 | 219 | 0 | 0 | 0 | 720 | 10 | 26 | 0 | 230 | 290 | 290 | 51 | 0 | 211 | 0 | 0 | 94 | 17 | 0 | 19 | 0 | 156 | 0 | 21 | 0 | 315 | 0 | 308 | 28 | 0 | 132 | 2 | 17 | 0 | 53 | 30 | 143 | 0 | 101 | 0 | 48 | 9.36 | 48 | 18 | 0.9 | 16.57 | 0 | 6182.36 | 890 | 0 | 0 | 0 | 32 | 38 | 0 | 0 | 0 | 0 | 0 | 43 | 1110 | 0 | 0 | 0 | 1487.56 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 25 | 0 | 19.69 | 47 | 0 | 0 | 17.88 | 0 | 0 | 186 | 0 | 186 | 0 | 383 | 0 | 0 | 182 | 35 | 95 | 14 | 0 | 0 | 0 | 0 | 1.2 | 71 | 0.38 | 0 | 226 | 65 | 180 | 0 | 799 | 1170 | 0 | 7403.71 | 13586.07 | 76.99
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 16 | 81 | 55 | 0 | 0 | 0 | 0 | 0 | 512 | 0 | 0 | 301 | 0 | 0 | 14 | 17 | 23.5 | 0 | 0 | 425 | 107 | 16 | 25 | 0 | 0 | 0 | 30 | 0 | 12 | 12 | 3.18 | 91 | 17 | 4 | 440 | 0 | 0 | 6 | 0 | 0 | 218 | 0 | 0 | 0 | 720 | 12 | 26 | 0 | 230 | 290 | 290 | 51 | 0 | 205 | 0 | 0 | 94 | 17 | 0 | 8 | 0 | 162 | 0 | 15 | 0 | 310 | 0 | 309 | 28 | 0 | 137 | 8 | 17 | 0 | 52 | 30 | 144 | 0 | 101 | 0 | 48 | 15.01 | 48 | 10 | 1 | 19.83 | 0 | 6195.52 | 889 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 78 | 1005 | 0 | 0 | 0 | 1418.89 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 24 | 0 | 37.99 | 72 | 0 | 0 | 38.18 | 0 | 0 | 187 | 0 | 187 | 0 | 354 | 0 | 3.22 | 185 | 36 | 95 | 17 | 0 | 0 | 0 | 0 | 3.8 | 49 | 0.51 | 0 | 171 | 65 | 180 | 0 | 702 | 1040 | 0 | 7005.59 | 13201.11 | 76.98
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 16 | 81 | 55 | 0 | 17 | 0 | 0 | 0 | 545 | 0 | 0 | 316 | 0 | 0 | 29 | 17 | 23.5 | 0 | 0 | 560 | 106 | 16 | 25 | 0 | 0 | 0 | 30 | 0 | 12 | 12 | 0.88 | 93 | 17 | 4 | 440 | 0 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 720 | 16 | 26 | 0 | 230 | 290 | 290 | 51 | 0 | 200 | 0 | 0 | 91 | 17 | 1 | 8 | 0 | 158 | 0 | 73 | 0 | 305 | 0 | 309 | 27 | 0 | 139 | 6 | 17 | 0 | 52 | 30 | 143 | 0 | 101 | 0 | 48 | 19.43 | 48 | 10 | 1 | 35.09 | 0 | 6473.9 | 890 | 0 | 0 | 0 | 20 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 800 | 0 | 0 | 0 | 1412.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 47.98 | 90 | 0 | 0 | 30.62 | 0 | 0 | 187 | 0 | 187 | 0 | 405 | 0 | 4.51 | 180 | 35 | 95 | 20 | 0 | 0 | 0 | 0 | 4.9 | 87 | 0.53 | 0 | 224 | 64 | 220 | 0 | 700 | 980 | 0 | 6812.32 | 13286.22 | 76.97
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 3 | 0 | 81 | 55 | 17 | 17 | 0 | 0 | 0 | 555 | 0 | 0 | 302 | 0 | 0 | 33 | 17 | 23.5 | 3 | 0 | 535 | 107 | 16 | 24 | 0 | 0 | 0 | 30 | 0 | 12 | 12 | 4.97 | 89 | 17 | 4 | 440 | 0 | 0 | 6 | 0 | 0 | 215 | 0 | 0 | 0 | 720 | 0 | 26 | 0 | 230 | 290 | 290 | 51 | 0 | 203 | 0 | 0 | 91 | 17 | 17 | 8 | 0 | 168 | 0 | 37 | 0 | 310 | 0 | 282 | 28 | 0 | 147 | 11 | 17 | 0 | 52 | 30 | 143 | 0 | 101 | 0 | 48 | 20 | 48 | 5 | 2.3 | 40.01 | 0 | 6445.78 | 890 | 0 | 0 | 0 | 20 | 38 | 0 | 0 | 0 | 0 | 0 | 53.7 | 390 | 0 | 0 | 0 | 1423.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 54.33 | 100 | 0 | 0 | 48.32 | 12 | 0 | 185 | 0 | 185 | 0 | 397 | 0 | 5.13 | 183 | 35 | 95 | 30 | 0 | 0 | 0 | 0 | 2.9 | 158 | 0.52 | 11 | 281 | 64 | 220 | 0 | 801 | 1120 | 17 | 6832.47 | 13278.25 | 76.96
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 34 | 0 | 81 | 55 | 35 | 17 | 0 | 0 | 0 | 555 | 0 | 0 | 300 | 0 | 0 | 23 | 17 | 21 | 21 | 0 | 490 | 107 | 16 | 18 | 0 | 7 | 0 | 30 | 0 | 12 | 12 | 1.33 | 89 | 17 | 5 | 520 | 0 | 0 | 6 | 0 | 0 | 215 | 0 | 0 | 0 | 720 | 20 | 26 | 0 | 230 | 290 | 290 | 51 | 0 | 201 | 0 | 6 | 90 | 17 | 18 | 8 | 0 | 172 | 0 | 76 | 0 | 320 | 0 | 285 | 28 | 0 | 151 | 6 | 17 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 58 | 21.3 | 67 | 5 | 2.1 | 37.01 | 0 | 6619.74 | 891 | 0 | 0 | 0 | 23 | 38 | 0 | 0 | 27 | 0 | 0 | 39.85 | 392 | 0 | 0 | 0 | 1479.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 55.69 | 100 | 0 | 0 | 49.7 | 10 | 0 | 179 | 0 | 178 | 0 | 377 | 0 | 5.24 | 175 | 35 | 95 | 23 | 0 | 0 | 0 | 0 | 6.3 | 167 | 0.31 | 16 | 272 | 62 | 220 | 0 | 1000 | 1160 | 17 | 7105.63 | 13725.37 | 76.95
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 34 | 0 | 81 | 55 | 35 | 17 | 0 | 0 | 0 | 556 | 0 | 0 | 292 | 0 | 0 | 32 | 17 | 21 | 21 | 0 | 500 | 106 | 16 | 20 | 0 | 3 | 0 | 41 | 0 | 12 | 12 | 1.98 | 89 | 17 | 2 | 650 | 0 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 720 | 15 | 26 | 0 | 230 | 290 | 290 | 51 | 0 | 195 | 0 | 33 | 90 | 17 | 17 | 8 | 0 | 176 | 0 | 31 | 0 | 320 | 0 | 225 | 28 | 0 | 149 | 12 | 17 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 58 | 21.3 | 67 | 5 | 2.2 | 19.04 | 0 | 6663.52 | 890 | 0 | 0 | 0 | 25 | 38 | 0 | 0 | 0 | 0 | 0 | 99.84 | 380 | 0 | 0 | 0 | 1468.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 55.97 | 100 | 0 | 0 | 54.99 | 17 | 0 | 179 | 0 | 179 | 0 | 386 | 0 | 5.29 | 180 | 36 | 95 | 26 | 0 | 0 | 0 | 0 | 4.8 | 129 | 0.3 | 16 | 279 | 62 | 220 | 0 | 1000 | 1160 | 35 | 7128.17 | 13791.69 | 76.93
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 2 | 34 | 0 | 81 | 42 | 35 | 17 | 0 | 0 | 0 | 553 | 0 | 0 | 303 | 0 | 0 | 21 | 41 | 21.5 | 21 | 0 | 460 | 106 | 16 | 18 | 0 | 11 | 0 | 41 | 0 | 12 | 12 | 1.78 | 83 | 17 | 5 | 735 | 0 | 0 | 6 | 0 | 0 | 213 | 0 | 0 | 0 | 720 | 15 | 20 | 0 | 220 | 290 | 290 | 51 | 0 | 188 | 0 | 34 | 90 | 27 | 0 | 8 | 0 | 172 | 0 | 36 | 0 | 325 | 0 | 239 | 28 | 0 | 146 | 8 | 17 | 0 | 51 | 30 | 143 | 0 | 101 | 0 | 58 | 20 | 68 | 0 | 1.9 | 41.88 | 0 | 6731.06 | 890 | 0 | 0 | 0 | 17 | 38 | 0 | 0 | 32 | 0 | 0 | 97.32 | 380 | 0 | 0 | 0 | 1489.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 50.26 | 99 | 0 | 0 | 49.88 | 16 | 0 | 179 | 0 | 179 | 0 | 353 | 0 | 4.52 | 180 | 35 | 95 | 25 | 0 | 0 | 0 | 0 | 0 | 54 | 0.68 | 16 | 275 | 62 | 180 | 0 | 1000 | 1165 | 35 | 7006.97 | 13738.03 | 76.91
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 17 | 55 | 0 | 81 | 40 | 35 | 17 | 0 | 0 | 0 | 555 | 0 | 0 | 311 | 0 | 0 | 23 | 51 | 20.5 | 21 | 0 | 555 | 106 | 16 | 15 | 0 | 26 | 0 | 41 | 0 | 12 | 12 | 3.41 | 85 | 17 | 2 | 735 | 0 | 0 | 6 | 0 | 0 | 213 | 0 | 0 | 0 | 720 | 8 | 20 | 0 | 220 | 290 | 290 | 51 | 0 | 201 | 0 | 35 | 90 | 34 | 0 | 8 | 0 | 180 | 0 | 48 | 0 | 325 | 0 | 244 | 28 | 0 | 145 | 8 | 17 | 0 | 51 | 28 | 143 | 0 | 100 | 0 | 58 | 15.3 | 68 | 0 | 1.6 | 31.27 | 0 | 6898.08 | 890 | 0 | 0 | 0 | 17 | 38 | 0 | 0 | 30 | 0 | 0 | 85.47 | 380 | 0 | 0 | 0 | 1486.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 39.79 | 79 | 0 | 0 | 39.22 | 18 | 0 | 179 | 0 | 179 | 0 | 387 | 0 | 3.83 | 210 | 36 | 95 | 6 | 12 | 0 | 0 | 0 | 0 | 104 | 0.16 | 16 | 276 | 62 | 220 | 0 | 1000 | 1140 | 17 | 7057.59 | 13955.67 | 76.89
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 17 | 82 | 0 | 81 | 40 | 35 | 17 | 0 | 0 | 0 | 527 | 0 | 17 | 310 | 0 | 0 | 14 | 51 | 20.5 | 21 | 0 | 510 | 107 | 16 | 22 | 0 | 28 | 0 | 41 | 0 | 12 | 12 | 1.3 | 87 | 17 | 0 | 785 | 0 | 0 | 6 | 0 | 0 | 212 | 0 | 0 | 0 | 720 | 10 | 18 | 0 | 220 | 290 | 290 | 51 | 0 | 204 | 0 | 35 | 90 | 19 | 5 | 8 | 0 | 192 | 0 | 17 | 0 | 320 | 0 | 244 | 28 | 0 | 148 | 6 | 17 | 0 | 51 | 28 | 143 | 0 | 100 | 0 | 58 | 11.05 | 68 | 0 | 1 | 6.55 | 0 | 6869.4 | 890 | 0 | 0 | 0 | 26 | 38 | 0 | 0 | 30 | 0 | 0 | 48.97 | 380 | 0 | 0 | 0 | 1483.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 26.92 | 41 | 0 | 0 | 24.82 | 19 | 0 | 179 | 0 | 179 | 0 | 378 | 0 | 2.5 | 225 | 38 | 95 | 12 | 12 | 0 | 0 | 0 | 4 | 72 | 0.1 | 16 | 276 | 62 | 220 | 0 | 1000 | 1122 | 17 | 6942.48 | 13811.88 | 76.87
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 17 | 96 | 0 | 81 | 55 | 35 | 17 | 0 | 0 | 0 | 520 | 0 | 35 | 300 | 0 | 0 | 8 | 65 | 19.5 | 0 | 0 | 540 | 106 | 16 | 24 | 0 | 18 | 0 | 47 | 0 | 12 | 12 | 0.3 | 89 | 17 | 0 | 935 | 0 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 720 | 4 | 15 | 0 | 220 | 290 | 290 | 51 | 0 | 207 | 0 | 33 | 90 | 25 | 26 | 8 | 0 | 174 | 0 | 16 | 0 | 320 | 0 | 244 | 28 | 0 | 150 | 1 | 17 | 0 | 51 | 28 | 143 | 0 | 100 | 0 | 58 | 0 | 76 | 0 | 0.5 | 12.87 | 9 | 7073.17 | 890 | 0 | 0 | 0 | 26 | 38 | 0 | 0 | 36 | 0 | 0 | 31.23 | 380 | 0 | 0 | 0 | 1475.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 12.65 | 28 | 0 | 0 | 11.65 | 51 | 0 | 179 | 0 | 178 | 0 | 392 | 0 | 1.24 | 230 | 37 | 95 | 5 | 15 | 0 | 0 | 0 | 2.1 | 24 | 0.06 | 16 | 277 | 62 | 220 | 0 | 1000 | 1120 | 17 | 6867.79 | 13940.96 | 76.85
18:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 10 | 17 | 104 | 0 | 146 | 55 | 35 | 50 | 0 | 0 | 0 | 500 | 0 | 35 | 290 | 0 | 0 | 2 | 95 | 19 | 21 | 0 | 370 | 107 | 16 | 35 | 0 | 22 | 0 | 47 | 4 | 12 | 12 | 0.39 | 89 | 17 | 10 | 1090 | 0 | 0 | 6 | 7 | 0 | 216 | 0 | 0 | 0 | 720 | 1 | 13 | 0 | 220 | 290 | 290 | 51 | 0 | 200 | 0 | 35 | 91 | 87 | 26 | 8 | 0 | 166 | 0 | 4 | 0 | 325 | 0 | 244 | 28 | 0 | 136 | 0 | 17 | 0 | 51 | 30 | 143 | 0 | 100 | 0 | 58 | 0 | 77 | 0 | 0.1 | 2.15 | 12 | 7214.64 | 890 | 0 | 0 | 0 | 34 | 38 | 0 | 0 | 102 | 0 | 0 | 8.29 | 380 | 0 | 0 | 0 | 1468.68 | 0 | 0 | 0 | 10 | 22 | 8 | 0 | 19 | 0 | 3.13 | 7 | 0 | 0 | 2.59 | 113 | 0 | 178 | 0 | 178 | 0 | 332 | 0 | 0.24 | 180 | 37 | 95 | 5 | 32 | 0 | 0 | 0 | 0.3 | 9 | 0.03 | 16 | 274 | 62 | 220 | 0 | 871 | 1140 | 17 | 6752.26 | 13966.9 | 76.83
19:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 35 | 17 | 132 | 0 | 146 | 55 | 35 | 108 | 0 | 0 | 0 | 330 | 0 | 35 | 310 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 560 | 106 | 16 | 47 | 0 | 10 | 33 | 48 | 50 | 12 | 12 | 0 | 89 | 17 | 13 | 1090 | 0 | 0 | 6 | 25.5 | 0 | 213 | 0 | 0 | 0 | 780 | 0 | 56 | 0 | 220 | 290 | 240 | 51 | 0 | 212 | 0 | 41 | 91 | 103 | 27 | 19 | 0 | 192 | 0 | 0 | 0 | 315 | 0 | 364 | 28 | 0 | 142 | 0 | 17 | 0 | 82 | 30 | 143 | 0 | 100 | 1 | 58 | 0 | 82 | 0 | 0 | 0 | 11 | 7856.5 | 890 | 0 | 0 | 0 | 40 | 38 | 0 | 0 | 30 | 0 | 15 | 0 | 380 | 0 | 0 | 0 | 1479.42 | 0 | 0 | 0 | 35 | 50 | 16 | 83 | 19 | 0 | 0 | 0 | 12 | 0 | 0 | 157 | 0 | 173 | 0 | 176 | 0 | 400 | 0 | 0 | 180 | 37 | 95 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 282 | 65 | 220 | 0 | 995 | 1170 | 17 | 7108.42 | 17 | 76.81
19:30 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 35 | 17 | 132 | 0 | 146 | 55 | 35 | 108 | 0 | 0 | 0 | 380 | 0 | 35 | 275 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 465 | 106 | 16 | 50 | 0 | 10 | 33 | 48 | 54.36 | 12 | 12 | 0 | 91 | 17 | 2 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 215 | 0 | 0 | 0 | 840 | 0 | 150 | 0 | 220 | 290 | 240 | 51 | 0 | 213 | 10 | 89 | 50 | 105 | 27 | 19 | 0 | 158 | 0 | 0 | 0 | 305 | 0 | 354 | 28 | 0 | 149 | 0 | 17 | 0 | 82 | 30 | 143 | 0 | 100 | 17 | 58 | 0 | 96 | 0 | 0 | 0 | 0 | 7950.86 | 892 | 0 | 0 | 0 | 42 | 38 | 0 | 0 | 100 | 0 | 15 | 0 | 380 | 0 | 0 | 0 | 1476.1 | 0 | 0 | 0 | 35 | 50 | 10 | 83 | 19 | 0 | 0 | 0 | 12 | 0 | 0 | 166 | 0 | 170 | 0 | 172 | 0 | 376 | 0 | 0 | 180 | 37 | 95 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 276 | 65 | 220 | 0 | 971 | 1085 | 26 | 7072.1 | 14964.92
20:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 17 | 132 | 5 | 146 | 55 | 35 | 125 | 0 | 0 | 0 | 413 | 0 | 35 | 282 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 380 | 106 | 16 | 50 | 0 | 14 | 33 | 55 | 54.36 | 12 | 12 | 0 | 91 | 17 | 4 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 216 | 0 | 0 | 0 | 889 | 0 | 150 | 0 | 220 | 290 | 240 | 51 | 0 | 214 | 10 | 83 | 51 | 103 | 27 | 19 | 0 | 152 | 0 | 0 | 0 | 305 | 0 | 356 | 28 | 0 | 141 | 0 | 17 | 0 | 82 | 30 | 143 | 0 | 100 | 17 | 58 | 0 | 97 | 0 | 0 | 0 | 0 | 7974.86 | 892 | 0 | 0 | 0 | 46 | 38 | 0 | 0 | 150 | 0 | 15 | 0 | 380 | 0 | 0 | 0 | 1476.33 | 0 | 10 | 0 | 35 | 50 | 10 | 83 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 170 | 0 | 171 | 0 | 348 | 0 | 0 | 180 | 36 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 263 | 65 | 180 | 0 | 863 | 1100 | 17 | 6947.33 | 15022.96 | 76.79
21:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 35 | 0 | 132 | 15 | 146 | 55 | 35 | 162 | 0 | 0 | 0 | 370 | 0 | 35 | 296 | 0 | 0 | 0 | 142 | 20 | 17 | 0 | 480 | 107 | 16 | 48 | 0 | 14 | 33 | 55 | 54.36 | 12 | 12 | 0 | 92 | 17 | 10 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 217 | 0 | 0 | 0 | 1100 | 0 | 55 | 0 | 220 | 290 | 240 | 51 | 0 | 214 | 10 | 88 | 50 | 104 | 27 | 19 | 0 | 154 | 0 | 0 | 0 | 310 | 0 | 319 | 28 | 0 | 148 | 0 | 17 | 0 | 82 | 30 | 143 | 0 | 100 | 17 | 58 | 0 | 97 | 0 | 0 | 0 | 0 | 8181.86 | 798 | 0 | 0 | 0 | 35 | 38 | 0 | 0 | 151 | 0 | 15 | 0 | 450 | 0 | 0 | 0 | 1476.39 | 0 | 47 | 0 | 35 | 50 | 10 | 83 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 50 | 0 | 165 | 0 | 377 | 0 | 0 | 180 | 37 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 284 | 65 | 220 | 0 | 1000 | 1165 | 17 | 7116.39 | 14922.19 | 76.77
22:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 35 | 0 | 132 | 16 | 146 | 55 | 35 | 162 | 0 | 0 | 0 | 450 | 0 | 35 | 304 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 480 | 106 | 16 | 49 | 0 | 12 | 33 | 55 | 18 | 12 | 12 | 0 | 92 | 17 | 16 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 216 | 0 | 0 | 0 | 1224 | 0 | 20 | 0 | 220 | 290 | 240 | 51 | 0 | 215 | 10 | 86 | 50 | 102 | 27 | 19 | 0 | 166 | 0 | 0 | 0 | 310 | 0 | 320 | 28 | 0 | 143 | 0 | 0 | 0 | 52 | 30 | 143 | 0 | 100 | 17 | 68 | 0 | 87 | 0 | 0 | 0 | 0 | 8248.5 | 798 | 0 | 0 | 0 | 33 | 38 | 0 | 0 | 151 | 0 | 0 | 0 | 460 | 0 | 0 | 0 | 1487.94 | 0 | 47 | 0 | 35 | 50 | 0 | 83 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 166 | 0 | 376 | 0 | 0 | 180 | 37 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 257 | 65 | 220 | 0 | 1050 | 1180 | 17 | 7099.94 | 15298.25 | 76.75
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 35 | 0 | 132 | 16 | 146 | 55 | 35 | 162 | 0 | 0 | 0 | 460 | 0 | 35 | 301 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 550 | 105 | 16 | 50 | 0 | 7 | 33 | 55 | 18 | 12 | 12 | 0 | 91 | 17 | 17 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 217 | 0 | 0 | 0 | 1224 | 0 | 20 | 0 | 220 | 290 | 240 | 51 | 0 | 216 | 10 | 69 | 50 | 103 | 0 | 19 | 0 | 176 | 0 | 0 | 0 | 305 | 0 | 320 | 28 | 0 | 151 | 0 | 0 | 0 | 52 | 30 | 143 | 0 | 100 | 17 | 68 | 0 | 87 | 0 | 0 | 0 | 0 | 8295.5 | 798 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 0 | 1483.76 | 0 | 47 | 0 | 35 | 35 | 0 | 83 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 167 | 0 | 383 | 0 | 0 | 180 | 37 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 287 | 64 | 220 | 0 | 1050 | 1190 | 17 | 6972.76 | 15348.44 | 76.75
Total KWH | 0 | 172800 | 50880 | 0 | 0 | 0 | 0 | 0 | 9000000 | 0 | 0 | 219960 | 110520 | 1398240 | 223680 | 2639815 | 1273060 | 531735 | 1048320 | 0 | 0 | 0 | 11940455 | 0 | 270277 | 7284312 | 0 | 0 | 212025 | 1344000 | 501600 | 374040 | 0 | 11730454.55 | 2553000 | 381382 | 732480 | 0 | 242400 | 230132 | 900432 | 331689 | 298560 | 288960 | 23766 | 2133020 | 424000 | 365280 | 16596363.64 | 0 | 0 | 151200 | 156709.8 | 12545 | 5136741 | 0 | 0 | 0 | 19063634 | 118800 | 953454 | 0 | 5677000 | 7412500 | 6700000 | 1226600 | 0 | 5064000 | 47952 | 701760 | 1922741 | 1128000 | 232680 | 364780 | 0 | 3942720 | 0 | 400618 | 96320 | 7592000 | 0 | 7175000 | 670000 | 0 | 3492654.55 | 65072 | 345024 | 0 | 1320000 | 707520 | 3267000 | 0 | 2403950 | 75600 | 1284000 | 138772 | 1512000 | 143040 | 14950 | 296130 | 32640 | 166873745.54 | 21065455 | 0 | 0 | 0 | 720896 | 912000 | 0 | 0 | 685727 | 0 | 40896 | 668160 | 16399997 | 0 | 0 | 0 | 35410909 | 0 | 178090 | 0 | 439968 | 549984 | 36119 | 483488 | 403635 | 0 | 399656 | 783030 | 49458 | 0 | 375728 | 1256636 | 0 | 3871764 | 0 | 4487927 | 0 | 9363927 | 0 | 36420 | 4594000 | 853091 | 2293643 | 190437 | 375120 | 0 | 0 | 0 | 33925.56 | 984240 | 3955 | 751391 | 6698000 | 1526000 | 5248230 | 0 | 22509090 | 28219636.36 | 415200 | 173315828.92 | 340189574.46