## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: May 2026
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2026-05-01 |  | 2026-04-01 |  | 2025-05-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 17200.79 | 2026-05-20 | 15199 | 2026-04-20 | 16603 | 2025-05-10 | 17200.79 | 2026-05-20
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr.
2 | Minimum Generation (MW) | 5755.52 | 2026-05-27 | 7093.7 | 2026-04-29 | 7297.96 | 2025-05-30 | - | -
|  |  | 09:00 Hr. |  | 08:00 Hr. |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 17200.79 | 2026-05-20 | 15199 | 2026-04-20 | 16365.8 | 2025-04-24 | 17200.79 | 2026-05-20
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 19:30 Hr. |  | 21:00 Hr.
4 | Maximum Day Peak Generation (MW) | 15418.78 | 2026-05-20 | 14194.78 | 2026-04-23 | 14834 | 2025-05-08 | 15418.78 | 2026-05-20
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 Hr.
5 | Maximum Evening Peak Demand (MW) Estimated | 17610.79 | 2026-05-20 | 16895.43 | 2026-04-23 | 16999.06 | 2025-05-10 | 17610.79 | 2026-05-20
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr.
6 | Average Generation (MW) at Evening Peak | 14127.9116 |  | 13883.6437 |  | 14759.5487 |  | - | -
7 | Average Generation (MW) at Day Peak | 12425.1735 |  | 12874.9397 |  | 13259.9958 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 940 | 2026-05-04 | 935 | 2026-04-27 | 941 | 2025-05-13 | 980 | 2026-02-20
|  |  | 10:40 |  | 11:30 |  | 1:30 |  | 0:30
9 | Maximum Power Import from Tripura, India (MW) | 189 | 2026-05-19 | 213 | 2026-04-22 | 62 | 2025-05-22 | 213 | 4/22/26
|  |  | 19:00 |  | 16:00 |  | 18:30 |  | 16:00
10 | Maximum Load Shed (MW) at Evening Peak | 674 | 2026-05-21 | 2086 | 2026-04-22 | 380 | 2025-05-27 | 4395 | 04/10/2022
|  |  | 21:00 Hr. |  | 20:00 Hr. |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 16531.26 | 2026-05-21 | 14467.04 | 2026-04-22 | 16023.29 | 2025-05-27 | 16531.26 | 2026-05-21
|  |  | 21:00 Hr. |  | 20:00 Hr. |  | 21:00 |  | 21:00 Hr.
12 | Minimum Load Shed (MW) at Evening Peak | 5 | 2026-05-26 | 35 | 2026-04-10 | 0 | 2025-05-01 | - | -
|  |  | 21:00 Hr. |  | 19:30 Hr. |  | 20:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 11164.63 | 2026-05-26 | 12714.59 | 2026-04-10 | 11428 | 2025-05-01 | - | -
|  |  | 21:00 Hr. |  | 19:30 Hr. |  | 20:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 449 | 2026-05-23 | 2493 | 2026-04-22 | 300 | 2025-05-14 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 14442.69 | 2026-05-23 | 13116.11 | 2026-04-22 | 13979.15 | 2025-05-14 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 30 | 2026-05-11 | 62 | 2026-04-03 | 0 | 2025-05-01 | - | -
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 13848.62 | 2026-05-11 | 13369.18 | 2026-04-03 | 10976.06 | 2025-05-01 | - | -
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 24 |  | 24 |  | 24 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 18 |  | 23 |  | 22 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 932.8558 |  | 961.1528 |  | 1192.13 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 19.0718 |  | 17.9504 |  | 56.7683 |  | - | -
22 | Net Generation of BPDB (MKWH) | 913.784 |  | 943.2024 |  | 1135.3617 |  | - | -
23 | Net Generation of IPP (MKWH) | 2521.7942 |  | 2382.4425 |  | 4035.8994 |  | - | -
23b | Net Generation by Generation Companies | 4303.233 |  | 4165.6817 |  | 2948.2899
24 | Net Generation of REB (MKWH) | 45.2413 |  | 47.8268 |  | 37.7987 |  | - | -
25 | Net Generation of Rental Power Plant (MKWH) | 85.8564 |  | 70.7437 |  | 130.595 |  | - | -
26 | Total Net Generation (MKHWh) (Excluding Import) | 7869.909 |  | 7609.897 |  | 8287.9448 |  | - | -
27 | Energy Generation by Gas (MKWH) | 3935.5908 |  | 3680.8197 |  | 4159.3337 |  | - | -
28 | Energy Generation by Diesel (MKWH) | 3.6008 |  | 20.2439 |  | 0.03 |  | - | -
29 | Energy Generation by Furnace Oil (MKWH) | 615.5792 |  | 934.0014 |  | 1116.0073 |  | - | -
30 | Energy Generation by Hydro (MKWH) | 37.396 |  | 44.552 |  | 28.7773 |  | - | -
31 | Energy Generation by Solar (MKWH) | 123.8147 |  | 124.9061 |  | 118.4392 |  | 149.04 | 2026-04-25
31b | Energy Generation by Wind (MKWH) | 6.8957 |  | 6.2407 |  | 9.2213 |  | - | -
32 | Energy Generation by Coal (MKWH) | 3166.1036 |  | 2817.0837 |  | 2912.9044 |  | 3166.1036
33 | Enegry Import from India (MKWH) | 1528.8924 |  | 1466.7946 |  | 1553.6413 |  | - | -
34 | Monthly Load Factor (%) | 73.5922 |  | 83.1071 |  | 80.1315 |  | 86.52 | 2026-09-25

## QF-LDC-22
QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: May 2026
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 17200.79 | 2026-05-20 | 21:00 Hr.
Generation Period
| Dhaka | MW | 6212.63
| Chattogram | MW | 1681.8
| Cumilla | MW | 1621
| Mymensingh | MW | 994
| Sylhet | MW | 678
a) | Total supply in East zone | MW | 11187.43
| Khulna | MW | 2058.5
| Barisal | MW | 533
| Rajshahi | MW | 1820.8
| Rangpur | MW | 1137
b) | Total supply in West zone | MW | 5549.3
c) | Total supply in both zone ( a+b) | MW | 16736.73
Ref: | 27.21.0000.603.16.087.20.978 | Date: 15/06/2026
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month: May 2026
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Maximum power Export through EWI/ NO-1
| a) Ishurdi end | AMPS | 577 | 2026-05-18 | 14:00
|  | MW | 238
| b) Ghorashal end | AMPS | 90 | 28/05/2026 | 8:00
|  | MW | 33
18 | Maximum power Import through EWI/ NO-1 |  |  | -
| a) Ishurdi end | AMPS | 88 | 28/05/2026 | 7:00
|  | MW | 29
| b) Ghorashal end | AMPS | 597 | 18/05/2026 | 22:00
|  | MW | 219
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ishurdi end | MWh | 4034.618 | 2026-05-09 | N/A
| b) Ghorashal end | MWh | 126.561 | 2026-05-28
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 123.781 | 2026-05-28
| b) Ghorashal end | MWh | 3828 | 2026-05-09 | N/A
21 | Total Energy Export through EWI/ NO-1
| a) Ishurdi end | MWh | 89444.07
| b) Ghorashal end | MWh | 201.58
22 | Total Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 195.7
| b) Ghorashal end | MWh | 86760.75
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Maximum power Export through EWI/ NO-2
| a) Sirajganj end | AMPS | 1990 | 2026-05-18
|  | MW | 772
| b) Sreepur end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
25 | Maximum power Import through EWI/ NO-2 |  | - | -
| a) Sirajganj end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
| b) Sreepur end | AMPS | 2042 | 2026-05-18 | -
|  | MW | 748
26 | Daily Maximum Energy Export through EWI/NO-2
| a) Sirajganj end | MWh | 8354 | - | -
| b) Sreepur end | MWh | - | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Sirajganj end | MWh | 0 | - | -
| b) Sreepur end | MWh | 7995 | - | -
28 | Total Energy Export through EWI/ NO-2
| a) Sirajganj end | MWh | 350024 | - | -
| b) Sreepur end | MWh | 0 | - | -
29 | Total Energy Import through EWI/ NO-2
| a) Sirajganj end | MWh | 0 | - | -
| b) Sreepur end | MWh | 339791.6 | - | -
30 | Transmission loss of EWI/ NO-2 | % | 2.92 | - | -
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 3512 | 2026-05-24 | 9:00
|  | MW | 2154
| b) Aminbazar end | AMPS | 0
|  | MW | 0
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | 0
|  | MW | 0
| b) Aminbazar end | AMPS | 3500 | 2026-05-24 | 9:00
|  | MW | 2153
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 45010 | 2026-05-23 | N/A
| a) Aminbazar end | MWh | 0
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0 | - | N/A
| a) Aminbazar end | MWh | 44884 | 2026-05-23
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 1053230
| b) Aminbazar end (ckt-1 ) | MWh | 0
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0
| b) Aminbazar end (ckt-2 ) | MWh | 1049332
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.37
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: May 2026
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH) |  |  | #REF!
Dhaka (North) Grid Circle : | [10 empty] | #REF!
Bhaluka 132/33kV | 03. Transformer-03 | 2026-05-15 15:38:00 | 2026-05-15 15:43:00 | 0.0034722 | T | Tripped | 7 | 0.58333 | Power interruption |  | #REF!
Bhaluka 132/33kV | 01. Transformer- 01 | 2026-05-19 21:47:00 | 2026-05-19 22:00:00 | 0.0090278 | T | None | 75 | 16.25 | Power interruption |  | #REF!
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-05-19 21:47:00 | 2026-05-19 22:00:00 | 0.0090278 | T | Tripped | 75 | 16.25 | Power interruption |  | #REF!
Bhaluka 132/33kV | 03. Transformer-03 | 2026-05-26 05:10:00 | 2026-05-26 05:42:00 | 0.022222 | T | Tripped | 2 | 1.0667 | Power interruption |  | #REF!
Ghatail 132/33kV | T-1 | 2026-05-21 06:18:00 | 2026-05-21 15:07:00 | 0.36736 | T | Birds flying | 56 | 493.7333 | Power interruption |  | #REF!
Ghatail 132/33kV | T-2 | 2026-05-21 06:18:00 | 2026-05-21 07:26 | 0.047222 | T | Birds flying | 28 | 31.7333 | Power interruption |  | 0.10556
Kishoreganj 132/33kV | Tr-3 (424T) | 2026-05-07 10:54:00 | 2026-05-07 11:11:00 | 0.011806 | T | Due to PBS 33 KV Pakundia feeder trip. | 25 | 7.0833 | Power interruption |  | 0.084722
Mymensingh 132/33kV | Transformer-1 (404T) | 2026-05-27 08:26:00 | 2026-05-27 08:46:00 | 0.013889 | T | 33 kv Akua feeder fault. | 30 | 10 | Power interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2026-05-27 08:26:00 | 2026-05-27 08:46:00 | 0.013889 | T | 33 Kv Akua feeder fault. | 30 | 10 | Power interruption |  | #REF!
Nabinagar 132/33kV | T-1 | 2026-05-16 12:08:00 | 2026-05-16 12:18:00 | 0.0069444 | T | Over Load | 105 | 17.5 | Power interruption |  | #REF!
Rajendrapur 132/33kV | MTR-1 | 2026-05-26 12:17:00 | 2026-05-26 12:39:00 | 0.015278 | T | Tripped | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2026-05-26 12:17:00 | 2026-05-26 12:40:00 | 0.015972 | T | Tripped | 2 | 0.76667 | Power interruption
Rajendrapur 132/33kV | MTR-3 | 2026-05-26 12:17:00 | 2026-05-26 12:40:00 | 0.015972 | T | Tripped | 2 | 0.76667 | Power interruption
Shahmirpur 132/33kV | 416T | 2026-05-02 20:20:00 | 2026-05-05 20:01:00 | 1900-01-01 23:41 | T | Earth fault | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2026-05-23 08:22:00 | 2026-05-23 08:56:00 | 0.023611 | T | Nalitabari 33 kv fedder fault & bad weather . | 8 | 4.5333 | Power interruption
Sherpur 132/33kV | Transformer- 02 | 2026-05-23 08:22:00 | 2026-05-23 08:56:00 | 0.023611 | T | Nalitabari 33 Kv feeder fault & bad weaher. | 8 | 4.5333 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2026-05-16 18:57:00 | 2026-05-16 19:15:00 | 0.0125 | T | Over Load | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2026-05-25 14:01:00 | 2026-05-25 14:10:00 | 0.00625 | T | df/dt | 29 | 4.35 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2026-05-30 15:38:00 | 2026-05-30 15:46:00 | 0.0055556 | T | df/dt | 22 | 2.9333 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2026-05-30 15:38:00 | 2026-05-30 15:46:00 | 0.0055556 | T | df/dt | 19 | 2.5333 | Power interruption
Tangail 132/33kV | Tr-1 | 2026-05-18 05:32:00 | 2026-05-18 10:45:00 | 0.21736 | T | 33kV Shakhipur feeder fault. | 0 | 0 | No interruption
Tangail 132/33kV | Tr-2 | 2026-05-18 05:32:00 | 2026-05-18 17:42:00 | 0.50694 | T | 33kV Shakhipur feeder fault. | 0 | 0 | No interruption
Tangail 132/33kV | Tr-1 | 2026-05-26 10:49:00 | 2026-05-26 11:32:00 | 0.029861 | T | 33kv kachuadanga feeder source DS Loop Out from 33kv Bus. | 47 | 33.6833 | Power interruption
Tangail 132/33kV | Tr-2 | 2026-05-26 10:49:00 | 2026-05-26 13:44:00 | 0.12153 | T | 33Kv kachuadanga Feeder source DS loop out from 33Kv bus. | 47 | 137.0833 | Power interruption
Tangail 132/33kV | Tr-1 | 2026-05-28 18:06:00 | 2026-05-28 18:16:00 | 0.0069444 | T | 33Kv bus PT Fail | 50 | 8.3333 | Power interruption
Tangail 132/33kV | Tr-2 | 2026-05-28 18:06:00 | 2026-05-28 18:28:00 | 0.015278 | T | 33 kv Bus PT Fail | 50 | 18.3333 | Power interruption
Aminbazar 400/230/132kV | 230/132kv Tr-01 | 2026-05-29 14:48:00 | 2026-05-29 18:44:00 | 0.16389 | E/O | Red hot maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 132 kv Bus 02 | 2026-05-29 15:09:00 | 2026-05-29 18:17:00 | 0.13056 | E/O | Red hot maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | Bus A | 2026-05-10 11:58:00 | 2026-05-10 13:55:00 | 0.08125 | E/O | High temperature maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-3 (424T) | 2026-05-16 15:02:00 | 2026-05-16 18:10:00 | 0.13056 | E/O | Oil sample collection | 0 | 0 | No interruption
Ghatail 132/33kV | T-2 | 2026-05-21 11:10:00 | 2026-05-21 14:50:00 | 0.15278 | E/O | Insulator disc replacement of 33kV bus section isolator/DS. | 30 | 110 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2026-05-08 09:41:00 | 2026-05-08 11:15:00 | 0.065278 | E/O | High Temperature maintenance work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 230kV Bus 1 | 2026-05-20 04:43:00 | 2026-05-20 04:43:00 | 0 | E/O | Trip | 0 | 0 | No interruption
New Tongi | T1(403T) | 2026-05-24 13:23:00 | 2026-05-24 14:36:00 | 0.050694 | E/O | S/down due to temperature rise at 33 kv loop joint | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 01 | 2026-05-30 09:01:00 | 2026-05-30 11:14:00 | 0.092361 | E/O | Rad hot maintenance Work. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2026-05-06 13:19:00 | 2026-05-06 14:55:00 | 0.066667 | E/O | CCCC's project measurement work | 48 | 76.8 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2026-05-24 20:22:00 | 2026-05-24 21:28:00 | 0.045833 | E/O | DS repair work (PBS end) | 0 | 0 | No interruption
Tangail 132/33kV | Tr-2 | 2026-05-30 09:59:00 | 2026-05-30 12:09:00 | 0.090278 | E/O | S/D taken by BPDB Due to red hot at 33kv T2 bus section DS. | 40 | 86.6667 | Power interruption
|  |  | Total : | 1900-01-04 14:01 |  | Unserved Energy: |  | 1095.5167
Dhaka (South) Grid Circle :
Madanganj 132/33kV | GT-2 | 2026-05-18 20:10:00 | 2026-05-18 20:37:00 | 0.01875 | T | Heavy rain and storm | 25 | 11.25 | Power interruption
Madanganj 132/33kV | GT-2 | 2026-05-25 13:02:00 | 2026-05-25 20:00:00 | 0.29028 | T | O/C & E/F | 14 | 7 | Power interruption 13:02 to 13:32
Madanganj 132/33kV | GT-2 | 2026-05-30 16:41:00 | 2026-05-30 16:57:00 | 0.011111 | T | 33kv Shah cement feeder earth fault | 10 | 2.6667 | Power interruption
Maniknagar 230/132kV | Auto Transformer-02 (715T) | 2026-05-26 04:45:00 | 2026-05-26 10:05:00 | 0.22222 | T | WTI/OTI Fault | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-1 | 2026-05-01 17:13:00 | 2026-05-01 17:34:00 | 0.014583 | T | Tripped | 30 | 10.5 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2026-05-01 17:13:00 | 2026-05-01 17:34:00 | 0.014583 | T | Tripped | 30 | 10.5 | Power interruption
Munshiganj 132/33kV | Transformer-1 | 2026-05-27 10:20:00 | 2026-05-27 11:19:00 | 0.040972 | T | Tripped | 20 | 19.6667 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2026-05-27 10:20:00 | 2026-05-27 11:08:00 | 0.033333 | T | Tripped | 20 | 16 | Power interruption
Munshiganj 132/33kV | Transformer-1 | 2026-05-27 14:01:00 | 2026-05-27 14:14:00 | 0.0090278 | T | Due to detect a Fault | 50 | 10.8333 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2026-05-27 14:01:00 | 2026-05-27 14:16:00 | 0.010417 | T | Due to detect a Fault | 50 | 12.5 | Power interruption
Nawabganj 132/33kV | TR-2 | 2026-05-02 12:14:00 | 2026-05-02 12:24:00 | 0.0069444 | T | Due to 33Kv Nikra feeder fault. | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-2 | 2026-05-29 16:53:00 | 2026-05-29 17:03:00 | 0.0069444 | T | 33kV Agla feeder earth fault. | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-2 | 2026-05-29 17:53:00 | 2026-05-29 18:05:00 | 0.0083333 | T | Agla feeder earth fault | 0 | 0 | No interruption
Siddhirganj 230/132kV | MTR 1 | 2026-05-01 17:10:00 | 2026-05-01 17:10:00 | 0 | T | Unexpectedly fire broke out in the MTR-1 and MTR-1 Tripped. | 0 | 0 | No interruption
Srinagar 132/33kV | Tr-01 | 2026-05-17 07:55:00 | 2026-05-17 08:03:00 | 0.0055556 | T | 33 KV Feeder 2 Tripped due to bad weather | 10 | 1.3333 | Power interruption
Srinagar 132/33kV | Tr-02 | 2026-05-17 07:55:00 | 2026-05-17 08:03:00 | 0.0055556 | T | 33 KV Feeder 2 Tripped due to bad weather | 10 | 1.3333 | Power interruption
Bhulta 132/33kV | GT1 | 2026-05-23 21:52:00 | 2026-05-24 05:50:00 | 0.33194 | E/O | 33 KV LT Bushing Red Hot | 50 | 398.3333 | Power interruption
Ghorashal 230kV | TARFO-2 | 2026-05-31 20:22:00 | 2026-05-31 20:38:00 | 0.011111 | E/O | Ghorasal PDB AIS Grid End fault | 60 | 16 | Power interruption
Hasnabad 230/132kV | AUTO TR-2 | 2026-05-01 09:05:00 | 2026-05-01 11:31:00 | 0.10139 | E/O | 132 kv R-Phse CT joint high temperature maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-3 | 2026-05-01 11:35:00 | 2026-05-01 14:31:00 | 0.12222 | E/O | DS -322M end temperature rising | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-2 | 2026-05-27 14:48:00 | 2026-05-27 16:12:00 | 0.058333 | E/O | 132kv reserve bus mintennce work | 0 | 0 | No interruption
Madanganj 132/33kV | BUS Coupler | 2026-05-02 11:25:00 | 2026-05-02 19:00:00 | 0.31597 | E/O | 132 KV Basundhara bay equipment test | 0 | 0 | No interruption
Madanganj 132/33kV | BUS Coupler | 2026-05-26 15:15:00 | 2026-05-26 18:55:00 | 0.15278 | E/O | Haripur-1 Main bus DS emergency maintenance | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-2 | 2026-05-29 09:18:00 | 2026-05-29 10:03:00 | 0.03125 | E/O | Red hot on 33KV incoming bus to PBS 33KV feeder | 40 | 30 | Power interruption
Nawabganj 132/33kV | TR-1 | 2026-05-02 20:03:00 | 2026-05-02 20:56:00 | 0.036806 | E/O | Emergency red hot maintenance 33kV incomer-01 bus side. | 9 | 7.95 | Power interruption
Nawabganj 132/33kV | TR-1 | 2026-05-04 07:05:00 | 2026-05-04 09:40:00 | 0.10764 | E/O | Redhot maintenance | 9 | 23.25 | Power interruption
Nawabganj 132/33kV | TR-2 | 2026-05-04 16:08:00 | 2026-05-04 18:51:00 | 0.11319 | E/O | Due to red hot maintenance(Bay-105, R-phase DS) | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-1 | 2026-05-14 07:03:00 | 2026-05-14 08:22:00 | 0.054861 | E/O | 33kV Nawabganj pbs feeder DS red hot maintenance. | 18 | 23.7 | Power interruption
Nawabganj 132/33kV | TR-2 | 2026-05-16 21:02:00 | 2026-05-16 23:08:00 | 0.0875 | E/O | Emergency red hot maintenance at 33kV incomer-02, BUS section-02 side. | 15 | 31.5 | Power interruption
|  |  | Total : | 1900-01-01 05:22 |  | Unserved Energy: |  | 634.3167
Chattogram Grid Circle :
Baroaulia 132/33kV | SASM | 2026-05-27 12:36:00 | 2026-05-27 12:50:00 | 0.0097222 | T | Bad weather | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2026-05-02 17:01:00 | 2026-05-03 11:34:00 | 0.77292 | T | Buchloz relay tripping | 0 | 0 | No interruption
TK chemical | 50/75 MVA T-1(405T) | 2026-05-28 14:23:00 | 2026-05-28 19:00:00 | 0.19236 | T | Cable problem in LT side of T-1 transformer | 1 | 4.6167 | Power interruption
Baroaulia 132/33kV | T-1(405T) | 2026-05-22 06:06:00 | 2026-05-22 09:15:00 | 0.13125 | E/O | High temperature maintenance. | 10 | 31.5 | Power interruption
Mirsorai 230/33kV | TR-1, 718T | 2026-05-23 11:00:00 | 2026-05-23 11:00:00 | 0 | E/O | Flashing has been noticed in the secondary side of the transformer. Therefore, it needs to be checked and maintenance | 0 | 0 | No interruption
Rampur 230/132/33 | TR 02 (417T) | 2026-05-13 06:30:00 | 2026-05-13 08:50:00 | 0.097222 | E/O | Red hot Maintenance | 0 | 0 | No interruption
TK chemical | 48/64MVA T-2(415T) | 2026-05-26 15:52:00 | 2026-05-26 16:49:00 | 0.039583 | E/O | “Due to sparking fault at the connector of Transformer-2 secondary blue bushing.” | 14 | 13.3 | Power interruption
|  |  | Total : | 1899-12-31 05:50 |  | Unserved Energy: |  | 49.4167
Cumilla Grid Circle :
Brahmanbaria 132/33kV | 402T | 2026-05-06 09:08:00 | 2026-05-06 09:30:00 | 0.015278 | T | Tripped | 55 | 20.1667 | Power interruption
Brahmanbaria 132/33kV | 402T | 2026-05-10 04:52:00 | 2026-05-10 05:10:00 | 0.0125 | T | Tripped | 70 | 21 | Power interruption
Chandpur 132/33kV | 412T (T-2) | 2026-05-29 19:21:00 | 2026-05-30 15:24:00 | 0.83542 | T | Tripped | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-05-26 11:55:00 | 2026-05-26 12:11:00 | 0.011111 | T | 33 KV Datter Hat Feeder Fault | 20 | 5.3333 | Power interruption
Chowmuhani 230/132/33kV | TR2-425T | 2026-05-26 11:55:00 | 2026-05-26 12:11:00 | 0.011111 | T | 33 KV Datter Hat Feeder Fault | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | TR2-425T | 2026-05-29 18:29:00 | 2026-05-29 19:38:00 | 0.047917 | T | Stromy weather REB Sadar feeder fault. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV ATR-02 | 2026-05-26 06:00:00 | 2026-05-26 12:50:00 | 0.28472 | T | Tripped | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-3 | 2026-05-09 16:27:00 | 2026-05-09 16:40:00 | 0.0090278 | T | Feeder fault | 30 | 6.5 | Power interruption
Cumilla(S) 132/33kV | TR-4 | 2026-05-09 16:27:00 | 2026-05-09 16:40:00 | 0.0090278 | T | FEEDER FAULT | 30 | 6.5 | Power interruption
Daganbhuiyan 132/33kV | Transformer-2 | 2026-05-25 20:22:00 | 2026-05-26 14:39:00 | 0.76181 | T | Due to PT Loop Disconnect of 33kv Companygonj Feeder | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2026-05-13 21:30:00 | 2026-05-13 21:57:00 | 0.01875 | T | Sultanpur 33kv feeder fault | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2026-05-01 18:30:00 | 2026-05-01 18:44:00 | 0.0097222 | T | None | 12 | 2.8 | Power interruption
Kulaura 132/33kV | TR-1 AB | 2026-05-24 04:17:00 | 2026-05-24 06:17:00 | 0.083333 | T | Over current fault | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 | 2026-05-27 11:02:00 | 2026-05-27 11:10:00 | 0.0055556 | T | 33 kv Sobornachar feeder closed and Trip. 132kv x-former T-1 Primary GCB403B, Secondary VCB407B Trip | 0 | 0 | No interruption
Maijdee 132/33kV | Tr-02 | 2026-05-29 19:14:00 | 2026-05-29 19:30:00 | 0.011111 | T | 33kv mohabbatpur feeder closed and Trip. 132kv X-former Tr-2 primary GCB 413B Trip & secondary VCB 417B Trip. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2026-05-17 23:48:00 | 2026-05-18 00:22:00 | 0.023611 | T | Heavy Rain and Stormy Weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2026-05-18 00:28:00 | 2026-05-18 00:41:00 | 0.0090278 | T | Shaistaganj Feeder Trip | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-02 | 2026-05-23 00:32:00 | 2026-05-23 00:53:00 | 0.014583 | T | Chunarughat and Shaitaganj Feeder Trip. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-05-24 09:25:00 | 2026-05-24 09:52:00 | 0.01875 | T | Pran jamuna-2 Flashing | 0 | 0 | No interruption
Sunamganj 132/33kV | Tr-1 | 2026-05-29 19:01:00 | 2026-05-29 20:20:00 | 0.054861 | T | OC phase L2, OC phase L1, General trip,HV OC, Mechanical protection etc | 20 | 26.3333 | Power interruption
Chandina 132/33kV | TR-2 | 2026-05-06 18:27:00 | 2026-05-08 04:21 | 1899-12-31 09:54 | T | Differential Trip | 0 | 0 | No interruption
Chandina 132/33kV | TR-2 | 2026-05-05 13:03:00 | 2026-05-05 15:10:00 | 0.088194 | E/O | For Rectification of Red Hot Issue at 33kV Bus DS. | 0 | 0 | No interruption
Chandina 132/33kV | TR-3 | 2026-05-05 16:50:00 | 2026-05-05 17:29:00 | 0.027083 | E/O | For rectification of Red hot . | 0 | 0 | No interruption
Chandina 132/33kV | TR-2 | 2026-05-12 17:02:00 | 2026-05-14 18:39:00 | 1900-01-01 01:37 | E/O | Due to the maintenance work for the 33kV CT of TR02. | 0 | 0 | No interruption
Beanibazar 132/33kV | 132KV Transformer TR-02 | 2026-05-24 13:52:00 | 2026-05-24 15:34:00 | 0.070833 | E/O | Red Hot Maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 401T | 2026-05-22 10:58:00 | 2026-05-22 11:40:00 | 0.029167 | E/O | redhot at 33 kv kasba feeder bus DS | 15 | 10.5 | Power interruption
Chandpur 132/33kV | Bus A | 2026-05-23 08:48:00 | 2026-05-23 17:48:00 | 0.375 | E/O | Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | Bus-B | 2026-05-24 09:30:00 | 2026-05-24 11:26:00 | 0.080556 | E/O | Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | 422T(T-5) | 2026-05-30 15:23:00 | 2026-05-30 15:23:00 | 0 | E/O | Emergency maint.work | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | TR2-425T | 2026-05-05 23:22:00 | 2026-05-06 00:58:00 | 0.066667 | E/O | 33 kV BUS Jumper R phase & Y Phase red-hot Maintenance. | 30 | 48 | Power interruption
Chowmuhani 230/132/33kV | TR1-415T | 2026-05-17 10:06:00 | 2026-05-17 13:53:00 | 0.15764 | E/O | Project equipment shift. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | TR2-425T | 2026-05-25 18:07:00 | 2026-05-25 20:40:00 | 0.10625 | E/O | 33kV LBUS BUS DS loop Redhot Maintenance. NPBS will do the maintenance work. | 20 | 51 | Power interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-05-26 19:43:00 | 2026-05-26 22:18:00 | 0.10764 | E/O | Redhot | 10 | 25.8333 | Power interruption
Chowmuhani 230/132/33kV | TR2-425T | 2026-05-26 23:25:00 | 2026-05-27 00:46:00 | 0.05625 | E/O | Emergency shutdown taken for 132/33 kV, TR-02 X-former today at 18:07 for 33kV LBUS BUS DS loop Redhot Maintenance. 20MW Load shed will occur. Informed all utilities. NPBS will do the maintenance work. | 20 | 27 | Power interruption
Chowmuhani 230/132/33kV | TR1 | 2026-05-29 22:30:00 | 2026-05-29 23:15:00 | 0.03125 | E/O | 33kV maijdee Feeder BUS DS redhot maintenance. | 30 | 22.5 | Power interruption
Chowmuhani 230/132/33kV | TR3 | 2026-05-29 23:38:00 | 2026-05-30 02:40:00 | 0.12639 | E/O | 33kv Bus loop Red-hot maintenance. | 25 | 75.8333 | Power interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2026-05-06 22:27:00 | 2026-05-06 23:58:00 | 0.063194 | E/O | 33 kv bus red hot maintenance | 10 | 15.1667 | Power interruption
Kasba 132/33kV | TR-1 | 2026-05-18 17:42:00 | 2026-05-18 17:50:00 | 0.0055556 | E/O | SD for pbs grounding wire repair | 10 | 1.3333 | Power interruption
Sylhet 132/33kV | T4 | 2026-05-14 09:24:00 | 2026-05-14 09:24:00 | 0 | E/O | Bockholz Alarm appeared on. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 02:51 |  | Unserved Energy: |  | 365.8
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-1 (403T) | 2026-05-01 19:01:00 | 2026-05-01 19:41:00 | 0.027778 | T | Earth Fault | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-1 (403T) | 2026-05-04 11:42:00 | 2026-05-04 16:44:00 | 0.20972 | T | Tripped | 0 | 0 | No interruption
Barishal 132/33kV | T-1 (405T) | 2026-05-16 18:47:00 | 2026-05-16 19:10:00 | 0.015972 | T | Due to auxiliary transformer fuse fault | 50 | 19.1667 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2026-05-18 20:06:00 | 2026-05-18 20:10:00 | 0.0027778 | T | 33kV Dopdopia WZPDCL feeder fault | 30 | 2 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2026-05-20 16:22:00 | 2026-05-20 16:31:00 | 0.00625 | T | 33 kv Dopdopia 1& Nolcity 33 feeder fault. | 47 | 7.05 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2026-05-26 13:34:00 | 2026-05-26 13:39:00 | 0.0034722 | T | Polashpur 33kV WZPDCL feeder fault | 40 | 3.3333 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2026-05-29 18:05:00 | 2026-05-29 18:19:00 | 0.0097222 | T | Dopdapia -2 WZPDCL (33kV feeder fault) | 6 | 1.4 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2026-05-03 18:37:00 | 2026-05-03 19:23:00 | 0.031944 | T | WZPDCL kathalia 33kv cable fault | 37 | 28.3667 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2026-05-03 18:37:00 | 2026-05-03 19:23:00 | 0.031944 | T | WZPDCL kathalia 33 kv Fault | 16 | 12.2667 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2026-05-18 20:21:00 | 2026-05-18 22:21:00 | 0.083333 | T | Oxilary transformer DS pin insulator Blust | 6 | 12 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2026-05-18 20:21:00 | 2026-05-18 22:24:00 | 0.085417 | T | Oxilary transformer DS pin insulator Blust | 6 | 12.3 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2026-05-29 16:52:00 | 2026-05-29 17:33:00 | 0.028472 | T | PBS Mathbaria 33kV Load side DS fault | 28 | 19.1333 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2026-05-29 16:52:00 | 2026-05-29 17:33:00 | 0.028472 | T | PBS Mathbaria 33kV Load side DS fault | 28 | 19.1333 | Power interruption
Gopalganj 132/33kV | T1 | 2026-05-27 08:06:00 | 2026-05-27 08:35:00 | 0.020139 | T | 33kv feeder fault with stormy weather. | 0 | 0 | No interruption
Gopalganj 132/33kV | T2 | 2026-05-27 08:06:00 | 2026-05-27 08:35:00 | 0.020139 | T | 33kv feeder fault with stormy weather | 0 | 0 | No interruption
Gopalganj 132/33kV | Modhumoti 100MW PS | 2026-05-29 16:21:00 | 2026-05-29 17:17:00 | 0.038889 | T | D/T due to heavy storm. | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-05-27 07:48:00 | 2026-05-27 08:40:00 | 0.036111 | T | 33kv feeder fault | 0 | 0 | No interruption
Mongla 132/33kV | T-1 | 2026-05-13 07:00:00 | 2026-05-13 07:56:00 | 0.038889 | T | Earth fault pro.trip | 22 | 20.5333 | Power interruption
Rajbari 132/33kV | Transformer-3 | 2026-05-27 07:28:00 | 2026-05-27 10:48:00 | 0.13889 | T | OVERFLUX | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2026-05-30 07:36:00 | 2026-05-30 07:42:00 | 0.0041667 | T | Due to kalaroa 33 kV feeder fault | 36 | 3.6 | Power interruption
Satkhira 132/33kV | Transformer-1 (T-1) | 2026-05-30 21:12:00 | 2026-05-30 21:15:00 | 0.0020833 | T | None | 86 | 4.3 | Power interruption
Benapole 132/33kV | Transformer-1(406T) | 2026-05-11 09:12:00 | 2026-05-11 11:12:00 | 0.083333 | E/O | Red Hot Maintenance at R phase Source side | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-2 | 2026-05-03 21:56:00 | 2026-05-03 23:30:00 | 0.065278 | E/O | Kathalia wz 33kv feeder source DS | 29 | 45.4333 | Power interruption
Borhanuddin 230/33kV | Bus | 2026-05-16 07:10:00 | 2026-05-16 07:10:00 | 0 | E/O | 33 kv incomer Breacar Red Hot maintains | 90 | 0 | No interruption
Mongla 132/33kV | T-2 | 2026-05-13 06:32:00 | 2026-05-13 08:29:00 | 0.08125 | E/O | Red hot | 25 | 48.75 | Power interruption
Noapara 132/33kV | T-1 | 2026-05-07 09:16:00 | 2026-05-07 09:34:00 | 0.0125 | E/O | Removal of kites from T-1 gentry tower. | 0 | 0 | No interruption
Rampal 400/230kV | Bus Reactor | 2026-05-30 13:26:00 | 2026-05-30 13:26:00 | 0 | E/O | NLDC DEMAND | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 02:34 |  | Unserved Energy: |  | 258.7667
HVDC Grid Circle :
BIPTC | 10CF16 | 2026-05-01 11:21:00 | 2026-05-03 11:34:00 | 1900-01-01 00:13 | T | Tripped by CPR04 Fault and 87 Differential Relay. | 0 | 0 | No interruption
BIPTC | 20DF43 | 2026-05-22 12:58:00 | 2026-05-23 16:13:00 | 1899-12-31 03:15 | T | Tripped | 0 | 0 | No interruption
BIPTC | 20DF13 | 2026-05-26 01:33:00 | 2026-05-26 12:22:00 | 0.45069 | T | Tripped by impedence 21R | 0 | 0 | No interruption
BIPTC | 10CF15 | 2026-05-28 23:04:00 | 2026-05-29 09:55:00 | 0.45208 | T | Tripped by C1 unbalance 60/61 instant L3 | 0 | 0 | No interruption
Bheramara(GK) 132/33kV | TR-3 | 2026-05-27 08:57:00 | 2026-05-27 09:07:00 | 0.0069444 | T | 33kV PBS Amla Feeder Fault | 11 | 1.8333 | Power interruption
Jashore 132/33kV | Cap. Bank-1 | 2026-05-08 13:16:00 | 2026-05-08 14:15:00 | 0.040972 | T | Grid failed | 0 | 0 | No interruption
Kushtia 132/33kV | T-1 | 2026-05-05 04:30:00 | 2026-05-05 05:01:00 | 0.021528 | T | Ov/Overflux Trip | 30 | 15.5 | Power interruption
Kushtia 132/33kV | T2 | 2026-05-05 04:30:00 | 2026-05-05 05:03:00 | 0.022917 | T | Ov/Overflux Trip | 41 | 22.55 | Power interruption
Kushtia 132/33kV | T-3 | 2026-05-05 04:50:00 | 2026-05-05 05:01:00 | 0.0076389 | T | Ov/Overflux Trip | 30 | 5.5 | Power interruption
Kushtia 132/33kV | T-1 | 2026-05-12 13:23:00 | 2026-05-12 17:36:00 | 0.17569 | T | Tripped | 0 | 0 | No interruption
Kushtia 132/33kV | T-3 | 2026-05-13 14:02:00 | 2026-05-13 14:33:00 | 0.021528 | T | ৩৩ কেভি আর-ফেইজ পিটি সাইডে সাপের দ্বারা শর্ট সার্কিট | 41 | 21.1833 | Power interruption
Magura 132/33kV | T-2 (415T) | 2026-05-07 05:23:00 | 2026-05-07 06:36:00 | 0.050694 | T | Differential protection-1 | 0 | 0 | No interruption
BIPTC | 10CF22 | 2026-05-18 15:50:00 | 2026-05-18 17:21:00 | 0.063194 | E/O | Corrective maintenance | 0 | 0 | No interruption
BIPTC | 10CF11 | 2026-05-20 11:58:00 | 2026-05-20 12:59:00 | 0.042361 | E/O | Emergency maintenance | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) | 2026-05-04 21:53:00 | 2026-05-04 22:32:00 | 0.027083 | E/O | RED HOT | 12 | 7.8 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-05-06 20:20:00 | 2026-05-06 22:57:00 | 0.10903 | E/O | Ct y phase redhot | 15 | 39.25 | Power interruption
Bhangura 132/33kV | Tr-1(403T) | 2026-05-10 15:55:00 | 2026-05-10 17:06:00 | 0.049306 | E/O | 33 kv bus red hot pbs side | 12 | 14.2 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-05-17 13:16:00 | 2026-05-17 15:48:00 | 0.10556 | E/O | Red Hot | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-05-25 20:47:00 | 2026-05-25 21:24:00 | 0.025694 | E/O | Red hot remove 33 kv bkr side | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-05-26 20:25:00 | 2026-05-26 21:03:00 | 0.026389 | E/O | Red hot 33 kv bkr | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) | 2026-05-30 20:06:00 | 2026-05-30 20:43:00 | 0.025694 | E/O | RED HOT | 0 | 0 | No interruption
Bheramara 230/132kV | Bus-B (132) | 2026-05-06 10:38:00 | 2026-05-06 12:42:00 | 0.086111 | E/O | Hotspot in Bus DS | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T1(416T) | 2026-05-24 10:26:00 | 2026-05-24 11:08:00 | 0.029167 | E/O | ঝড়ে খুলে যাওয়া PRD এর ঢাকনা লাগানো কাজ। | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-2 | 2026-05-03 07:10:00 | 2026-05-03 08:26:00 | 0.052778 | E/O | 33kV Y phase(Bus) Loop Conductor changing. | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-1 | 2026-05-03 07:11:00 | 2026-05-03 08:25:00 | 0.051389 | E/O | 33kV Y phase(Bus) Loop Conductor changing. | 40 | 49.3333 | Power interruption
Jhenaidah 132/33kV | Transformer T-3 | 2026-05-19 17:12:00 | 2026-05-19 18:10:00 | 0.040278 | E/O | 33kv T3A side DS, Y-phase nut bolt redhot under the T3 transformer. | 20 | 19.3333 | Power interruption
Jhenaidah 132/33kV | Transformer T-2 | 2026-05-26 12:03:00 | 2026-05-26 13:08:00 | 0.045139 | E/O | 33kV WZPDCL kotchadpur feeder DS bus side Red hot Maintenance. | 50 | 54.1667 | Power interruption
Kushtia 132/33kV | T-3 | 2026-05-06 15:48:00 | 2026-05-06 20:22:00 | 0.19028 | E/O | A fire incident occurred in the Y-phase control cable under the CT terminal box of the 132 kV CT of T-3 transformer. | 30 | 137 | Power interruption
Kushtia 132/33kV | T-1 | 2026-05-06 17:20:00 | 2026-05-07 13:31:00 | 0.84097 | E/O | Emergency redhot maintenance | 22 | 22 | Power interruption 17:20 to 18:20
Kushtia 132/33kV | T-3 | 2026-05-27 10:14:00 | 2026-05-27 12:06:00 | 0.077778 | E/O | Khoksha feeder red hot maintenance | 15 | 28 | Power interruption
Kushtia 132/33kV | T2 | 2026-05-27 12:10:00 | 2026-05-27 13:33:00 | 0.057639 | E/O | T-2A 33kV side R-phase CT source end red hot maintenance. | 0 | 0 | No interruption
Pabna 132/33kV | T-1 | 2026-05-04 10:30:00 | 2026-05-04 10:34:00 | 0.0027778 | E/O | 132 kv CB Maintenance work. | 0 | 0 | No interruption
Pabna 132/33kV | T-3 | 2026-05-13 06:55:00 | 2026-05-13 07:35:00 | 0.027778 | E/O | Atgoria 33 kv Redhot | 12 | 8 | Power interruption
Shahjadpur 132/33kV | T-1(405T) | 2026-05-28 20:14:00 | 2026-05-28 20:56:00 | 0.029167 | E/O | Emergency redhot maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 09:37 |  | Unserved Energy: |  | 445.65
Bogura Grid Circle:
Bogura 230/132kV | T-03 | 2026-05-27 05:42:00 | 2026-05-27 12:58:00 | 0.30278 | T | Raining, Storming, Thundering | 0 | 0 | No interruption
Bogura 230/132kV | T-03 | 2026-05-29 18:25:00 | 2026-05-29 19:26:00 | 0.042361 | T | Tripped | 0 | 0 | No interruption
Kurigram 132/33kV | Transformer T-1 (Tr-403T) | 2026-05-25 06:42:00 | 2026-05-25 07:03:00 | 0.014583 | T | Over voltage | 20 | 7 | Power interruption
Kurigram 132/33kV | Transformer T-2 (Tr-413T) | 2026-05-25 06:42:00 | 2026-05-25 07:03:00 | 0.014583 | T | Over Voltage | 20 | 7 | Power interruption
Kurigram 132/33kV | Transformer T-1 (Tr-403T) | 2026-05-31 12:25:00 | 2026-05-31 12:41:00 | 0.011111 | T | None | 29 | 7.7333 | Power interruption
Kurigram 132/33kV | Transformer T-2 (Tr-413T) | 2026-05-31 12:25:00 | 2026-05-31 12:41:00 | 0.011111 | T | None | 29 | 7.7333 | Power interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2026-05-26 09:13:00 | 2026-05-26 09:26:00 | 0.0090278 | T | Due to Niamatpur 33 kV faulty feeder trip | 1 | 0.21667 | Power interruption
Niamatpur 132/33kV | Transformer-3(426T) | 2026-05-26 09:50:00 | 2026-05-26 10:08:00 | 0.0125 | T | Due to Manda-1 33kV faulty feeder trip. | 2 | 0.6 | Power interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2026-05-27 08:22:00 | 2026-05-27 08:40:00 | 0.0125 | T | Niamatpur-2 feeder faulty | 13 | 3.9 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-05-30 11:03:00 | 2026-05-30 11:17:00 | 0.0097222 | T | PBS 33kv Sapahar feeder O/C & E/F Tripped. | 14 | 3.2667 | Power interruption
Purbasadipur 230/132/33kV | AIS Old TR-1 | 2026-05-06 12:08:00 | 2026-05-06 12:46:00 | 0.026389 | T | Cable blast of 33 kV Khansama Feeder (PBS) | 20 | 12.6667 | Power interruption
Purbasadipur 230/132/33kV | TR-4 | 2026-05-22 15:44:00 | 2026-05-22 15:59:00 | 0.010417 | T | Bochaganj 33kv feeder fault | 35 | 8.75 | Power interruption
Rangpur 132/33kV | T-1(414T) | 2026-05-17 07:10:00 | 2026-05-17 07:40:00 | 0.020833 | T | "Heavy rain and thunderstorms." | 0 | 0 | No interruption
Rangpur 132/33kV | T-2 (404T) | 2026-05-17 07:10:00 | 2026-05-17 07:40:00 | 0.020833 | T | "Heavy rain and thunderstorms." | 0 | 0 | No interruption
Saidpur 132/33kV | TR-5 (434T) | 2026-05-25 07:30:00 | 2026-05-25 07:55:00 | 0.017361 | T | Tripped | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-3, 404T | 2026-05-02 04:40:00 | 2026-05-02 14:28:00 | 0.40833 | E/O | Due to 33KV incoming panel annunciator burning | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T | 2026-05-11 16:36:00 | 2026-05-11 17:51:00 | 0.052083 | E/O | IED Device change work | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-3 | 2026-05-29 07:40:00 | 2026-05-29 11:40:00 | 0.16667 | E/O | 33kV Incoming DS (R-Phase) Red-Hot Maintenance work | 25 | 100 | Power interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2026-05-05 12:02:00 | 2026-05-06 18:10:00 | 1899-12-31 06:08 | E/O | Instructed by ALDC | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2026-05-11 19:02:00 | 2026-05-13 07:06:00 | 1899-12-31 12:04 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2026-05-19 13:48:00 | 2026-05-25 05:59:00 | 1900-01-04 16:11 | E/O | Increase system voltage. | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2026-05-26 17:36:00 | 2026-05-27 05:54:00 | 0.5125 | E/O | As per NLDC's Instruction | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2026-05-27 19:02:00 | 2026-05-27 19:02:00 | 0 | E/O | Voltage Up. | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-2 (415T) | 2026-05-09 11:05:00 | 2026-05-09 11:25:00 | 0.013889 | E/O | Transformer breaker Commission | 0 | 0 | No interruption
Mithapukur 132/33kV | TR-1(404T) | 2026-05-04 11:19:00 | 2026-05-04 13:15:00 | 0.080556 | E/O | Red hot maintenance work | 15 | 29 | Power interruption
Mithapukur 132/33kV | TR-1(404T) | 2026-05-18 08:34:00 | 2026-05-18 09:46:00 | 0.05 | E/O | Red hot in isolator clam | 14.5 | 17.4 | Power interruption
Mithapukur 132/33kV | TR-1(404T) | 2026-05-31 11:11:00 | 2026-05-31 12:55:00 | 0.072222 | E/O | Red hot maintenance. | 22 | 38.1333 | Power interruption
Niamatpur 132/33kV | Transformer-2 (417T) | 2026-05-24 07:06:00 | 2026-05-24 09:13:00 | 0.088194 | E/O | 33 kV Bus -2 PBS maintenance | 23 | 48.6833 | Power interruption
Palashbari 132/33kV | TR3-424T | 2026-05-10 14:47:00 | 2026-05-10 16:50:00 | 0.085417 | E/O | Red Hot Maintenance. | 0 | 0 | No interruption
Palashbari 132/33kV | BUS-B | 2026-05-10 14:48:00 | 2026-05-10 16:50:00 | 0.084722 | E/O | Red Hot Maintenance. | 0 | 0 | No interruption
Panchagarh 132/33kV | T-3(A+B)(427T) | 2026-05-22 09:28:00 | 2026-05-22 12:23:00 | 0.12153 | E/O | Red hot Maintenance work | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-05-30 22:33:00 | 2026-05-30 23:41:00 | 0.047222 | E/O | Red hot removing work at 33 Kv BUS side of Poba feeder. | 20 | 22.6667 | Power interruption
Rangpur 132/33kV | T-2 (404T) | 2026-05-21 20:20:00 | 2026-05-21 21:58:00 | 0.068056 | E/O | 33kv bus coupler -2 connector red hot | 30 | 49 | Power interruption
Rangpur 132/33kV | T-1(414T) | 2026-05-22 09:41:00 | 2026-05-22 11:39:00 | 0.081944 | E/O | Red hot | 0 | 0 | No interruption
Saidpur 132/33kV | TR-2 (404T) | 2026-05-25 13:12:00 | 2026-05-25 15:15:00 | 0.085417 | E/O | Red hot maintainance | 0 | 0 | No interruption
Sirajganj 132/33kV | T4-(445) | 2026-05-28 11:30:00 | 2026-05-28 12:17:00 | 0.032639 | E/O | Red hot bolt Replacement work at Tarash 33 kv incoming DS. | 8 | 6.2667 | Power interruption
Bog-Sherpur 132/33kV | Transformer-3 (424T) | 2026-05-16 15:02:00 | 2026-05-16 18:10:00 | 0.13056 | E/O | Oil sample collection | 0 | 0 | No interruption
|  |  | Total : | 1900-01-10 03:37 |  | Unserved Energy: |  | 370.0167
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-02-02 19:52 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-05-19 21:47:00 | 2026-05-19 21:57:00 | 0.0069444 | T | Tripped | 100 | 16.6667 | Power interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2026-05-19 21:47:00 | 2026-05-19 21:57:00 | 0.0069444 | T | Tripped | 100 | 16.6667 | Power interruption
Bog-Sherpur 132/33kV | Sherpur-Bogura Ckt-1 | 2026-05-09 02:05:00 | 2026-05-09 03:24:00 | 0.054861 | T | Tripped | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Sherpur-Sirajgonj Ckt-2 | 2026-05-18 02:59:00 | 2026-05-18 03:26:00 | 0.01875 | T | unknown | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2026-05-18 07:03:00 | 2026-05-18 07:27:00 | 0.016667 | T | O/C, E/F | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2026-05-25 09:45:00 | 2026-05-25 10:16:00 | 0.021528 | T | Trip | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2026-05-20 15:55:00 | 2026-05-20 16:10:00 | 0.010417 | T | Tripped | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2026-05-26 04:38:00 | 2026-05-26 04:42:00 | 0.0027778 | T | Grid Voltage High | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-2 | 2026-05-04 05:54:00 | 2026-05-04 06:06:00 | 0.0083333 | T | None | 62 | 12.4 | Power interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-05-10 14:01:00 | 2026-05-10 14:38:00 | 0.025694 | T | Bad weather | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-05-31 15:42:00 | 2026-05-31 16:20:00 | 0.026389 | T | Tripped | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2026-05-26 12:05:00 | 2026-05-26 21:22:00 | 0.38681 | E/O | DS maintenance Work | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-1 | 2026-05-04 12:25:00 | 2026-05-04 13:25:00 | 0.041667 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-1 | 2026-05-05 01:02:00 | 2026-05-05 02:59:00 | 0.08125 | E/O | Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 0.70903 |  | Unserved Energy: |  | 45.7333
Dhaka (South) Grid Circle :
Ghorashal 230kV | Ghorashal GIS- AIS Ckt-2 | 2026-05-31 19:26:00 | 2026-06-01 01:00:00 | 0.23194 | T | Ghorasal PDB AIS Grid End fault | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal power plant (4th unit- Main) - Ghorashal 230kv GIS S/S | 2026-05-31 19:26:00 | 2026-05-31 21:17:00 | 0.077083 | T | Ghorasal PDB AIS Grid End fault | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal power plant (4th unit- Main) - Ghorashal 230kv GIS S/S | 2026-05-31 19:26:00 | 2026-05-31 21:17:00 | 0.077083 | T | Ghorasal PDB AIS Grid End fault | 0 | 0 | No interruption
Haripur 230/132kV | Siddhirganj-1 | 2026-05-01 17:11:00 | 2026-05-01 18:16:00 | 0.045139 | T | Transformer fault at 230/132kV Siddhirganj S/S. | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2026-05-17 04:48:00 | 2026-05-17 05:05:00 | 0.011806 | T | Heavy Rain | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2026-05-24 17:50:00 | 2026-05-24 18:01:00 | 0.0076389 | T | Heavy rainfall (potential cause) | 0 | 0 | No interruption
Haripur 230/132kV | Madanganj-1 | 2026-05-25 13:12:00 | 2026-05-25 13:54:00 | 0.029167 | T | Rain & Storm | 0 | 0 | No interruption
Haripur 230/132kV | Siddhirganj-1 | 2026-05-29 17:45:00 | 2026-05-29 17:57:00 | 0.0083333 | T | Unknown. | 0 | 0 | No interruption
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2026-05-11 14:25:00 | 2026-05-11 15:18:00 | 0.036806 | T | Unknown | 70 | 61.8333 | Power interruption
Hasnabad 230/132kV | Hasnabad-Keraniganj Ckt-2 | 2026-05-26 12:14:00 | 2026-05-26 16:10:00 | 0.16389 | T | Flashing during heavy raining | 0 | 0 | No interruption
Hasnabad 230/132kV | Hasnabad-Keraniganj Ckt-2 | 2026-05-27 08:18:00 | 2026-05-30 20:10:00 | 1900-01-02 11:52 | T | Building construction within the right-of-way. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Hasnabad Ckt. 2 | 2026-05-26 12:14:00 | 2026-05-26 16:11:00 | 0.16458 | T | SOTF trip,B-phase pick up, | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Hasnabad Ckt. 2 | 2026-05-26 12:14:00 | 2026-05-26 16:11:00 | 0.16458 | T | SOTF trip,B-phase pick up, | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 2 | 2026-05-26 12:17:00 | 2026-05-26 13:13:00 | 0.038889 | T | 50-67N Earth fault trip,R-phase pick up,Zone-1 trip(16.3km) | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Hasnabad Ckt. 2 | 2026-05-27 08:17:00 | 2026-05-30 20:12:00 | 1900-01-02 11:55 | T | Zone-1 trip, R,Y,B phase pick up (7.9Km) | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Haripur 132 kv Ckt-2 | 2026-05-25 13:14:00 | 2026-05-25 13:40:00 | 0.018056 | T | Over current & earth fault. | 52 | 22.5333 | Power interruption
Madanganj 132/33kV | Madanganj -Summit 55 MW 132 kv Ckt | 2026-05-27 08:30:00 | 2026-05-27 08:54:00 | 0.016667 | T | Tripped | 0 | 0 | No interruption
Maniknagar 230/132kV | 230kV Siddhirganj-Maniknagar ckt-2 | 2026-05-13 18:57:00 | 2026-05-14 04:30:00 | 0.39792 | T | OPGW Cable failure under siddirganj Grid. | 0 | 0 | No interruption
Maniknagar 230/132kV | 230kV Siddhirganj-Maniknagar ckt-1 | 2026-05-17 04:25:00 | 2026-05-17 05:11:00 | 0.031944 | T | Thunderstrom | 0 | 0 | No interruption
Maniknagar 230/132kV | 230kV Siddhirganj-Maniknagar ckt-2 | 2026-05-17 04:34:00 | 2026-05-17 06:41:00 | 0.088194 | T | Thunderstrom | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Reliance PP 400KV Ckt-1 | 2026-05-30 15:38:00 | 2026-05-30 16:18:00 | 0.027778 | T | Tripped by Line Differential, Directional Earth Fault, Over current, 86.1 & 86.2 | 415 | 276.6667 | Power interruption
Nawabganj 132/33kV | Keraniganj-2 | 2026-05-26 12:17:00 | 2026-05-26 13:14:00 | 0.039583 | T | Due to heavy storm | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2026-05-07 22:42:00 | 2026-05-07 23:24:00 | 0.029167 | T | Weather | 0 | 0 | No interruption
Rampura 230/132kV | Dhaka University - 01 | 2026-05-09 18:06:00 | 2026-05-09 18:06:00 | 0 | T | Tripped | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2026-05-17 04:25:00 | 2026-05-17 04:58:00 | 0.022917 | T | Tripped | 0 | 0 | No interruption
Siddhirganj 132/33kV | Ullon 1 | 2026-05-17 04:35:00 | 2026-05-17 05:01:00 | 0.018056 | T | DiSTANCE RELAY 9.4 KM , heavy Rainy & stromy wind. | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT1 | 2026-05-25 13:12:00 | 2026-05-25 13:58:00 | 0.031944 | T | heavy rain strom | 0 | 0 | No interruption
Siddhirganj 132/33kV | 100MW Dutch Bangla | 2026-05-29 17:45:00 | 2026-05-29 19:28:00 | 0.071528 | T | DPDC'S earthing wire breaks and falls in to the line | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT2 | 2026-05-29 17:45:00 | 2026-05-29 19:36:00 | 0.077083 | T | Unknown | 0 | 0 | No interruption
Siddhirganj 230/132kV | Maniknagar 2 | 2026-05-13 18:58:00 | 2026-05-14 04:29:00 | 0.39653 | T | Trip | 0 | 0 | No interruption
Siddhirganj 230/132kV | Maniknagar 1 | 2026-05-17 04:27:00 | 2026-05-17 05:10:00 | 0.029861 | T | Trip | 0 | 0 | No interruption
Siddhirganj 230/132kV | Maniknagar 2 | 2026-05-17 04:34:00 | 2026-05-17 06:41:00 | 0.088194 | T | Trip | 194 | 410.6333 | Power interruption
Sonargaon 132/33kV | Bashundhara Line | 2026-05-16 03:40:00 | 2026-05-18 18:43:00 | 1900-01-01 15:03 | T | Due To line distance and diffential fault | 0 | 0 | No interruption
Sonargaon 132/33kV | OPSL(IEL-2) | 2026-05-25 13:05:00 | 2026-05-25 13:55:00 | 0.034722 | T | Bad weather | 0 | 0 | No interruption
Bhulta 400/230kV | Ghorashal-01 | 2026-05-23 12:18:00 | 2026-05-23 15:12:00 | 0.12083 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bhulta 400/230kV | Ghorashal-02 | 2026-05-23 17:14:00 | 2026-05-24 01:07:00 | 0.32847 | E/O | Emergency maint.work | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Shyampur-2 | 2026-05-24 19:50:00 | 2026-05-24 19:50:00 | 0 | E/O | Emergency maint.work | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2026-05-31 19:58:00 | 2026-05-31 20:33:00 | 0.024306 | E/O | Ghorasal PDB AIS Grid End fault | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal power plant (4th unit- Stand by) - Ghorashal 230kv GIS S/S | 2026-05-31 20:27:00 | 2026-05-31 21:17:00 | 0.034722 | E/O | Ghorasal PDB AIS Grid End fault | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal power plant (3rd unit) - Ghorashal 230kv GIS switching Station. | 2026-05-31 20:27:00 | 2026-05-31 21:18:00 | 0.035417 | E/O | Ghorasal PDB AIS Grid End fault | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2026-05-31 20:28:00 | 2026-05-31 21:46:00 | 0.054167 | E/O | Ghorasal PDB AIS Grid End fault | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal power plant (4th unit- Main) - Ghorashal 230kv GIS S/S | 2026-05-31 20:30:00 | 2026-05-31 21:17:00 | 0.032639 | E/O | Ghorasal PDB AIS Grid End fault | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal GIS- AIS Ckt-1 | 2026-05-31 22:20:00 | 2026-05-31 22:20:00 | 0 | E/O | Fault at Ghorashal AIS Grid End | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Bashundhara 132 kv Ckt | 2026-05-02 11:26:00 | 2026-05-02 18:07:00 | 0.27847 | E/O | 132 KV Basundhara bay equipment test | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2026-05-26 13:46:00 | 2026-05-26 21:20:00 | 0.31528 | E/O | Requested by Aminbazar SS | 0 | 0 | No interruption
Sonargaon 132/33kV | OPSL(IEL-2) | 2026-05-17 10:05:00 | 2026-05-17 13:06:00 | 0.12569 | E/O | NLDC instruction | 0 | 0 | No interruption
|  |  | Total : | 1900-01-12 10:41 |  | Unserved Energy: |  | 771.6667
Chattogram Grid Circle :
Bakulia 132/33kV | Bakalia-Kulshi Ckt | 2026-05-25 03:30:00 | 2026-05-25 04:17:00 | 0.032639 | T | Tripped | 0 | 0 | No interruption
Baroaulia 132/33kV | Hat-1 | 2026-05-02 15:47:00 | 2026-05-02 22:44:00 | 0.28958 | T | The opgw is torn due to the stormy whether | 0 | 0 | No interruption
Baroaulia 132/33kV | Hat-1 | 2026-05-27 11:03:00 | 2026-05-27 11:50:00 | 0.032639 | T | Thunder storm and heavy rain. | 0 | 0 | No interruption
Baroaulia 132/33kV | KSRM | 2026-05-03 12:30:00 | 2026-05-03 12:47:00 | 0.011806 | T | Null | 9 | 2.55 | Power interruption
Baroirhat 132/33kV | Feni-1 | 2026-05-24 12:11:00 | 2026-05-24 13:48:00 | 0.067361 | T | Unknown. | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-1 | 2026-05-27 11:36:00 | 2026-05-27 12:53:00 | 0.053472 | T | Storm & thundering | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-2 | 2026-05-27 11:55:00 | 2026-05-27 12:32:00 | 0.025694 | T | Storm & thundering | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-1 | 2026-05-27 11:31:00 | 2026-05-27 14:12:00 | 0.11181 | T | Tripped | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-01 | 2026-05-25 12:19:00 | 2026-05-25 13:02:00 | 0.029861 | T | Tripped | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-02 | 2026-05-25 12:19:00 | 2026-05-25 13:05:00 | 0.031944 | T | Tripped | 0 | 0 | No interruption
Hathazari 230/132/33kV | Madunaghat-02 | 2026-05-26 09:01:00 | 2026-05-26 10:54:00 | 0.078472 | T | Tripped | 0 | 0 | No interruption
Hathazari 230/132/33kV | Kaptai-02 | 2026-05-27 11:14:00 | 2026-05-27 15:46:00 | 0.18889 | T | heavy rain, thunderstrome | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Sikalbaha | 2026-05-26 09:40:00 | 2026-05-26 11:08:00 | 0.061111 | T | Lightning strike | 21 | 30.8 | Power interruption
Khagrachori 132/33kV | RANGAMATI-2 | 2026-05-15 12:35:00 | 2026-05-16 14:37:00 | 1899-12-31 02:02 | T | Rangamati Ckt-2 Y ph Loop Broken | 0 | 0 | No interruption
Khagrachori 132/33kV | RANGAMATI-2 | 2026-05-26 10:10:00 | 2026-05-26 10:34:00 | 0.016667 | T | Tripped due to Thundering | 0 | 0 | No interruption
Korerhat 400/230/132kV | Madunaghat-1 | 2026-05-25 12:19:00 | 2026-05-25 13:29:00 | 0.048611 | T | Lightning | 0 | 0 | No interruption
Korerhat 400/230/132kV | Hathajari-1 | 2026-05-25 12:04:00 | 2026-05-25 13:01:00 | 0.039583 | T | Lightning | 0 | 0 | No interruption
Korerhat 400/230/132kV | Hathajari-2 | 2026-05-25 12:19:00 | 2026-05-25 13:04:00 | 0.03125 | T | Lightning | 70 | 52.5 | Power interruption
Korerhat 400/230/132kV | Hathajari-2 | 2026-05-27 10:35:00 | 2026-05-27 11:16:00 | 0.028472 | T | R-Y Phase fault | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Meghnaghat 400kV Ckt.-1 | 2026-05-25 12:19:00 | 2026-05-25 13:28:00 | 0.047917 | T | General Trip, Y phase Fault, Line Differential Trip | 0 | 0 | No interruption
Patiya 132/33kV | Patiya-Dohazari Ckt-01 | 2026-05-27 11:37:00 | 2026-05-27 12:52:00 | 0.052083 | T | Tripped | 0 | 0 | No interruption
Baroaulia 132/33kV | Kulshi | 2026-05-02 07:50:00 | 2026-05-02 12:44:00 | 0.20417 | E/O | Re conductor Survy | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-02 | 2026-05-20 10:41:00 | 2026-05-20 12:47:00 | 0.0875 | E/O | Emergency ROW | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Julda Ckt. line | 2026-05-08 06:02:00 | 2026-05-08 06:50:00 | 0.033333 | E/O | Due to romove bird nest from Julda line Gantry. | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-05-08 06:03:00 | 2026-05-08 06:33:00 | 0.020833 | E/O | S/D Taken from halishahar end to remove bird nest . | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-05-22 10:00:00 | 2026-05-22 10:35:00 | 0.024306 | E/O | Order of NLDC | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-05-27 08:44:00 | 2026-05-27 09:00:00 | 0.011111 | E/O | Shutdown taken by NLDC due to voltage control | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 17:54 |  | Unserved Energy: |  | 85.85
Cumilla Grid Circle :
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-1 | 2026-05-10 13:33:00 | 2026-05-10 13:54:00 | 0.014583 | T | Tripped | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-05-13 14:20:00 | 2026-05-13 15:16:00 | 0.038889 | T | Tripped | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-05-18 01:19:00 | 2026-05-18 01:58:00 | 0.027083 | T | Tripped | 30 | 19.5 | Power interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-05-24 05:02:00 | 2026-05-24 05:29:00 | 0.01875 | T | Fault | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-1 | 2026-05-24 17:47:00 | 2026-05-26 14:18:00 | 1899-12-31 20:31 | T | Tripped | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2026-05-25 14:03:00 | 2026-05-25 15:01:00 | 0.040278 | T | Unknown | 0 | 0 | No interruption
Feni 132/33kV | PHP (ISML) Ckt | 2026-05-02 13:49:00 | 2026-05-02 14:11:00 | 0.015278 | T | Tripped | 12 | 4.4 | Power interruption
Feni 132/33kV | Barayerhat Ckt | 2026-05-24 12:12:00 | 2026-05-24 13:49:00 | 0.067361 | T | Tripped | 0 | 0 | No interruption
Kachua 230/132/33kV | Chandpur CKT-2 | 2026-05-25 14:09:00 | 2026-05-25 15:00:00 | 0.035417 | T | rain and storm | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-05-06 18:28:00 | 2026-05-06 18:36:00 | 0.0055556 | T | Stormy weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-01 | 2026-05-10 13:33:00 | 2026-05-10 13:57:00 | 0.016667 | T | Non | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-01 | 2026-05-11 17:07:00 | 2026-05-11 17:14:00 | 0.0048611 | T | Non | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-05-13 14:20:00 | 2026-05-13 15:18:00 | 0.040278 | T | Stormy Weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-05-18 01:21:00 | 2026-05-18 02:01:00 | 0.027778 | T | Stormy Weather | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-05-24 05:03:00 | 2026-05-24 05:30:00 | 0.01875 | T | Stormy Weather. | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-01 | 2026-05-24 17:27:00 | 2026-05-26 14:17:00 | 1899-12-31 20:50 | T | Heavy Rain With Thundering | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2026-05-16 09:56:00 | 2026-05-16 12:32:00 | 0.10833 | T | Tripped | 20 | 52 | Power interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-05-26 14:21:00 | 2026-05-26 20:40:00 | 0.26319 | E/O | Emergency maint.work | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Desh Energy Ckt-1 | 2026-05-24 08:15:00 | 2026-05-24 11:20:00 | 0.12847 | E/O | Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Desh Energy Ckt-2 | 2026-05-24 11:45:00 | 2026-05-24 12:42:00 | 0.039583 | E/O | Maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | 53.2MW Lakthanavi | 2026-05-10 16:21:00 | 2026-05-10 16:56:00 | 0.024306 | E/O | To remove bird nest near jumper | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhani Ckt-2 | 2026-05-20 16:00:00 | 2026-05-20 17:39:00 | 0.06875 | E/O | Chowmuhani S/S project Work. | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Kosba Ckt-02 | 2026-05-23 12:53:00 | 2026-05-23 13:40:00 | 0.032639 | E/O | for kite remove | 0 | 0 | No interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2026-05-23 14:19:00 | 2026-05-23 15:58:00 | 0.06875 | E/O | Due to LA grounding replacement | 0 | 0 | No interruption
Sylhet 132/33kV | 75 MW ST PS | 2026-05-14 12:15:00 | 2026-05-23 17:30:00 | 1900-01-08 05:15 | E/O | Emergency maintenance work their side. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-13 01:08 |  | Unserved Energy: |  | 75.9
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-05-27 08:25:00 | 2026-05-27 12:52:00 | 0.18542 | T | Over Voltage Trip | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-05-29 16:29:00 | 2026-05-29 21:02:00 | 0.18958 | T | Bad weather,Over Voltage | 0 | 0 | No interruption
Barishal 230/132kV | Madaripur ckt-02 | 2026-05-29 17:09:00 | 2026-05-30 00:35:00 | 0.30972 | T | Distance trip | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2026-05-25 23:12:00 | 2026-05-25 23:37:00 | 0.017361 | T | None | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-2 | 2026-05-25 23:12:00 | 2026-05-25 23:34:00 | 0.015278 | T | None | 0 | 0 | No interruption
Madaripur 132/33kV | Barishal CKT-02 | 2026-05-29 17:09:00 | 2026-05-30 00:36:00 | 0.31042 | T | E/F Z-1 Distance:18:98kM | 0 | 0 | No interruption
Patuakhali 132/33kV | Bakergonj-Pautakhali 132kV Line | 2026-05-26 13:37:00 | 2026-05-26 14:17:00 | 0.027778 | T | E/F, Phase -C, 27.4 km, 3.3kA | 30 | 20 | Power interruption
Patuakhali 132/33kV | Bakergonj-Pautakhali 132kV Line | 2026-05-27 09:05:00 | 2026-05-27 09:34:00 | 0.020139 | T | E/F ,O/C | 24 | 11.6 | Power interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2026-05-25 23:12:00 | 2026-05-25 23:41:00 | 0.020139 | T | Earth fault phase(L-3) distance from khulna south substation at 103.2km | 76 | 36.7333 | Power interruption
Satkhira 132/33kV | Khulna South-2 (L-2) | 2026-05-25 23:12:00 | 2026-05-25 23:35:00 | 0.015972 | T | Earth fault phase(L-3) distance from khulna south substation at 101.7km | 76 | 29.1333 | Power interruption
Amtali 400/132kV | Amtali - RNPL 400 kV Ckt - 2 | 2026-05-12 02:48:00 | 2026-05-13 13:02:00 | 1899-12-31 10:14 | E/O | Blue Phase DS Red hot. | 0 | 0 | No interruption
Benapole 132/33kV | Jashore-1 | 2026-05-09 08:39:00 | 2026-05-09 13:48:00 | 0.21458 | E/O | VT MCB fail Maintenance | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Khulna Central-2 | 2026-05-02 02:24:00 | 2026-05-03 17:29:00 | 1899-12-31 15:05 | E/O | order by SAE Rubel ALDC Khulna. | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-1 | 2026-05-10 12:10:00 | 2026-05-10 13:05:00 | 0.038194 | E/O | Cutting trees | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Gopalganj Ckt-1 | 2026-05-10 11:10:00 | 2026-05-10 13:05:00 | 0.079861 | E/O |  | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Goalpara-2 | 2026-05-02 02:27:00 | 2026-05-03 17:28:00 | 1899-12-31 15:01 | E/O | Distance relay DC fail. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Jhenaidah Ckt-1 | 2026-05-27 08:32:00 | 2026-05-27 12:50:00 | 0.17917 | E/O | Due to High Voltage. | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-1 Reactor | 2026-05-03 11:56:00 | 2026-05-27 07:10:00 | 1900-01-22 19:14 | E/O | NLDC Demand | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-2 Reactor | 2026-05-03 11:57:00 | 2026-05-27 07:12:00 | 1900-01-22 19:15 | E/O | NLDC Demand | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-1 | 2026-05-30 13:39:00 | 2026-05-30 13:39:00 | 0 | E/O | NLDC DEMAND | 0 | 0 | No interruption
Rampal 400/230kV | Gopalganj Line-2 | 2026-05-30 13:40:00 | 2026-05-30 13:40:00 | 0 | E/O | NLDC DEMAND | 0 | 0 | No interruption
|  |  | Total : | 1900-02-21 21:47 |  | Unserved Energy: |  | 97.4667
HVDC Grid Circle :
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2026-05-26 02:19:00 | 2026-05-26 11:08:00 | 0.36736 | T | Tripped | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2026-05-27 06:07:00 | 2026-05-27 13:43:00 | 0.31667 | T | Tripped | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2026-05-31 19:27:00 | 2026-05-31 20:32:00 | 0.045139 | T | A-G fault 1201Km from Isd Side. Z-2 opdt | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2026-05-31 21:55:00 | 2026-05-31 22:24:00 | 0.020139 | T | UNKNOWN | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Kushtia 132kV Circuit-1(L1) | 2026-05-18 21:40:00 | 2026-05-18 22:25:00 | 0.03125 | T | Tripped | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-1 | 2026-05-08 13:15:00 | 2026-05-08 16:13:00 | 0.12361 | T | Tripped | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-2 | 2026-05-08 13:15:00 | 2026-05-08 14:49:00 | 0.065278 | T | Tripped | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia-Jhenaidah-1 | 2026-05-18 21:39:00 | 2026-05-18 22:23:00 | 0.030556 | T | Tripped | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Ishurdi -1 | 2026-05-03 10:30:00 | 2026-05-03 23:02:00 | 0.52222 | E/O | DFDR Integration work. | 0 | 0 | No interruption
Bheramara 230/132kV | GK 2 | 2026-05-06 10:25:00 | 2026-05-06 12:30:00 | 0.086806 | E/O | Hotspot | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Pabna | 2026-05-14 09:44:00 | 2026-05-14 17:04:00 | 0.30556 | E/O | pabna end breaker gas pressure problem | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Khulna (South) Ckt-1 | 2026-05-27 08:31:00 | 2026-05-27 12:50:00 | 0.17986 | E/O | Aldc order | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia-Jhenaidah-2 | 2026-05-11 10:37:00 | 2026-05-12 15:38:00 | 1899-12-31 05:01 | E/O | For changing Distance Relay. | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Ishwardi Line | 2026-05-14 09:47:00 | 2026-05-14 17:05:00 | 0.30417 | E/O | Gas leakage Maintenance of 132 kv CB | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Ishwardi Line | 2026-05-16 13:18:00 | 2026-05-16 19:52:00 | 0.27361 | E/O | Emergency maint.work | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Ishwardi Line | 2026-05-21 10:40:00 | 2026-05-21 18:27:00 | 0.32431 | E/O | Emergency maint.work | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Ishwardi Line | 2026-05-21 21:14:00 | 2026-05-21 21:37:00 | 0.015972 | E/O | None | 15 | 5.75 | Power interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Pabna | 2026-05-16 08:52:00 | 2026-05-16 11:30:00 | 0.10972 | E/O | পাবনা গ্রিডে জরুরি সংরক্ষণ কাজের জন্য। | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 07:57 |  | Unserved Energy: |  | 5.75
Bogura Grid Circle:
Barapukuria 230/132/33kV | Bogura 230 KV Ckt2 | 2026-05-05 13:07:00 | 2026-05-05 13:57:00 | 0.034722 | T | Tripped | 333 | 277.5 | Power interruption
Bogura 132/33kV | Natore-1 | 2026-05-21 09:18:00 | 2026-05-21 10:31:00 | 0.050694 | T | Tripped | 0 | 0 | No interruption
Bogura 230/132kV | Sherpur 132 KV Line-1 | 2026-05-09 02:05:00 | 2026-05-09 03:23:00 | 0.054167 | T | Storm | 0 | 0 | No interruption
Bogura 230/132kV | Confidance UN-2 | 2026-05-26 02:38:00 | 2026-05-26 09:07:00 | 0.27014 | T | None | 0 | 0 | No interruption
Bogura 230/132kV | Confidance UN-2 | 2026-05-27 05:35:00 | 2026-05-27 09:45:00 | 0.17361 | T | Raining, Storming, Thundering | 0 | 0 | No interruption
Bogura 230/132kV | Confidance UN-2 | 2026-05-29 16:38:00 | 2026-05-29 18:49:00 | 0.090972 | T | Tripped | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-2 | 2026-05-26 01:40:00 | 2026-05-26 10:37:00 | 0.37292 | T | Zone-1 Trip | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-05-27 06:05:00 | 2026-05-27 14:41:00 | 0.35833 | T | Directional Earth Fault | 0 | 0 | No interruption
Chapai 132/33kV | Chapai Rahanpur ckt 1 | 2026-05-20 14:52:00 | 2026-05-20 16:20:00 | 0.061111 | T | General trip | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Rangpur-Lalmonirhat | 2026-05-25 06:43:00 | 2026-05-25 07:05:00 | 0.015278 | T | Heavy Thunderstorm | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Rangpur-Lalmonirhat | 2026-05-31 12:25:00 | 2026-05-31 12:56:00 | 0.021528 | T | Tripped | 0 | 0 | No interruption
Mithapukur 132/33kV | Palashbari-2 | 2026-05-05 13:06:00 | 2026-05-05 13:18:00 | 0.0083333 | T | None | 34 | 6.8 | Power interruption
Mithapukur 132/33kV | Palashbari-2 | 2026-05-21 08:20:00 | 2026-05-21 10:38:00 | 0.095833 | T | Bad Weather | 0 | 0 | No interruption
Mithapukur 132/33kV | Confidence-1 | 2026-05-31 13:41:00 | 2026-05-31 14:14:00 | 0.022917 | T | Tripped | 15 | 8.25 | Power interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-05-17 04:05:00 | 2026-05-17 04:48:00 | 0.029861 | T | Thunderstorms | 0 | 0 | No interruption
Natore 132/33kV | Bogura-1 | 2026-05-21 09:18:00 | 2026-05-21 10:32:00 | 0.051389 | T | Tripped | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-2 | 2026-05-03 22:05:00 | 2026-05-03 22:57:00 | 0.036111 | T | Over Current | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-2 | 2026-05-04 13:22:00 | 2026-05-04 14:11:00 | 0.034028 | T | Tripped | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-2 | 2026-05-04 14:32:00 | 2026-05-04 17:26:00 | 0.12083 | T | Tripped | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-01 | 2026-05-05 13:08:00 | 2026-05-05 13:19:00 | 0.0076389 | T | Unknown. | 0 | 0 | No interruption
Palashbari 132/33kV | Mithapukur-02 | 2026-05-21 08:15:00 | 2026-05-21 10:43:00 | 0.10278 | T | Tripped | 0 | 0 | No interruption
Panchagarh 132/33kV | Thakurgaon-1 | 2026-05-23 20:46:00 | 2026-05-23 21:06:00 | 0.013889 | T | Heavy Thundering | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Taraganj-2 | 2026-05-08 11:48:00 | 2026-05-08 12:44:00 | 0.038889 | T | heavy Storm | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2026-05-25 06:43:00 | 2026-05-25 07:05:00 | 0.015278 | T | Thundering | 26 | 9.5333 | Power interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2026-05-31 12:30:00 | 2026-05-31 12:54:00 | 0.016667 | T | Unknown | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Purbosadipur CKT-02 | 2026-05-25 05:20:00 | 2026-05-25 05:52:00 | 0.022222 | T | Tripped | 0 | 0 | No interruption
Sirajganj 132/33kV | Sherpur-2 | 2026-05-18 02:32:00 | 2026-05-18 03:30:00 | 0.040278 | T | Thundering. | 0 | 0 | No interruption
Taraganj 132/33kV | Taraganj-Rangpur CKT-02 | 2026-05-08 11:47:00 | 2026-05-08 12:48:00 | 0.042361 | T | heavy rain and strom | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-1 | 2026-05-05 07:29:00 | 2026-05-05 12:47:00 | 0.22083 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-1 | 2026-05-08 07:34:00 | 2026-05-08 19:40:00 | 0.50417 | E/O | Conductor Stringing In Barapukuria Side. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-05-18 17:05:00 | 2026-05-18 21:57:00 | 0.20278 | E/O | instructed by NLDC AE sir due to reduce system voltage | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-05-18 17:05:00 | 2026-05-18 21:56:00 | 0.20208 | E/O | instructed by NLDC AE sir due to reduce system voltage | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-05-18 17:11:00 | 2026-05-18 21:57:00 | 0.19861 | E/O | instructed by NLDC AE sir due to reduce system voltage | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2026-05-18 17:11:00 | 2026-05-18 21:57:00 | 0.19861 | E/O | instructed by NLDC AE sir due to reduce system voltage | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-05-26 04:56:00 | 2026-05-26 17:16:00 | 0.51389 | E/O | Reduce system voltage | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-05-26 04:56:00 | 2026-05-26 17:16:00 | 0.51389 | E/O | Reduce system voltage | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Kurigram-Lalmonirhat Ckt | 2026-05-19 07:06:00 | 2026-05-19 08:40:00 | 0.065278 | E/O | 132kv bus B phase Red hot | 50 | 78.3333 | Power interruption
Kurigram 132/33kV | 132 Kv Rangpur-kurigram Ckt | 2026-05-19 07:06:00 | 2026-05-19 08:45:00 | 0.06875 | E/O | 132kv bus B phase Red hot | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Kurigram-Lalmonirhat Ckt | 2026-05-19 11:04:00 | 2026-05-19 13:11:00 | 0.088194 | E/O | Emergency maint.work | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Kurigram-Lalmonirhat Ckt | 2026-05-24 12:15:00 | 2026-05-24 13:10:00 | 0.038194 | E/O | Tree Trimming at line | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Kurigram-Lalmonirhat Ckt | 2026-05-27 00:56:00 | 2026-05-27 01:37:00 | 0.028472 | E/O | Emergency tree trimming | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2026-05-19 07:15:00 | 2026-05-19 08:25:00 | 0.048611 | E/O | Kurigram bus maintenance | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2026-05-27 01:05:00 | 2026-05-27 01:37:00 | 0.022222 | E/O | Kurigram grid work | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-2 | 2026-05-29 11:07:00 | 2026-05-29 11:53:00 | 0.031944 | E/O | ALDC | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Raj(new)-1 | 2026-05-05 10:31:00 | 2026-05-05 11:02:00 | 0.021528 | E/O | The Work Of Remove a Kite | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2026-05-19 22:26:00 | 2026-05-20 02:38:00 | 0.175 | E/O | CT (Current Transformer) connection strip burned at the 132kV Lalmonirhat Control & Relay Panel requires an emergency maintenance. | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Teesta Solar-2 | 2026-05-21 10:10:00 | 2026-05-22 21:54:00 | 1899-12-31 11:44 | E/O | Due to Thundering Breaker pole discrepancy as well as trip supervision relay 1&2 unhealthy. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 20:02 |  | Unserved Energy: |  | 380.4167
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-04-05 00:30 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:May 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2026-05-08 06:42:00 | 2026-05-08 10:34:00 | 3:52 | S/O | Red hot maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 132 kv Bus 01 | 2026-05-08 07:40:00 | 2026-05-08 10:34:00 | 2:54 | S/O | Red hot maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2026-05-15 07:05:00 | 2026-05-15 08:53:00 | 1:48 | S/O | Maintenance work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 132 kv Bus 02 | 2026-05-15 07:20:00 | 2026-05-15 08:58:00 | 1:38 | S/O | Maintenance work | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-1(404T) | 2026-05-21 08:52:00 | 2026-05-21 11:32:00 | 2:40 | S/O | 132kV transformer LV side y-phase high temperature maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-2(414T) | 2026-05-24 09:59:00 | 2026-05-24 11:16:00 | 1:17 | S/O | Maintenance work | 0 | 0 | No interruption
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-05-10 14:59:00 | 2026-05-10 15:37:00 | 0:38 | S/O | High temperature maintenance work | 0 | 0 | No interruption
Bhaluka 132/33kV | 01. Transformer- 01 | 2026-05-20 06:27:00 | 2026-05-20 06:59:00 | 0:32 | S/O | High temp. maintenance . | 45 | 24 | Power interruption
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-05-20 07:01:00 | 2026-05-20 08:15:00 | 1:14 | S/O | High temperature maintenance. | 50 | 61.6667 | Power interruption
Bhaluka 132/33kV | 03. Transformer-03 | 2026-05-20 08:21:00 | 2026-05-20 08:55:00 | 0:34 | S/O | High temp. maientence. | 23 | 13.0333 | Power interruption
Bog-Sherpur 132/33kV | Transformer-1 (404T) | 2026-05-10 15:44:00 | 2026-05-10 17:43:00 | 1:59 | S/O | 33kV feeder red hot maintenance | 45 | 89.25 | Power interruption
Bog-Sherpur 132/33kV | Main Bus-2 | 2026-05-24 09:50:00 | 2026-05-24 13:03:00 | 3:13 | S/O | Loop Maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV | Bus-A | 2026-05-02 12:19:00 | 2026-05-02 13:25:00 | 1:06 | S/O | 132kv D.S. Upgradation Work purpose. | 0 | 0 | No interruption
Jamalpur 132/33kV | Bus-B | 2026-05-02 13:32:00 | 2026-05-02 16:30:00 | 2:58 | S/O | 132kv D.S. Upgradation Work purpose. | 0 | 0 | No interruption
Jamalpur 132/33kV | Bus-B | 2026-05-12 07:20:00 | 2026-05-12 09:33:00 | 2:13 | S/O | T3 DS Upgradation | 0 | 0 | No interruption
Jamalpur 132/33kV | T-2 | 2026-05-22 06:43:00 | 2026-05-22 12:16:00 | 5:33 | S/O | Auxiliary T-2 transformer shifting work. | 25 | 138.75 | Power interruption
Jamalpur 132/33kV | T-3 | 2026-05-22 12:22:00 | 2026-05-22 12:22:00 | 0:00 | S/O | Auxiliary T-2 Shifting work | 0 | 0 | No interruption
Jamalpur 132/33kV | T-4 | 2026-05-24 07:53:00 | 2026-05-24 09:02:00 | 1:09 | S/O | High temperature | 15 | 17.25 | Power interruption
Jamalpur 132/33kV | T-1 | 2026-05-24 09:17:00 | 2026-05-24 10:17:00 | 1:00 | S/O | Temperature reduce work | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-05-17 15:02:00 | 2026-05-17 17:44:00 | 2:42 | S/O | 33 kV Nabinagar feeder R phase bus loop connecting work | 100 | 270 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2026-05-18 11:25:00 | 2026-05-18 12:42:00 | 1:17 | S/O | 33 kV bus maintenance. | 70 | 89.8333 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-05-23 15:13:00 | 2026-05-23 17:10:00 | 1:57 | S/O | Red Hot Maintanence of Kashimpur -2 Bus DS. | 80 | 156 | Power interruption
Kaliakoir 400/230/132kV | 400/132kV TR-3 | 2026-05-02 09:42:00 | 2026-05-02 17:19:00 | 7:37 | S/O | DFDR testing and commissioning | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR-3 | 2026-05-17 08:22:00 | 2026-05-17 11:46:00 | 3:24 | S/O | Ds-1209S maintenance due to red-hot. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2026-05-17 08:43:00 | 2026-05-17 11:34:00 | 2:51 | S/O | DS-1209S maintenance due to red-hot. | 0 | 0 | No interruption
Kallyanpur 132/33kV | Main bus | 2026-05-12 07:07:00 | 2026-05-12 08:57:00 | 1:50 | S/O | Aminbazar Ckt-2 Reserve Bus Isolator Finger Maintenance Work | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2026-05-19 13:42:00 | 2026-05-19 16:06:00 | 2:24 | S/O | Pbs redhot maintenance | 15 | 36 | Power interruption
Kodda 132/33kV | Tr-1 (406T) | 2026-05-02 07:04:00 | 2026-05-02 18:52:00 | 11:48 | S/O | T1&T2 33kv incomer bus DS change work(work by energypack) | 20 | 236 | Power interruption
Kodda 132/33kV | Tr-2 (416T) | 2026-05-02 07:04:00 | 2026-05-02 18:53:00 | 11:49 | S/O | T1&T2 33kv incomer bus DS change work(work by energypack) | 10 | 118.1667 | Power interruption
Kodda 132/33kV | Tr-3 (426T) | 2026-05-02 10:30:00 | 2026-05-02 12:12:00 | 1:42 | S/O | 33kv (section -2)incomer bus DS change work(work by energypack) | 25 | 42.5 | Power interruption
Kodda 132/33kV | Tr-4 (436T) | 2026-05-02 10:30:00 | 2026-05-02 12:12:00 | 1:42 | S/O | 33kv (section -2)incomer bus DS change work(work by energypack) | 25 | 42.5 | Power interruption
Kodda 132/33kV | Tr-1 (406T) | 2026-05-03 08:28:00 | 2026-05-03 15:37:00 | 7:09 | S/O | LDS change (33kv T1) | 25 | 178.75 | Power interruption
Kodda 132/33kV | Tr-2 (416T) | 2026-05-21 11:30:00 | 2026-05-21 12:32:00 | 1:02 | S/O | Red hot maintenance | 40 | 41.3333 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2026-05-16 12:33:00 | 2026-05-16 13:30:00 | 0:57 | S/O | 33kV GT-4 Redhot. | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2026-05-21 11:40:00 | 2026-05-21 12:50:00 | 1:10 | S/O | Oil Fill in Oil temp. Sensor | 10 | 11.6667 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2026-05-24 06:14:00 | 2026-05-24 13:10:00 | 6:56 | S/O | Due to Temperature rise at 33 kV side. | 30 | 68 | Power interruption06:14 to 08:30
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2026-05-24 13:45:00 | 2026-05-24 14:52:00 | 1:07 | S/O | Maintenance work | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-1 (404T) | 2026-05-06 07:10:00 | 2026-05-06 09:30:00 | 2:20 | S/O | Maintenance work | 0 | 0 | No interruption
Mymensingh 132/33kV | T-1 Bus | 2026-05-06 07:28:00 | 2026-05-08 04:59:00 | 45:31 | S/O | 33kV Bhal -1 Feeder, Raiser Change on source side | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2026-05-09 10:02:00 | 2026-05-10 17:19:00 | 31:17 | S/O | For oil Centrfuse | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-1 (404T) | 2026-05-16 07:16:00 | 2026-05-16 08:42:00 | 1:26 | S/O | Maintenance work | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2026-05-16 07:16:00 | 2026-05-16 08:43:00 | 1:27 | S/O | Maintenance work | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-1 (404T) | 2026-05-19 05:33:00 | 2026-05-19 10:10:00 | 4:37 | S/O | To perform high temperature mitigate works of 132kV B-Bus DS Net-1 and T-1 (404T). | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus B | 2026-05-19 06:53:00 | 2026-05-19 08:26:00 | 1:33 | S/O | To perform high temperature mitigate works of 132kV B-Bus DS Net-1 R-phase and T-1 (404T) R-phase. | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-3 (424T) | 2026-05-19 10:12:00 | 2026-05-19 14:03:00 | 3:51 | S/O | None | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2026-05-22 00:18:00 | 2026-05-22 01:21:00 | 1:03 | S/O | Shambuganj -1 Red hot 33 kV bus -2 | 74 | 77.7 | Power interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2026-05-25 06:16:00 | 2026-05-25 08:21:00 | 2:05 | S/O | To perform high temperature mitigate works of 33kV Gafargaon feeder Bus DS Y-phase. | 80 | 166.6667 | Power interruption
Nabinagar 132/33kV | T-1 | 2026-05-10 14:27:00 | 2026-05-10 17:24:00 | 2:57 | S/O | Red hot maintenance. | 10 | 29.5 | Power interruption
Nabinagar 132/33kV | T-2 | 2026-05-20 16:40:00 | 2026-05-21 16:12:00 | 23:32 | S/O | CT, PT sealing and metering | 0 | 0 | No interruption
Nabinagar 132/33kV | T-2 | 2026-05-24 13:15:00 | 2026-05-24 15:35:00 | 2:20 | S/O | Hot spot maintenance. | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2026-05-01 09:56:00 | 2026-05-01 18:11:00 | 8:15 | S/O | Painting | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2026-05-02 10:07:00 | 2026-05-02 12:53:00 | 2:46 | S/O | Painting | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2026-05-02 12:55:00 | 2026-05-02 17:20:00 | 4:25 | S/O | Maintenance work | 0 | 0 | No interruption
Savar 132/33kV | T-1 | 2026-05-09 09:20:00 | 2026-05-09 12:53:00 | 3:33 | S/O | Maintenance work | 0 | 0 | No interruption
Savar 132/33kV | T-2 | 2026-05-09 09:22:00 | 2026-05-09 16:03:00 | 6:41 | S/O | Maintenance work | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2026-05-09 09:26:00 | 2026-05-09 16:10:00 | 6:44 | S/O | Maintenance work | 0 | 0 | No interruption
Savar 132/33kV | T-4 | 2026-05-09 09:28:00 | 2026-05-09 16:06:00 | 6:38 | S/O | Maintenance work | 0 | 0 | No interruption
Savar 132/33kV | Main Bus-I | 2026-05-09 09:40:00 | 2026-05-09 16:00:00 | 6:20 | S/O | Maintenance work | 0 | 0 | No interruption
Savar 132/33kV | Bus-A | 2026-05-09 09:44:00 | 2026-05-09 13:54:00 | 4:10 | S/O | Maintenance work | 0 | 0 | No interruption
Savar 132/33kV | Bus-B | 2026-05-09 09:45:00 | 2026-05-09 16:01:00 | 6:16 | S/O | Maintenance work | 0 | 0 | No interruption
Savar 132/33kV | T-2 | 2026-05-23 09:22:00 | 2026-05-23 18:35:00 | 9:13 | S/O | Relay change work. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2026-05-08 08:18:00 | 2026-05-09 00:01:00 | 15:43 | S/O | CT & Loop Conductor change by CCCE | 30 | 471.5 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2026-05-09 12:27:00 | 2026-05-09 16:06:00 | 3:39 | S/O | R phase CT Oil Leakage Maintenance | 10 | 36.5 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2026-05-10 14:28:00 | 2026-05-10 15:28:00 | 1:00 | S/O | CT test & measurement | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2026-05-13 13:39:00 | 2026-05-13 20:17:00 | 6:38 | S/O | PTR-2 Load Test | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2026-05-14 13:53:00 | 2026-05-14 15:38:00 | 1:45 | S/O | Redhot Maintenance | 10 | 17.5 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2026-05-15 08:28:00 | 2026-05-20 16:43:00 | 128:15 | S/O | PTR-1 transformer dismantle by project-2 | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230 kV Bus-1 | 2026-05-15 10:24:00 | 2026-05-15 12:12:00 | 1:48 | S/O | PSDC Project Work. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-2 | 2026-05-21 15:04:00 | 2026-05-21 16:12:00 | 1:08 | S/O | Project work By PSDC | 25 | 28.3333 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2026-05-25 10:13:00 | 2026-05-25 14:44:00 | 4:31 | S/O | Neutral Bushing Repair work. | 0 | 0 | No interruption
Tangail 132/33kV | Tr-3 | 2026-05-16 10:48:00 | 2026-05-16 15:56:00 | 5:08 | S/O | 33 kv ghatail feeder redhot maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | T-04 | 2026-05-07 13:35:00 | 2026-05-07 19:18:00 | 5:43 | S/O | Maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV | T-04 | 2026-05-09 09:10:00 | 2026-05-09 18:13:00 | 9:03 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-18 23:03 |  | Unserved Energy: |  | 2462.4
Dhaka (South) Grid Circle :
Bhulta 132/33kV | GT2 | 2026-05-18 12:00:00 | 2026-05-18 13:47:00 | 1:47 | S/O | 33 kV side Cable's heat srink leakage. | 45 | 80.25 | Power interruption
Haripur 230/132kV | Bus-2 | 2026-05-14 13:29:00 | 2026-05-14 16:28:00 | 2:59 | S/O | Corrective maintenance of high temperature point of Meghnaghat-2 Bus Isolator. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132kV Main Bus | 2026-05-01 11:50:00 | 2026-05-01 14:23:00 | 2:33 | S/O | Auto Tr-3 Main Bus D/S maintenance. | 0 | 0 | No interruption
Hasnabad 230/132kV | Bus-1 | 2026-05-21 06:08:00 | 2026-05-21 08:09:00 | 2:01 | S/O | High temperature maintenance at DS-801, DS-803 | 0 | 0 | No interruption
Hasnabad 230/132kV | Bus-2 | 2026-05-21 08:15:00 | 2026-05-21 10:28:00 | 2:13 | S/O | high temp | 0 | 0 | No interruption
Keranigonj 230/132/33kV | ATR-3 | 2026-05-01 08:45:00 | 2026-05-01 11:48:00 | 3:03 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-1 | 2026-05-23 07:34:00 | 2026-05-23 09:04:00 | 1:30 | S/O | High temperature maintenance work. | 15 | 22.5 | Power interruption
Maniknagar 132/33kV | Transformer GT-1 | 2026-05-08 08:43:00 | 2026-05-08 16:30:00 | 7:47 | S/O | DPDC-PDSD project works by DPDC | 0 | 0 | No interruption
Maniknagar 132/33kV | Reserve Bus | 2026-05-21 23:19:00 | 2026-05-21 23:19:00 | 0:00 | S/O | 132kv Incomer 1 Reserve Bus DS hot Temperature point Maintenance work. | 0 | 0 | No interruption
Maniknagar 230/132kV | Auto Transformer-01(705T) | 2026-05-22 07:10:00 | 2026-05-22 07:10:00 | 0:00 | S/O | Red Hot remove of 132 kV DS | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2026-05-16 11:38:00 | 2026-05-16 13:21:00 | 1:43 | S/O | টি-৪ ,৩৩ কেভি বাসের আওতাধীন শিবপুর ৩৩ কেভি ফিডারের সোর্স সাইডর রাইজার রেড হট হওয়ায় জরুরী রক্ষনাবেক্ষন কাজ | 17 | 29.1833 | Power interruption
Narshingdi 132/33kV | T-2 | 2026-05-17 21:19:00 | 2026-05-17 22:20:00 | 1:01 | S/O | Narsingdi -1, PBS 33kV Mohishasura feeder OC&EF Tripp then T-2 33kV incomer B-phase DS fingers Flashing and Damage. | 20 | 20.3333 | Power interruption
Narshingdi 132/33kV | T-2 | 2026-05-20 07:20:00 | 2026-05-20 09:03:00 | 1:43 | S/O | 33 kv bus DS redhot | 35 | 60.0833 | Power interruption
Narshingdi 132/33kV | T-4 | 2026-05-28 10:30:00 | 2026-05-28 12:58:00 | 2:28 | S/O | 33 kv redhot | 35 | 86.3333 | Power interruption
Shyampur 230/132kV | Auto TR-1 | 2026-05-23 14:53:00 | 2026-05-23 17:57:00 | 3:04 | S/O | Connect with 132kV Bus 1 for commissioning of 132kV Shyampur 01 Bay-E07 | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-2 | 2026-05-21 08:15:00 | 2026-05-22 23:28:00 | 39:13 | S/O | Shutdown taken by DPDC due to power cable shifting from AIS to GIS switchgear under PDSPD Project. | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 | 2026-05-14 13:43:00 | 2026-05-14 14:53:00 | 1:10 | S/O | Due to 33KV PBS source side Barpa feeder's cable heat shrink work. | 62 | 72.3333 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2026-05-14 16:22:00 | 2026-05-14 17:49:00 | 1:27 | S/O | Due to 33KV PBS source side Barpa feeder's cable heat shrink work. | 62 | 89.9 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2026-05-23 08:22:00 | 2026-05-23 12:50:00 | 4:28 | S/O | 33kv bushing To Jack bus loop change due To excessive temperature. | 50 | 223.3333 | Power interruption
Srinagar 132/33kV | Tr-02 | 2026-05-04 17:14:00 | 2026-05-04 18:28:00 | 1:14 | S/O | Red Hot Maintenance at Mpbs feeder-05. | 12 | 14.8 | Power interruption
Srinagar 132/33kV | Tr-02 | 2026-05-09 22:21:00 | 2026-05-09 23:46:00 | 1:25 | S/O | Red Hot Maintenance by PBS at Feeder No -05 | 12 | 17 | Power interruption
Srinagar 132/33kV | Tr-02 | 2026-05-17 16:57:00 | 2026-05-17 18:25:00 | 1:28 | S/O | Redhot maintenance in 33Kv bus-2 by PBS. | 12 | 17.6 | Power interruption
Srinagar 132/33kV | Tr-01 | 2026-05-27 20:51:00 | 2026-05-27 21:38:00 | 0:47 | S/O | Red hot maintenance in 33 KV side in TR-01 | 24 | 18.8 | Power interruption
|  |  | Total : | 1900-01-02 13:04 |  | Unserved Energy: |  | 752.45
Chattogram Grid Circle :
Agrabad 132/33kV | MTR-01 (406T) | 2026-05-23 09:04:00 | 2026-05-23 12:05:00 | 3:01 | S/O | Oil leakage problem in the Vacuum Valve. | 0 | 0 | No interruption
Agrabad 132/33kV | Auxiliary Transformer-01 | 2026-05-23 09:19:00 | 2026-05-23 11:45:00 | 2:26 | S/O | Oil leakage problem in the Vacuum Valve. | 0 | 0 | No interruption
BSRM 230/33kV | 230/33 kV Transformer-3 (125/140 MVA) | 2026-05-13 10:12:00 | 2026-05-19 11:58:00 | 145:46 | S/O | Maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV | 415T-T2 | 2026-05-09 06:33:00 | 2026-05-10 13:40:00 | 31:07 | S/O | Commission the new CRP of Transformer-3 & 33kv Incomer-3 at New Control Room. | 90 | 2800.5 | Power interruption
Dohazari 132/33kV | Power Transformer -T-1 | 2026-05-16 01:32:00 | 2026-05-16 02:16:00 | 0:44 | S/O | Banshkhali 33 kv feeder redhot maintenance | 25 | 18.3333 | Power interruption
Dohazari 132/33kV | Power Transformer -T-1 | 2026-05-22 16:10:00 | 2026-05-22 17:10:00 | 1:00 | S/O | Due to Banshkhali 33 KV BUS DS redhot maintenance | 25 | 25 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2026-05-24 09:24:00 | 2026-05-24 10:08:00 | 0:44 | S/O | Due to Satkania 33 KV BUS DS red hot maintenance. | 54 | 39.6 | Power interruption
GPH 230/33kV | Transformer-01(D05) | 2026-05-15 09:37:00 | 2026-05-15 09:38:00 | 0:01 | S/O | for general maintenance | 0 | 0 | No interruption
GPH 230/33kV | Transformer -2 (D07) | 2026-05-15 09:37:00 | 2026-05-15 16:38:00 | 7:01 | S/O | for general maintenance | 0 | 0 | No interruption
GPH 230/33kV | Transformer-01(D05) | 2026-05-16 11:13:00 | 2026-05-16 15:44:00 | 4:31 | S/O | for general maintenance | 0 | 0 | No interruption
Halishahar 132/33kV | 415T(TR-2) | 2026-05-10 17:15:00 | 2026-05-10 17:38:00 | 0:23 | S/O | To remove birds nest | 0 | 0 | No interruption
Halishahar 132/33kV | 405T(TR-1) | 2026-05-10 17:44:00 | 2026-05-10 17:58:00 | 0:14 | S/O | To remove birds nest | 0 | 0 | No interruption
Halishahar 132/33kV | 425T(TR-3) | 2026-05-14 08:51:00 | 2026-05-14 14:49:00 | 5:58 | S/O | Maintenance | 0 | 0 | No interruption
Halishahar 132/33kV | 405T(TR-1) | 2026-05-15 06:53:00 | 2026-05-15 14:06:00 | 7:13 | S/O | Maintenance | 0 | 0 | No interruption
Halishahar 132/33kV | 415T(TR-2) | 2026-05-15 06:57:00 | 2026-05-15 14:09:00 | 7:12 | S/O | Maintenance | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 | 2026-05-10 09:05:00 | 2026-05-10 17:41:00 | 8:36 | S/O | Baraulia -ksrm line tree trimming and loop changed in 12 no pole . | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-02 | 2026-05-10 09:07:00 | 2026-05-10 17:42:00 | 8:35 | S/O | Baraulia -ksrm line tree trimming and loop changed in 12 no pole . | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-03 | 2026-05-10 09:09:00 | 2026-05-10 17:43:00 | 8:34 | S/O | Baraulia -ksrm line tree trimming and loop changed in 12 no pole . | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2026-05-19 06:36:00 | 2026-05-19 10:33:00 | 3:57 | S/O | High temperature | 0 | 0 | No interruption
Khulshi 132/33kV | 405T (T1) | 2026-05-24 05:55:00 | 2026-05-24 08:27:00 | 2:32 | S/O | Red hot maintenance | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7103T) | 2026-05-24 07:11:00 | 2026-05-25 13:12:00 | 30:01 | S/O | Shutdown taken by CNTIC due to project work. | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-1 | 2026-05-25 11:05:00 | 2026-05-25 16:15:00 | 5:10 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-1 | 2026-05-25 17:43:00 | 2026-05-25 19:20:00 | 1:37 | S/O | PDB End Maintenance. | 0 | 0 | No interruption
Shikalbaha 230/132kV | ATR 02 | 2026-05-22 06:56:00 | 2026-05-22 06:56:00 | 0:00 | S/O | Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-10 22:23 |  |  |  | 2883.4333
Cumilla Grid Circle :
Ashuganj 230/132/33kV | TR-OAT-12 | 2026-05-10 14:15:00 | 2026-05-10 16:41:00 | 2:26 | S/O | GI wire has been found hanging dangerously on the 132kV Bus-1 | 0 | 0 | No interruption
Ashuganj 230/132/33kV | T-4 Kalabagan | 2026-05-10 15:17:00 | 2026-05-10 15:54:00 | 0:37 | S/O | GI wire has been found hanging dangerously on the 132kV Bus-1 | 50 | 30.8333 | Power interruption
Chandpur 132/33kV | 402T (T-01) | 2026-05-09 06:32:00 | 2026-05-09 10:03:00 | 3:31 | S/O | Maintainace | 10 | 35.1667 | Power interruption
Chandpur 132/33kV | 422T(T-5) | 2026-05-11 09:40:00 | 2026-05-29 20:30:00 | 442:50 | S/O | Transformer Colouring | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-1 | 2026-05-18 23:17:00 | 2026-05-19 01:12:00 | 1:55 | S/O | Red hot maintenance for PBS end. | 40 | 76.6667 | Power interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-05-14 13:59:00 | 2026-05-14 15:32:00 | 1:33 | S/O | Red hot maintenance | 20 | 31 | Power interruption
Chowmuhani 230/132/33kV | ATR-02 | 2026-05-17 09:44:00 | 2026-05-18 15:57:00 | 30:13 | S/O | AVR Replacement. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | ATR-03 | 2026-05-19 08:57:00 | 2026-05-20 18:07:00 | 33:10 | S/O | AVR Replacement & testing work. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | TR1-415T | 2026-05-24 11:50:00 | 2026-05-24 12:50:00 | 1:00 | S/O | Red hot Maintenance of 33kv Incoming DS LOOP | 20 | 20 | Power interruption
Chowmuhani 230/132/33kV | TR3 | 2026-05-27 09:12:00 | 2026-05-27 14:34:00 | 5:22 | S/O | Emergency shutdown taken for 132/33 kV, TR-03 X-former today at 09:12 for 132kVJack BUS Maintenance. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-05-27 23:45:00 | 2026-05-28 00:45:00 | 1:00 | S/O | Red Hot Maintenance Of 33 kV Tr-03 Bus | 10 | 10 | Power interruption
Chowmuhani 230/132/33kV | TR2-425T | 2026-05-28 01:10:00 | 2026-05-28 01:55:00 | 0:45 | S/O | Red Hot Maintenance of 33KV L Bus Incoming Loop | 20 | 15 | Power interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-05-27 23:45 | 2026-05-28 00:45 | 1:00 | S/O | Red Hot Maintenance of 33KV L Bus Incoming Loop | 20 | 20 | Power interruption
Cumilla(S) 132/33kV | TR-2 | 2026-05-01 07:20:00 | 2026-05-01 11:44:00 | 4:24 | S/O | Tr-01 Replacement work. | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-2 | 2026-05-02 17:59:00 | 2026-05-02 20:30:00 | 2:31 | S/O | Energypac work. | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-2 | 2026-05-05 07:58:00 | 2026-05-05 09:38:00 | 1:40 | S/O | T-1 Transformer replacement work | 12 | 20 | Power interruption
Cumilla(S) 132/33kV | TR-2 | 2026-05-06 06:24:00 | 2026-05-06 17:53:00 | 11:29 | S/O | Tr-01 replacing work by energypac. | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2026-05-26 09:15:00 | 2026-05-26 10:52:00 | 1:37 | S/O | Red hot maintenance at 33kv daganbhuiyan feeder | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-2 | 2026-05-26 14:39:00 | 2026-05-26 20:09:00 | 5:30 | S/O | Bus PT change at Companiganj 33 kv feeder | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-2 | 2026-05-03 16:08:00 | 2026-05-03 17:31:00 | 1:23 | S/O | Red hot maintenance at 33 kV switchyard by Comilla PBS-3 | 0 | 0 | No interruption
Daudkandi 132/33kV | Transformer-2 | 2026-05-09 09:19:00 | 2026-05-09 12:06:00 | 2:47 | S/O | 33 kV bay extension works by Comilla PBS-3 | 60 | 167 | Power interruption
Daudkandi 132/33kV | Transformer-3 | 2026-05-15 07:01:00 | 2026-05-15 09:42:00 | 2:41 | S/O | T-3 Shutdown for 33 KV Side Bay Extension work by PBS-3 Team | 32 | 85.8667 | Power interruption
Daudkandi 132/33kV | Transformer-2 | 2026-05-15 07:08:00 | 2026-05-15 10:32:00 | 3:24 | S/O | Transformer-2 Shutdown for bay extension, & electrical wiring related works at 33 kV switchyard by Comilla PBS-3 | 32 | 108.8 | Power interruption
Daudkandi 132/33kV | Transformer-1 | 2026-05-24 23:37:00 | 2026-05-25 00:43:00 | 1:06 | S/O | Red hot maintenance at 33 kV switchyard by PBS-3 | 16 | 17.6 | Power interruption
Feni 132/33kV | T-1(405T) | 2026-05-09 07:35:00 | 2026-05-09 09:17:00 | 1:42 | S/O | Shutdown taken for PDB 33 KV bus loop maintenance work. | 40 | 68 | Power interruption
Feni 132/33kV | T-1(405T) | 2026-05-19 22:08:00 | 2026-05-19 23:47:00 | 1:39 | S/O | For PDB 33KV Doreen Ckt Red Hot Maintenance Work. | 40 | 66 | Power interruption
Feni 132/33kV | T-2(415T) | 2026-05-23 09:17:00 | 2026-05-23 18:31:00 | 9:14 | S/O | T-2 Breaker Pre Commission | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2026-05-24 09:17:00 | 2026-05-25 00:16:00 | 14:59 | S/O | T2 132KV breaker Commissioning. | 0 | 0 | No interruption
Feni 132/33kV | T-2(415T) | 2026-05-24 09:17:00 | 2026-05-25 00:16:00 | 14:59 | S/O | T2 132KV breaker Commissioning. | 0 | 0 | No interruption
Feni 230/132kV | ATR-1 | 2026-05-13 09:04:00 | 2026-05-13 18:07:00 | 9:03 | S/O | Due to testing and painting work by project | 0 | 0 | No interruption
Feni 230/132kV | ATR-1 | 2026-05-14 09:06:00 | 2026-05-14 19:31:00 | 10:25 | S/O | SAS Testing and painting work | 0 | 0 | No interruption
Feni 230/132kV | ATR-3 | 2026-05-17 10:48:00 | 2026-05-17 13:36:00 | 2:48 | S/O | water supply system pipe installation & spray nozzle installation. | 0 | 0 | No interruption
Kachua 230/132/33kV | TR-2 | 2026-05-14 06:36:00 | 2026-05-14 08:53:00 | 2:17 | S/O | Red Hot Maintenance for 33kv shahrasti feeder . | 0 | 0 | No interruption
Kachua 230/132/33kV | TR-2 | 2026-05-24 08:13:00 | 2026-05-24 08:25:00 | 0:12 | S/O | Remove kite from 33 kV bus | 40 | 8 | Power interruption
Kachua 230/132/33kV | TR-1 | 2026-05-25 07:13:00 | 2026-05-25 09:56:00 | 2:43 | S/O | 33 kV Adda feeder source DS damage issue. | 0 | 0 | No interruption
Kasba 132/33kV | TR-1 | 2026-05-18 20:41:00 | 2026-05-18 21:49:00 | 1:08 | S/O | for grounding maintenance at 33 kV switch yard. | 18 | 20.4 | Power interruption
Kulaura 132/33kV | TR-2 | 2026-05-09 08:28:00 | 2026-05-09 12:30:00 | 4:02 | S/O | PDB bus DS maintenance.shudown taken by PDB authority. | 10 | 40.3333 | Power interruption
Kulaura 132/33kV | TR-1 AB | 2026-05-19 16:31:00 | 2026-05-19 17:10:00 | 0:39 | S/O | TR -1(A+B) 132 KV CT Red Hot maintenance.Load shared by TR-2 via 33 kv bus coupler DS. | 0 | 0 | No interruption
Maijdee 132/33kV | Tr-02 | 2026-05-15 09:48:00 | 2026-05-15 12:58:00 | 3:10 | S/O | Mohabbotpur Feeder 33KV Bus Red Hot Maintenance. | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 | 2026-05-15 09:57:00 | 2026-05-15 12:55:00 | 2:58 | S/O | Subarnochor Feeder 33KV Bus Red Hot Maintenance. | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 | 2026-05-27 14:53:00 | 2026-05-28 03:30:00 | 12:37 | S/O | due to the burning of the CT clamp and wire at the 33 kV bus source side of BREB. | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-01 | 2026-05-06 12:24:00 | 2026-05-06 12:48:00 | 0:24 | S/O | kite remove | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-05-06 09:13:00 | 2026-05-06 09:58:00 | 0:45 | S/O | S/D Taken by PBS for Red Hot maintenance. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-05-14 22:28:00 | 2026-05-14 23:45:00 | 1:17 | S/O | Redhot maintenance | 90 | 115.5 | Power interruption
Shahjibazar 132/33kV | TR-04 | 2026-05-20 07:00:00 | 2026-05-20 08:02:00 | 1:02 | S/O | Redhot Maintenance. | 60 | 62 | Power interruption
Shahjibazar 132/33kV | TR-02 | 2026-05-20 14:30:00 | 2026-05-20 15:26:00 | 0:56 | S/O | Maint.work | 30 | 28 | Power interruption
Shahjibazar 132/33kV | TR-04 | 2026-05-24 08:15:00 | 2026-05-24 08:51:00 | 0:36 | S/O | Redhot Maintenance at 33kv bus Taken by pbs | 0 | 0 | No interruption
Sylhet (South) | Trafo-2 | 2026-05-01 06:15:00 | 2026-05-01 08:47:00 | 2:32 | S/O | 33 kv bus coupler redhot maint..work. | 10 | 25.3333 | Power interruption
Sylhet (South) | Trafo-1 | 2026-05-01 06:16:00 | 2026-05-01 08:41:00 | 2:25 | S/O | 33 kv bus coupler redhot maint..work. | 0 | 0 | No interruption
Sylhet (South) | Trafo-2 | 2026-05-18 07:20:00 | 2026-05-18 09:35:00 | 2:15 | S/O | 33kv bus section- 2 feeder work | 24 | 54 | Power interruption
Sylhet 132/33kV | T1 | 2026-05-17 21:05:00 | 2026-05-17 22:58:00 | 1:53 | S/O | 33KV Upashahar feeder Bus side D/S (Y-Phase) Red hot maintanance by S&D-2 (BPDB). | 15 | 28.25 | Power interruption
|  |  | Total : | 1900-01-27 00:34 |  |  |  | 1153.75
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-1 (403T) | 2026-05-02 11:29:00 | 2026-05-02 16:37:00 | 5:08 | S/O |  | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-1 (403T) | 2026-05-04 16:45:00 | 2026-05-04 19:54:00 | 3:09 | S/O | CT Cable Change work. | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-3 ( 423 T) | 2026-05-22 07:27:00 | 2026-05-22 10:01:00 | 2:34 | S/O | Maintenance work. | 10 | 25.6667 | Power interruption
Barguna 132/33kV | Transformer-1 | 2026-05-04 12:46:00 | 2026-05-04 16:04:00 | 3:18 | S/O | WZPDCL-2(Barguna) Redhot Maintenance | 0 | 0 | No interruption
Barishal 132/33kV | T-1 (405T) | 2026-05-22 07:38:00 | 2026-05-22 09:08:00 | 1:30 | S/O | Red hot maintenance work of WZPDCL (Dopdapia - 2) at 33kV Bus | 40 | 60 | Power interruption
Barishal 230/132kV | T-5 | 2026-05-20 06:11:00 | 2026-05-20 08:50:00 | 2:39 | S/O | 33kv jhalokathi feeder DS maintenance | 35 | 92.75 | Power interruption
Barishal 230/132kV | T-5 | 2026-05-22 21:15:00 | 2026-05-22 22:37:00 | 1:22 | S/O | Banaripara 33kv feeder DS problem | 52 | 71.0667 | Power interruption
Barishal 230/132kV | ATR-1 | 2026-05-23 15:33:00 | 2026-05-23 16:57:00 | 1:24 | S/O |  | 0 | 0 | No interruption
Barishal 230/132kV | T-4 | 2026-05-24 06:37:00 | 2026-05-24 08:46:00 | 2:09 | S/O | Red Hot Repair | 12.5 | 26.875 | Power interruption
Barishal 230/132kV | T-4 | 2026-05-31 07:40:00 | 2026-05-31 09:51:00 | 2:11 | S/O | Babuganj 33 kV Bus DS Maintenance by PBS | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-1 | 2026-05-06 10:40:00 | 2026-05-06 15:03:00 | 4:23 | S/O | Shutdown for 33 kv Bus PT change given by Pirojpur PBS | 10 | 43.8333 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2026-05-22 07:01:00 | 2026-05-22 10:47:00 | 3:46 | S/O | Aux. Transformer DS pin insulator Change | 23 | 86.6333 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2026-05-22 07:01:00 | 2026-05-22 10:48:00 | 3:47 | S/O | Aux. Transformer DS pin insulator Change | 23 | 87.0167 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2026-05-08 07:15:00 | 2026-05-08 11:17:00 | 4:02 | S/O | Red hot maintenance. | 25 | 100.8333 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2026-05-10 07:53:00 | 2026-05-10 08:56:00 | 1:03 | S/O | Maint.work | 25 | 26.25 | Power interruption
Faridpur 132/33kV | Transformer-3 | 2026-05-10 08:05:00 | 2026-05-10 09:00:00 | 0:55 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-2 | 2026-05-16 07:45:00 | 2026-05-16 12:39:00 | 4:54 | S/O | Maint.work | 39 | 191.1 | Power interruption
Faridpur 132/33kV | ATR-1 | 2026-05-20 08:35:00 | 2026-05-20 09:47:00 | 1:12 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | ATR-2 | 2026-05-24 08:41:00 | 2026-05-24 11:43:00 | 3:02 | S/O | WTI Replacement | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-1 | 2026-05-30 07:33:00 | 2026-05-30 09:33:00 | 2:00 | S/O | Red Hot Maintenance | 6 | 12 | Power interruption
Goalpara 132/33kV | Bus 1 | 2026-05-04 12:08:00 | 2026-05-05 20:37:00 | 32:29 | S/O | Bus-1 PT problem testing | 0 | 0 | No interruption
Goalpara 132/33kV | T-6 | 2026-05-23 07:33:00 | 2026-05-23 11:23:00 | 3:50 | S/O | Heat removal work | 0 | 0 | No interruption
Goalpara 132/33kV | Bus 1 | 2026-05-23 11:41:00 | 2026-05-23 13:12:00 | 1:31 | S/O | NWPGCL Line High Tempareture Removing Work. | 0 | 0 | No interruption
Goalpara 132/33kV | T1 | 2026-05-27 10:25:00 | 2026-05-27 12:18:00 | 1:53 | S/O | Red hot Khulna pbs shutdown | 12 | 22.6 | Power interruption
Goalpara 132/33kV | T-5 | 2026-05-27 10:28:00 | 2026-05-27 12:18:00 | 1:50 | S/O | Red hot Khulna pbs shutdown | 0 | 0 | No interruption
Goalpara 132/33kV | T-6 | 2026-05-27 10:33:00 | 2026-05-27 12:12:00 | 1:39 | S/O | Red hot Khulna pbs shutdown | 0 | 0 | No interruption
Gopalganj 132/33kV | Modhumoti 100MW PS | 2026-05-09 13:24:00 | 2026-05-09 18:04:00 | 4:40 | S/O | Main bus connection of T3 | 0 | 0 | No interruption
Gopalganj 132/33kV | Main Bus | 2026-05-09 13:38:00 | 2026-05-09 17:24:00 | 3:46 | S/O | Bus connection of T3 | 82 | 308.8667 | Power interruption
Khulna (C) | TR-1 425T | 2026-05-02 09:24:00 | 2026-05-02 19:11:00 | 9:47 | S/O | Tr1 shutdown for project work. | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-05-03 08:10:00 | 2026-05-03 17:51:00 | 9:41 | S/O | Maint.work | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-05-04 08:12:00 | 2026-05-04 16:42:00 | 8:30 | S/O | Painting work | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-05-06 07:07:00 | 2026-05-06 09:29:00 | 2:22 | S/O | Hot spot Maintenance | 12 | 28.4 | Power interruption
Khulna (C) | TR-1 425T | 2026-05-13 14:42:00 | 2026-05-13 16:58:00 | 2:16 | S/O | South circuit 2 Hot spot maintenance. | 20 | 45.3333 | Power interruption
Khulna (C) | Tr-2 415 T | 2026-05-16 11:07:00 | 2026-05-16 13:20:00 | 2:13 | S/O | Wz red hot maintenance | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-05-21 16:23:00 | 2026-05-21 17:19:00 | 0:56 | S/O | 33 kv seromoni# 1 red hot maintenance | 12 | 11.2 | Power interruption
Khulna (C) | TR-1 425T | 2026-05-23 06:03:00 | 2026-05-23 08:16:00 | 2:13 | S/O | project work | 22 | 48.7667 | Power interruption
Khulna (C) | Tr-2 415 T | 2026-05-23 08:39:00 | 2026-05-23 11:31:00 | 2:52 | S/O | project work | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-05-23 16:22:00 | 2026-05-23 18:37:00 | 2:15 | S/O | 33 kv loop connector clamp upgradation by using bymetal. | 0 | 0 | No interruption
Mongla 132/33kV | T-1 | 2026-05-16 07:02:00 | 2026-05-16 09:33:00 | 2:31 | S/O | WZPDCL 33KV BUS SIDE RED HOT | 7 | 17.6167 | Power interruption
Narail 132/33kV | TR2 (413-T) | 2026-05-26 07:10:00 | 2026-05-26 08:46:00 | 1:36 | S/O | Red hot maintenance | 15 | 24 | Power interruption
Narail 132/33kV | TR1 (403-T) | 2026-05-26 09:16:00 | 2026-05-26 11:08:00 | 1:52 | S/O | Red hot maintenance by JPBS-02 | 30 | 56 | Power interruption
Noapara 132/33kV | T-1 | 2026-05-12 09:12:00 | 2026-05-12 13:16:00 | 4:04 | S/O | Maint.work | 0 | 0 | No interruption
Noapara 132/33kV | T-2 | 2026-05-20 21:41:00 | 2026-05-21 00:03:00 | 2:22 | S/O | Due to REB-1 Feeder Red Hot Maintenance by PBS | 0 | 0 | No interruption
Noapara 132/33kV | Bus Section-2 | 2026-05-20 21:47:00 | 2026-05-20 23:56:00 | 2:09 | S/O | Due to REB-1 Feeder Red Hot Maintenance by PBS | 20 | 43 | Power interruption
Noapara 132/33kV | T-2 | 2026-05-23 17:09:00 | 2026-05-23 18:18:00 | 1:09 | S/O | Due to Reb-1 Red hot Maintenance. | 13 | 14.95 | Power interruption
Noapara 132/33kV | T-2 | 2026-05-26 08:32:00 | 2026-05-26 10:32:00 | 2:00 | S/O | Due to REB-1 Feeder Red Hot Maintenance by PBS | 0 | 0 | No interruption
Noapara 132/33kV | Bus Section-2 | 2026-05-26 08:36:00 | 2026-05-26 10:36:00 | 2:00 | S/O | Due to REB-1 Feeder Red Hot Maintenance by PBS | 5 | 10 | Power interruption
Shariatpur 132/33kV | T1-406T | 2026-05-16 07:03:00 | 2026-05-16 11:30:00 | 4:27 | S/O | Maintenance Work by PBS. | 30 | 133.5 | Power interruption
Shariatpur 132/33kV | T2-416T | 2026-05-16 11:42:00 | 2026-05-16 15:49:00 | 4:07 | S/O | Maintenance Work by PBS. | 32 | 131.7333 | Power interruption
|  |  | Total : | 1900-01-06 09:28 |  | Unserved Energy : |  | 1719.9917
HVDC Grid Circle
Baghabari 230/132kV | T-2 Bank | 2026-05-11 09:55:00 | 2026-05-11 21:01:00 | 11:06 | S/O | DFDR commissioning | 0 | 0 | No interruption
Baghabari 230/132kV | T-1 | 2026-05-12 10:05:00 | 2026-05-12 18:03:00 | 7:58 | S/O | DFDR Commissioning. | 0 | 0 | No interruption
Baghabari 230/132kV | Bus-2 | 2026-05-13 10:49:00 | 2026-05-14 13:26:00 | 26:37 | S/O | DFDR commissioning work | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T2(426T) | 2026-05-09 07:25:00 | 2026-05-09 11:36:00 | 4:11 | S/O | Maint.work | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T3 | 2026-05-09 07:25:00 | 2026-05-09 11:31:00 | 4:06 | S/O | Maint.work | 40 | 164 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T1(416T) | 2026-05-09 11:41:00 | 2026-05-09 13:56:00 | 2:15 | S/O | 33kV Busbar Maintenance. | 45 | 101.25 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-3 | 2026-05-16 08:34:00 | 2026-05-16 17:26:00 | 8:52 | S/O | Maint.work | 20 | 177.3333 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-3 | 2026-05-21 07:30:00 | 2026-05-21 09:39:00 | 2:09 | S/O | 33kv busber maintenance work. | 34 | 73.1 | Power interruption
Ishurdi 132/33kV | 132/33 kV T-1 | 2026-05-22 09:12:00 | 2026-05-22 09:49:00 | 0:37 | S/O | maintenance work on station auxiliary x-former | 30 | 18.5 | Power interruption
Ishurdi 230/132kV | 230 kV Bus 2 | 2026-05-11 09:15:00 | 2026-05-11 19:34:00 | 10:19 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Bus 2 | 2026-05-12 09:25:00 | 2026-05-12 21:09:00 | 11:44 | S/O | loop jumper connection | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Bus 1 | 2026-05-13 09:20:00 | 2026-05-13 18:14:00 | 8:54 | S/O | Loop jumper connecting new bay with busbar. | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Bus 1 | 2026-05-14 09:20:00 | 2026-05-14 18:43:00 | 9:23 | S/O | upgradation of jack bus at T03 | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Bus 2 | 2026-05-24 07:33:00 | 2026-05-24 11:03:00 | 3:30 | S/O | Maint.work | 0 | 0 | No interruption
Pabna 132/33kV | T-3 | 2026-05-24 07:27:00 | 2026-05-24 09:37:00 | 2:10 | S/O | Redhot maintenance work | 15 | 32.5 | Power interruption
|  |  | Total : | 1900-01-03 17:51 |  | Unserved Energy : |  | 566.6833
Bogura Grid Circle:
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T | 2026-05-08 08:54:00 | 2026-05-08 13:17:00 | 4:23 | S/O | emergency maintenance | 25 | 109.5833 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-3, 404T | 2026-05-08 15:03:00 | 2026-05-08 18:02:00 | 2:59 | S/O | emergency maintenance work | 15 | 44.75 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-3, 404T | 2026-05-11 15:03:00 | 2026-05-11 15:31:00 | 0:28 | S/O | TRTUD Bogura work | 0 | 0 | No interruption
Bogura 230/132kV | T-02 | 2026-05-24 06:04:00 | 2026-05-24 08:52:00 | 2:48 | S/O | Red-hot Maintenance | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-2 (415T) | 2026-05-06 15:57:00 | 2026-05-06 17:43:00 | 1:46 | S/O | 132kv Circuit Breaker Replace work | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-05-21 16:14:00 | 2026-05-21 17:54:00 | 1:40 | S/O | Pirob 33 kV Feeder Red hot Maintenance. | 25 | 41.6667 | Power interruption
Naogaon 132/33kV | T-2 33kV BUS | 2026-05-02 07:10:00 | 2026-05-02 09:58:00 | 2:48 | S/O | Bus DS change | 8 | 22.4 | Power interruption
Naogaon 132/33kV | T-2 33kV BUS | 2026-05-02 16:22:00 | 2026-05-02 18:14:00 | 1:52 | S/O | 33KV Bus Isolator change. | 8 | 14.9333 | Power interruption
Naogaon 132/33kV | T-2 33kV BUS | 2026-05-03 15:40:00 | 2026-05-03 17:02:00 | 1:22 | S/O | Red hot maintenance work of 33 KV PBS Potnitola feeder. | 0 | 0 | No interruption
Naogaon 132/33kV | T-2 33kV BUS | 2026-05-24 07:20:00 | 2026-05-24 08:55:00 | 1:35 | S/O | T-2 33kV CB loop connection | 10 | 15.8333 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-05-25 07:08:00 | 2026-05-25 11:04:00 | 3:56 | S/O | PBS AUX T-1 Maintenance | 15 | 59 | Power interruption
Panchagarh 132/33kV | T-1(407T) | 2026-05-21 09:53:00 | 2026-05-21 13:19:00 | 3:26 | S/O | Red Hot Maintenance on 33kV Bus Section 01 | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | 132kV BUS-B | 2026-05-03 11:38:00 | 2026-05-03 17:03:00 | 5:25 | S/O |  | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | AIS Old TR-1 | 2026-05-11 07:29:00 | 2026-05-11 09:33:00 | 2:04 | S/O | TR-1 33KV BUS maintenance | 20 | 41.3333 | Power interruption
Purbasadipur 230/132/33kV | AIS Old T-4 Transformer | 2026-05-18 07:39:00 | 2026-05-18 08:02:00 | 0:23 | S/O | Heat sink maintenance at Khanshama 33kV feeder | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | AIS Old T-4 Transformer | 2026-05-18 16:19:00 | 2026-05-18 17:19:00 | 1:00 | S/O | 33kv PBS feeder maintenance. | 20 | 20 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-05-23 06:55:00 | 2026-05-23 09:46:00 | 2:51 | S/O | Cleaning & maintenance work. | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2026-05-23 06:55:00 | 2026-05-23 09:48:00 | 2:53 | S/O | Cleaning & maintenance work. | 10 | 28.8333 | Power interruption
Rajshahi 132/33kV | Transformer T-1(405T) | 2026-05-23 10:27:00 | 2026-05-23 11:47:00 | 1:20 | S/O | Maintenance Work | 0 | 0 | No interruption
Rangpur 132/33kV | T-1(414T) | 2026-05-20 06:49:00 | 2026-05-20 08:20:00 | 1:31 | S/O | 33kV BUS Section-1 shutdown due to NESCO Burihat-1 feeder raiser red hot. | 0 | 0 | No interruption
Saidpur 132/33kV | TR-3 (424T) | 2026-05-05 05:54:00 | 2026-05-05 08:15:00 | 2:21 | S/O | Red hot maintainance. | 20 | 47 | Power interruption
Saidpur 132/33kV | TR-3 (424T) | 2026-05-26 07:10:00 | 2026-05-26 08:31:00 | 1:21 | S/O | Red hot maintainance. | 20 | 27 | Power interruption
Sirajganj 132/33kV | T2-(425) | 2026-05-05 06:58:00 | 2026-05-05 08:44:00 | 1:46 | S/O | NESCO Sirajganj has taken S/D due to BUSBAR jumping the new puthiyabari feeder | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-1 (404T) | 2026-05-10 15:44:00 | 2026-05-10 17:43:00 | 1:59 | S/O | 33kV feeder red hot maintenance | 45 | 89.25 | Power interruption
|  |  | Total : | 1900-01-01 05:57 |  | Unserved Energy : |  | 561.5833
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1868:20 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:May 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bajitpur 132/33kV | Kishoreganj Ckt-1 | 2026-05-24 08:39:00 | 2026-05-24 09:50:00 | 1:11 | S/O | Maint.Work | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2026-05-12 07:13:00 | 2026-05-12 09:29:00 | 2:16 | S/O | T3 DS Upgradation | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2026-05-24 15:22:00 | 2026-05-24 16:49:00 | 1:27 | S/O | Maintenance work of C.T. connector due to temperature increased. | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2026-05-15 14:56:00 | 2026-05-15 17:18:00 | 2:22 | S/O | Maint.work | 60 | 142 | Power interruption
Kaliakoir 400/230/132kV | Tangail-1 | 2026-05-02 06:00:00 | 2026-05-02 15:09:00 | 9:09 | S/O | Line bypass by kabirpur grid ss | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana1 | 2026-05-31 10:30:00 | 2026-05-31 16:25:00 | 5:55 | S/O | Disc cleaning | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Lalbag Ckt-01 | 2026-05-12 06:51:00 | 2026-05-12 09:12:00 | 2:21 | S/O | Reserve Bus Isolator Finger Maintenance Work | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Lalbag Ckt-02 | 2026-05-12 06:51:00 | 2026-05-12 09:12:00 | 2:21 | S/O | Aminbazar Ckt-2 Reserve Bus Isolator Finger Maintenance Work | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2026-05-12 07:11:00 | 2026-05-12 09:10:00 | 1:59 | S/O | Reserve Bus Isolator Finger Maintenance Work | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2026-05-19 06:36:00 | 2026-05-19 18:16:00 | 11:40 | S/O | OPGW Maintenance Work | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-1 | 2026-05-08 05:48:00 | 2026-05-08 18:17:00 | 12:29 | S/O | 400 kV Shomvugonj line conductor stringing work. | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-2 | 2026-05-08 06:12:00 | 2026-05-08 18:01:00 | 11:49 | S/O | 400 kV Shomvugonj line conductor stringing work. | 0 | 0 | No interruption
Kodda 132/33kV | Summit 149 MW PS | 2026-05-31 10:10:00 | 2026-05-31 12:20:00 | 2:10 | S/O | work by Summit | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2026-05-26 04:43:00 | 2026-05-26 20:45:00 | 16:02 | S/O | By NLDC | 0 | 0 | No interruption
Mirzapur 132/33kV | Mirzapur-Tangail-ckt-2A(E04) | 2026-05-04 06:49:00 | 2026-05-04 06:49:00 | 0:00 | S/O | Tangail-Kaliakair Ckt Tower Replacing Work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-RPCL Ckt-1 | 2026-05-04 10:15:00 | 2026-05-04 13:00:00 | 2:45 | S/O | None | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Kishoreganj Ckt-1 | 2026-05-08 05:50:00 | 2026-05-08 18:18:00 | 12:28 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-2 | 2026-05-12 07:14:00 | 2026-05-12 09:28:00 | 2:14 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Netrakona Ckt-1 | 2026-05-19 05:45:00 | 2026-05-19 09:04:00 | 3:19 | S/O | To perform high temperature mitigate works of 132kV B-Bus DS Net-1 and T-1 (404T). | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Jamalpur Ckt-1 | 2026-05-24 15:20:00 | 2026-05-24 16:49:00 | 1:29 | S/O | Maint.work | 0 | 0 | No interruption
Nabinagar 132/33kV | Nabinagar-Dhamrai Ckt-1 | 2026-05-08 07:35:00 | 2026-05-08 09:13:00 | 1:38 | S/O | Scaffolding removing work from Nabinagar-Dhamrai line. | 0 | 0 | No interruption
Nabinagar 132/33kV | Nabinagar-Dhamrai Ckt-2 | 2026-05-08 07:44:00 | 2026-05-08 09:13:00 | 1:29 | S/O | Scaffolding removing work from Nabinagar-Dhamrai line. | 20 | 29.6667 | Power interruption
Pubail 132/33kV | Ghorasal-2 | 2026-05-15 07:56:00 | 2026-05-15 12:14:00 | 4:18 | S/O | line maintenance | 0 | 0 | No interruption
Pubail 132/33kV | Joydebpur-1 | 2026-05-15 08:41:00 | 2026-05-15 11:55:00 | 3:14 | S/O | line maintenance | 0 | 0 | No interruption
Tangail 132/33kV | Kaliakair-1 | 2026-05-02 06:00:00 | 2026-05-02 15:07:00 | 9:07 | S/O | Maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-05-07 15:33:00 | 2026-05-07 19:53:00 | 4:20 | S/O | Maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-05-09 12:20:00 | 2026-05-09 19:17:00 | 6:57 | S/O | Project work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-05-09 20:31:00 | 2026-05-09 21:42:00 | 1:11 | S/O | SCADA integration | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-1 | 2026-05-10 16:14:00 | 2026-05-10 18:25:00 | 2:11 | S/O | Tree trimming | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Ghorashal Ckt-1 | 2026-05-13 08:57:00 | 2026-05-13 09:43:00 | 0:46 | S/O | Maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-1 | 2026-05-15 22:26:00 | 2026-05-15 23:28:00 | 1:02 | S/O | Hotspot maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 21:39 |  | Unserved Energy: |  | 171.6667
Dhaka (South) Grid Circle :
Bhulta 400/230kV | Ghorashal-02 | 2026-05-22 11:18:00 | 2026-05-22 22:52:00 | 11:34 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230kV | Ghorashal-01 | 2026-05-29 18:59:00 | 2026-05-29 20:15:00 | 1:16 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230kV | Ghorashal-02 | 2026-05-31 06:25:00 | 2026-05-31 19:25:00 | 13:00 | S/O | Maint.work | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal GIS- AIS Ckt-3 | 2026-05-31 22:20:00 | 2026-05-31 22:20:00 | 0:00 | S/O | As NLDC SDE instruction | 0 | 0 | No interruption
Haripur 230/132kV | Siddhirganj-2 | 2026-05-01 17:29:00 | 2026-05-01 18:12:00 | 0:43 | S/O | Ordered by NLDC. | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-1 | 2026-05-15 06:47:00 | 2026-05-15 20:34:00 | 13:47 | S/O | Work on another S/S. | 0 | 0 | No interruption
Hasnabad 230/132kV | Hasnabad-Keraniganj Ckt-2 | 2026-05-27 15:36:00 | 2026-05-30 20:10:00 | 76:34 | S/O | line conductor maintenace work | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Nawabganj Ckt. 1 | 2026-05-18 09:06:00 | 2026-05-18 17:48:00 | 8:42 | S/O | OPGW maintenance work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2026-05-19 12:08:00 | 2026-05-24 13:45:00 | 121:37 | S/O | Maintenance work at hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Hasnabad Ckt. 2 | 2026-05-27 15:37:00 | 2026-05-30 20:12:00 | 76:35 | S/O | Maintenance at Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Hasnabad Ckt. 2 | 2026-05-27 15:37:00 | 2026-05-30 20:12:00 | 76:35 | S/O | Maintenance at Hasnabad end. | 0 | 0 | No interruption
Maniknagar 132/33kV | Narinda Ckt-1 | 2026-05-13 07:34:00 | 2026-05-13 10:09:00 | 2:35 | S/O | Red hot ( temperature rising) maintenance at 132 kv main bus DS and line DS. | 0 | 0 | No interruption
Maniknagar 132/33kV | Narinda Ckt-1 | 2026-05-22 11:57:00 | 2026-05-22 13:01:00 | 1:04 | S/O | Dc supply replacement work with new charger /distribution panel for main and backup protection relay. | 0 | 0 | No interruption
Maniknagar 132/33kV | Narinda Ckt-2 | 2026-05-22 15:03:00 | 2026-05-22 16:03:00 | 1:00 | S/O | New DC connection with new DC distribution panel | 0 | 0 | No interruption
Maniknagar 132/33kV | Motijheel Ckt-1 | 2026-05-22 16:21:00 | 2026-05-22 17:34:00 | 1:13 | S/O | New DC connection with new DC distribution panel | 0 | 0 | No interruption
Maniknagar 132/33kV | Motijheel Ckt-2 | 2026-05-22 17:44:00 | 2026-05-22 18:10:00 | 0:26 | S/O | Connect new DC from new DC distribution panel. | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Haripur-01 | 2026-05-15 06:44:00 | 2026-05-15 20:32:00 | 13:48 | S/O | Clam connector changing. | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Comilla-02 | 2026-05-13 10:25:00 | 2026-05-13 13:05:00 | 2:40 | S/O | Project Work | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Comilla-01 | 2026-05-13 13:35:00 | 2026-05-23 17:04:00 | 243:29 | S/O | Project Work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Summit PP 400KV Ckt-1 | 2026-05-11 11:16:00 | 2026-05-11 17:40:00 | 6:24 | S/O | For maintenance work. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat- Shyampur 230kv -Ckt 2 | 2026-05-15 05:33:00 | 2026-05-15 20:29:00 | 14:56 | S/O | 230 kV Shyampur ckt- 02 shutdown instructed by NLDC. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat- Shyampur 230kv -Ckt 2 | 2026-05-16 05:39:00 | 2026-05-16 17:21:00 | 11:42 | S/O | for maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-1 | 2026-05-18 09:32:00 | 2026-05-18 12:09:00 | 2:37 | S/O | 400 kV Korerhat ckt- 01 shutdown instructed by NLDC. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-1 | 2026-05-18 10:31:00 | 2026-05-18 12:24:00 | 1:53 | S/O | for maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-2 | 2026-05-18 12:19:00 | 2026-05-18 16:15:00 | 3:56 | S/O | Instruction by NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2026-05-20 13:13:00 | 2026-05-20 18:43:00 | 5:30 | S/O | Mainenance work at Munshiganj | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat- Shyampur 230kv -Ckt 2 | 2026-05-22 05:55:00 | 2026-05-22 11:36:00 | 5:41 | S/O | 230 kV Shyampur ckt- 02 shutdown instructed by NLDC. | 0 | 0 | No interruption
Nawabganj 132/33kV | Keraniganj-1 | 2026-05-18 09:07:00 | 2026-05-18 17:49:00 | 8:42 | S/O | OPGW Maintenance. | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-2(D05) | 2026-05-15 05:38:00 | 2026-05-15 20:32:00 | 14:54 | S/O | OPGW Conductor Reconducting From Tower no 20 to 26. | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Hasnabad-1(D02) | 2026-05-15 09:35:00 | 2026-05-15 20:32:00 | 10:57 | S/O | To control the load flow of Meghnaghat Ckt-01 | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-2(D05) | 2026-05-16 05:38:00 | 2026-05-16 17:21:00 | 11:43 | S/O | OPGW Conductor repairing at tower no-22-26 | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-2(D05) | 2026-05-22 05:54:00 | 2026-05-22 11:37:00 | 5:43 | S/O | OPGW reparing work at 20-26 tower. | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Fatullah-2(E05) | 2026-05-24 19:51:00 | 2026-05-24 19:51:00 | 0:00 | S/O | After triping, the SF6 Gas quality doesn't satisfy,so it has to be refilled new SF6 Gas. | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-2(E10) | 2026-05-31 11:11:00 | 2026-05-31 17:02:00 | 5:51 | S/O | Maintenance work at Shyampur old Substation end | 0 | 0 | No interruption
Siddhirganj 132/33kV | 120MW EGCB GT2 | 2026-05-30 09:40:00 | 2026-05-30 15:02:00 | 5:22 | S/O | Line DS Maintenance Work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-31 14:29 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Baroaulia 132/33kV | Hat-1 | 2026-05-02 06:59:00 | 2026-05-02 15:29:00 | 8:30 | S/O | Line maintanance at hathazari grud | 0 | 0 | No interruption
Baroaulia 132/33kV | Hat-1 | 2026-05-09 06:26:00 | 2026-05-09 19:42:00 | 13:16 | S/O | Baraulia-Hathazari ckt-01 165 no tower to 166no tower and 166no tower to Gentry. OPGW Wire Pulling Work | 20 | 265.3333 | Power interruption
Baroaulia 132/33kV | Kulshi | 2026-05-02 07:50:00 | 2026-05-02 12:44:00 | 4:54 | S/O | Due line re-conductoring servey | 0 | 0 | No interruption
Baroaulia 132/33kV | KSRM | 2026-05-10 09:01:00 | 2026-05-10 17:43:00 | 8:42 | S/O | Baraula KSRM transmission line's 12 no. Tower loop change and right of way work. | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-01 | 2026-05-16 09:33:00 | 2026-05-16 11:08:00 | 1:35 | S/O | Relay functional test performed by SPMD | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-02 | 2026-05-16 11:10:00 | 2026-05-16 13:30:00 | 2:20 | S/O | Relay functional test performed by SPMD | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona- Rangamati Ckt-01 | 2026-05-16 11:51:00 | 2026-05-16 12:57:00 | 1:06 | S/O | Relay functional test performed by SPMD | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona- Rangamati Ckt-02 | 2026-05-16 13:04:00 | 2026-05-16 13:46:00 | 0:42 | S/O | Relay functional test performed by SPMD | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Madunaghat Ckt-01 | 2026-05-16 14:19:00 | 2026-05-16 14:57:00 | 0:38 | S/O | Relay functional test performed by SPMD | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Madunaghat Ckt-02 | 2026-05-16 15:00:00 | 2026-05-16 15:38:00 | 0:38 | S/O | Relay functional test performed by SPMD | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroaulia-01 | 2026-05-02 07:00:00 | 2026-05-02 14:05:00 | 7:05 | S/O | Dead end clamp change | 0 | 0 | No interruption
Hathazari 230/132/33kV | Kaptai-02 | 2026-05-27 15:47:00 | 2026-05-27 20:31:00 | 4:44 | S/O | Disk blast | 0 | 0 | No interruption
KSRM 132/33kV | Baraulia Main | 2026-05-10 08:58:00 | 2026-05-10 17:49:00 | 8:51 | S/O | Baraulia line tree trimming & Tower 12 loop change | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Baraulia Circuit-2 | 2026-05-02 07:48:00 | 2026-05-02 12:45:00 | 4:57 | S/O | Line survey for Re-conducting work. | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Madunaghat CKT-2 | 2026-05-23 05:46:00 | 2026-05-23 10:15:00 | 4:29 | S/O | Red hot maintenance Work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Feni -2 | 2026-05-18 08:49:00 | 2026-05-18 19:31:00 | 10:42 | S/O | Project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-05-18 09:32:00 | 2026-05-18 12:08:00 | 2:36 | S/O | Project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-2 | 2026-05-18 12:20:00 | 2026-05-18 16:16:00 | 3:56 | S/O | Project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Feni -1 | 2026-05-19 09:28:00 | 2026-05-19 19:40:00 | 10:12 | S/O | project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Feni -1 | 2026-05-20 10:45:00 | 2026-05-20 20:10:00 | 9:25 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Feni -2 | 2026-05-23 07:58:00 | 2026-05-23 16:57:00 | 8:59 | S/O | Maint.work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Hathajari-2 | 2026-05-07 13:40:00 | 2026-05-07 19:00:00 | 5:20 | S/O | Maint.work | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-1 | 2026-05-16 14:21:00 | 2026-05-16 14:57:00 | 0:36 | S/O | Annual Relay functional test by SPMD Chattogram at Chandraghona grid . | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Chandraghona-2 | 2026-05-16 15:01:00 | 2026-05-16 15:37:00 | 0:36 | S/O | Annual Relay functional test by SPMD at Chandraghona Grid | 0 | 0 | No interruption
Sholosohor 132/33kV | Sholoshahar-Khulshi Ckt-2 | 2026-05-23 05:52:00 | 2026-05-23 10:34:00 | 4:42 | S/O | Maintenance regarding red hot on overhead line | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 09:31 |  | Unserved Energy: |  | 265.3333
Cumilla Grid Circle :
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2026-05-23 07:43:00 | 2026-05-23 14:40:00 | 6:57 | S/O | Maintenance work | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-1 | 2026-05-23 15:35:00 | 2026-05-23 17:30:00 | 1:55 | S/O | Maintenance work | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Korerhat-04 | 2026-05-17 09:53:00 | 2026-05-17 17:49:00 | 7:56 | S/O | Relay Replacement. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Feni line-02 | 2026-05-20 16:02:00 | 2026-05-20 17:37:00 | 1:35 | S/O | PT R Phase Secondary Ground. | 0 | 0 | No interruption
Feni 230/132kV | Cumilla(North)-2 | 2026-05-14 15:23:00 | 2026-05-14 18:00:00 | 2:37 | S/O | Witnessing SAS & DFDR | 0 | 0 | No interruption
Feni 230/132kV | Cumilla(North)-1 | 2026-05-17 10:16:00 | 2026-05-17 21:54:00 | 11:38 | S/O | 230kV SAS & DFDR witnessing | 0 | 0 | No interruption
Feni 230/132kV | Korerhat-2 | 2026-05-18 08:48:00 | 2026-05-18 19:32:00 | 10:44 | S/O | Witness Work of SAS & DFDR | 0 | 0 | No interruption
Feni 230/132kV | Korerhat-1 | 2026-05-19 09:31:00 | 2026-05-19 20:41:00 | 11:10 | S/O | Witness Work of SAS And DFDR | 0 | 0 | No interruption
Feni 230/132kV | Korerhat-1 | 2026-05-20 10:44:00 | 2026-05-20 20:20:00 | 9:36 | S/O | Witness of SAS and DFDR work | 0 | 0 | No interruption
Feni 230/132kV | Cumilla(North)-1 | 2026-05-21 11:40:00 | 2026-05-21 20:19:00 | 8:39 | S/O | SAS & DRDR work witnessing | 0 | 0 | No interruption
Feni 230/132kV | Korerhat-2 | 2026-05-23 09:00:00 | 2026-05-23 16:55:00 | 7:55 | S/O | SAS AND DFDR work witnessing | 0 | 0 | No interruption
Feni 230/132kV | Cumilla(North)-1 | 2026-05-24 10:33:00 | 2026-05-24 11:47:00 | 1:14 | S/O | Due to work at cumilla north end | 0 | 0 | No interruption
Kachua 230/132/33kV | Chandpur CKT-2 | 2026-05-23 07:40:00 | 2026-05-23 14:41:00 | 7:01 | S/O | 132 kv Chandpur -2 has been S/D By Backup NLDC | 0 | 0 | No interruption
Kachua 230/132/33kV | Chandpur CKT-1 | 2026-05-23 15:09:00 | 2026-05-23 17:17:00 | 2:08 | S/O | 132 kv Chandpur -1 has been S/D By Backup NLDC | 0 | 0 | No interruption
Kasba 132/33kV | Muradnagar-Kasba Ckt-2 | 2026-05-23 12:49:00 | 2026-05-23 13:40:00 | 0:51 | S/O | Shutdown has been taken from Muranagar Substation for removing kite. | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-05-26 14:23:00 | 2026-05-26 20:40:00 | 6:17 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 02:13 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-05-02 09:50:00 | 2026-05-02 09:55:00 | 0:05 | S/O | Emergency tree trimming work. | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-1 | 2026-05-04 09:55:00 | 2026-05-04 18:07:00 | 8:12 | S/O | Shutdown by ALDC | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-1 | 2026-05-05 08:14:00 | 2026-05-05 18:38:00 | 10:24 | S/O | OPGW Upgration Work of OFCN | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-1 | 2026-05-06 08:25:00 | 2026-05-06 18:34:00 | 10:09 | S/O | OPGW Upgration work of OFCN | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-1 | 2026-05-07 07:41:00 | 2026-05-07 18:37:00 | 10:56 | S/O | Optical Fiber upgraded work. | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-1 | 2026-05-08 07:53:00 | 2026-05-08 18:51:00 | 10:58 | S/O | OPGW Upgration work of OFCN | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-1 | 2026-05-09 07:45:00 | 2026-05-09 18:22:00 | 10:37 | S/O | OPGW upgration work | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-1 | 2026-05-10 07:37:00 | 2026-05-10 18:34:00 | 10:57 | S/O | Ofcn work | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-1 | 2026-05-11 09:12:00 | 2026-05-11 18:09:00 | 8:57 | S/O | for OPGW Upgradation work by OFCN | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-1 | 2026-05-12 07:31:00 | 2026-05-12 17:16:00 | 9:45 | S/O | OPGW Upgradation work done by OFCN | 0 | 0 | No interruption
Barishal 230/132kV | Barishal ckt-01 | 2026-05-04 10:02:00 | 2026-05-04 18:07:00 | 8:05 | S/O | Replace of OPGW | 0 | 0 | No interruption
Barishal 230/132kV | Barishal ckt-01 | 2026-05-05 08:15:00 | 2026-05-05 18:38:00 | 10:23 | S/O | OPGW Replace | 0 | 0 | No interruption
Barishal 230/132kV | Barishal ckt-01 | 2026-05-06 08:25:00 | 2026-05-06 18:31:00 | 10:06 | S/O | Repalace of OPGW | 0 | 0 | No interruption
Barishal 230/132kV | Barishal ckt-01 | 2026-05-07 07:41:00 | 2026-05-07 18:37:00 | 10:56 | S/O | OPGW Replament work | 0 | 0 | No interruption
Barishal 230/132kV | Barishal ckt-01 | 2026-05-08 07:53:00 | 2026-05-08 18:51:00 | 10:58 | S/O | Replace of OPGW | 0 | 0 | No interruption
Barishal 230/132kV | Barishal ckt-01 | 2026-05-09 06:54:00 | 2026-05-09 18:17:00 | 11:23 | S/O | OPGW change | 0 | 0 | No interruption
Barishal 230/132kV | Barishal ckt-01 | 2026-05-10 07:38:00 | 2026-05-10 18:34:00 | 10:56 | S/O |  | 0 | 0 | No interruption
Barishal 230/132kV | Barishal ckt-01 | 2026-05-11 09:13:00 | 2026-05-11 18:09:00 | 8:56 | S/O |  | 0 | 0 | No interruption
Barishal 230/132kV | Barishal ckt-01 | 2026-05-12 07:32:00 | 2026-05-12 17:17:00 | 9:45 | S/O | Replace of OPGW | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-NWPGCL | 2026-05-04 11:59:00 | 2026-05-05 20:46:00 | 32:47 | S/O | BUS-1 PT Test | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-NWPGCL | 2026-05-23 09:24:00 | 2026-05-23 14:02:00 | 4:38 | S/O | High Temperature Removing Work | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj 100 MW PS | 2026-05-09 13:26:00 | 2026-05-09 17:48:00 | 4:22 | S/O | Main bus connection of T3 | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-1 | 2026-05-09 13:26:00 | 2026-05-09 17:52:00 | 4:26 | S/O | Bus connection of T3 | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-2 | 2026-05-09 13:27:00 | 2026-05-09 17:55:00 | 4:28 | S/O | Bus connection of T 3 | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-1 | 2026-05-09 13:29:00 | 2026-05-09 17:24:00 | 3:55 | S/O | Bus connection of T3 | 40 | 156.6667 | Power interruption
Gopalganj 132/33kV | Gopalganj North-2 | 2026-05-09 13:38:00 | 2026-05-09 17:39:00 | 4:01 | S/O | Bus connection of T3 | 40 | 160.6667 | Power interruption
Gopalganj 400/132kV | 132kV Gopalganj Ckt-1 | 2026-05-09 13:29:00 | 2026-05-09 17:23:00 | 3:54 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Gopalganj Ckt-2 | 2026-05-09 13:38:00 | 2026-05-09 17:39:00 | 4:01 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-1 | 2026-05-19 09:21:00 | 2026-05-19 17:28:00 | 8:07 | S/O | Tree trimming | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-2 | 2026-05-19 09:22:00 | 2026-05-19 17:28:00 | 8:06 | S/O | Tree Trimming | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-1 | 2026-05-20 08:44:00 | 2026-05-20 16:56:00 | 8:12 | S/O | None | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-2 | 2026-05-20 08:44:00 | 2026-05-20 16:56:00 | 8:12 | S/O | Maint.work | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Noapara-1 | 2026-05-03 09:12:00 | 2026-05-08 13:58:00 | 124:46 | S/O | Project work | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2026-05-03 09:13:00 | 2026-05-04 20:59:00 | 35:46 | S/O | Project work | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2026-05-05 06:13:00 | 2026-05-05 07:32:00 | 1:19 | S/O | For red hot maintenance. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2026-05-07 07:20:00 | 2026-05-07 19:50:00 | 12:30 | S/O | Project work. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2026-05-08 07:41:00 | 2026-05-08 13:58:00 | 6:17 | S/O | Project work. | 0 | 0 | No interruption
Khulna (C) | North-WestCkt-1 | 2026-05-13 14:45:00 | 2026-05-13 17:07:00 | 2:22 | S/O | South circuit 2 Hot spot maintenance | 0 | 0 | No interruption
Khulna (C) | North- West Ckt-2 | 2026-05-13 14:45:00 | 2026-05-13 17:07:00 | 2:22 | S/O | South circuit 2 Hot spot maintenance | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2026-05-13 15:35:00 | 2026-05-13 16:55:00 | 1:20 | S/O | South circuit 2 Hot spot maintenance | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2026-05-25 06:24:00 | 2026-05-25 11:28:00 | 5:04 | S/O | Project Work. | 15 | 76 | Power interruption
Khulna (C) | 132 kV Central- South -2 | 2026-05-31 08:39:00 | 2026-05-31 12:18:00 | 3:39 | S/O | Due to replacement of DS arms for reduce temperature. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rampal Ckt-1 | 2026-05-01 07:20:00 | 2026-05-01 14:52:00 | 7:32 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rampal Ckt-2 | 2026-05-01 07:21:00 | 2026-05-01 14:53:00 | 7:32 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Rupsha Ckt-1 | 2026-05-03 09:37:00 | 2026-05-03 13:52:00 | 4:15 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2026-05-09 08:36:00 | 2026-05-09 15:01:00 | 6:25 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-2 | 2026-05-09 08:36:00 | 2026-05-09 15:06:00 | 6:30 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2026-05-13 15:34:00 | 2026-05-13 16:53:00 | 1:19 | S/O | MAINTENANCE WORK AT KHULNA CENTRAL S/S END. | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2026-05-25 06:24:00 | 2026-05-25 11:25:00 | 5:01 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-2 | 2026-05-31 08:40:00 | 2026-05-31 12:18:00 | 3:38 | S/O | Maint.work | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-01 | 2026-05-19 09:21:00 | 2026-05-19 17:29:00 | 8:08 | S/O | Gopalgonj (N) 400 KV Work Purpose | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-02 | 2026-05-19 09:22:00 | 2026-05-19 17:30:00 | 8:08 | S/O | Gopalgonj (N) 400KV work purpose | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 1 | 2026-05-03 09:12:00 | 2026-05-08 13:59:00 | 124:47 | S/O | By the instruction of ALDC. | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2026-05-03 09:13:00 | 2026-05-04 20:58:00 | 35:45 | S/O | By the instruction of ALDC. | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2026-05-05 06:13:00 | 2026-05-05 07:33:00 | 1:20 | S/O | By the instruction of ALDC. | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2026-05-07 07:20:00 | 2026-05-07 19:51:00 | 12:31 | S/O | According to ALDC's instructions. | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2026-05-08 07:40:00 | 2026-05-08 14:00:00 | 6:20 | S/O | By the instruction of ALDC. | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 1 | 2026-05-11 06:28:00 | 2026-05-11 07:29:00 | 1:01 | S/O | Removal of kite from Terminal Tower. | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-1 | 2026-05-01 10:35:00 | 2026-05-01 11:48:00 | 1:13 | S/O | Line DS Red Hot Maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-1 | 2026-05-19 10:38:00 | 2026-05-19 13:04:00 | 2:26 | S/O | S/D by ALDC | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-2 | 2026-05-19 13:20:00 | 2026-05-19 14:55:00 | 1:35 | S/O | S/D by ALDC | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-2 | 2026-05-22 06:06:00 | 2026-05-22 10:33:00 | 4:27 | S/O | 400/132kV payra grid side high temperature | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-01 | 2026-05-01 10:40:00 | 2026-05-01 11:47:00 | 1:07 | S/O | Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-01 | 2026-05-19 10:40:00 | 2026-05-19 13:00:00 | 2:20 | S/O | High temperature at primary junction point of CT | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-02 | 2026-05-19 13:20:00 | 2026-05-19 14:53:00 | 1:33 | S/O | High temperature at primary junction point of CT | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-02 | 2026-05-22 06:16:00 | 2026-05-22 10:32:00 | 4:16 | S/O | High temperature at primary junction point of CT | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-01 | 2026-05-22 10:37:00 | 2026-05-22 12:20:00 | 1:43 | S/O | High temperature at primary junction point of CT | 0 | 0 | No interruption
Rampal 400/230kV | Khulna Line-1 | 2026-05-01 07:39:00 | 2026-05-01 14:52:00 | 7:13 | S/O | Asper requirement of Khulna ALDC | 0 | 0 | No interruption
Rampal 400/230kV | Khulna Line-2 | 2026-05-01 07:39:00 | 2026-05-01 14:53:00 | 7:14 | S/O | Asper requirement of Khulna ALDC | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2026-05-09 08:35:00 | 2026-05-09 15:03:00 | 6:28 | S/O | 110v DC system installation work | 43 | 278.0667 | Power interruption
Satkhira 132/33kV | Khulna South-2 (L-2) | 2026-05-09 08:35:00 | 2026-05-09 15:06:00 | 6:31 | S/O | 110v DC system installation work | 42.5 | 276.9583 | Power interruption
|  |  | Total : | 1900-01-30 21:20 |  | Unserved Energy: |  | 948.3583
HVDC Grid Circle :
BIPTC | Baharampur-3 | 2026-05-22 09:37:00 | 2026-05-22 20:09:00 | 10:32 | S/O | Maint.work | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2026-05-23 11:28:00 | 2026-05-23 18:51:00 | 7:23 | S/O | Maint.work | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Ishurdi -1 | 2026-05-04 14:16:00 | 2026-05-04 21:56:00 | 7:40 | S/O | Project Work | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-1 | 2026-05-06 12:01:00 | 2026-05-06 21:02:00 | 9:01 | S/O | DFDR Commissioning. | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-2 | 2026-05-07 10:04:00 | 2026-05-07 22:58:00 | 12:54 | S/O | DFDR Commissioning | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Sirajgonj-1 | 2026-05-09 09:35:00 | 2026-05-09 21:14:00 | 11:39 | S/O | DFDR Commissioning work | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Sirajgonj-2 | 2026-05-10 10:30:00 | 2026-05-10 20:46:00 | 10:16 | S/O | DFDR Commissioning | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-1 | 2026-05-13 10:29:00 | 2026-05-13 20:16:00 | 9:47 | S/O | DFDR commissioning work | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Sirajgonj-1 | 2026-05-14 15:35:00 | 2026-05-14 20:14:00 | 4:39 | S/O | Maint.work | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-1 | 2026-05-21 10:21:00 | 2026-05-21 22:56:00 | 12:35 | S/O | Telecommunication Work. | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-2 | 2026-05-23 09:45:00 | 2026-05-23 16:40:00 | 6:55 | S/O | টেলিকমিউনিকেশন সিস্টেম টেস্টিং এন্ড কমিশনিং | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Ishurdi -1 | 2026-05-24 07:39:00 | 2026-05-24 12:13:00 | 4:34 | S/O | Maint.work | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Ishurdi -1 | 2026-05-25 08:01:00 | 2026-05-25 14:41:00 | 6:40 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-2 | 2026-05-29 11:07:00 | 2026-05-29 11:52:00 | 0:45 | S/O | Red hot maintenance R-Phase line DS | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Pabna | 2026-05-16 13:21:00 | 2026-05-16 19:51:00 | 6:30 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Pabna | 2026-05-19 10:01:00 | 2026-05-19 12:58:00 | 2:57 | S/O | remove scaffolding work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-2 | 2026-05-20 09:57:00 | 2026-05-20 12:28:00 | 2:31 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-1 | 2026-05-20 12:30:00 | 2026-05-20 16:31:00 | 4:01 | S/O | Maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Pabna | 2026-05-21 10:45:00 | 2026-05-21 16:30:00 | 5:45 | S/O | Maint.work | 0 | 0 | No interruption
Jashore 132/33kV | JH-2(L1) | 2026-05-24 09:28:00 | 2026-05-24 14:05:00 | 4:37 | S/O | Project Work | 0 | 0 | No interruption
Jashore 132/33kV | BEN-1 | 2026-05-09 08:40:00 | 2026-05-09 13:48:00 | 5:08 | S/O | Maint.work | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Kushtia 132kV Circuit-1(L1) | 2026-05-02 08:51:00 | 2026-05-02 15:56:00 | 7:05 | S/O | Maint.work | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Kushtia 132kV Circuit-2(L2) | 2026-05-02 08:52:00 | 2026-05-02 15:56:00 | 7:04 | S/O | Maint.work | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Kushtia 132kV Circuit-2(L2) | 2026-05-11 10:36:00 | 2026-05-12 15:38:00 | 29:02 | S/O | 132kV Jhenaidah-Kushtia CKT-2 Distance Relay Changing work. | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-2 | 2026-05-24 09:30:00 | 2026-05-24 12:07:00 | 2:37 | S/O | Kaligonj Circuit -2 Pole Discripency problem | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-1 | 2026-05-24 12:20:00 | 2026-05-24 13:15:00 | 0:55 | S/O | maintenance work. | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia-Jhenaidah-1 | 2026-05-02 08:52:00 | 2026-05-02 15:53:00 | 7:01 | S/O | maintenance work. | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia-Jhenaidah-2 | 2026-05-02 08:52:00 | 2026-05-02 15:54:00 | 7:02 | S/O | maintenance work. | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Shahjadpur Line | 2026-05-16 08:53:00 | 2026-05-16 11:08:00 | 2:15 | S/O | Redhot Maintenance | 0 | 0 | No interruption
Ruppur 132/11kV | 132kv Ishurdi Line-1 | 2026-05-20 12:30:00 | 2026-05-20 16:23:00 | 3:53 | S/O | Project Work | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Bghabari-2 | 2026-05-04 11:05:00 | 2026-05-04 14:37:00 | 3:32 | S/O | S/D taken by Baghabari Power Station | 0 | 0 | No interruption
|  |  | Total : | 1900-01-08 01:15 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2026-05-05 07:27:00 | 2026-05-05 14:42:00 | 7:15 | S/O | ERS erection / conductor stringing work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2026-05-06 07:47:00 | 2026-05-06 17:58:00 | 10:11 | S/O | Tower errection | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2026-05-07 07:51:00 | 2026-05-07 16:28:00 | 8:37 | S/O | project work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2026-05-07 07:51:00 | 2026-05-07 16:28:00 | 8:37 | S/O | project work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt1 | 2026-05-08 07:35:00 | 2026-05-08 19:15:00 | 11:40 | S/O | conductor stringing (G2G project) | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt2 | 2026-05-16 09:44:00 | 2026-05-16 15:40:00 | 5:56 | S/O | ERS | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Bogura 230 KV Ckt2 | 2026-05-17 08:59:00 | 2026-05-17 14:10:00 | 5:11 | S/O | Project work ERS | 0 | 0 | No interruption
Bogura 132/33kV | New Bogura-1 | 2026-05-09 09:42:00 | 2026-05-09 10:58:00 | 1:16 | S/O | New Bogura-1 Sf6 gas pressar meetar repear | 0 | 0 | No interruption
Bogura 230/132kV | Bogra 132KV Line-1 | 2026-05-09 09:43:00 | 2026-05-09 10:58:00 | 1:15 | S/O | Old Bogura132 Kv Substation issue. | 0 | 0 | No interruption
Bogura 230/132kV | Sherpur 132 KV Line-1 | 2026-05-12 09:28:00 | 2026-05-12 15:42:00 | 6:14 | S/O | Sherpur (Bogura) 132kV | 0 | 0 | No interruption
Bogura 230/132kV | Sherpur 132 KV Line-2 | 2026-05-24 09:33:00 | 2026-05-24 13:15:00 | 3:42 | S/O | Maint.work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-1 | 2026-05-06 07:47:00 | 2026-05-06 18:13:00 | 10:26 | S/O | Due to Conductor stringing at Barapukuria site. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-1 | 2026-05-07 07:50:00 | 2026-05-07 16:36:00 | 8:46 | S/O | Project work (Conductor Stringing ).As per ALDCs instruction. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Rahanpur 400 KV CKT-02 | 2026-05-10 07:00:00 | 2026-05-10 08:00:00 | 1:00 | S/O | Energy Meter Change at Rahanpur | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Rahanpur 400 KV CKT-02 | 2026-05-13 07:12:00 | 2026-05-13 08:28:00 | 1:16 | S/O | As per instruction by NLDC | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-05-15 09:46:00 | 2026-05-15 18:36:00 | 8:50 | S/O | Due to Conductor Shifting from Exiting line tower to ERS tower. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2026-05-15 09:46:00 | 2026-05-15 18:36:00 | 8:50 | S/O | Due to Conductor Shifting from Exiting line tower to ERS tower. | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-2 | 2026-05-16 09:41:00 | 2026-05-16 15:46:00 | 6:05 | S/O | Project work shutdown | 0 | 0 | No interruption
Bogura 400/230kV | Bogura-Baropukuria 230 KV Ckt-2 | 2026-05-17 09:56:00 | 2026-05-17 14:12:00 | 4:16 | S/O | Conductor Shifting from Exiting line tower to ERS tower | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-05-17 11:55:00 | 2026-05-17 20:14:00 | 8:19 | S/O | Conductor Shifting from Exiting line tower to ERS tower | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2026-05-17 11:55:00 | 2026-05-17 20:14:00 | 8:19 | S/O | Conductor Shifting from Exiting line tower to ERS tower | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-05-18 11:15:00 | 2026-05-18 16:47:00 | 5:32 | S/O | Conductor Shifting from Exiting line tower to ERS tower | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2026-05-18 11:15:00 | 2026-05-18 16:47:00 | 5:32 | S/O | Conductor Shifting from Exiting line tower to ERS tower | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-05-20 10:21:00 | 2026-05-20 16:45:00 | 6:24 | S/O | Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2026-05-20 10:21:00 | 2026-05-20 16:45:00 | 6:24 | S/O | Project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-05-21 12:05:00 | 2026-05-21 18:21:00 | 6:16 | S/O | Conductor Jumper Installing work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2026-05-21 12:05:00 | 2026-05-21 18:21:00 | 6:16 | S/O | Conductor Jumper Installing work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2026-05-22 10:32:00 | 2026-05-22 15:53:00 | 5:21 | S/O | As per ALDC 's instruction | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2026-05-22 10:32:00 | 2026-05-22 15:53:00 | 5:21 | S/O | As per ALDC 's instruction | 0 | 0 | No interruption
Chapai 132/33kV | Chapai Rahanpur ckt 1 | 2026-05-21 14:12:00 | 2026-05-21 16:20:00 | 2:08 | S/O | For breaking bird nest | 0 | 0 | No interruption
Joypurhat 132/33kV | Patnitola Ckt.-1 | 2026-05-24 16:56:00 | 2026-05-26 14:35:00 | 45:39 | S/O | bay loop stinging | 0 | 0 | No interruption
Joypurhat 132/33kV | Patnitola Ckt.-2 | 2026-05-24 16:56:00 | 2026-05-26 14:37:00 | 45:41 | S/O | bay loop stinging | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2026-05-19 11:02:00 | 2026-05-19 13:11:00 | 2:09 | S/O | Line clearing from 33 ke feer | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Niamatpur Ckt-1 | 2026-05-01 10:28:00 | 2026-05-03 15:15:00 | 52:47 | S/O | Shutdown get Niamatpur end | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Niamatpur Ckt-2 | 2026-05-01 10:28:00 | 2026-05-03 14:22:00 | 51:54 | S/O | Shutdown get Niamatpur end | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-1 | 2026-05-01 10:25:00 | 2026-05-03 14:13:00 | 51:48 | S/O | Conductor Stringing | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-2 | 2026-05-01 10:25:00 | 2026-05-03 14:22:00 | 51:57 | S/O | Conductor Stringing | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-2 | 2026-05-05 17:28:00 | 2026-05-05 18:12:00 | 0:44 | S/O | Project work | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | EPVTL-1 | 2026-05-03 11:24:00 | 2026-05-03 17:17:00 | 5:53 | S/O | Maint.work | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | EPVTL-2 | 2026-05-07 16:32:00 | 2026-05-07 20:25:00 | 3:53 | S/O | Relay rectification | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | Saidpur Line-2 | 2026-05-07 17:12:00 | 2026-05-08 09:54:00 | 16:42 | S/O | Project work | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Bogura 400 KV Line Ckt-02 | 2026-05-10 07:01:00 | 2026-05-10 08:03:00 | 1:02 | S/O | Due to check energy meter change. | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Bogura 400 KV Line Ckt-02 | 2026-05-13 07:13:00 | 2026-05-13 08:28:00 | 1:15 | S/O | due to check Energy Meter change from Rohonpur side. | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Chapainawabganj 132 KV Line Ckt-01 | 2026-05-21 14:13:00 | 2026-05-21 16:20:00 | 2:07 | S/O | ALDC BOGURA taken S/D due to Maintenance work at chapainawabganj grid. | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Purbosadipur CKT-02 | 2026-05-08 09:50:00 | 2026-05-08 18:04:00 | 8:14 | S/O | For project work. | 0 | 0 | No interruption
Sirajgonj 230 | Baghabari -01 | 2026-05-09 09:36:00 | 2026-05-09 21:13:00 | 11:37 | S/O | DFDR commitioning and testing Baghabari end | 0 | 0 | No interruption
Sirajgonj 230 | Baghabari -01 | 2026-05-14 15:36:00 | 2026-05-14 20:13:00 | 4:37 | S/O | DFDR wor at Baghabari End. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-21 15:14 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-04-20 13:41 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:May 2026
| Area | Previous Month (April' 2026) |  |  |  | Current Month (May'2026)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 51 | 18 | 57 | 126 | 37 | 15 | 104 | 156
2 | Dhaka (South) Grid Circle. | 49 | 8 | 37 | 94 | 50 | 25 | 58 | 133
3 | Chattogram Grid Circle. | 18 | 15 | 18 | 51 | 24 | 10 | 49 | 83
4 | Cumilla Grid Circle. | 51 | 21 | 93 | 165 | 38 | 26 | 67 | 131
5 | Khulna Grid Circle. | 32 | 11 | 71 | 114 | 31 | 17 | 120 | 168
6 | HVDC Grid Circle | 26 | 19 | 33 | 78 | 20 | 32 | 46 | 98
7 | Bogura Grid Circle. | 32 | 42 | 66 | 140 | 43 | 41 | 70 | 154
8 | Others
9 | Total | 259 | 134 | 375 | 768 | 243 | 166 | 514 | 923
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month: May 2026
| Area | Previous Month (April' 2026) |  |  |  | Current Month (May '2026)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 485.48 | 260.8 | 1670.58 | 2416.86 | 867.78 | 273.47 | 2634.07 | 3775.32
2 | Dhaka (South) Grid Circle. | 577.47 | 298.33 | 473.75 | 1349.55 | 875.26 | 530.73 | 752.45 | 2158.44
3 | Chattogram Grid Circle. | 70.48 | 25.03 | 7.08 | 102.59 | 90.47 | 44.8 | 3148.76 | 3284.03
4 | Cumilla Grid Circle. | 133.85 | 212.4 | 1375.35 | 1721.6 | 164.53 | 277.17 | 1153.75 | 1595.45
5 | Khulna Grid Circle. | 275.6 | 361.08 | 741.83 | 1378.51 | 262.05 | 94.18 | 2668.35 | 3024.58
6 | HVDC Grid Circle | 240.3 | 352.95 | 1293.33 | 1886.58 | 66.57 | 384.83 | 566.68 | 1018.08
7 | Bogura Grid Circle. | 340.12 | 570.63 | 244 | 1154.75 | 360.95 | 389.48 | 561.58 | 1312.01
8 | Others | bar: Energy unserved ( MWH ) due to Total; Energy unserved ( MWH ) due to Total
9 | Total | 2123.3 | 2081.22 | 5805.92 | 10010.44 | 2687.61 | 1994.66 | 11485.64 | 16167.91
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:May 2026
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 24 | 25 | 49 | 14 | 6 | 29 | 3557.916
2 | Dhaka (South) | 5031.6 | 18 | 13 | 31 | 9 | 5 | 17 | 1386.77
3 | Chattogram | 2042 | 3 | 4 | 7 | 1 | 3 | 3 | 2932.85
4 | Khulna | 2434 | 16 | 26 | 42 | 7 | 6 | 29 | 1978.76
5 | HVDC | 5954.3 | 15 | 6 | 21 | 2 | 7 | 12 | 1012.33
6 | Bogura | 3145.6 | 18 | 13 | 31 | 9 | 2 | 20 | 931.6
7 | Cumilla | 2981 | 16 | 24 | 40 | 8 | 8 | 24 | 1519.55
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 13319.776
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | HVDC | 99.99%
6 | Bogura | 99.99%
7 | Cumilla | 99.99% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:May 2026
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 3 | 2 | 5 | 3 | - | 2 | 217.4
2 | Dhaka (South) | 990.29 | - | 4 | - | 4 | 1 | 2 | 1 | 771.67
3 | Chattogram | 917 | - | 3 | 1 | 4 | 1 | 1 | 2 | 351.18
4 | Khulna | 1238.4 | - | 4 | 5 | 9 | 3 | 1 | 5 | 1045.82
5 | HVDC | 1325 | - | 1 | - | 1 | 1 | - |  | 5.75
6 | Bogura | 1803.3 |  | 5 | - | 5 | 2 | 2 | 1 | 380.4167
7 | Cumilla | 1648.16 | - | 3 | - | 3 | 1 | 1 | 1 | 75.9
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 2848.1367
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.99%
6 | Bogura | 99.99%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:May 2026
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2026-05-01 | 10 | - | 5 | 10 hr 52 min | 2 | 1 hr 57 min
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:May 2026
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Bhaluka 132/33kV | 4 | 0.04375 | 34.15
Ghatail 132/33kV | 2 | 9:57 | 525.47
Kishoreganj 132/33kV | 1 | 0.011806 | 7.0833
Mymensingh 132/33kV | 2 | 0.027778 | 20
Nabinagar 132/33kV | 1 | 0.0069444 | 17.5
Rajendrapur 132/33kV | 2 | 0.031944 | 1.53
Sherpur 132/33kV | 2 | 0.047222 | 9.07
Sreepur 230/132/33kV | 3 | 0.017361 | 9.82
Tangail 132/33kV | 4 | 0.17361 | 197.43
Ghatail 132/33kV | 1 | 0.15278 | 110
Sreepur 230/132/33kV | 1 | 0.066667 | 76.8
Tangail 132/33kV | 1 | 2:10 | 86.6667
Bhaluka 132/33kV | 2 | 0:20 | 33.33
Rajendrapur 132/33kV | 1 | 0:12 | 12.4
Bhaluka 132/33kV | 3 | 2:20 | 98.7
Bog-Sherpur 132/33kV | 1 | 1:59 | 89.25
Jamalpur 132/33kV | 2 | 6:42 | 156
Kabirpur 132/33kV | 3 | 5:56 | 515.83
Kishoreganj 132/33kV | 1 | 2:24 | 36
Kodda 132/33kV | 6 | 35:12 | 659.25
Manikganj 132/33kV | 2 | 8:06 | 79.67
Mymensingh 132/33kV | 2 | 3:08 | 244.37
Nabinagar 132/33kV | 1 | 2:57 | 29.5
Sreepur 230/132/33kV | 4 | 22:15 | 553.83
Joydebpur 132/33kV | 1 | 2:22 | 142
Nabinagar 132/33kV | 1 | 1:29 | 29.6667
Madanganj 132/33kV | 3 | 7:41 | 20.92
Munshiganj 132/33kV | 6 | 2:57 | 80
Srinagar 132/33kV | 2 | 0:16 | 2.67
Bhulta 132/33kV | 1 | 7:58 | 398.3333
Ghorashal 230kV | 1 | 0:16 | 16
Munshiganj 132/33kV | 1 | 0:45 | 30
Nawabganj 132/33kV | 4 | 6:53 | 86.4
Hasnabad 132/33kV | 1 | 0:53 | 61.8333
Madanganj 132/33kV | 1 | 0:26 | 22.5333
Meghnaghat 400/230kV | 1 | 0:40 | 276.6667
Siddhirganj 230/132kV | 1 | 2:07 | 410.6333
Bhulta 132/33kV | 1 | 1:47 | 80.25
Keranigonj 230/132/33kV | 1 | 1:30 | 22.5
Narshingdi 132/33kV | 4 | 6:55 | 195.93
Sonargaon 132/33kV | 3 | 7:05 | 385.57
Srinagar 132/33kV | 4 | 4:54 | 68.2
TK chemical | 1 | 4:37 | 4.6167
Baroaulia 132/33kV | 1 | 3:09 | 31.5
TK chemical | 1 | 0:57 | 13.3
Baroaulia 132/33kV | 1 | 0:17 | 2.55
Juldah 132/33kV | 1 | 1:28 | 30.8
Korerhat 400/230/132kV | 1 | 0:45 | 52.5
Coxsbazar 132/33kV | 1 | 31:07 | 2800.5
Dohazari 132/33kV | 3 | 2:28 | 82.93
Baroaulia 132/33kV | 1 | 13:16 | 265.3333
Brahmanbaria 132/33kV | 1 | 0:40 | 41.17
Chowmuhani 230/132/33kV | 2 | 0:32 | 5.33
Cumilla(S) 132/33kV | 2 | 0:26 | 13
Kulaura 132/33kV | 1 | 0:14 | 2.8
Sunamganj 132/33kV | 1 | 1:19 | 26.3333
Brahmanbaria 132/33kV | 1 | 0:42 | 10.5
Chowmuhani 230/132/33kV | 6 | 11:52 | 250.17
Daganbhuiyan 132/33kV | 1 | 1:31 | 15.1667
Kasba 132/33kV | 1 | 0:08 | 1.3333
Brahmanbaria 132/33kV | 1 | 0:39 | 19.5
Feni 132/33kV | 1 | 0:22 | 4.4
Sylhet 132/33kV | 1 | 2:36 | 52
Ashuganj 230/132/33kV | 1 | 0:37 | 30.8333
Chandpur 132/33kV | 1 | 3:31 | 35.1667
Chauddagram 132/33kV | 1 | 1:55 | 76.6667
Chowmuhani 230/132/33kV | 5 | 5:04 | 96
Cumilla(S) 132/33kV | 1 | 1:40 | 20
Daudkandi 132/33kV | 4 | 9:58 | 379.27
Feni 132/33kV | 2 | 3:21 | 134
Kachua 230/132/33kV | 1 | 0:12 | 8
Kasba 132/33kV | 1 | 1:08 | 20.4
Kulaura 132/33kV | 1 | 4:02 | 40.3333
Shahjibazar 132/33kV | 3 | 3:15 | 205.5
Sylhet (South) | 2 | 4:47 | 79.33
Sylhet 132/33kV | 1 | 1:53 | 28.25
Barishal 132/33kV | 5 | 0:55 | 32.95
Bhandaria 132/33kV | 6 | 6:57 | 103.2
Mongla 132/33kV | 1 | 0:56 | 20.5333
Satkhira 132/33kV | 2 | 0:09 | 7.9
Bhandaria 132/33kV | 1 | 1:34 | 45.4333
Mongla 132/33kV | 1 | 1:57 | 48.75
Patuakhali 132/33kV | 2 | 1:09 | 31.6
Satkhira 132/33kV | 2 | 0:52 | 65.87
Bagerhat 132/33kV | 1 | 2:34 | 25.6667
Barishal 132/33kV | 1 | 1:30 | 60
Barishal 230/132kV | 3 | 6:10 | 190.69
Bhandaria 132/33kV | 3 | 11:56 | 217.48
Faridpur 132/33kV | 4 | 11:59 | 330.18
Goalpara 132/33kV | 2 | 5:39 | 331.47
Khulna (C) | 4 | 7:47 | 133.7
Mongla 132/33kV | 1 | 2:31 | 17.6167
Narail 132/33kV | 2 | 3:28 | 80
Noapara 132/33kV | 3 | 5:18 | 67.95
Shariatpur 132/33kV | 2 | 8:34 | 265.23
Gopalganj 132/33kV | 2 | 7:56 | 317.33
Khulna (C) | 1 | 5:04 | 76
Satkhira 132/33kV | 2 | 12:59 | 555.02
Bheramara(GK) 132/33kV | 1 | 0:10 | 1.8333
Kushtia 132/33kV | 4 | 1:46 | 64.73
Bhangura 132/33kV | 3 | 4:27 | 61.25
Jhenaidah 132/33kV | 3 | 3:17 | 122.83
Kushtia 132/33kV | 3 | 26:37 | 187
Pabna 132/33kV | 2 | 1:03 | 13.75
Chuadanga 132/33kV | 2 | 6:21 | 265.25
Ishurdi 132/33kV | 3 | 11:38 | 268.93
Pabna 132/33kV | 1 | 2:10 | 32.5
Kurigram 132/33kV | 4 | 2:07 | 29.47
Niamatpur 132/33kV | 4 | 1:03 | 7.98
Purbasadipur 230/132/33kV | 2 | 0:53 | 21.42
Bogura 132/33kV | 1 | 4:00 | 100
Mithapukur 132/33kV | 3 | 4:52 | 84.53
Niamatpur 132/33kV | 1 | 2:07 | 48.6833
Rajshahi 132/33kV | 1 | 1:08 | 22.6667
Rangpur 132/33kV | 1 | 1:38 | 49
Sirajganj 132/33kV | 1 | 0:47 | 6.2667
Barapukuria 230/132/33kV | 1 | 0.034722 | 277.5
Mithapukur 132/33kV | 2 | 0.03125 | 15.05
Rangpur 132/33kV | 1 | 0.015278 | 9.5333
Kurigram 132/33kV | 1 | 0.065278 | 78.3333
Barapukuria 230/132/33kV | 2 | 7:22 | 154.33
Mahasthangarh 132/33kV | 1 | 1:40 | 41.6667
Naogaon 132/33kV | 3 | 6:15 | 53.17
Niamatpur 132/33kV | 1 | 3:56 | 59
Purbasadipur 230/132/33kV | 2 | 3:04 | 61.33
Rajshahi 132/33kV | 1 | 2:53 | 28.8333
Saidpur 132/33kV | 2 | 3:42 | 74
Bog-Sherpur 132/33kV | 1 | 1:59 | 89.25
| 252 | 438:27 | 16167.8967
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: May-2026
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 21 | 2026-05-07 21:00
2 | AKSML | 161.3 | 2026-05-02 07:00
3 | Aftabnagar | 50 | 2026-05-20 23:00
4 | Agargaon | 144 | 2026-05-24 13:00
5 | Agrabad | 94 | 2026-05-14 15:00
6 | Amnura | 48 | 2026-05-23 15:00
7 | Ashuganj | 110 | 2026-05-24 23:00
8 | BSRM | 207 | 2026-05-02 18:30
9 | Bagerhat | 98 | 2026-05-25 01:00
10 | Bajitpur | 103 | 2026-05-31 19:30
11 | Bakerganj | 18 | 2026-05-31 23:00
12 | Bakulia | 117 | 2026-05-20 20:00
13 | Banani | 62.6 | 2026-05-20 13:00
14 | Bangabhaban | 23 | 2026-05-21 10:00
15 | Barapukuria | 72 | 2026-05-20 20:00
16 | Barguna | 28 | 2026-05-22 22:00
17 | Barishal | 126 | 2026-05-24 23:00
18 | Barishal-230 | 128 | 2026-05-24 22:00
19 | Baroaulia | 78 | 2026-05-20 12:00
20 | Baroirhat | 81 | 2026-05-23 19:00
21 | Bashundhara | 223 | 2026-05-20 19:00
22 | BashundharaCement | 13 | 2026-05-10 13:00
23 | Beanibazar | 88 | 2026-05-21 21:00
24 | Benapole | 81 | 2026-05-23 19:00
25 | Bhaluka | 187 | 2026-05-19 20:00
26 | Bhandaria | 71 | 2026-05-31 23:00
27 | Bhangura | 48 | 2026-05-23 19:00
28 | Bheramara(GK) | 79 | 2026-05-20 23:00
29 | Bhulta | 238 | 2026-05-19 15:00
30 | Bog-Sherpur | 90 | 2026-05-20 21:00
31 | Bogura | 191 | 2026-05-20 21:00
32 | Borhanuddin | 100 | 2026-05-28 21:00
33 | Brahmanbaria | 152 | 2026-05-31 21:00
34 | Cantonment | 144 | 2026-05-24 16:00
35 | Chandina | 44 | 2026-05-21 00:00
36 | Chandpur | 100 | 2026-05-23 19:30
37 | Chandraghona | 41 | 2026-05-20 20:00
38 | Chapai | 82 | 2026-05-20 22:00
39 | Charsaidpur | 45 | 2026-05-11 00:00
40 | Chauddagram | 100 | 2026-05-23 22:00
41 | Chhatak | 43 | 2026-05-21 19:00
42 | Chowmuhani | 214 | 2026-05-21 19:30
43 | Chuadanga | 133 | 2026-05-21 21:00
44 | Coxsbazar | 159 | 2026-05-19 13:00
45 | Cumilla(N) | 137 | 2026-05-16 18:30
46 | Cumilla(S) | 189 | 2026-05-19 19:00
47 | Daganbhuiyan | 49 | 2026-05-23 14:00
48 | Daudkandi | 162 | 2026-05-16 20:00
49 | DhakaUniversity | 106 | 2026-05-20 13:00
50 | Dhamrai | 130 | 2026-05-09 20:00
51 | Dhanmondi | 163 | 2026-05-10 13:00
52 | Dohazari | 121 | 2026-05-30 21:00
53 | Faridpur | 199 | 2026-05-21 19:00
54 | Fatullah | 102 | 2026-05-21 12:00
55 | Fenchuganj | 50 | 2026-05-21 21:00
56 | Feni | 129 | 2026-05-21 21:00
57 | GPH | 79 | 2026-05-07 01:00
58 | Ghatail | 106 | 2026-05-30 00:00
59 | Ghorashal | 1 | 2026-05-01 00:00
60 | Ghorashal-230 | 117 | 2026-05-18 12:00
61 | Goalpara | 48 | 2026-05-23 19:00
62 | Gollamari | 132 | 2026-05-24 00:00
63 | Gopalganj | 133 | 2026-05-20 20:00
64 | Gulshan | 152 | 2026-05-20 16:00
65 | Halishahar | 120 | 2026-05-02 16:00
66 | HaripurSBU | 142 | 2026-05-18 01:00
67 | Hasnabad | 107 | 2026-05-21 20:00
68 | Hathazari | 103 | 2026-05-21 00:00
69 | Hatirjheel | 64 | 2026-05-23 13:00
70 | Ishurdi | 97 | 2026-05-16 21:00
71 | Jaldhaka | 91 | 2026-05-20 19:30
72 | Jamalpur | 132 | 2026-05-31 21:00
73 | Jashore | 185 | 2026-05-20 19:30
74 | Jhenaidah | 145 | 2026-05-24 19:00
75 | Joydebpur | 178 | 2026-05-14 19:00
76 | Joypurhat | 74 | 2026-05-17 00:00
77 | Juldah | 22 | 2026-05-24 09:00
78 | KSRM | 21 | 2026-05-16 11:00
79 | Kabirpur | 291 | 2026-05-09 18:30
80 | Kachua | 114 | 2026-05-31 22:00
81 | Kaliganj | 27 | 2026-05-28 21:00
82 | Kallyanpur | 138 | 2026-05-20 23:00
83 | Kalurghat | 82 | 2026-05-30 06:00
84 | Kamrangirchar | 93 | 2026-05-16 13:00
85 | Kaptai | N/A | N/A
86 | Kasba | 44 | 2026-05-31 21:00
87 | Kazla | 130 | 2026-05-16 13:00
88 | Keranigonj | 94 | 2026-05-19 19:30
89 | Khagrachori | 36 | 2026-05-06 20:00
90 | Khulna | 73 | 2026-05-14 12:00
91 | Khulshi | 216 | 2026-05-23 16:00
92 | Kishoreganj | 150 | 2026-05-30 19:30
93 | Kodda | 339 | 2026-05-19 19:00
94 | Kulaura | 62 | 2026-05-20 19:00
95 | Kurigram | 76 | 2026-05-20 19:30
96 | Kushtia | 181 | 2026-05-16 19:30
97 | Laksam | 39 | 2026-05-19 22:00
98 | Lakshmipur | 56 | 2026-05-20 00:00
99 | Lalbag | 88 | 2026-05-12 17:00
100 | Lalmonirhat | 76 | 2026-05-31 19:30
101 | MI_Cement | 18.2 | 2026-05-08 15:00
102 | Madanganj | 49 | 2026-05-19 21:00
103 | Madaripur | 140 | 2026-05-23 22:00
104 | Madartek | 97 | 2026-05-21 00:00
105 | Madunaghat | 70 | 2026-05-23 19:00
106 | Magura | 80 | 2026-05-23 19:00
107 | Mahasthangarh | 92 | 2026-05-20 20:00
108 | Maijdee | 57 | 2026-05-17 23:00
109 | Manikganj | 155 | 2026-05-21 19:30
110 | Maniknagar | 87 | 2026-05-23 13:00
111 | Matarbari | 62 | 2026-05-24 02:00
112 | Matuail | 88 | 2026-05-21 13:00
113 | Metrorail_Motijheel | 35 | 2026-05-19 17:00
114 | Metrorail_Uttara | 9 | 2026-05-29 14:00
115 | Millgate | 112 | 2026-05-21 14:00
116 | Mirpur | 177 | 2026-05-20 19:00
117 | Mirsorai | 61 | 2026-05-04 10:00
118 | Mirzapur | 50 | 2026-05-17 17:00
119 | Mithapukur | 70 | 2026-05-31 19:30
120 | Modern | N/A | N/A
121 | Mogbazar | 129.4 | 2026-05-20 15:00
122 | Mongla | 53 | 2026-05-11 15:00
123 | Motijheel | 58 | 2026-05-23 13:00
124 | Muktagacha | 42 | 2026-05-30 19:30
125 | Munshiganj | 133 | 2026-05-23 23:00
126 | Muradnagar | 57 | 2026-05-30 22:00
127 | Mymensingh | 181 | 2026-05-16 22:00
128 | Nabinagar | 101 | 2026-05-16 12:00
129 | Naogaon | 159 | 2026-05-23 19:30
130 | Narail | 72.5 | 2026-05-24 21:00
131 | Narinda | 83 | 2026-05-20 13:00
132 | Narshingdi | 198 | 2026-05-09 21:00
133 | Natore | 182 | 2026-05-20 23:00
134 | Nawabganj | 77.4 | 2026-05-20 21:00
135 | Netrakona | 165 | 2026-05-30 19:30
136 | New | 92.2 | 2026-05-23 15:00
137 | Niamatpur | 90 | 2026-05-20 22:00
138 | Noapara | 56 | 2026-05-24 21:00
139 | PHP | 14 | 2026-05-03 12:00
140 | Pabna | 123 | 2026-05-24 19:00
141 | Palashbari | 142 | 2026-05-20 19:30
142 | Panchagarh | 68 | 2026-05-20 19:30
143 | Patiya | 14.8 | 2026-05-28 22:00
144 | Patuakhali | 87.6 | 2026-05-29 00:00
145 | Payra | 42 | 2026-05-31 23:00
146 | Postogola | 63 | 2026-05-20 23:00
147 | Pubail | 46 | 2026-05-03 15:00
148 | Purbachal | 41 | 2026-05-23 13:00
149 | Purbasadipur | 156 | 2026-05-20 19:30
150 | Rahanpur | 46 | 2026-05-22 22:00
151 | Rahim | 49 | 2026-05-13 13:00
152 | Rajbari | 102 | 2026-05-24 19:00
153 | Rajendrapur | 131 | 2026-05-16 12:00
154 | Rajshahi | 150 | 2026-05-19 21:00
155 | Rajshahi-230 | 116 | 2026-05-23 14:00
156 | Ramganj | 126 | 2026-05-20 21:00
157 | Rampur | 60 | 2026-05-03 18:30
158 | Rangamati | 20 | 2026-05-16 18:30
159 | Rangpur | 162 | 2026-05-20 20:00
160 | Ruppur | 4.6 | 2026-05-17 15:00
161 | SSM | 12 | 2026-05-01 04:00
162 | Saidpur | 118 | 2026-05-20 19:30
163 | Santhia | 40 | 2026-05-17 21:00
164 | Satkhira | 157 | 2026-05-24 22:00
165 | Satmasjid | 121 | 2026-05-24 16:00
166 | Savar | 238 | 2026-05-21 20:00
167 | SevenRings | 22.39 | 2026-05-20 12:00
168 | ShahCement | 44 | 2026-05-07 23:00
169 | Shahjadpur | 104 | 2026-05-20 20:00
170 | Shahjibazar | 130 | 2026-05-20 18:30
171 | Shahmirpur | 67 | 2026-05-18 01:00
172 | Shariatpur | 112 | 2026-05-31 23:00
173 | Sherpur | 170 | 2026-05-31 19:30
174 | Shikalbaha | 38 | 2026-05-09 00:00
175 | Shitalakhya | 98.7 | 2026-05-23 15:00
176 | Sholosohor | 54 | 2026-05-21 16:00
177 | Shomvuganj | 24 | 2026-05-31 20:00
178 | Shyampur | 200 | 2026-05-09 13:00
179 | Siddhirganj | 138 | 2026-05-20 18:30
180 | Sirajganj | 142 | 2026-05-20 20:00
181 | Sonargaon | 155 | 2026-05-23 20:00
182 | Sreemongol | 97 | 2026-05-20 22:00
183 | Sreepur | 130 | 2026-05-20 21:00
184 | Srinagar | 59 | 2026-05-20 19:30
185 | Sunamganj | 66 | 2026-05-20 20:00
186 | Sylhet | 77 | 2026-05-20 19:00
187 | Sylhet-132 | 135 | 2026-05-20 23:00
188 | TK | 30 | 2026-05-21 19:00
189 | Tangail | 194 | 2026-05-16 18:00
190 | Taraganj | 30 | 2026-05-08 19:00
191 | Tasnim | 37 | 2026-05-18 15:00
192 | Thakurgaon | 122 | 2026-05-20 19:30
193 | Tongi | 177 | 2026-05-20 11:00
194 | Ullahpara | 47 | 2026-05-16 19:00
195 | Ullon | 65 | 2026-05-08 13:00
196 | Uttara | 114 | 2026-05-24 15:00
197 | UttaraNew | 65 | 2026-05-20 23:00
198 | Zigatola | 110 | 2026-05-20 16:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: May 2026
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 6212.63 | 2026-05-20 | 21:00
Chattogram | 1710.3 | 2026-05-21 | 0:00
Cumilla | 1694 | 2026-05-23 | 23:00
Mymensingh | 1103 | 2026-05-24 | 20:00
Sylhet | 695 | 2026-05-20 | 19:00
Khulna | 2088.7 | 2026-05-20 | 19:00
Barishal | 579 | 2026-05-24 | 23:00
Rajshahi | 1820.8 | 2026-05-20 | 21:00
Rangpur | 1160 | 2026-05-20 | 19:30
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May-2026
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 414 | 2026-05-27 09:00 | 346 | 2026-05-23 15:00
2 | Amtali | 400 | 422 | 2026-05-27 09:00 | 398 | 2026-05-22 19:00
3 | Ashuganj | 400 | N/A | N/A | N/A | N/A
4 | Bhulta | 400 | 422 | 2026-05-26 05:00 | 363 | 2026-05-14 08:00
5 | Bibiana | 400 | 417 | 2026-05-27 11:00 | 378 | 2026-05-23 14:00
6 | BIPTC | 400 | 409 | 2026-05-01 04:00 | 386 | 2026-05-23 15:00
7 | Bogura | 400 | 417 | 2026-05-04 05:00 | 367 | 2026-05-18 19:30
8 | Gopalganj | 400 | 417 | 2026-05-27 09:00 | 366 | 2026-05-24 00:00
9 | Kaliakoir | 400 | 415 | 2026-05-27 09:00 | 345 | 2026-05-23 15:00
10 | Korerhat | 400 | 422 | 2026-05-27 12:00 | 374 | 2026-05-18 16:00
11 | Madunaghat | 400 | 417 | 2026-05-27 12:00 | 383 | 2026-05-18 16:00
12 | Meghnaghat | 400 | 415 | 2026-05-27 09:00 | 351 | 2026-05-23 15:00
13 | Payra | 400 | 423 | 2026-05-27 10:00 | 400 | 2026-05-22 19:00
14 | Rahanpur | 400 | 425 | 2026-05-04 05:00 | 383 | 2026-05-18 19:30
15 | Rampal | 400 | 415 | 2026-05-27 09:00 | 372 | 2026-05-21 16:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 250 | 2026-05-09 14:00 | 208 | 2026-05-18 16:00
2 | AKSML | 230 | 242 | 2026-05-27 12:00 | 220 | 2026-05-24 09:00
3 | Aminbazar | 230 | 245 | 2026-05-26 05:00 | 210 | 2026-05-23 15:00
4 | Ashuganj | 230 | 242 | 2026-05-26 06:00 | 212 | 2026-05-18 15:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 243 | 2026-05-29 18:00 | 221 | 2026-05-18 15:00
7 | Barapukuria | 230 | 238 | 2026-05-26 04:00 | 198 | 2026-05-31 20:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 242 | 2026-05-27 08:00 | 214 | 2026-05-21 15:00
10 | Bheramara | 230 | 243 | 2026-05-27 08:00 | 219 | 2026-05-23 15:00
11 | Bhulta | 230 | 246 | 2026-05-27 08:00 | 206 | 2026-05-21 12:00
12 | Bibiana | 230 | 246 | 2026-05-27 08:00 | 220 | 2026-05-24 11:00
13 | BIPTC | 230 | 244 | 2026-05-27 08:00 | 219 | 2026-05-18 15:00
14 | Bogura | 230 | 249 | 2026-05-27 06:00 | 220 | 2026-05-18 19:30
15 | Bogura-400 | 230 | 249 | 2026-05-29 17:00 | 220 | 2026-05-18 19:30
16 | Borhanuddin | 230 | 242 | 2026-05-29 18:00 | 219 | 2026-05-22 22:00
17 | BSRM | 230 | 242 | 2026-05-27 10:00 | 218 | 2026-05-06 12:00
18 | Chowmuhani | 230 | 246 | 2026-05-27 10:00 | 213 | 2026-05-24 15:00
19 | Cumilla(N) | 230 | 243 | 2026-05-27 10:00 | 213 | 2026-05-10 12:00
20 | Faridpur | 230 | 247 | 2026-05-27 08:00 | 205 | 2026-05-20 22:00
21 | Fenchuganj | 230 | 249 | 2026-05-27 10:00 | 225 | 2026-05-10 12:00
22 | Feni | 230 | 244 | 2026-05-27 10:00 | 213 | 2026-05-18 15:00
23 | Ghorashal | 230 | 248 | 2026-05-27 08:00 | 210 | 2026-05-18 15:00
24 | Ghorashal-230 | 230 | 242 | 2026-05-27 06:00 | 204 | 2026-05-21 10:00
25 | Gopalganj | 230 | 246 | 2026-05-27 08:00 | 206 | 2026-05-21 15:00
26 | GPH | 230 | 239 | 2026-05-01 02:00 | 221 | 2026-05-07 12:00
27 | Haripur | 230 | 243 | 2026-05-26 05:00 | 209 | 2026-05-18 15:00
28 | Hasnabad | 230 | 246 | 2026-05-27 07:00 | 208 | 2026-05-10 12:00
29 | Hathazari | 230 | 238 | 2026-05-26 12:00 | 220 | 2026-05-18 15:00
30 | Ishurdi | 230 | 245 | 2026-05-27 08:00 | 220 | 2026-05-18 15:00
31 | Jhenaidah | 230 | 244 | 2026-05-27 08:00 | 207 | 2026-05-21 19:00
32 | Kachua | 230 | 246 | 2026-05-27 10:00 | 216 | 2026-05-14 12:00
33 | Kaliakoir | 230 | 247 | 2026-05-27 08:00 | 211 | 2026-05-18 15:00
34 | Keranigonj | 230 | 245 | 2026-05-26 05:00 | 207 | 2026-05-18 16:00
35 | Khulna(S) | 230 | 245 | 2026-05-27 08:00 | 205 | 2026-05-21 16:00
36 | Korerhat | 230 | 244 | 2026-05-27 10:00 | 217 | 2026-05-06 13:00
37 | Madunaghat | 230 | 240 | 2026-05-01 05:00 | 222 | 2026-05-24 08:00
38 | Madunaghat-400 | 230 | 241 | 2026-05-01 06:00 | 223 | 2026-05-18 16:00
39 | Maniknagar | 230 | 243 | 2026-05-26 06:00 | 206 | 2026-05-23 14:00
40 | Meghnaghat | 230 | 249 | 2026-05-27 10:00 | 216 | 2026-05-14 12:00
41 | Meghnaghat-400 | 230 | 245 | 2026-05-27 06:00 | 212 | 2026-05-23 15:00
42 | Mirsorai | 230 | 245 | 2026-05-27 12:00 | 217 | 2026-05-18 16:00
43 | Naogaon | 230 | 241 | 2026-05-07 19:00 | 199 | 2026-05-18 19:30
44 | Purbasadipur | 230 | 237 | 2026-05-26 03:00 | 195 | 2026-05-20 20:00
45 | Rajshahi | 230 | 242 | 2026-05-27 08:00 | 216 | 2026-05-23 15:00
46 | Rampal | 230 | 242 | 2026-05-27 08:00 | 207 | 2026-05-20 22:00
47 | Rampur | 230 | N/A | N/A | N/A | N/A
48 | Rampura | 230 | 244 | 2026-05-27 06:00 | 202 | 2026-05-21 13:00
49 | Shikalbaha | 230 | 239 | 2026-05-27 12:00 | 220 | 2026-05-18 15:00
50 | Shyampur | 230 | 244 | 2026-05-26 05:00 | 208 | 2026-05-23 15:00
51 | Siddhirganj | 230 | 245 | 2026-05-27 08:00 | 208 | 2026-05-23 20:00
52 | Sirajgonj | 230 | 248 | 2026-05-27 08:00 | 220 | 2026-05-25 18:00
53 | Sreepur | 230 | 240 | 2026-05-26 05:00 | 210 | 2026-05-18 15:00
54 | Tongi | 230 | 242 | 2026-05-26 05:00 | 201 | 2026-05-21 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 140 | 2026-05-17 05:00 | 120 | 2026-05-18 15:00
2 | Agargaon | 132 | 144 | 2026-05-26 05:00 | 118 | 2026-05-23 15:00
3 | Agrabad | 132 | 141 | 2026-05-27 12:00 | 125 | 2026-05-07 12:00
4 | AKS | 132 | 140 | 2026-05-27 12:00 | 124 | 2026-05-19 00:00
5 | Aminbazar | 132 | 143 | 2026-05-27 08:00 | 114 | 2026-05-18 15:00
6 | Amnura | 132 | 141 | 2026-05-29 17:00 | 120 | 2026-05-30 01:00
7 | Ashuganj | 132 | N/A | N/A | N/A | N/A
8 | Ashuganj-230 | 132 | 146 | 2026-05-26 06:00 | 127 | 2026-05-19 16:00
9 | Bagerhat | 132 | 141 | 2026-05-26 13:00 | 108 | 2026-05-20 22:00
10 | Bajitpur | 132 | 142 | 2026-05-26 05:00 | 117 | 2026-05-20 16:00
11 | Bakerganj | 132 | 140 | 2026-05-27 10:00 | 122 | 2026-05-23 23:00
12 | Bakulia | 132 | 142 | 2026-05-27 12:00 | 125 | 2026-05-07 12:00
13 | Banani | 132 | 140 | 2026-05-11 05:00 | 119 | 2026-05-19 16:00
14 | Bangabhaban | 132 | 143 | 2026-05-26 13:00 | 118 | 2026-05-23 13:00
0 | Barapukuria | 132 | 140 | 2026-05-26 02:00 | 116 | 2026-05-31 20:00
16 | Barguna | 132 | 142 | 2026-05-27 10:00 | 121 | 2026-05-23 23:00
17 | Barishal | 132 | 142 | 2026-05-27 10:00 | 121 | 2026-05-21 15:00
18 | Barishal-230 | 132 | 141 | 2026-05-27 10:00 | 122 | 2026-05-21 15:00
19 | Baroaulia | 132 | 142 | 2026-05-27 12:00 | 126 | 2026-05-24 09:00
20 | Baroirhat | 132 | 140 | 2026-05-27 11:00 | 124 | 2026-05-07 12:00
21 | Bashundhara | 132 | 140 | 2026-05-24 17:00 | 117 | 2026-05-18 15:00
22 | BashundharaCement | 132 | 143 | 2026-05-26 06:00 | 121 | 2026-05-10 12:00
23 | Beanibazar | 132 | 134 | 2026-05-02 06:00 | 113 | 2026-05-30 22:00
24 | Benapole | 132 | 141 | 2026-05-27 08:00 | 110 | 2026-05-21 19:00
25 | Bhaluka | 132 | 140 | 2026-05-26 04:00 | 118 | 2026-05-18 15:00
26 | Bhandaria | 132 | 143 | 2026-05-27 09:00 | 112 | 2026-05-23 23:00
27 | Bhangura | 132 | 142 | 2026-05-29 17:00 | 125 | 2026-05-12 13:00
28 | Bheramara | 132 | 141 | 2026-05-27 08:00 | 127 | 2026-05-20 19:30
29 | Bheramara(GK) | 132 | 141 | 2026-05-27 08:00 | 127 | 2026-05-20 19:30
30 | Bhulta | 132 | 138 | 2026-05-26 05:00 | 117 | 2026-05-18 15:00
31 | Bog-Sherpur | 132 | 144 | 2026-05-29 17:00 | 126 | 2026-05-05 19:30
32 | Bogura | 132 | 145 | 2026-05-27 06:00 | 128 | 2026-05-04 19:00
33 | Bogura-230 | 132 | 145 | 2026-05-27 06:00 | 126 | 2026-05-18 19:30
34 | Brahmanbaria | 132 | 146 | 2026-05-26 05:00 | 118 | 2026-05-20 12:00
35 | Cantonment | 132 | 141 | 2026-05-26 04:00 | 119 | 2026-05-23 12:00
36 | Chandina | 132 | 144 | 2026-05-27 10:00 | 123 | 2026-05-10 10:00
37 | Chandpur | 132 | 141 | 2026-05-27 10:00 | 120 | 2026-05-29 14:00
39 | Chandraghona | 132 | 142 | 2026-05-27 12:00 | 127 | 2026-05-24 09:00
40 | Chapai | 132 | 140 | 2026-05-27 05:00 | 124 | 2026-05-18 21:00
41 | Charsaidpur | 132 | 144 | 2026-05-26 05:00 | 120 | 2026-05-10 13:00
42 | Chauddagram | 132 | 141 | 2026-05-27 10:00 | 122 | 2026-05-10 12:00
43 | Chhatak | 132 | 134 | 2026-05-02 07:00 | 110 | 2026-05-30 22:00
44 | Chowmuhani | 132 | 140 | 2026-05-27 10:00 | 121 | 2026-05-09 16:00
45 | Chuadanga | 132 | 142 | 2026-05-27 08:00 | 113 | 2026-05-23 15:00
46 | Coxsbazar | 132 | 136 | 2026-05-27 13:00 | 108 | 2026-05-19 19:30
47 | Cumilla(N) | 132 | 144 | 2026-05-27 10:00 | 123 | 2026-05-10 11:00
48 | Cumilla(S) | 132 | 143 | 2026-05-27 10:00 | 118 | 2026-05-19 14:00
49 | Daganbhuiyan | 132 | 140 | 2026-05-27 10:00 | 122 | 2026-05-10 12:00
50 | Daudkandi | 132 | 141 | 2026-05-26 06:00 | 113 | 2026-05-10 12:00
51 | DhakaUniversity | 132 | 141 | 2026-05-24 17:00 | 119 | 2026-05-21 13:00
52 | Dhamrai | 132 | 142 | 2026-05-25 11:00 | 120 | 2026-05-07 12:00
53 | Dhanmondi | 132 | 143 | 2026-05-26 05:00 | 120 | 2026-05-23 10:00
54 | Dohazari | 132 | 140 | 2026-05-27 13:00 | 120 | 2026-05-19 13:00
55 | Faridpur | 132 | 142 | 2026-05-27 09:00 | 119 | 2026-05-21 15:00
56 | Fatullah | 132 | 143 | 2026-05-27 09:00 | 119 | 2026-05-10 12:00
57 | Fenchuganj | 132 | 142 | 2026-05-26 05:00 | 126 | 2026-05-09 19:00
58 | Feni | 132 | 139 | 2026-05-26 07:00 | 122 | 2026-05-06 12:00
59 | Feni-230 | 132 | 141 | 2026-05-27 10:00 | 122 | 2026-05-09 00:00
60 | Ghatail | 132 | 141 | 2026-05-26 05:00 | 112 | 2026-05-20 23:00
61 | Ghorashal | 132 | 145 | 2026-05-26 03:00 | 123 | 2026-05-18 15:00
62 | Goalpara | 132 | 142 | 2026-05-01 00:00 | 117 | 2026-05-21 16:00
63 | Gollamari | 132 | 142 | 2026-05-27 08:00 | 110 | 2026-05-23 23:00
64 | Gopalganj | 132 | 141 | 2026-05-27 08:00 | 117 | 2026-05-21 15:00
65 | Gopalganj-400 | 132 | 144 | 2026-05-27 08:00 | 121 | 2026-05-21 15:00
66 | Gulshan | 132 | 140 | 2026-05-24 17:00 | 140 | 2026-05-18 16:00
67 | Halishahar | 132 | 141 | 2026-05-27 12:00 | 125 | 2026-05-07 12:00
68 | Haripur | 132 | 142 | 2026-05-26 05:00 | 121 | 2026-05-23 20:00
69 | HaripurSBU | 132 | 142 | 2026-05-26 05:00 | 122 | 2026-05-10 12:00
70 | Hasnabad | 132 | 143 | 2026-05-26 05:00 | 117 | 2026-05-18 16:00
71 | Hathazari | 132 | 141 | 2026-05-27 14:00 | 127 | 2026-05-07 12:00
72 | Hatirjheel | 132 | 141 | 2026-05-26 05:00 | 120 | 2026-05-18 15:00
73 | Ishurdi | 132 | 144 | 2026-05-29 17:00 | 129 | 2026-05-18 15:00
74 | Jaldhaka | 132 | 141 | 2026-05-26 02:00 | 111 | 2026-05-31 20:00
75 | Jamalpur | 132 | 143 | 2026-05-26 03:00 | 112 | 2026-05-18 23:00
76 | Jashore | 132 | 142 | 2026-05-27 08:00 | 111 | 2026-05-21 15:00
77 | Jhenaidah | 132 | 144 | 2026-05-27 08:00 | 113 | 2026-05-20 19:30
78 | Jhenaidah-230 | 132 | 143 | 2026-05-27 08:00 | 121 | 2026-05-16 19:00
79 | Joydebpur | 132 | 144 | 2026-05-26 05:00 | 116 | 2026-05-19 16:00
80 | Joypurhat | 132 | 143 | 2026-05-29 17:00 | 121 | 2026-05-11 19:00
81 | Juldah | 132 | 141 | 2026-05-27 12:00 | 126 | 2026-05-09 03:00
82 | Kabirpur | 132 | 144 | 2026-05-26 12:00 | 114 | 2026-05-10 12:00
83 | Kachua | 132 | 141 | 2026-05-27 10:00 | 123 | 2026-05-06 15:00
84 | Kaliakoir | 132 | 145 | 2026-05-26 12:00 | 108 | 2026-05-03 04:00
85 | Kaliganj | 132 | 143 | 2026-05-27 08:00 | 120 | 2026-05-08 15:00 |  | 125
86 | Kallyanpur | 132 | 143 | 2026-05-26 05:00 | 115 | 2026-05-18 15:00
87 | Kalurghat | 132 | 141 | 2026-05-27 12:00 | 128 | 2026-05-06 14:00
88 | Kamrangirchar | 132 | 141 | 2026-05-26 04:00 | 114 | 2026-05-18 15:00
89 | Kaptai | 132 | N/A | N/A | N/A | N/A
90 | Kasba | 132 | 143 | 2026-05-27 10:00 | 117 | 2026-05-10 12:00
91 | Kazla | 132 | 143 | 2026-05-26 13:00 | 118 | 2026-05-23 13:00
92 | Keranigonj | 132 | 141 | 2026-05-26 04:00 | 121 | 2026-05-18 16:00
93 | Khagrachori | 132 | 142 | 2026-05-27 12:00 | 124 | 2026-05-24 09:00
94 | Khulna | 132 | 142 | 2026-05-27 08:00 | 115 | 2026-05-20 22:00
95 | Khulna(S) | 132 | 141 | 2026-05-26 13:00 | 118 | 2026-05-21 19:00
96 | Khulshi | 132 | 141 | 2026-05-27 12:00 | 123 | 2026-05-07 12:00
97 | Kishoreganj | 132 | 141 | 2026-05-26 05:00 | 115 | 2026-05-21 19:00
98 | Kodda | 132 | 142 | 2026-05-26 12:00 | 119 | 2026-05-23 15:00
99 | Korerhat | 132 | 140 | 2026-05-27 11:00 | 126 | 2026-05-22 21:00
100 | KSRM | 132 | 142 | 2026-05-27 12:00 | 126 | 2026-05-19 12:00
101 | Kulaura | 132 | 140 | 2026-05-25 12:00 | 124 | 2026-05-09 19:00
102 | Kurigram | 132 | 141 | 2026-05-26 02:00 | 107 | 2026-05-31 20:00
103 | Kushtia | 132 | 142 | 2026-05-27 07:00 | 120 | 2026-05-20 19:30
104 | Laksam | 132 | 142 | 2026-05-27 10:00 | 122 | 2026-05-06 13:00
105 | Lakshmipur | 132 | 140 | 2026-05-27 10:00 | 120 | 2026-05-06 15:00
106 | Lalbag | 132 | 140 | 2026-05-01 06:00 | 121 | 2026-05-19 16:00
107 | Lalmonirhat | 132 | 136 | 2026-05-25 07:00 | 108 | 2026-05-31 20:00
108 | Madanganj | 132 | 143 | 2026-05-26 06:00 | 121 | 2026-05-10 12:00
109 | Madaripur | 132 | 141 | 2026-05-27 09:00 | 121 | 2026-05-20 14:00
110 | Madartek | 132 | 141 | 2026-05-26 05:00 | 119 | 2026-05-18 15:00
111 | Madunaghat | 132 | 141 | 2026-05-27 12:00 | 117 | 2026-05-07 14:00
112 | Magura | 132 | 143 | 2026-05-27 08:00 | 117 | 2026-05-21 19:00
113 | Mahasthangarh | 132 | 143 | 2026-05-27 06:00 | 123 | 2026-05-18 19:30
114 | Maijdee | 132 | 139 | 2026-05-27 10:00 | 120 | 2026-05-06 15:00
115 | Manikganj | 132 | 142 | 2026-05-26 12:00 | 113 | 2026-05-10 12:00
116 | Maniknagar | 132 | 143 | 2026-05-26 13:00 | 119 | 2026-05-10 13:00
117 | Matarbari | 132 | 138 | 2026-05-27 13:00 | 105 | 2026-05-29 13:00
118 | Matuail | 132 | 142.6 | 2026-05-26 05:00 | 120 | 2026-05-14 13:00
119 | Metrorail_Motijheel | 132 | 142 | 2026-05-26 05:00 | 119 | 2026-05-10 13:00
120 | Metrorail_Uttara | 132 | 138 | 2026-05-01 09:00 | 118 | 2026-05-10 11:00
121 | Millgate | 132 | 139 | 2026-05-02 04:00 | 117 | 2026-05-18 15:00
122 | Mirpur | 132 | 142 | 2026-05-26 05:00 | 116 | 2026-05-18 16:00
123 | Mirzapur | 132 | 142 | 2026-05-26 05:00 | 116 | 2026-05-24 00:00
124 | Mithapukur | 132 | 142 | 2026-05-26 04:00 | 117 | 2026-05-31 20:00
125 | MI_Cement | 132 | 144 | 2026-05-27 09:00 | 115 | 2026-05-10 12:00
126 | Modern | 132 | N/A | N/A | N/A | N/A
127 | Mogbazar | 132 | 142 | 2026-05-17 06:00 | 120 | 2026-05-19 16:00
128 | Mongla | 132 | 140 | 2026-05-27 09:00 | 110 | 2026-05-21 15:00
129 | Motijheel | 132 | 143 | 2026-05-26 13:00 | 118 | 2026-05-23 13:00
130 | Muktagacha | 132 | 140 | 2026-05-26 03:00 | 111 | 2026-05-20 23:00
131 | Munshiganj | 132 | 141 | 2026-05-26 06:00 | 119 | 2026-05-10 12:00
132 | Muradnagar | 132 | 143 | 2026-05-27 10:00 | 113 | 2026-05-21 01:00
133 | Mymensingh | 132 | 143 | 2026-05-26 04:00 | 108 | 2026-05-21 19:00
134 | Nabinagar | 132 | 144 | 2026-05-27 08:00 | 117 | 2026-05-07 12:00
135 | Naogaon | 132 | 144 | 2026-05-27 06:00 | 120 | 2026-05-18 19:30
136 | Narail | 132 | 145 | 2026-05-27 08:00 | 117 | 2026-05-21 19:00
137 | Narinda | 132 | 0 | 2026-05-01 00:00 | N/A | N/A
139 | Narshingdi | 132 | 145 | 2026-05-26 05:00 | 112 | 2026-05-10 11:00
140 | Natore | 132 | 141 | 2026-05-27 07:00 | 124 | 2026-05-18 15:00
141 | Nawabganj | 132 | 140 | 2026-05-01 06:00 | 118 | 2026-05-18 16:00
142 | Netrakona | 132 | 137 | 2026-05-26 04:00 | 103 | 2026-05-21 18:30
143 | New | 132 | 141 | 2026-05-27 08:00 | 119 | 2026-05-18 15:00
144 | Niamatpur | 132 | 141 | 2026-05-27 05:00 | 122 | 2026-05-18 19:30
145 | Noapara | 132 | 141 | 2026-05-27 08:00 | 114 | 2026-05-20 22:00
146 | Pabna | 132 | 141 | 2026-05-27 07:00 | 115 | 2026-05-19 12:00
147 | Palashbari | 132 | 141 | 2026-05-26 03:00 | 113 | 2026-05-31 20:00
148 | Panchagarh | 132 | 142 | 2026-05-26 03:00 | 121 | 2026-05-18 19:30
149 | Patiya | 132 | 141 | 2026-05-27 13:00 | 123 | 2026-05-29 13:00
150 | Patuakhali | 132 | 139 | 2026-05-27 10:00 | 122 | 2026-05-21 15:00
151 | Payra | 132 | 139 | 2026-05-27 10:00 | 129 | 2026-05-20 23:00
152 | PHP | 132 | 140 | 2026-05-27 12:00 | 124 | 2026-05-14 13:00
153 | Postogola | 132 | 144 | 2026-05-27 09:00 | 116 | 2026-05-18 15:00
154 | Pubail | 132 | 146 | 2026-05-26 05:00 | 120 | 2026-05-18 15:00
155 | Purbachal | 132 | 141 | 2026-05-24 17:00 | 117 | 2026-05-18 15:00
156 | Purbasadipur | 132 | 141 | 2026-05-26 02:00 | 118 | 2026-05-18 19:30
157 | Rahanpur | 132 | 142 | 2026-05-27 05:00 | 126 | 2026-05-18 19:30
158 | Rahanpur-400 | 132 | 141 | 2026-05-04 05:00 | 126 | 2026-05-18 19:30
159 | Rahim | 132 | 139 | 2026-05-01 18:00 | 121 | 2026-05-10 12:00
160 | Rajbari | 132 | 142 | 2026-05-27 08:00 | 115 | 2026-05-20 19:00
161 | Rajendrapur | 132 | 140 | 2026-05-26 04:00 | 116 | 2026-05-18 15:00
162 | Rajshahi | 132 | 139 | 2026-05-29 17:00 | 122 | 2026-05-18 15:00
163 | Rajshahi-230 | 132 | 139 | 2026-05-27 08:00 | 123 | 2026-05-23 15:00
164 | Ramganj | 132 | 139 | 2026-05-27 10:00 | 118 | 2026-05-15 23:00
165 | Rampur | 132 | 141 | 2026-05-27 12:00 | 124 | 2026-05-07 12:00
166 | Rampura | 132 | 141 | 2026-05-26 05:00 | 120 | 2026-05-18 15:00
167 | Rangamati | 132 | 142 | 2026-05-27 12:00 | 126 | 2026-05-21 10:00
168 | Rangpur | 132 | 141 | 2026-05-26 03:00 | 116 | 2026-05-31 20:00
169 | Ruppur | 132 | 142 | 2026-05-29 17:00 | 128 | 2026-05-18 15:00
170 | Saidpur | 132 | 142 | 2026-05-26 04:00 | 115 | 2026-05-11 19:00
171 | Santhia | 132 | 142 | 2026-05-27 07:00 | 127 | 2026-05-11 19:00
172 | Satkhira | 132 | 139 | 2026-05-01 00:00 | 108 | 2026-05-21 19:00
173 | Satmasjid | 132 | 144 | 2026-05-26 05:00 | 118 | 2026-05-23 13:00
174 | Savar | 132 | 141 | 2026-05-27 09:00 | 114 | 2026-05-18 15:00
175 | SevenRings | 132 | 147 | 2026-05-26 05:00 | 123 | 2026-05-18 15:00
176 | ShahCement | 132 | 144 | 2026-05-26 05:00 | 120 | 2026-05-10 13:00
177 | Shahjadpur | 132 | 145 | 2026-05-29 17:00 | 130 | 2026-05-11 12:00
178 | Shahjibazar | 132 | 143 | 2026-05-26 05:00 | 118 | 2026-05-20 12:00
179 | Shahmirpur | 132 | 142 | 2026-05-27 12:00 | 126 | 2026-05-06 12:00
180 | Shariatpur | 132 | 142 | 2026-05-27 09:00 | 118 | 2026-05-20 22:00
181 | Sherpur | 132 | 141 | 2026-05-26 03:00 | 108 | 2026-05-30 22:00
182 | Shikalbaha | 132 | 130 | 2026-05-27 12:00 | 116 | 2026-05-07 12:00
183 | Shikalbaha-230 | 132 | 142 | 2026-05-27 12:00 | 126 | 2026-05-19 15:00
184 | Shitalakhya | 132 | 144 | 2026-05-27 09:00 | 113 | 2026-05-23 15:00
185 | Sholosohor | 132 | 141 | 2026-05-27 12:00 | 125 | 2026-05-24 09:00
186 | Shomvuganj | 132 | 136 | 2026-05-26 05:00 | 109 | 2026-05-21 19:00
187 | Shyampur | 132 | 141 | 2026-05-26 05:00 | 120 | 2026-05-05 12:00
188 | Shyampur-230 | 132 | 142 | 2026-05-24 17:00 | 120 | 2026-05-10 12:00
189 | Siddhirganj | 132 | 143 | 2026-05-26 05:00 | 121 | 2026-05-23 20:00
190 | Sirajganj | 132 | 142 | 2026-05-29 17:00 | 122 | 2026-05-12 11:00
191 | Sonargaon | 132 | 141 | 2026-05-26 05:00 | 119 | 2026-05-10 12:00
192 | Sreemongol | 132 | 140 | 2026-05-26 05:00 | 119 | 2026-05-09 21:00
193 | Sreepur | 132 | 139 | 2026-05-26 04:00 | 121 | 2026-05-18 15:00
194 | Srinagar | 132 | 140 | 2026-05-01 06:00 | 120 | 2026-05-18 16:00
195 | SSM | 132 | 148 | 2026-05-27 13:00 | 126 | 2026-05-08 04:00
196 | Sunamganj | 132 | 136 | 2026-05-26 05:00 | 105 | 2026-05-30 23:00
197 | Sylhet | 132 | 137 | 2026-05-26 05:00 | 117 | 2026-05-30
198 | Sylhet-132 | 132 | 134 | 2026-05-04 04:00 | 117 | 2026-05-30 00:00
199 | Tangail | 132 | 141 | 2026-05-26 12:00 | 112 | 2026-05-22 08:00
200 | Taraganj | 132 | 140 | 2026-05-17 01:00 | 115 | 2026-05-04 19:30
201 | Tasnim | 132 | 142 | 2026-05-26 05:00 | 118 | 2026-05-23 14:00
202 | Thakurgaon | 132 | 142 | 2026-05-26 03:00 | 119 | 2026-05-18 19:30
203 | TK | 132 | 140 | 2026-05-27 12:00 | 127 | 2026-05-24 09:00
204 | Tongi | 132 | 141 | 2026-05-25 12:00 | 120 | 2026-05-18 15:00
205 | Ullahpara | 132 | 142 | 2026-05-27 07:00 | 124 | 2026-05-12 12:00
206 | Ullon | 132 | 141 | 2026-05-26 05:00 | 120 | 2026-05-19 16:00
207 | Uttara | 132 | 140 | 2026-05-27 08:00 | 116 | 2026-05-18 15:00
208 | UttaraNew | 132 | 138 | 2026-05-01 07:00 | 117 | 2026-05-18 15:00
209 | Zigatola | 132 | 141 | 2026-05-26 05:00 | 121 | 2026-05-18 16:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: May 2026
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 16-05-2026 | 14:00 | 444 | 211 | 94.5358
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 16-05-2026 | 11:00 | 440 | 224 | 94.9494
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 16-05-2026 | 11:00 | 440 | 224 | 94.9494
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 01-05-2026 | 00:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 21-05-2026 | 14:00 | 313 | 128 | 65.031
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 21-05-2026 | 14:00 | 313 | 128 | 65.031
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 31-05-2026 | 11:00 | 157 | 56 | 32.0554
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 31-05-2026 | 11:00 | 150 | 48 | 30.2871
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 18-05-2026 | 20:00 | 378 | 66 | 51.1625
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 18-05-2026 | 20:00 | 378 | 66 | 51.1625
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 18-05-2026 | 20:00 | 378 | 66 | 51.1625
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 23-05-2026 | 23:00 | 154 | 77 | 52.9776
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 24-05-2026 | 16:00 | 159 | 60 | 52.2905
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 23-05-2026 | 23:00 | 154 | 77 | 52.9776
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 27-05-2026 | 10:00 | 169 | 40 | 23.1559
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 18-05-2026 | 11:00 | 345 | 288 | 86.4249
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 21-05-2026 | 13:00 | 348 | 230 | 80.2188
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 08-05-2026 | 20:00 | 257 | 66 | 81.6429
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 04-05-2026 | 14:00 | 254 | 113 | 85.539
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 12-05-2026 | 12:00 | 370 | 147 | 53.0843
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 15-05-2026 | 05:00 | 396 | 154 | 56.6521
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 15-05-2026 | 05:00 | 396 | 154 | 56.6521
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 20-05-2026 | 19:00 | -483 | 198 | 69.6011
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 20-05-2026 | 19:00 | -483 | 197 | 69.5507
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750 | 20-05-2026 | 19:00 | -494 | 193 | 70.7151
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 25-05-2026 | 01:00 | -371 | 73 | 72.7142
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 25-05-2026 | 01:00 | -367 | 72 | 71.9223
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 25-05-2026 | 22:00 | -201 | 60 | 64.5428
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 25-05-2026 | 22:00 | -201 | 60 | 64.5428
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 20-05-2026 | 23:00 | 177 | 49 | 35.3187
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 20-05-2026 | 23:00 | 177 | 49 | 35.3187
Koerhat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 1000 | 18-05-2026 | 15:00 | 342 | 68 | 34.8695
Koerhat 400/132kV Grid Sub-Station | ATR-4 | 400/230 | 1000 | 18-05-2026 | 15:00 | 342 | 68 | 34.8695
Koerhat 400/132kV Grid Sub-Station | ATR-2 | 400/132 | 325 |  |  |  |  | 0
Koerhat 400/132kV Grid Sub-Station | ATR-3 | 400/132 | 325 | 18-05-2026 | 23:00 | 158 | 2 | 48.6193
Mirsharai 400/230 kV Grid Sub-Station | ATR-1 | 400/230 | 1000 |  |  |  |  | 0
Mirsharai 400/230 kV Grid Sub-Station | ATR-2 | 400/230 | 1000 | 20/5/2026 | 15:00 | 183 | 96 | 20.6652
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-1 | 400/230 | 325 |  |  |  |  | 0
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-2 | 400/230 | 325 |  |  |  |  | 0
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 24-05-2026 | 15:00 | 197 | 83 | 71.257
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 24-05-2026 | 15:00 | 197 | 83 | 71.257
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 08-05-2026 | 09:00 | 195 | 99 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 08-05-2026 | 09:00 | 195 | 99 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 12-05-2026 | 13:00 | 184 | 80 | 83.2263
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 09-05-2026 | 19:00 | 200 | 134 | 80.2468
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 20-05-2026 | 08:00 | 245 | 60 | 84.08
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 11-05-2026 | 19:30 | 237 | 82 | 83.5949
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 12-05-2026 | 17:00 | 170 | 67 | 81.2118
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 06-05-2026 | 14:00 | 152 | 28 | 68.6922
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 31-05-2026 | 21:00 | 120 | 92 | 67.2038
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 31-05-2026 | 20:00 | 119 | 34 | 41.254
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 19-05-2026 | 14:00 | 128 | 34 | 44.1462
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 19-05-2026 | 14:00 | 128 | 34 | 44.1462
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 19-05-2026 | 22:00 | -124 | -1 | 55.1129
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 19-05-2026 | 22:00 | -124 | -1 | 55.1129
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 24-05-2026 | 19:00 | 149 | 47 | 69.4387
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 24-05-2026 | 19:00 | 149 | 47 | 69.4387
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 24-05-2026 | 19:00 | 200 | 66 | 70.2029
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 24-05-2026 | 19:00 | 200 | 66 | 70.2029
Naogaon 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 2026-05-01 | 00:00 | 0 | 0 | 0
Naogaon 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 2026-05-01 | 00:00 | 0 | 0 | 0
Naogaon 230/132kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 2026-05-01 | 00:00 | 0 | 0 | 0
Purbasadipur 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 11-05-2026 | 19:00 | -142 | -35 | 48.7499
Purbasadipur 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 11-05-2026 | 19:00 | -142 | -35 | 48.7499
Purbasadipur 230/132kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 15-05-2026 | 20:00 | -101 | -9 | 33.8001
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 24-05-2026 | 05:00 | 114 | 53 | 55.8746
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 24-05-2026 | 05:00 | 114 | 53 | 55.8746
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 24-05-2026 | 05:00 | 124 | 56 | 60.4706
Chowmohani 230/132 kV Grid Sub-Station | ATR-1 | 230/132 | 350 | 20-05-2026 | 04:00 | 116 | 23 | 33.7881
Chowmohani 230/132 kV Grid Sub-Station | ATR-2 | 230/132 | 350 | 20-05-2026 | 04:00 | 116 | 23 | 33.7881
Chowmohani 230/132 kV Grid Sub-Station | ATR-3 | 230/132 | 350 | 18-05-2026 | 14:00 | 108 | 22 | 31.4908
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 30-05-2026 | 23:00 | 194 | 102 | 73.0601
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 21-05-2026 | 19:00 | 239 | 93 | 85.4855
Feni 230/132 kV GIS Grid Sub-Station | ATR-1 | 230/132 | 300 | 24-05-2026 | 05:00 | 67 | 52 | 28.2705
Feni 230/132 kV GIS Grid Sub-Station | ATR-2 | 230/132 | 300 | 24-05-2026 | 05:00 | 67 | 52 | 28.2705
Feni 230/132 kV GIS Grid Sub-Station | ATR-3 | 230/132 | 300 | 17-05-2026 | 13:00 | 74 | 12 | 24.9889
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 31-05-2026 | 19:00 | 100 | 0 | 80
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 17-05-2026 | 19:00 | 97 | 0 | 77.6
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 09-05-2026 | 16:00 | 144 | 75 | 72.1603
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 09-05-2026 | 16:00 | 158 | 74 | 77.5425
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 09-05-2026 | 16:00 | 149 | 79 | 74.9545
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 20-05-2026 | 15:00 | 120 | 64 | 60.4444
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 20-05-2026 | 15:00 | 120 | 64 | 60.4444
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 20-05-2026 | 15:00 | 120 | 64 | 60.4444
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 19-05-2026 | 15:00 | 104 | 44 | 75.2832
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 01-05-2026 | 00:00 | 0 | 0 | 0
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 19-05-2026 | 15:00 | 104 | 44 | 75.2832
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 19-05-2026 | 15:00 | 104 | 44 | 75.2832
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 19-05-2026 | 22:00 | 129 | 69 | 65.0197
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 19-05-2026 | 22:00 | 129 | 69 | 65.0197
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 01-05-2026 | 00:00 | 0 | 0 | 0
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 07-05-2026 | 19:30 | -233 | -59 | 80.118
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 07-05-2026 | 19:30 | -233 | -59 | 80.118
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 09-05-2026 | 16:00 | 218 | 110 | 81.3934
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 20-05-2026 | 21:00 | 141 | 47 | 49.5424
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 20-05-2026 | 21:00 | 141 | 47 | 49.5424
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 20-05-2026 | 21:00 | 141 | 47 | 49.5424
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 23-05-2026 | 19:00 | -167 | -73 | 81.0036
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 23-05-2026 | 19:00 | -167 | -73 | 81.0036
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 15-05-2026 | 03:00 | -231 | -50 | 78.7831
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 13-05-2026 | 18:30 | 131 | 0 | 43.6667
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 13-05-2026 | 18:30 | 131 | 0 | 43.6667
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 13-05-2026 | 18:30 | 131 | 0 | 43.6667
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 13-05-2026 | 19:00 | 256 | 80 | 89.403
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 22-05-2026 | 09:00 | 245 | 92 | 87.2347
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 18-05-2026 | 19:30 | -111 | -29 | 38.2419
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 18-05-2026 | 19:30 | -111 | -29 | 38.2419
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-05-2026 | 00:00 | 0 | 0 | 0
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-05-2026 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 20-05-2026 | 13:00 | 290 | 51 | 65.4334
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 20-05-2026 | 13:00 | 290 | 51 | 65.4334
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 20-05-2026 | 13:00 | 290 | 51 | 65.4334
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 21-05-2026 | 15:00 | 236 | 131 | 89.9735
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 21-05-2026 | 15:00 | 236 | 131 | 89.9735
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 23-05-2026 | 17:00 | 173 | 94 | 65.6294
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 23-05-2026 | 15:00 | 184 | 75 | 66.2328
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 01-05-2026 | 00:00 | 0 | 0 | 0
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 2026-09-05 | 15:00 | 177 | 22 | 59.454
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 12-05-2026 | 19:00 | 251 | 105 | 90.6924
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 12-05-2026 | 19:00 | 251 | 105 | 90.6924
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 07-05-2026 | 18:30 | 215 | 33 | 96.6746
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 07-05-2026 | 18:30 | 197 | 41 | 89.4317
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 07-05-2026 | 18:30 | 197 | 41 | 89.4317
Tongi 230/132/33kV Grid Sub-Station | T-04 | 230/132 | 450 | 20-05-2026 | 11:00 | 310 | 140 | 75.5882
Bhulta 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 2026-10-05 | 0:30 | 151 | 62 | 54.411
Bhulta 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 2026-10-05 | 0:30 | 151 | 62 | 54.411
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: May-2026 |  |  |  | (For Evening Peak) | [10 empty] | Month: May-2026 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2026-05-01 | 10790.5 | 10790.5 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-01 | 9226.33 | 9226.33 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-02 | 11435.13 | 11435.13 | 0 | 20:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-02 | 10754.59 | 10754.59 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-03 | 13192.2 | 13192.2 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-03 | 11965.97 | 11965.97 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-04 | 13888.26 | 13888.26 | 0 | 19:30 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-04 | 12185.25 | 12185.25 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-05 | 14490.35 | 14620.35 | 124 | 19:30 Hr. | 15 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-05 | 13289.02 | 13289.02 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-06 | 11938 | 11938 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-06 | 13260.94 | 13291.94 | 30 | 12:00 Hr. | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | -
2026-05-07 | 14451.57 | 14634.57 | 175 | 19:30 Hr. | 40 | 10 | 0 | 105 | 0 | 20 | 0 | 0 | 0 | - | 2026-05-07 | 13171.98 | 13171.98 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-08 | 13986.97 | 13986.97 | 0 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-08 | 12165 | 13986.97 | 1821.97 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-09 | 15288 | 15414 | 121 | 19:30 Hr. | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-09 | 12601.97 | 12642.97 | 39 | 12:00 Hr. | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-10 | 14163.66 | 14210.66 | 45 | 19:30 Hr. | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-10 | 14167.08 | 14214.08 | 45 | 12:00 Hr. | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | - | 0
2026-05-11 | 14611 | 14750 | 133 | 19:30 Hr. | 9 | 16 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-11 | 13848.62 | 13879.62 | 30 | 12:00 Hr. | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-12 | 15766.53 | 15999.53 | 223 | 19:30 Hr. | 18 | 45 | 0 | 140 | 0 | 20 | 0 | 0 | 0 | - | 2026-05-12 | 13818.43 | 13818.43 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-13 | 13749.23 | 13899.23 | 144 | 19:30 Hr. | 20 | 78 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-13 | 13508.39 | 13596.17 | 84 | 12:00 Hr. | 40 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-14 | 14539 | 14560 | 187 | 19:30 Hr. | 5 | 75 | 0 | 90 | 0 | 17 | 0 | 0 | 0 | - | 2026-05-14 | 13756.92 | 13874.92 | 113 | 12:00 Hr. | 25 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-15 | 14544.5 | 14599.89 | 53 | 21:00 Hr. | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-15 | 12921.82 | 12982.82 | 58 | 12:00 Hr. | 34 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | -
2026-05-16 | 16412.2 | 16620.2 | 199 | 21:00 Hr. | 0 | 29 | 0 | 140 | 0 | 30 | 0 | 0 | 0 | - | 2026-05-16 | 13333.91 | 13373.91 | 38 | 12:00 Hr. | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-17 | 16200.93 | 16479.93 | 267 | 21:00 Hr. | 20 | 60 | 0 | 132 | 0 | 55 | 0 | 0 | 0 | - | 2026-05-17 | 13852.34 | 13946.34 | 90 | 12:00 Hr. | 15 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-18 | 14670.82 | 14974.82 | 291 | 19:00 Hr. | 30 | 100 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-18 | 13590.47 | 13684.47 | 90 | 12:00 Hr. | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-19 | 16676 | 16995 | 305 | 20:00 Hr. | 33 | 10 | 16 | 197 | 0 | 49 | 0 | 0 | 0 | - | 2026-05-19 | 14381.46 | 14433.71 | 50 | 12:00 Hr. | 10 | 15 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | -
2026-05-20 | 17200.79 | 17610.79 | 392 | 21:00 Hr. | 70 | 0 | 40 | 220 | 0 | 62 | 0 | 0 | 0 | - | 2026-05-20 | 15418.78 | 15733.78 | 301 | 12:00 Hr. | 180 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | -
2026-05-21 | 16531.26 | 17235.26 | 674 | 21:00 Hr. | 136 | 14 | 106 | 304 | 44 | 70 | 0 | 0 | 0 | - | 2026-05-21 | 13890.88 | 14341.88 | 432 | 12:00 Hr. | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-22 | 15768 | 16080 | 299 | 21:00 Hr. | 53 | 13 | 29 | 167 | 0 | 37 | 0 | 0 | 0 | - | 2026-05-22 | 13078.51 | 13140.51 | 59 | 09:00 Hr. | 0 | 51 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | -
2026-05-23 | 16446.41 | 16957.41 | 489 | 19:30 Hr. | 213 | 37 | 27 | 200 | 0 | 6 | 6 | 0 | 0 | - | 2026-05-23 | 14442.69 | 14911.69 | 449 | 12:00 Hr. | 334 | 0 | 37 | 64 | 0 | 12 | 2 | 0 | 0 | -
2026-05-24 | 14501.86 | 14701.86 | 191 | 21:00 Hr. | 68 | 0 | 21 | 102 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-24 | 14325.43 | 14666.1 | 326 | 12:00 Hr. | 290 | 0 | 0 | 12 | 0 | 24 | 0 | 0 | 0 | -
2026-05-25 | 13587 | 13615 | 27 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | - | 2026-05-25 | 11346.2 | 11416.22 | 67 | 10:00 Hr. | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | -
2026-05-26 | 11164.63 | 11169.63 | 5 | 21:00 Hr. | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-26 | 9169.2 | 9169.2 | 0 | 09:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-27 | 9968 | 9968 | 0 | 20:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-27 | 6576.89 | 6576.89 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-28 | 12364.7 | 12379.7 | 14 | 21:00 Hr. | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-28 | 7819.3 | 7819.3 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-29 | 10776.11 | 10781.11 | 5 | 21:00 Hr. | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-29 | 11107 | 11107 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-05-30 | 13659.5 | 13672.5 | 12 | 21:00 Hr. | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2026-05-30 | 10488.98 | 10540.98 | 50 | 12:00 Hr. | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | -
2026-05-31 | 14206.5 | 14255.5 | 47 | 21:00 Hr. | 0 | 0 | 3 | 33 | 11 | 0 | 0 | 0 | 0 | - | 2026-05-31 | 11716.03 | 11716.03 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
[16 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: May 2026
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 17200.79 | 2026-05-20 | 21:00 Hr.
2 | Maximum Day Peak Genaration | MW | 15418.78 | 2026-05-20 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 17610.79 | 2026-05-20 | 21:00 Hr.
4 | Minimum Generation | MW | 5755.52 | 2026-05-27 | 09:00 Hr.
5 | Average of the daily evening peak Genaration | MW | 14127.9116 | - | -
6 | Average of the daily day peak Genaration | MW | 12425.1735 | - | -
7 | Maximum load shed (Evening Peak) | MW | 674 | 2026-05-21 | 21:00 Hr.
8 | Minimum load shed | MW | 5 | 2026-05-26 | 21:00 Hr.
9 | Total nos. of load shed days | Day | 24 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 145.8333 | - | -
11 | Total Generation | MkWh | 9417.8731 | - | -
12 | Total Generation by BPDB | MkWh | 932.8558 | % of total Gen. | 9.905%
13 | Total Generation by IPP | MkWh | 2521.7942 | '' | 26.78%
14 | A) Total Generation by Generation Companies | MkWh | 4303.233 | '' | 45.69%
| B) Total Generation by REB | MkWh | 45.2413 | " | 0.4804%
| C) Total Generation by RENTAL | MkWh | 85.8564 | " | 0.9116%
| D) Total Imported from India (BIPTC) | MkWh | 633.2531 | " | 6.724%
| E) Total Imported from Tripura, India (A.C) | MkWh | 95.9553 | " | 1.019%
| F) Total Imported from Nepal | MkWh | 0 | " | 0%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 799.684 | " | 8.491%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3935.5908 | % of total Gen. | 41.79%
| B) Oil | MkWh | 619.18 | '' | 6.575%
| C) Hydro | MkWh | 37.396 | '' | 0.3971%
| D) Solar | MkWh | 123.8147 | '' | 1.315%
| E) Coal | MkWh | 3166.1036 | '' | 33.62%
| F) BIPTC (Import from India) | MkWh | 633.2531 | '' | 6.724%
| G) A.C (Import from Tripura, India) | MkWh | 95.9553 | '' | 1.019%
| H) Total Imported from Nepal | MkWh | 0 | '' | 0%
| I) Adani (Import from India) | MkWh | 799.684 | '' | 8.491%
| J) Wind | MkWh | 6.8957 | '' | 0.07322%
16 | Maximun of the daily total Generation . | MkWh | 372.2378 | 2026-05-20
17 | Monthly Load factor | % | 73.5922 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 56048.6103 | - | -
| A) Gas | M.Taka | 13817.5675 | - | -
| B) Coal | M.Taka | 20904.431 | - | -
| C) HFO | M.Taka | 10411.8858 | - | -
| D) HSD | M.Taka | 106.3524 | - | -
| E) Hydro | M.Taka | 3.7396 | - | -
| F) Solar | M.Taka | 1984.6698 | - | -
| G) Total Import | M.Taka | 8718.5289 | - | -
| H) Wind | M.Taka | 101.4353 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2600.8642 | 2026-05-20
| A) Gas | M.Taka | 568.4088 | 2026-05-31
| B) Coal | M.Taka | 1095.4428 | 2026-05-26
| C) HFO | M.Taka | 858.7715 | 2026-05-20
| D) HSD | M.Taka | 31.9972 | 2026-05-21 | -
| E) Hydro | M.Taka | 0.19265 | 2026-05-12 | -
| F) Solar | M.Taka | 86.8043 | 2026-05-09 | -
| G) Total Import | M.Taka | 349.1334 | 2026-05-20
| H) Wind | M.Taka | 9.984 | 2026-05-03
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.9513
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.0595
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 76.2 | 31/5/2026 | 06:00
b) | Actual | FT (MSL) | 76.15 | 31/5/2026 | 06:00
22 | Peak Genaration of May 2025 | MW | 16603 | 2025-05-10 | 21:00 Hr.
23 | Peak Demand of May 2025 | MW | 16999.06 | 2025-05-10 | 21:00 Hr.
24 | Maximum peak Generation recorded upto 31/05/2026 | MW | 17200.79 | 2026-05-20 | 21:00 Hr.
25 | Maximum peak Demand recorded upto 31/05/2026 | MW | 17610.79 | 2026-05-20 | 21:00 Hr.
26 | Maximum load shed recorded upto 31/05/2026 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [66 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Fuel | Installed capacity (MW) | Capability Status of Last Week | 28.05.2026 | 21.05.2026 | 14.05.2026 | 07.05.2026 | 30.04.2026 | 23.04.2026 | 16.04.2026 | 09.04.2026 | 02.04.2026 | 26.03.2026 | 19.03.2026 | 12.03.2026 | 05.03.2026 | 26.02.2026 | 19.02.2026 | 12.02.2026 | 05.02.2026 | 29.01.2026 | 22.01.2026 | 15.01.2026 | 08.01.2026 | 01.01.2026 | 25.12.2025 | 18.12.2025 | 11.12.2025 | 04.12.2025 | 27.11.2025 | 20.11.2025 | 13.11.2025 | 06.11.2025 | 30.10.2025 | 23.10.2025 | 16.10.2025 | 09.10.2025 | 02.10.2025 | 25.09.2025 | 18.09.2025 | 11.09.2025 | 04.09.2025 | 28.08.2025 | 21.08.2025 | 14.08.2025 | 07.08.2025 | 31.07.2025 | 24.07.2025 | 17.07.2025 | 10.07.2025 | 03.07.2025 | 26.06.2025 | 19.06.2025 | 12.06.2025 | 05.06.2025 | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | Capable | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | Capable | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | Capable | [41 empty] | 20 | 20 | [7 empty] | 20 | [41 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 | Capable | [22 empty] | 20 | 20 | [18 empty] | 20 | [5 empty] | 20 | 20 | 20 | 20 | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | Capable | [32 empty] | 7 | 7 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | Capable | [12 empty] | 30 | 30 | 30 | 30 | 30 | [56 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | Capable | 20 | 20 | 20 | [5 empty] | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410 | Capable | [42 empty] | 45 | [47 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 | Capable | [5 empty] | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97 | Capable |  | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [24 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163 | Capable
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210 | Capable
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225 | Capable
14 | Shikalbaha Peaking GT | BPDB | Gas | 150 | Capable
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330 | Capable | [66 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 | Capable | [8 empty] | 20 | 20 | 20 | [52 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104 | Capable | [5 empty] | 2 | 2 | 2 | [32 empty] | 2 |  |  | 2 | 2 | [18 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
18 | Bhola 225 MW CCPP | BPDB | Gas | 194 | Capable | [45 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365 | Capable
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | Capable | [14 empty] | 16 | 16 |  |  | 20 | 20 | 20 | 20 |  |  | 20 | 20 | 20 |  |  |  | 20 | [10 empty] | 20 | 16 | [7 empty] | 20 | 20 | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | Capable |  | 30 | 30 | 30 | [47 empty] | 30 | 30 | 30 | 30 |  | 30 | 30
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | Capable | [6 empty] | 30 | 30 | 30 | 30 | 30 | 35 | 35 | 35 | 35 | [11 empty] | 30 | 30 | 30 | 30 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231 | Capable
24 | RPCL 210 MW CCPP | IPP | Gas | 210 | Capable but not tested recently
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100 | Not Capable but feasible
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50 | Not Capable but feasible
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410 | Not Capable but feasible
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400 | Capable | [71 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274 | Not Capable but feasible
16 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | Capable | 30 | 30 | 30 | [5 empty] | 20 | 20 | 20 | 30 | 30 | 30 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 60 |  |  |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [7 empty] | 20 | 20
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | Capable | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 16 | 16 | 30 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
32 | Bhola Nutan Bidyut | IPP | Gas | 220 | Capable
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360 | Not Capable but feasible
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450 | Not Capable but feasible
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150 | Capable | [40 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30
36 | Anwara 300 MW PP (United) | IPP | HFO | 300 | Capable
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | Capable
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104 | Capable
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105 | Capable
40 | Gazipur 100 MW PP | IPP | HFO | 105 | Capable
41 | United Payra Power Ltd. | IPP | HFO | 150 | Capable
42 | Madhumati 100 MW PP | IPP | HFO | 100 | Capable
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | Capable
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | Capable
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300 | Capable
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55 | Capable
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | HFO | 149 | Capable
48 | Feni Lanka Power | IPP | HFO | 114 | Capable
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110 | Capable
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | Capable
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55 | Capable
52 | Zodiac 54 MW | IPP | HFO | 54 | Capable
53 | Anlima Energy Ltd | IPP | HFO | 116 | Capable
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115 | Capable
55 | Confidence Unit-2 Bogura | IPP | HFO | 113 | Capable
56 | Confidence Unit-1 Bogura | IPP | HFO | 113 | Capable
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | Capable
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55 | Capable
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149 | Capable
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | Capable
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55 | Capable
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | Capable | 16.5 | 33 | 33 | 33 | 33 | 33 |  | 40 | 20 | 20 | 40 | 66 | 66 | 66 | 66 |  | 66 | 33 | 66 | 66 | 66 | 66 | 66 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | Capable | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 66 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  | 50 | 50 | 50 | 50 | 20 | 20 | 40 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | Capable | 15 | 15 | 30 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 50 | 50 | 50 | 50 | 25 | 40 | 25 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 50 | 50 | 50 | 50
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | Capable | 20 | 20 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 25 | 30 | 30 | 30 | 30 | [11 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
66 | Unique Meghnaghat Power Ltd(UMPL) | IPP | Gas | 584 | Capable | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 |  | 30 | [12 empty] | 24 | 24 | 24 |  |  |  |  | 50 | 24 | 24 | 50
67 | Meghnaghat CCPP Unit 2 (Summit) | IPP | Gas | 583 | Capable | [9 empty] | 25 | 25 | 50 | 50 | 50 | 50 |  |  |  | 50 | 50 | 50 | 50 | 50 | 50
68 | Jera Meghnaghat Power Ltd. | IPP | Gas | 718 | Capable | 20 | 20 | 20 | 20 | [11 empty] | 50 | 70
| Payra 1320 MW Unit-2 | BCPCL |  | 622 | Capable | [55 empty] | 20 | 20
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70 | Capable
| Shajibazar 100 MW PP | BPDB |  | 100 | Not Capable but feasible
| Khulna 225 MW CCPP | NWPGCL |  | 230 | Capable but not tested recently
Total Installed capacity | [5 empty] | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 20506 | 20506 | 20506 | 20506 | 20506 | 20506 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19739 | 19739 | 19739 | 19739 | 14388 | 14388 | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity | [5 empty] | 4864 | 6567 | 6861 | 6051 | 4051 | 4051 | 4246 | 4752 | 5680 | 6978 | 8164 | 7834 | 8174 | 8174 | 7698 | 7298 | 6286 | 4146 | 5722 | 6660 | 6754 | 7086 | 6756 | 5564 | 5851 | 5937 | 5232 | 5185 | 3503 | 3503 | 6403 | 6525 | 5821 | 6221 | 6871 | 7523 | 8031 | 7313 | 7523 | 6939 | 8121 | 8527 | 9061 | 8099 | 8099 | 7580 | 8537 | 6163 | 6795 | 6632 | 2862 | 3135 | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve | [5 empty] | 232.5 | 291 | 286 | 236 | 186 | 186 | 198 | 238 | 304 | 349 | 394 | 489 | 519 | 519 | 490 | 455 | 419 | 256 | 359 | 399 | 429 | 443 | 398 | 365 | 358 | 358 | 328 | 324 | 228 | 228 | 351 | 372 | 349 | 379 | 427 | 477 | 471 | 451 | 477 | 427 | 459 | 452 | 503 | 386 | 404 | 382 | 452 | 356 | 424 | 408 | 262 | 288 | 218 | 193 | 193 | 202 | 232 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO | [5 empty] | 11 | 13 | 12 | 10 | 8 | 8 | 9 | 10 | 14 | 15 | 15 | 14 |  |  | 15 | 14 | 12 | 10 | 11 | 12 | 12 | 11 | 10 | 10 | 9 | 9 | 9 | 9 | 7 | 7 | 9 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 12 | 14 | 13 | 15 | 12 | 12 | 12 | 13 | 11 | 14 | 13 | 11 | 12 | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list | [5 empty] | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 68 | 68 | 68 | 68 | 64 | 64 | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list | [5 empty] | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 74 | 74 | 74 | 74 | 70 | 70 | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable | [5 empty] | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 63 | 63 | 61 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 58 | 58 | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible | [5 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: May 2026
SL | Plant Name | Owner | Fuel | Installed capacity | FGMO Status
|  |  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | √ | √ | √ | √ | √ |  | √ | √ |  | √ | √ |  | √ | √ | √ | √ | √ | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | √ | √ | √ | √ | [25 empty] | √
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 |  |  | √ | [26 empty] | √
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | √ | √ | √ | √ | √ |  |  | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ | √ | √ | √ | [5 empty] | √
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410
9 | Haripur 412 MW CCPP | EGCB | Gas | 412
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225
14 | Shikalbaha Peaking GT | BPDB | Gas | 150
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104
18 | Bhola 225 MW CCPP | BPDB | Gas | 194
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | [10 empty] | √ |  |  | √ |  |  |  | √
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231
24 | RPCL 210 MW CCPP | IPP | Gas | 210
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ | √ | √ | [5 empty] | √
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | √ | √ | √ | √ | √ | √ |  | √ |  | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  |  | √ | √ | √
32 | Bhola Nutan Bidyut | IPP | Gas | 220
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150
36 | Anwara 300 MW PP (United) | IPP | HFO | 300
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | [10 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105
40 | Gazipur 100 MW PP | IPP | HFO | 105
41 | United Payra Power Ltd. | IPP | HFO | 150
42 | Madhumati 100 MW PP | IPP | HFO | 100 | [21 empty] | √ | √ | √ | √ | √ | √ | √ | √
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | [10 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | [5 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55
47 | Kodda 150 MW PP BRPL | IPP | HFO | 149
48 | Feni Lanka Power | IPP | HFO | 114 | [18 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55
52 | Jodiac Power | IPP | HFO | 54
53 | Anlima Energy Ltd | IPP | HFO | 116 | [10 empty] | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115
55 | Confidence Unit-2 Bogura | IPP | HFO | 113
56 | Confidence Unit-1 Bogura | IPP | HFO | 113
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | √ | √ | √ | [8 empty] | √
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | [10 empty] | √ | √ | √ | [9 empty] | √
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | √ |  | √ |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | [10 empty] | √
66 | Unique Meghnaghat Power Limited (UMPL) | IPP | Gas | 584 | [9 empty] | √ | [19 empty] | √
67 | Meghnaghat CCPP(Summit)-2 | IPP | Gas/HSD | 583
| JERA Meghnaghat Power Limited | IPP | Gas | 718
| United Payra Power Ltd. | IPP |  | 150
| Mirsharai 150 MW | IPP | HFO/Gas | 150 | [10 empty] | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
Jangalia 52 MW PP (Lakdanavi)
| Ashuganj 420 MW CCPP(East) | APSCL |  | 400 |  |  |  |  | √ | [24 empty] | √
| Ashuganj 55 MW PP (Precision) | QRPP |  | 55
| Bagura 113 MW PP (Confidence)-2 | IPP |  | 113
| Energypac Power Venture Thakurgaon Ltd. | IPP |  | 115
| Chandpur 150 MW CCPP | BPDB |  | 163
| Khulna 225 MW CCPP | NWPGCL |  | 230
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70
| Shajibazar 100 MW PP | BPDB |  | 100
| Payra 1320 MW Unit-1 | BCPCL |  | 622