## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 30-06-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-06-2026 | during | 30-06-2026 | during | 30-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 398 | 383 | 412 | 412 | 380 | 380 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 30 | 15 | 55 | 55 | 30 | 30 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 328 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 110 | 146 | 149.36 | 149.36 | 15 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17.5 | 18 | 33 | 33 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 42 | 52.19 | 52.19 | 8 | 24 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 172 | 195 | 300 | 300 | 146 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 55 | 132 | 149 | 149 | 70 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 88 | 105 | 105 | 35 | 70 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 22 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 510 | 500 | 584 | 584 | 526 | 526 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 495 | 539 | 583 | 583 | 525 | 525 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2602.5 | 2833 | 5817.22 | 5792.22 | 2331 | 2737
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 2 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 6 | 50 | 50 | 6 | 19 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 87 | 107 | 91 | 91 | 91 | 91 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 0 | 105 | 105 | 17 | 17 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 8 | 8 | 40 | 56 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 33 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 8 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 25 | 70 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.83 | 0 | 2.25 | 0 | 2.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 35 | 54.36 | 54.36 | 0 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 68 | 89 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1224 | 1224 | 1224 | 1200 | 1200
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 15 | 9 | 18 | 9 | 18 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1135 | 1135 | 1150 | 1150 | 1135 | 1135 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2758.83 | 3021.5 | 3789.11 | 3854.86 | 2901.25 | 3092
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 214 | 167 | 221.25 | 221.25 | 205.25 | 205.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 320 | 350.01 | 350.01 | 350.01 | 350.01
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 260 | 250 | 342.01 | 342.01 | 250 | 250 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 350 | 270 | 393 | 393 | 240 | 240 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 10 | 40 | 41.65 | 41.65 | 10 | 10 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 46 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 130 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 139 | 138 | 163 | 163 | 140 | 140 | Low gas pressure
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 103 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 140 | 156 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 114 | 114 | 17 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 18 | 27 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 90 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 26 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1588 | 1824 | 2712.44 | 2656.44 | 1605.26 | 1875.26
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-06-2026 | during | 30-06-2026 | during | 30-06-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 0.4 | 0 | 18 | 0 | 18 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 106 | 70 | 90 | 70 | 90 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 78 | 60 | 80 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 31.22 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 127.62 | 184 | 484.6 | 456.5 | 198.1 | 177
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 29 | 29 | 28 | 28 | 28 | 28 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 150 | 151 | 163 | 163 | 163 | 163 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 143 | 142 | 145 | 145 | 145 | 145 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 22 | 30 | 0 | 0 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 83 | 83 | 83 | 52 | 52 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 100 | 102 | 102 | 102 | 102 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 325 | 341 | 341 | 315 | 315 | Machine Problem
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 308 | 294 | 320 | 320 | 300 | 300 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1148 | 1171 | 1227 | 1227 | 1152 | 1152
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 892 | 892 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 21 | 0 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 45 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 400 | 488 | 520 | 520 | 900 | 900 | machine problem
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1396 | 1433 | 2865 | 2790 | 2638 | 2563
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 936 | 1050 | 1050 | 1050 | 1050 | 1050 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 48 | 48 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 65 | 64 | 65 | 65 | 65 | 65 | GT-1 & ST under maint
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1100 | 1140 | 1244 | 1244 | 1200 | 1200 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 240 | 307 | 307 | 307 | 287 | 287 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.18 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2561.18 | 2832 | 3147 | 3146 | 2888 | 2887
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 30.64 | 0 | 55 | 0 | 55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 32 | 32 | 0 | 10 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 188 | 171 | 214 | 214 | 170 | 170 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 160 | 160 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 177 | 130 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 371 | 404 | 413.79 | 413.79 | 400 | 400 | AGC+Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 18 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 103 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 0.8 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1389.64 | 1427.64 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 7.21 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 68 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2232.29 | 2403.64 | 3248.72 | 3027.12 | 2508.73 | 2459.13
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 37 | 39 | 35 | 35 | 37 | 37 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 202 | 180 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 66 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.3 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 95 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 8 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 4 | 0 | 63.94 | 0 | 63.94 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 255.3 | 380 | 559.94 | 463 | 428.94 | 367
System Total |  |  |  |  | 28843.2 | 29323.517 | 14669.72 | 16082.14 | 23851.03 | 23413.14 | 16651.28 | 17309.39
Forecast Scenario (30-06-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15040 |  | 2731.3 |  | 17900
|  |  |  | 1:00 | 14430 |  | 2845.9 |  | 17410
|  |  |  | 2:00 | 14200 |  | 2950.95 |  | 17290
|  |  |  | 3:00 | 14070 |  | 2989.15 |  | 17200
|  |  |  | 4:00 | 14230 |  | 2759.95 |  | 17120
|  |  |  | 5:00 | 14220 |  | 2607.15 |  | 16950
|  |  |  | 6:00 | 13790 |  | 2845.9 |  | 16770
|  |  |  | 7:00 | 13580 |  | 2912.75 |  | 16630
|  |  |  | 8:00 | 13730 |  | 2712.2 |  | 16570
|  |  |  | 9:00 | 13960 |  | 2807.7 |  | 16900
|  |  |  | 10:00 | 14120 |  | 2721.75 |  | 16970
|  |  |  | 11:00 | 14260 |  | 1804.95 |  | 16150
|  |  |  | 12:00 | 14670 |  | 2349.3 |  | 17130
|  |  |  | 13:00 | 14500 |  | 2292 |  | 16900
|  |  |  | 14:00 | 14370 |  | 2607.15 |  | 17100
|  |  |  | 15:00 | 14100 |  | 3332.95 |  | 17590
|  |  |  | 16:00 | 14460 |  | 2473.45 |  | 17050
|  |  |  | 17:00 | 14270 |  | 2463.9 |  | 16850
|  |  |  | 18:00 | 14220 |  | 2034.15 |  | 16350
|  |  |  | 18:30 | 15090 |  | 1824.05 |  | 17000
|  |  |  | 19:00 | 15660 |  | 1919.55 |  | 17670
|  |  |  | 19:30 | 16080 |  | 1728.55 |  | 17890
|  |  |  | 20:00 | 15880 |  | 1766.75 |  | 17730
|  |  |  | 21:00 | 15920 |  | 2320.65 |  | 18350
|  |  |  | 22:00 | 15820 |  | 1824.05 |  | 17730
|  |  |  | 23:00 | 15900 |  | 1843.15 |  | 17830
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 17130.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2321
Probable Maximum Demand at Evening Peak: |  |  | 18350.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16080.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 349.40 MKWHr. |  | 450 | 250 | 221 | 350 | 100 | 400 | 100 | 250 | 200 | 2321
*** This report is generated digitally from Operation Information System (OIS) at 08:39 hrs on 30-06-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 29-06-2026 | [28 empty] | Date: | 29-06-2026 | [28 empty] | Date: | 29-06-2026 | [28 empty] | Date: | 29-06-2026 | [28 empty] | Date: | 29-06-2026 | [18 empty] | Date: | 29-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 54 | 16 | 195 | 30 | 35 | 35 | 0 | 0 | 0 | 560 | 0 | 0 | 310 | 0 | 0 | 0 | 142 | 19 | 21 | 0 | 545 | 106 | 16 | 43 | 0 | 19 | 33 | 8 | 35 | 12 | 12 | 0 | 89 | 0 | 26 | 1135 | 0 | 0 | 6 | 8 | 17 | 220 | 0 | 0 | 0 | 1025 | 0 | 58 | 0 | 240 | 290 | 230 | 51 | 0 | 213 | 10 | 69 | 138 | 36 | 0 | 19 | 16 | 176 | 0 | 0 | 0 | 315 | 0 | 295 | 29 | 0 | 152 | 0 | 17 | 0 | 52 | 28 | 142 | 0 | 101 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 8024 | 703 | 0 | 0 | 0 | 26 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 0 | 0 | 1472.92 | 0 | 32 | 0 | 35 | 35 | 0 | 93 | 23 | 0 | 0 | 0 | 22 | 0 | 0 | 175 | 0 | 0 | 0 | 173 | 0 | 398 | 0 | 0 | 180 | 36 | 95 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 64 | 220 | 0 | 1050 | 1202 | 17 | 7012.92 | 15036.92 | 76.41
01:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 34 | 16 | 155 | 30 | 35 | 35 | 0 | 0 | 0 | 535 | 0 | 0 | 296 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 510 | 107 | 16 | 27 | 0 | 19 | 33 | 8 | 18 | 12 | 12 | 0 | 85 | 0 | 26 | 1135 | 0 | 0 | 6 | 8 | 17 | 220 | 0 | 0 | 0 | 788 | 0 | 20 | 0 | 240 | 290 | 230 | 51 | 0 | 215 | 10 | 54 | 138 | 20 | 0 | 19 | 34 | 164 | 0 | 0 | 0 | 310 | 0 | 301 | 28 | 0 | 151 | 0 | 17 | 0 | 52 | 30 | 143 | 0 | 101 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7556 | 703 | 0 | 0 | 0 | 21 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 0 | 0 | 1494.56 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 22 | 0 | 0 | 0 | 22 | 0 | 0 | 175 | 0 | 0 | 0 | 173 | 0 | 397 | 0 | 0 | 181 | 37 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 64 | 220 | 0 | 1050 | 1190 | 17 | 6876.56 | 14432.56 | 76.41
02:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 34 | 16 | 145 | 30 | 35 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 305 | 0 | 0 | 0 | 142 | 20 | 21 | 0 | 540 | 106 | 16 | 25 | 0 | 12 | 33 | 8 | 18 | 12 | 12 | 0 | 85 | 0 | 26 | 1135 | 0 | 0 | 6 | 8 | 17 | 220 | 0 | 0 | 0 | 720 | 0 | 20 | 0 | 240 | 290 | 230 | 51 | 0 | 215 | 10 | 0 | 138 | 16 | 0 | 19 | 34 | 160 | 0 | 0 | 0 | 305 | 0 | 320 | 28 | 0 | 152 | 0 | 17 | 0 | 52 | 30 | 143 | 0 | 101 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7341 | 703 | 0 | 0 | 0 | 21 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 0 | 0 | 1487.59 | 0 | 32 | 0 | 35 | 35 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 173 | 0 | 405 | 0 | 0 | 180 | 38 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 64 | 220 | 0 | 1050 | 1190 | 17 | 6851.59 | 14192.59 | 76.4
03:00 | 0 | 40 | 25 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 34 | 16 | 145 | 30 | 0 | 0 | 0 | 0 | 0 | 485 | 0 | 0 | 302 | 0 | 0 | 0 | 105 | 20 | 21 | 0 | 435 | 107 | 16 | 25 | 0 | 24 | 0 | 8 | 18 | 12 | 12 | 0 | 85 | 0 | 26 | 1135 | 0 | 0 | 6 | 8 | 17 | 220 | 0 | 0 | 0 | 722 | 0 | 20 | 0 | 240 | 290 | 230 | 51 | 0 | 215 | 10 | 0 | 138 | 16 | 0 | 19 | 34 | 156 | 0 | 0 | 0 | 305 | 0 | 320 | 28 | 0 | 146 | 0 | 17 | 0 | 52 | 30 | 143 | 0 | 101 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7123 | 797 | 0 | 0 | 0 | 21 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 0 | 0 | 1480.36 | 0 | 32 | 0 | 50 | 50 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 175 | 0 | 380 | 0 | 0 | 180 | 37 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 65 | 220 | 0 | 1050 | 1190 | 17 | 6945.36 | 14068.36 | 76.4
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 34 | 16 | 145 | 30 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 314 | 0 | 0 | 0 | 105 | 20 | 21 | 0 | 525 | 106 | 16 | 24 | 0 | 19 | 0 | 8 | 18 | 12 | 12 | 0 | 85 | 0 | 26 | 1135 | 0 | 0 | 6 | 0 | 17 | 220 | 0 | 0 | 0 | 720 | 0 | 20 | 0 | 240 | 290 | 230 | 51 | 0 | 216 | 10 | 0 | 139 | 16 | 0 | 19 | 34 | 152 | 0 | 0 | 0 | 310 | 0 | 320 | 28 | 0 | 147 | 0 | 17 | 0 | 52 | 30 | 143 | 0 | 101 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7183 | 891 | 0 | 0 | 0 | 17 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 0 | 0 | 1480.24 | 0 | 32 | 0 | 50 | 50 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 177 | 0 | 389 | 0 | 0 | 180 | 37 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 65 | 220 | 0 | 1050 | 1190 | 17 | 7046.24 | 14229.24 | 76.4
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 34 | 16 | 145 | 30 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 0 | 308 | 0 | 0 | 0 | 105 | 20 | 21 | 0 | 505 | 107 | 16 | 24 | 0 | 13 | 0 | 8 | 18 | 12 | 12 | 0 | 85 | 0 | 28 | 1135 | 0 | 0 | 6 | 0 | 17 | 220 | 0 | 0 | 0 | 720 | 0 | 20 | 0 | 240 | 290 | 230 | 51 | 0 | 218 | 10 | 0 | 140 | 16 | 0 | 19 | 17 | 148 | 0 | 0 | 0 | 305 | 0 | 320 | 28 | 0 | 152 | 0 | 17 | 0 | 52 | 30 | 144 | 0 | 101 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7149 | 891 | 0 | 0 | 0 | 17 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 0 | 0 | 1497.52 | 0 | 32 | 0 | 50 | 50 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 177 | 0 | 389 | 0 | 0 | 180 | 37 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 65 | 220 | 0 | 1050 | 1190 | 17 | 7064.52 | 14213.52 | 76.4
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 34 | 16 | 145 | 30 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 298 | 0 | 0 | 1 | 105 | 20 | 21 | 0 | 380 | 107 | 16 | 25 | 0 | 19 | 0 | 8 | 0 | 12 | 12 | 0.27 | 87 | 0 | 29 | 1135 | 0 | 0 | 6 | 0 | 17 | 220 | 0 | 0 | 0 | 726 | 0 | 20 | 0 | 240 | 290 | 230 | 51 | 0 | 216 | 10 | 0 | 140 | 16 | 0 | 19 | 17 | 128 | 0 | 1 | 0 | 310 | 0 | 330 | 28 | 0 | 133 | 1 | 17 | 0 | 52 | 30 | 141 | 0 | 102 | 0 | 48 | 1.1 | 48 | 0 | 0.1 | 1.73 | 0 | 6912.2 | 891 | 0 | 0 | 0 | 16 | 38 | 0 | 0 | 0 | 0 | 0 | 2.38 | 520 | 0 | 0 | 0 | 1485.26 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0.95 | 4 | 0 | 0 | 1.67 | 178 | 0 | 0 | 0 | 176 | 0 | 350 | 0 | 0.19 | 180 | 36 | 95 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.03 | 48 | 307 | 65 | 220 | 0 | 1003 | 1190 | 17 | 6874.68 | 13786.88 | 76.39
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 34 | 16 | 145 | 26 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 310 | 0 | 0 | 6 | 105 | 20 | 21 | 0 | 430 | 106 | 16 | 25 | 0 | 13 | 0 | 8 | 0 | 12 | 12 | 0.75 | 87 | 0 | 29 | 1070 | 0 | 0 | 6 | 0 | 17 | 219 | 0 | 0 | 0 | 720 | 5 | 20 | 0 | 220 | 290 | 230 | 51 | 0 | 216 | 10 | 0 | 139 | 16 | 0 | 19 | 17 | 138 | 0 | 1 | 0 | 305 | 0 | 331 | 28 | 0 | 132 | 2 | 17 | 0 | 52 | 30 | 143 | 0 | 101 | 0 | 48 | 2 | 48 | 0 | 0.1 | 6.56 | 0 | 6749.41 | 892 | 0 | 0 | 0 | 16 | 38 | 0 | 0 | 0 | 0 | 0 | 16.91 | 515 | 0 | 0 | 0 | 1494.17 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 6.71 | 15 | 0 | 0 | 4.67 | 178 | 0 | 0 | 0 | 176 | 0 | 356 | 0 | 0.62 | 180 | 36 | 95 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.04 | 48 | 276 | 65 | 180 | 0 | 982 | 1190 | 17 | 6828.32 | 13577.73 | 76.39
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 45 | 145 | 30 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 306 | 0 | 0 | 4 | 105 | 19 | 21 | 0 | 420 | 106 | 16 | 24 | 0 | 22 | 0 | 8 | 0 | 12 | 12 | 2.14 | 89 | 0 | 7 | 1070 | 0 | 0 | 6 | 0 | 17 | 217 | 0 | 0 | 0 | 723 | 10 | 20 | 0 | 220 | 290 | 230 | 51 | 0 | 216 | 10 | 0 | 139 | 17 | 0 | 19 | 17 | 140 | 0 | 1 | 0 | 310 | 0 | 331 | 29 | 0 | 136 | 2 | 17 | 0 | 52 | 25 | 143 | 0 | 101 | 0 | 48 | 3.8 | 48 | 0 | 0.3 | 7.91 | 0 | 6859.15 | 892 | 0 | 0 | 0 | 17 | 38 | 0 | 0 | 0 | 0 | 0 | 36.11 | 470 | 0 | 0 | 0 | 1491.06 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 12.29 | 17 | 0 | 0 | 9.18 | 179 | 0 | 0 | 0 | 176 | 0 | 362 | 0 | 1.31 | 181 | 37 | 95 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0.02 | 48 | 275 | 65 | 220 | 0 | 994 | 1190 | 17 | 6873.37 | 13732.52 | 76.39
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 34 | 85 | 145 | 30 | 0 | 17 | 0 | 0 | 0 | 420 | 0 | 0 | 306 | 0 | 0 | 12 | 124 | 18 | 21 | 0 | 450 | 106 | 16 | 25 | 0 | 21 | 0 | 8 | 0 | 12 | 12 | 2.65 | 89 | 0 | 2 | 1135 | 0 | 0 | 6 | 0 | 17 | 216 | 0 | 0 | 0 | 720 | 12 | 20 | 0 | 220 | 290 | 230 | 51 | 0 | 196 | 0 | 0 | 138 | 17 | 0 | 19 | 17 | 146 | 0 | 0 | 0 | 315 | 0 | 332 | 29 | 0 | 143 | 3 | 17 | 0 | 52 | 25 | 143 | 0 | 101 | 0 | 48 | 3.6 | 48 | 0 | 0.3 | 17.76 | 0 | 7068.31 | 892 | 0 | 0 | 0 | 21 | 38 | 0 | 0 | 0 | 0 | 0 | 44.74 | 470 | 0 | 0 | 0 | 1473.1 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 24.06 | 29 | 0 | 0 | 8.7 | 187 | 0 | 0 | 0 | 176 | 0 | 355 | 0 | 0.64 | 200 | 37 | 95 | 1 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0.03 | 16 | 278 | 65 | 220 | 0 | 1012 | 1180 | 17 | 6891.87 | 13960.18 | 76.38
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 34 | 110 | 145 | 30 | 17 | 17 | 0 | 0 | 0 | 445 | 0 | 0 | 306 | 0 | 0 | 8 | 142 | 18 | 21 | 0 | 400 | 106 | 16 | 24 | 0 | 17 | 0 | 8 | 0 | 12 | 12 | 1.5 | 89 | 0 | 2 | 1135 | 0 | 0 | 6 | 0 | 17 | 214 | 0 | 0 | 0 | 871 | 13 | 20 | 0 | 240 | 290 | 300 | 51 | 0 | 196 | 0 | 0 | 139 | 17 | 2 | 19 | 17 | 144 | 0 | 1 | 0 | 310 | 0 | 332 | 29 | 0 | 137 | 7 | 17 | 0 | 51 | 25 | 143 | 0 | 101 | 0 | 48 | 9.8 | 48 | 0 | 0.5 | 18.42 | 0 | 7326.22 | 893 | 0 | 0 | 0 | 21 | 38 | 0 | 0 | 0 | 0 | 0 | 31.38 | 470 | 0 | 0 | 0 | 1442.67 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 9.66 | 30 | 0 | 0 | 15.11 | 189 | 0 | 0 | 0 | 177 | 0 | 363 | 0 | 1.46 | 200 | 37 | 95 | 3 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0.1 | 16 | 242 | 65 | 220 | 0 | 1004 | 1170 | 17 | 6795.98 | 14122.2 | 76.38
11:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 34 | 110 | 145 | 30 | 17 | 17 | 0 | 0 | 0 | 415 | 0 | 0 | 260 | 0 | 0 | 21 | 142 | 18 | 21 | 0 | 480 | 91 | 16 | 24 | 0 | 32 | 0 | 0 | 0 | 12 | 12 | 2.66 | 89 | 0 | 0 | 1135 | 0 | 0 | 6 | 0 | 17 | 215 | 0 | 0 | 0 | 1105 | 18 | 20 | 0 | 350 | 290 | 260 | 51 | 0 | 205 | 0 | 0 | 139 | 17 | 19 | 19 | 17 | 144 | 0 | 10 | 0 | 315 | 0 | 317 | 29 | 0 | 135 | 6 | 17 | 0 | 52 | 25 | 143 | 0 | 101 | 0 | 48 | 9.2 | 48 | 0 | 0.2 | 20.31 | 0 | 7683.37 | 892 | 0 | 0 | 0 | 20 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 457 | 0 | 0 | 0 | 1401.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 28.56 | 57 | 0 | 0 | 16.39 | 189 | 0 | 0 | 0 | 177 | 0 | 398 | 0 | 1.55 | 202 | 38 | 17 | 4 | 0 | 0 | 0 | 0 | 3.3 | 1 | 0.16 | 0 | 249 | 65 | 180 | 0 | 982 | 1130 | 0 | 6571.4 | 14254.77 | 76.38
12:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 17 | 0 | 55 | 110 | 172 | 30 | 35 | 162 | 0 | 0 | 0 | 495 | 0 | 0 | 330 | 0 | 0 | 22 | 142 | 17.5 | 21 | 0 | 510 | 68 | 16 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 1.83 | 87 | 0 | 0 | 1135 | 0 | 0 | 6 | 0 | 17 | 217 | 0 | 0 | 0 | 1160 | 2 | 20 | 0 | 350 | 290 | 260 | 51 | 0 | 214 | 10 | 17 | 139 | 17 | 18 | 19 | 17 | 140 | 0 | 26 | 0 | 315 | 0 | 308 | 29 | 0 | 150 | 11 | 17 | 0 | 52 | 22 | 143 | 0 | 101 | 0 | 48 | 0.4 | 48 | 0 | 0 | 31.22 | 0 | 8224.95 | 892 | 0 | 0 | 0 | 21 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 400 | 0 | 0 | 0 | 1389.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.64 | 68 | 0 | 0 | 7.21 | 188 | 0 | 0 | 0 | 177 | 0 | 371 | 0 | 0.8 | 202 | 37 | 0 | 8 | 0 | 0 | 0 | 0 | 4.3 | 4 | 0.18 | 0 | 240 | 65 | 220 | 0 | 936 | 1100 | 0 | 6444.77 | 14669.72 | 76.37
13:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 17 | 0 | 88 | 110 | 179 | 30 | 35 | 162 | 0 | 0 | 0 | 510 | 0 | 0 | 329 | 0 | 0 | 21 | 142 | 17.5 | 0 | 0 | 480 | 60 | 16 | 28 | 0 | 1 | 0 | 0 | 0 | 12 | 12 | 0.81 | 83 | 0 | 2 | 975 | 0 | 0 | 6 | 0 | 17 | 217 | 0 | 0 | 0 | 1160 | 3 | 20 | 0 | 300 | 290 | 220 | 51 | 0 | 200 | 10 | 35 | 139 | 17 | 22 | 19 | 17 | 152 | 0 | 52 | 0 | 310 | 0 | 294 | 29 | 0 | 145 | 10 | 17 | 0 | 52 | 25 | 142 | 0 | 101 | 0 | 48 | 1.8 | 67 | 0 | 0 | 2.99 | 0 | 7998.1 | 892 | 0 | 0 | 0 | 23 | 38 | 0 | 0 | 0 | 0 | 0 | 58 | 427 | 0 | 0 | 0 | 1375.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.31 | 66 | 0 | 0 | 1.78 | 182 | 0 | 0 | 0 | 176 | 0 | 368 | 0 | 0.12 | 201 | 38 | 70 | 2 | 18 | 0 | 0 | 0 | 1.1 | 6 | 0.2 | 1 | 238 | 65 | 220 | 0 | 906 | 1100 | 2 | 6502.15 | 14500.25 | 76.37
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 17 | 0 | 88 | 78 | 179 | 30 | 35 | 162 | 0 | 0 | 0 | 520 | 0 | 0 | 326 | 0 | 0 | 16 | 142 | 18 | 21 | 0 | 520 | 60 | 16 | 25 | 0 | 9 | 0 | 0 | 0 | 12 | 12 | 1.46 | 81 | 14 | 2 | 865 | 0 | 0 | 6 | 0 | 17 | 216 | 0 | 0 | 0 | 1160 | 2 | 20 | 0 | 315 | 320 | 250 | 51 | 0 | 204 | 10 | 34 | 139 | 17 | 0 | 19 | 17 | 148 | 0 | 30 | 0 | 315 | 0 | 294 | 29 | 0 | 143 | 10 | 17 | 0 | 52 | 25 | 143 | 0 | 101 | 0 | 48 | 2.4 | 76 | 0 | 0 | 3.61 | 0 | 7926.47 | 892 | 0 | 0 | 0 | 27 | 38 | 0 | 0 | 0 | 0 | 0 | 23 | 465 | 0 | 0 | 0 | 1357.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.62 | 3 | 0 | 0 | 6.19 | 180 | 0 | 0 | 0 | 177 | 0 | 365 | 0 | 0.6 | 202 | 38 | 95 | 7 | 19 | 0 | 0 | 0 | 5.1 | 16 | 0.3 | 16 | 238 | 65 | 220 | 0 | 867 | 1076 | 17 | 6436.75 | 14363.22 | 76.4
15:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 88 | 46 | 145 | 30 | 35 | 126 | 0 | 0 | 0 | 545 | 0 | 0 | 326 | 0 | 0 | 1 | 142 | 0 | 21 | 0 | 530 | 60 | 16 | 25 | 0 | 24 | 0 | 0 | 0 | 12 | 12 | 2.39 | 78 | 17 | 2 | 960 | 0 | 0 | 6 | 0 | 0 | 216 | 0 | 0 | 0 | 1160 | 4 | 20 | 0 | 315 | 320 | 250 | 51 | 0 | 203 | 10 | 35 | 137 | 17 | 0 | 19 | 17 | 148 | 0 | 30 | 0 | 315 | 0 | 282 | 29 | 0 | 147 | 3 | 17 | 0 | 52 | 25 | 142 | 0 | 101 | 0 | 48 | 7.3 | 77 | 0 | 0.4 | 5.57 | 0 | 7859.66 | 518 | 0 | 0 | 0 | 27 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 480 | 0 | 0 | 0 | 1385.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.68 | 10 | 0 | 0 | 18.9 | 180 | 0 | 0 | 0 | 178 | 0 | 400 | 0 | 1.86 | 201 | 38 | 35 | 11 | 19 | 0 | 0 | 0 | 3.3 | 44 | 0.34 | 16 | 278 | 64 | 220 | 0 | 980 | 1055 | 17 | 6241.04 | 14100.7 | 76.4
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 88 | 46 | 145 | 30 | 35 | 126 | 0 | 0 | 0 | 565 | 0 | 17 | 326 | 0 | 0 | 2 | 142 | 0 | 21 | 0 | 530 | 67 | 16 | 25 | 0 | 2 | 0 | 0 | 0 | 12 | 12 | 2.46 | 81 | 17 | 2 | 1045 | 0 | 0 | 6 | 0 | 0 | 215 | 0 | 0 | 0 | 1165 | 4 | 20 | 0 | 315 | 320 | 250 | 51 | 0 | 205 | 10 | 34 | 137 | 17 | 0 | 19 | 17 | 154 | 0 | 23 | 0 | 320 | 0 | 282 | 29 | 0 | 149 | 3 | 17 | 0 | 52 | 25 | 142 | 0 | 102 | 0 | 48 | 6.51 | 77 | 0 | 0.6 | 3.25 | 9 | 8004.82 | 519 | 0 | 0 | 0 | 27 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 500 | 0 | 0 | 0 | 1437.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 15 | 0 | 0 | 12.48 | 180 | 0 | 0 | 0 | 176 | 0 | 402 | 0 | 1.13 | 201 | 39 | 35 | 12 | 16 | 0 | 0 | 0 | 1.6 | 52 | 0.13 | 16 | 284 | 64 | 220 | 0 | 1050 | 1130 | 17 | 6449.81 | 14454.63 | 76.4
17:00 | 0 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 5 | 125 | 130 | 145 | 28 | 35 | 126 | 0 | 0 | 0 | 535 | 0 | 17 | 326 | 0 | 0 | 0 | 142 | 17.5 | 21 | 0 | 490 | 79 | 16 | 25 | 0 | 0 | 33 | 0 | 0 | 12 | 12 | 1.21 | 83 | 17 | 4 | 940 | 0 | 0 | 6 | 0 | 0 | 216 | 0 | 0 | 0 | 1160 | 1 | 20 | 0 | 312 | 320 | 250 | 51 | 0 | 200 | 10 | 35 | 137 | 21 | 18 | 19 | 17 | 148 | 0 | 8 | 0 | 320 | 0 | 283 | 29 | 0 | 148 | 2 | 17 | 0 | 53 | 25 | 142 | 0 | 101 | 0 | 58 | 3.26 | 69 | 0 | 0.4 | 2.76 | 7 | 8005.13 | 505 | 0 | 0 | 0 | 28 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 500 | 0 | 0 | 0 | 1424.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6.01 | 176 | 0 | 0 | 0 | 174 | 0 | 391 | 0 | 0.53 | 201 | 38 | 35 | 4 | 28 | 0 | 0 | 0 | 1.5 | 31 | 0.04 | 16 | 257 | 64 | 220 | 0 | 965 | 1135 | 17 | 6263.33 | 14268.46 | 76.4
18:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 17 | 132 | 149 | 145 | 15 | 35 | 126 | 0 | 0 | 0 | 530 | 0 | 35 | 322 | 0 | 0 | 0 | 142 | 17 | 21 | 0 | 500 | 89 | 16 | 45 | 0 | 12 | 33 | 0 | 0 | 12 | 12 | 0.18 | 85 | 17 | 7 | 875 | 0 | 0 | 6 | 1 | 0 | 216 | 0 | 0 | 0 | 1065 | 0 | 20 | 0 | 315 | 320 | 250 | 51 | 14 | 202 | 35 | 34 | 138 | 83 | 26 | 19 | 17 | 148 | 0 | 5 | 0 | 320 | 0 | 283 | 29 | 0 | 145 | 0 | 17 | 0 | 53 | 25 | 143 | 0 | 102 | 0 | 58 | 1.04 | 69 | 0 | 0.1 | 2.38 | 12 | 8098.7 | 505 | 0 | 0 | 0 | 34 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 500 | 0 | 0 | 0 | 1351.39 | 0 | 0 | 0 | 0 | 0 | 4 | 48 | 14 | 0 | 0.11 | 3 | 18 | 0 | 3.46 | 174 | 0 | 0 | 0 | 171 | 0 | 383 | 0 | 0.32 | 180 | 38 | 35 | 2 | 47 | 0 | 0 | 0 | 0.5 | 17 | 0.02 | 16 | 244 | 64 | 220 | 0 | 890 | 1100 | 20 | 6122.8 | 14221.5 | 76.35
19:00 | 0 | 88 | 26 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 35 | 17 | 132 | 146 | 160 | 15 | 35 | 150 | 0 | 0 | 0 | 540 | 0 | 35 | 325 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 550 | 89 | 16 | 48 | 0 | 12 | 33 | 0 | 2 | 12 | 12 | 0 | 85 | 17 | 4 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 217 | 0 | 0 | 0 | 1224 | 0 | 35 | 0 | 315 | 320 | 250 | 51 | 37 | 189 | 40 | 35 | 138 | 102 | 26 | 19 | 17 | 166 | 0 | 0 | 0 | 325 | 0 | 283 | 29 | 0 | 151 | 0 | 17 | 0 | 70 | 30 | 143 | 0 | 102 | 0 | 68 | 0 | 87 | 0 | 0 | 0 | 12 | 8810.5 | 882 | 0 | 0 | 0 | 37 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 463 | 0 | 0 | 0 | 1383.33 | 0 | 0 | 0 | 50 | 14 | 5 | 103 | 25 | 0 | 0 | 0 | 18 | 0 | 0 | 171 | 0 | 0 | 0 | 133 | 0 | 395 | 0 | 0 | 181 | 38 | 89 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 1050 | 1070 | 35 | 6851.33 | 15661.83 | 76.35
19:30 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 35 | 17 | 132 | 146 | 195 | 15 | 35 | 162 | 0 | 0 | 0 | 539 | 0 | 35 | 328 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 500 | 89 | 16 | 70 | 0 | 15 | 33 | 0 | 35 | 12 | 12 | 0 | 107 | 17 | 8 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 217 | 0 | 0 | 0 | 1224 | 0 | 130 | 0 | 270 | 320 | 250 | 51 | 46 | 167 | 40 | 90 | 138 | 103 | 27 | 19 | 17 | 156 | 0 | 0 | 0 | 325 | 0 | 294 | 29 | 0 | 151 | 0 | 17 | 0 | 83 | 30 | 142 | 0 | 100 | 0 | 78 | 0 | 106 | 0 | 0 | 0 | 0 | 9033.5 | 892 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 488 | 0 | 0 | 0 | 1427.64 | 0 | 0 | 0 | 50 | 70 | 5 | 103 | 25 | 0 | 0 | 0 | 18 | 0 | 0 | 171 | 0 | 0 | 0 | 130 | 0 | 404 | 0 | 0 | 180 | 39 | 95 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 1050 | 1140 | 35 | 7048.64 | 16082.14
20:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 35 | 17 | 132 | 146 | 195 | 15 | 35 | 162 | 0 | 0 | 0 | 530 | 0 | 55 | 327 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 430 | 89 | 16 | 65 | 0 | 21 | 33 | 0 | 48 | 12 | 12 | 0 | 97 | 17 | 14 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 217 | 0 | 0 | 0 | 1224 | 0 | 122 | 0 | 230 | 290 | 250 | 51 | 47 | 170 | 40 | 79 | 138 | 101 | 27 | 19 | 17 | 152 | 0 | 0 | 0 | 325 | 0 | 294 | 29 | 0 | 145 | 0 | 17 | 0 | 82 | 30 | 143 | 0 | 100 | 0 | 78 | 0 | 107 | 0 | 0 | 0 | 0 | 8883.5 | 892 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 500 | 0 | 0 | 0 | 1383.56 | 0 | 25 | 0 | 50 | 70 | 12 | 102 | 26 | 0 | 0 | 0 | 18 | 0 | 0 | 170 | 0 | 0 | 0 | 127 | 0 | 355 | 0 | 0 | 181 | 39 | 95 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 64 | 220 | 0 | 1050 | 1155 | 35 | 6995.56 | 15879.06 | 76.35
21:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 35 | 17 | 132 | 146 | 195 | 15 | 35 | 162 | 0 | 0 | 0 | 470 | 0 | 55 | 327 | 0 | 0 | 0 | 142 | 18 | 21 | 0 | 495 | 90 | 16 | 62 | 0 | 15 | 33 | 0 | 54.36 | 12 | 12 | 0 | 99 | 17 | 17 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 218 | 0 | 0 | 0 | 1224 | 0 | 137 | 0 | 220 | 290 | 220 | 51 | 14 | 196 | 37 | 89 | 138 | 102 | 28 | 19 | 17 | 158 | 0 | 0 | 0 | 320 | 0 | 295 | 29 | 0 | 140 | 0 | 17 | 0 | 82 | 30 | 142 | 0 | 100 | 0 | 78 | 0 | 108 | 0 | 0 | 0 | 0 | 8864.86 | 892 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 500 | 0 | 0 | 0 | 1359.02 | 0 | 33 | 0 | 58 | 70 | 18 | 102 | 26 | 0 | 0 | 0 | 18 | 0 | 0 | 170 | 0 | 0 | 0 | 137 | 0 | 368 | 0 | 0 | 181 | 40 | 95 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 64 | 220 | 0 | 1050 | 1200 | 17 | 7049.02 | 15913.88 | 76.34
22:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 35 | 17 | 132 | 146 | 195 | 7 | 35 | 162 | 0 | 0 | 0 | 493 | 0 | 35 | 328 | 0 | 0 | 0 | 142 | 17.5 | 21 | 0 | 500 | 90 | 16 | 57 | 0 | 9 | 33 | 0 | 54.36 | 12 | 12 | 0 | 99 | 17 | 22 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 218 | 0 | 0 | 0 | 1224 | 0 | 140 | 0 | 220 | 290 | 220 | 51 | 10 | 199 | 40 | 75 | 139 | 102 | 27 | 19 | 17 | 158 | 0 | 0 | 0 | 320 | 0 | 295 | 29 | 0 | 141 | 0 | 17 | 0 | 52 | 27 | 143 | 0 | 102 | 0 | 79 | 0 | 108 | 0 | 0 | 0 | 0 | 8822.36 | 892 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 1300.75 | 0 | 33 | 0 | 57 | 70 | 18 | 102 | 26 | 0 | 0 | 0 | 18 | 0 | 0 | 170 | 0 | 0 | 0 | 149 | 0 | 364 | 0 | 0 | 180 | 41 | 95 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 1050 | 1200 | 17 | 6998.75 | 15821.11 | 76.34
23:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 35 | 17 | 132 | 146 | 195 | 10 | 29 | 108 | 0 | 0 | 0 | 520 | 0 | 35 | 329 | 0 | 0 | 0 | 142 | 17 | 21 | 0 | 410 | 107 | 16 | 66 | 0 | 22 | 33 | 0 | 18 | 12 | 12 | 0 | 100 | 19 | 24 | 1135 | 0 | 0 | 13 | 25.5 | 1 | 219 | 0 | 0 | 0 | 1224 | 0 | 140 | 0 | 230 | 290 | 220 | 51 | 13 | 216 | 40 | 69 | 139 | 103 | 27 | 19 | 17 | 158 | 0 | 0 | 0 | 315 | 0 | 295 | 29 | 0 | 145 | 0 | 17 | 0 | 52 | 25 | 143 | 0 | 100 | 5 | 79 | 0 | 107 | 0 | 0 | 0 | 0 | 8727.5 | 892 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 100 | 0 | 0 | 0 | 490 | 0 | 0 | 0 | 1486.03 | 0 | 33 | 0 | 57 | 70 | 0 | 102 | 26 | 0 | 0 | 0 | 18 | 0 | 0 | 170 | 0 | 0 | 0 | 165 | 0 | 355 | 0 | 0 | 181 | 40 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 1050 | 1200 | 17 | 7263.03 | 15990.53 | 76.34
Total KWH | 0 | 1217280 | 469440 | 0 | 0 | 0 | 0 | 0 | 9079200 | 0 | 0 | 257400 | 132840 | 1840320 | 1938240 | 3874036 | 618269 | 538896 | 1859040 | 0 | 0 | 0 | 11717273 | 0 | 269094 | 7573694 | 0 | 0 | 113866 | 3260400 | 419400 | 480960 | 0 | 11513181.82 | 2248145 | 386400 | 864960 | 0 | 352800 | 332490 | 79680 | 322685 | 295680 | 295680 | 21359 | 2097460 | 224145 | 327360 | 25898181.82 | 0 | 0 | 183360 | 161492.4 | 273491 | 5021055 | 0 | 0 | 0 | 23798179 | 71820 | 1077236 | 0 | 6524500 | 7585500 | 5830000 | 1245496 | 156960 | 5064000 | 409608 | 705600 | 3387031 | 996000 | 277200 | 466270 | 511860 | 3620160 | 0 | 196755 | 0 | 7553000 | 0 | 7454000 | 692000 | 0 | 3462545.46 | 61558 | 391584 | 0 | 1347840 | 645600 | 3264200 | 0 | 2424380 | 61560 | 1332000 | 48250 | 1605600 | 0 | 3050 | 129500 | 41040 | 189001136.5 | 19362909 | 0 | 0 | 0 | 416896 | 912000 | 0 | 0 | 111069 | 0 | 37872 | 305280 | 11760003 | 0 | 0 | 0 | 34261671 | 0 | 462207 | 0 | 544320 | 629856 | 45401 | 639440 | 323000 | 0 | 164720 | 312321 | 30519 | 0 | 100896 | 4290545 | 0 | 19400 | 0 | 4295118 | 0 | 9176581 | 0 | 10380 | 4658000 | 893236 | 1869554 | 46709 | 547516 | 0 | 0 | 0 | 20741.4 | 177840 | 1609 | 607392 | 6829000 | 1554000 | 5363420 | 0 | 24225455 | 28512000 | 446400 | 163965276.4 | 352966412.9

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 29-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14669.72 | MW | 12:00 Hr. | Energy Generated |  |  | 352.9664 |  | MKWHr.
| Day Peak Demand |  |  | 15023.72 | MW | 12:00 Hr. | Energy Unserverd |  |  | 21.369 |  | MKWHr.
| Evening Peak Generation |  |  | 16082.14 | MW | 19:30 Hr. | Energy Demand |  |  | 374.3354 |  | MKWHr.
| Evening Peak Demand |  |  | 16487.88 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32 |  | °C
| Minimum Generation of the Day |  |  | 13577.73 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 921.67 |  | MMCFD
| Maximum Generation of the Day |  |  | 16082.14 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.4515 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.7837 | 0 | 16.2753 | 0 | 0 | 0.11387 | 0 | 0 | 57.1728 | Gas | 128.7357 | Gas | 426328039.8026
| Chattogram Zone |  |  | 5.3484 | 49.6964 | 5.6682 | 0 | 2.0975 | 0.093179 | 0 | 0.3528 | 63.2564 | Coal | 126.5741 | Coal | 836303414.5246
| Cumilla Zone |  |  | 30.6694 | 0 | 3.5679 | 0 | 0 | 0.19676 | 3.6202 | 0 | 38.0542 | HFO | 35.1519 | HFO | 615958976.074
| Mymensingh Zone |  |  | 0 | 0 | 3.0402 | 0 | 0 | 0.1808 | 0 | 0 | 3.221 | HSD | 0.11107 | HSD | 2243593.8
| Sylhet Zone |  |  | 27.2351 | 0 | 0 | 0 | 0 | 0.061558 | 0 | 0 | 27.2967 | Hydro | 2.0975 | Hydro | 7991322.6
| Khulna Zone |  |  | 0 | 11.76 | 0.45477 | 0.11107 | 0 | 0.30528 | 20.2749 | 0 | 32.906 | Solar | 1.7867 | Solar | 27777211.278
| Barishal Zone |  |  | 6.9174 | 59.5665 | 1.0538 | 0 | 0 | 0.001609 | 0 | 0 | 67.5393 | Import | 58.1567 | Import | 355385703.45
| Rajshahi Zone |  |  | 17.7816 | 0 | 2.6747 | 0 | 0 | 0.58832 | 34.2617 | 0 | 55.3064 | Wind | 0.3528 | Wind | 5189688
| Rangpur Zone |  |  | 0 | 5.5512 | 2.4171 | 0 | 0 | 0.24529 | 0 | 0 | 8.2136
| Total |  |  | 128.7357 | 126.5741 | 35.1519 | 0.11107 | 2.0975 | 1.7867 | 58.1567 | 0.3528 | 352.9664
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 426328039.8026 |  | Hydro | 7991322.6
|  |  |  | Coal | 836303414.5246 |  | Solar | 27777211.278
|  |  |  | HFO | 615958976.074 |  | Import | 355385703.45
|  |  |  | HSD | 2243593.8 |  | Wind | 5189688
[5 empty] | Total: | 227,71,77,949 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.3629 | Peak Hr Flow | 892.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 49170054.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 34.2617 | Peak Hr Flow | 1427.64 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1995 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.6202 | Peak Hr Flow | 156.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2751 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 57.2447 | Peak Hr Flow | 2475.64 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 30 |  | 5991
|  |  |  | Chattogram |  | 0 |  | 1484
|  |  |  | Cumilla |  | 48 |  | 1541
|  |  |  | Mymensingh |  | 93 |  | 1217
|  |  |  | Sylhet |  | 96 |  | 672
|  |  |  | Khulna |  | 0 |  | 1856
|  |  |  | Barishal |  | 0 |  | 491
|  |  |  | Rajshahi |  | 0 |  | 1514
|  |  |  | Rangpur |  | 0 |  | 975
|  |  |  | Total |  | 267 |  | 15741
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Karnaphuli Hydro PP Unit-5 |  |  | 50
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 350 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 400
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:20 | Muradnagar 132/33kV S/S 132 KV Muradnagar- Cumilla(N) Ckt-01 is restored.
| 08:40 | 16:29 | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Daganbhuiyan 132/33kV end Due to
Shutdown taken at feni 230 kv end due to project work. and from Feni 230/132kV end Due to
project work
| 08:47 |  | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Gopalganj 400/132kV end.
|  | 08:50 | Jashore 132/33kV S/S T-2 HT is restored.
|  | 08:51 | Jashore 132/33kV S/S T-2 LT is restored.
| 09:00 | 16:56 | KSRM 132/33kV S/S Transformer-01 HT Scheduled S/D Due to secondary CT (33kv side)
maintenance
| 09:16 | 10:31 | Panchagarh 132/33kV S/S T-2(417T) HT Scheduled S/D Due to Red Hot Maintenance work on | [7 empty] | 8.0MW load
|  |  | 33kv bus Section-02 (T-2) | [7 empty] | interrup.
| 09:16 | 10:31 | Panchagarh 132/33kV S/S T-2(417T) LT Scheduled S/D Due to Red Hot Maintenance work on | [7 empty] | 8.0MW load
|  |  | 33kv bus Section-02 (T-2) | [7 empty] | interrup.
| 09:17 |  | Khulshi-Madunaghat 132kV Ckt-2 Tripped from Madunaghat 132/33kV end showing REL 670
relays Due to Jumper out
| 09:45 | 17:04 | Ruppur 132/11kV S/S TR-02 LT Forced S/D Due to Emergency maintenance work
| 09:46 | 16:55 | Ruppur 132/11kV S/S TR-02 HT Forced S/D Due to Emergency maintenance work
| 09:48 | 14:46 | Madunaghat 132/33kV S/S TR-2(517T) HT Scheduled S/D Due to B phase cable ceiling
maintenance.full load served by T-01.
| 10:41 | 11:47 | Cumilla(S) 132/33kV S/S Cumilla North-2 Forced S/D Due to Red hot maintenance at Cum
(North) End
| 10:51 | 13:58 | Haripur 230/132kV S/S 132kV Reserve Bus Sec-2 Scheduled S/D Due to project work.
| 11:10 |  | Khulshi-Madunaghat 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to B-phase
jumper maintenance at 822 tower by Khulsi SS
| 12:00 |  | Day peak generation is 14670 MW.
| 12:04 | 12:56 | Bhulta-Haripur 132 kV Ckt-1 Tripped from Bhulta 132/33kV end showing Impedance Relay | [7 empty] | 160.0MW load
|  |  | relays Due to সূবর্ণগ্রাম পিকনিক স্পটে ১৩২কেভি লাইনের সাথে অ্যালুমিনিয়ামের মই লাগার কারণে | [7 empty] | interrup. Bhulta
|  |  | ভুলতা নিউ সাবস্টেশনের ব্রেকার ট্রিপ করে এবং ভুলতা ওল্ড সাবস্টেশন ব্লাক আউট হয়ে যায়। | [7 empty] | 132/33kV end
| 12:40 |  | Purbasadipur 230/132/33kV S/S TR-2 HT Project Work S/D Due to old name T-1. project
work. transformer in open condition
| 12:45 |  | Purbasadipur 230/132/33kV S/S TR-3 HT Project Work S/D Due to old name T-2. project
work. transformer in open condition
| 12:46 | 14:45 | BSRM-Cumilla(N) 230 kV Ckt-1 Scheduled S/D from Feni 230/132kV end Due to Red hot
maintainance Cumilla north Grid end
|  | 13:58 | Haripur 230/132kV S/S 132kV Bus Coupler-2 is restored.
| 15:35 | 17:40 | Lalmonirhat 132/33kV S/S T-2 (415T) LT Forced S/D Due to T-2 33 kV riser DS (R phase) | [7 empty] | 5.0MW load
|  |  | emergency red hot maintenance work. | [7 empty] | interrup.
|  | 18:10 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 LT is restored.
|  | 18:10 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 HT is restored.
| 19:30 |  | Evening Peak Generation: 16082
| 19:31 | 21:43 | Barishal-Bhandaria 132 kV Ckt-1 Tripped from Barishal 132/33kV end showing Distance
relays Due to Conductor cut
| 19:44 | 19:57 | Gopalganj 132/33kV S/S T2 LT Tripped showing Instantineous earth fault relays. | [7 empty] | 46.0MW load
interrup.
| 19:44 | 19:56 | Gopalganj 132/33kV S/S T1 LT Tripped showing Instantineous Earth fault relays Due to Deu | [7 empty] | 44.0MW load
|  |  | to Gopalganj REB-2 feder trip | [7 empty] | interrup.
| 21:44 |  | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to for | [7 empty] | 54.0MW load
|  |  | repair the line | [7 empty] | interrup. Barishal
132/33kV end
| 22:49 |  | Khulna 330MW GT was sync.
| 22:50 | 23:24 | Chhatak 132/33kV S/S T-1 LT Scheduled S/D Due to For 33kV T-1 Bus DS Red Hot Maintenance | [7 empty] | 11.0MW load
|  |  | Work. | [7 empty] | interrup.
| 22:50 | 23:24 | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to For 33kV T-1 Bus DS Red Hot Maintenance | [7 empty] | 11.0MW load
|  |  | Work. | [7 empty] | interrup.
| 23:04 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- GT
| 23:04 |  | Sirajganj unit-2 GT was sync.
| 23:55 | 00:12 | Khulna(C )-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end Due to By the
instruction of ALDC.
| 00:27 |  | Nabinagar 132/33kV S/S T-1 LT Tripped showing Intertrip from HV DIFF. relays.
| 00:27 |  | Nabinagar 132/33kV S/S T-1 HT Tripped showing PRD Trip relays.
| 02:35 |  | Sirajganj unit-2 ST was sync.
| 02:35 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- ST
| 06:08 | 07:20 | Saidpur 132/33kV S/S TR-2 (404T) HT Scheduled S/D Due to 33 KV EPZ Feeder (Bus DS) red
hot maintainance.
| 06:08 | 07:21 | Saidpur 132/33kV S/S TR-2 (404T) LT Scheduled S/D Due to 33 KV EPZ Feeder (Bus DS) red
hot maintainance.
| 06:37 |  | Sirajganj unit-3 was shutdown.
| 06:48 |  | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT Scheduled S/D Due to High
Temparature Maintenance
| 06:48 |  | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT Scheduled S/D Due to High
Temparature Maintenance
| 07:24 |  | Rampal 1320 MW (BIFPCL) unit-2 was sync.
| 07:24 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U2
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 29-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 383 | 9079200 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 618269 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 7573694 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 257400 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 146 | 1938240 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 538896 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 269094 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 419400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 480960 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 42 | 469440 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 3874036 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1840320 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1217280 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1859040 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 113866 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 132840 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 11513181.82 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 539 | 11717273 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3260400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2833 | 57172829.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 161492.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 71820 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 183360 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 107 | 2097460 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5021055 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 273491 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 79680 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 33 | 332490 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 295680 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 327360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 70 | 864960 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21359 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 386400 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 35 | 322685 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 224145 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 295680 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 89 | 2248145 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | Under Maintenance
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 23798179 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 15 | 352800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1135 | 25898181.82 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 3021.5 | 63256423.22
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 167 | 5064000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 320 | 7585500 | plant availability zero
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 250 | 5830000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 270 | 6524500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 409608 | Gas shortage, Plant availability zero
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 46 | 156960 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1245496 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 130 | 1077236 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 138 | 3387031 | Low gas pressure, Plant Availability Zero
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 103 | 996000 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 156 | 3620160 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 466270 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 511860 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 277200 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 705600 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 196755 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1824 | 38054176
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 48250 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 3050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 106 | 1605600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1332000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 129500 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 41040 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 61560 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 184 | 3221000
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 61558 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 29 | 692000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3462545.46 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 3264200 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 645600 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1347840 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2424380 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 391584 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 325 | 7553000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 294 | 7454000 | Machine Problem, Plant Availability Zero
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1171 | 27296707.46
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 892 | 19362909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 416896 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 37872 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 305280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 111069 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 488 | 11760003 | U-2 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1433 | 32906029
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1050 | 24225455 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 607392 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 64 | 1554000 | GT-1 & ST under maint
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1140 | 28512000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5363420 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 446400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6829000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1609 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2832 | 67539276
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 164720 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 462207 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 45401 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 323000 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 171 | 4290545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 19400 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 130 | 4295118 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 404 | 9176581 | AGC
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 18 | 30519 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 103 | 639440 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 629856 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 544320 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 10380 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1427.64 | 34261671 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 100896 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 312321 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2403.64 | 55306375
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 39 | 893236 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4658000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 66 | 547516 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 20741.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1869554 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 46709 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 177840 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 380 | 8213596.4
Eastern Grid Total |  |  |  |  | 17438.042 | 9033.5 | 189001136.5
Western Grid Total |  |  |  |  | 11885.475 | 7048.64 | 163965276.4
National Grid Total |  |  |  |  | 29323.517 | 16082.14 | 352966412.9
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 29-06-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10691.47 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4836 | MW
i) Dhaka area |  |  | 5961.27 |  | MW | i) Khulna area |  |  |  | 1856.4 | MW
ii) Chattogram area |  |  | 1537.2 |  | MW | ii) Barishal area |  |  |  | 491 | MW
iii) Cumilla area |  |  | 1493 |  | MW | iii) Rajshahi area |  |  |  | 1513.6 | MW
iv) Mymensingh area |  |  | 1124 |  | MW | iv) Rangpur area |  |  |  | 975 | MW
v) Sylhet area |  |  | 576 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15527.47 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 1110 | 01:00 | 133 | Narshingdi | 190 | 23:00 | 199 | UttaraNew | 60 | 00:00
2 | AKSML | 153.9 | 11:00 | 68 | Hasnabad | 98 | 11:00 | 134 | Natore | 166 | 04:00 | 200 | Zigatola | 98 | 12:00
3 | Aftabnagar | 50 | 00:00 | 69 | Hathazari | 95 | 20:00 | 135 | Nawabganj | 66.4 | 22:00
4 | Agargaon | 133 | 13:00 | 70 | Hatirjheel | 50 | 12:00 | 136 | Netrakona | 140 | 19:30
5 | Agrabad | 74 | 11:00 | 71 | Ishurdi | 84 | 13:00 | 137 | New | 77.3 | 12:00
6 | Amnura | 31 | 00:00 | 72 | Jaldhaka | 72 | 22:00 | 138 | Niamatpur | 82 | 23:00
7 | Ashuganj | 100 | 00:00 | 73 | Jamalpur | 118 | 20:00 | 139 | Noapara | 55 | 13:00
8 | BSRM | 201 | 21:00 | 74 | Jashore | 168 | 13:00 | 140 | PHP | 13 | 14:00
9 | Bagerhat | 84 | 07:00 | 75 | Jhenaidah | 94 | 04:00 | 141 | Pabna | 100 | 13:00
10 | Bajitpur | 97 | 23:00 | 76 | Joydebpur | 165 | 19:00 | 142 | Palashbari | 130 | 04:00
11 | Bakerganj | 15.4 | 21:00 | 77 | Joypurhat | 62 | 04:00 | 143 | Panchagarh | 65 | 00:00
12 | Bakulia | 97 | 19:00 | 78 | Juldah | 22 | 15:00 | 144 | Patiya | 11 | 19:30
13 | Banani | 74 | 11:00 | 79 | KSRM | 21 | 05:00 | 145 | Patuakhali | 73 | 21:00
14 | Bangabhaban | 23 | 11:00 | 80 | Kabirpur | 257 | 12:00 | 146 | Payra | 34 | 04:00
15 | Barapukuria | 62 | 19:30 | 81 | Kachua | 100 | 22:00 | 147 | Postogola | 65 | 13:00
16 | Barguna | 22 | 04:00 | 82 | Kaliganj | 39 | 13:00 | 148 | Pubail | 43 | 14:00
17 | Barishal | 106 | 13:00 | 83 | Kallyanpur | 138 | 00:00 | 149 | Purbachal | 34 | 14:00
18 | Barishal-230 | 114 | 23:00 | 84 | Kalurghat | 42 | 12:00 | 150 | Purbasadipur | 134 | 19:30
19 | Baroaulia | 51 | 14:00 | 85 | Kamrangirchar | 85 | 13:00 | 151 | Rahanpur | 43 | 21:00
20 | Baroirhat | 64 | 23:00 | 86 | Kaptai | N/A | N/A | 152 | Rahim | 26 | 16:00
21 | Bashundhara | 221 | 12:00 | 87 | Kasba | 39 | 04:00 | 153 | Rajbari | 84.5 | 19:30
22 | BashundharaCement | 1 | 00:00 | 88 | Kazla | 124 | 12:00 | 154 | Rajendrapur | 117 | 19:00
23 | Beanibazar | 82 | 19:00 | 89 | Keranigonj | 88 | 19:30 | 155 | Rajshahi | 131 | 00:00
24 | Benapole | 70 | 05:00 | 90 | Khagrachori | 36 | 22:00 | 156 | Rajshahi-230 | 96 | 13:00
25 | Bhaluka | 164 | 20:00 | 91 | Khulna | 63 | 12:00 | 157 | Ramganj | 116 | 22:00
26 | Bhandaria | 54 | 19:30 | 92 | Khulshi | 190 | 21:00 | 158 | Rampur | 42 | 19:00
27 | Bhangura | 38 | 04:00 | 93 | Kishoreganj | 120 | 13:00 | 159 | Rangamati | 16 | 19:00
28 | Bheramara(GK) | 70 | 21:00 | 94 | Kodda | 296 | 20:00 | 160 | Rangpur | 134 | 19:30
29 | Bhulta | 222 | 18:00 | 95 | Kulaura | 59 | 19:00 | 161 | Ruppur | 4.8 | 11:00
30 | Bog-Sherpur | 80 | 21:00 | 96 | Kurigram | 63 | 04:00 | 162 | SSM | 4 | 04:00
31 | Bogura | 206 | 00:00 | 97 | Kushtia | 166 | 13:00 | 163 | Saidpur | 93 | 20:00
32 | Borhanuddin | 80 | 23:00 | 98 | Laksam | 30 | 23:00 | 164 | Santhia | 34 | 04:00
33 | Brahmanbaria | 140 | 19:00 | 99 | Lakshmipur | 41 | 21:00 | 165 | Satkhira | 137 | 23:00
34 | Cantonment | 160 | 12:00 | 100 | Lalbag | 80 | 12:00 | 166 | Satmasjid | 112 | 13:00
35 | Chandina | 36 | 01:00 | 101 | Lalmonirhat | 56 | 20:00 | 167 | Savar | 214 | 12:00
36 | Chandpur | 90 | 21:00 | 102 | MI_Cement | 8.3 | 04:00 | 168 | SevenRings | 19.26 | 12:00
37 | Chandraghona | 33 | 19:00 | 103 | Madanganj | 45 | 19:30 | 169 | ShahCement | 33 | 09:00
38 | Chapai | 84 | 12:00 | 104 | Madaripur | 115 | 19:30 | 170 | Shahjadpur | 84 | 07:00
39 | Charfasson | 34 | 22:00 | 105 | Madartek | 90 | 00:00 | 171 | Shahjibazar | 135 | 19:00
40 | Charsaidpur | 43 | 18:30 | 106 | Madunaghat | 55 | 20:00 | 172 | Shahmirpur | 52 | 19:00
41 | Chauddagram | 76 | 19:30 | 107 | Magura | 67 | 21:00 | 173 | Shariatpur | 93 | 20:00
42 | Chhatak | 43 | 04:00 | 108 | Mahasthangarh | 74 | 20:00 | 174 | Sherpur | 138 | 19:30
43 | Chowmuhani | 156 | 19:00 | 109 | Maijdee | 41 | 23:00 | 175 | Shikalbaha | 32.5 | 19:30
44 | Chuadanga | 126 | 22:00 | 110 | Manikganj | 147 | 20:00 | 176 | Shitalakhya | 80.6 | 15:00
45 | Coxsbazar | 137 | 21:00 | 111 | Maniknagar | 84 | 13:00 | 177 | Sholosohor | 45 | 19:00
46 | Cumilla(N) | 125 | 19:00 | 112 | Matarbari | 53 | 19:00 | 178 | Shomvuganj | 42 | 22:00
47 | Cumilla(S) | 174 | 00:00 | 113 | Matuail | 80 | 12:00 | 179 | Shyampur | 176 | 04:00
48 | Daganbhuiyan | 35 | 22:00 | 114 | Metrorail_Motijheel | 30 | 18:00 | 180 | Siddhirganj | 139 | 12:00
49 | Daudkandi | 156 | 20:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Sirajganj | 124 | 00:00
50 | DhakaUniversity | 98 | 13:00 | 116 | Millgate | 141 | 14:00 | 182 | Sitakunda | 21 | 21:00
51 | Dhamrai | 98 | 22:00 | 117 | Mirpur | 166 | 14:00 | 183 | Sonargaon | 160 | 12:00
52 | Dhanmondi | 136.5 | 13:00 | 118 | Mirsorai | 40 | 12:00 | 184 | Sreemongol | 93 | 22:00
53 | Dohazari | 111 | 19:30 | 119 | Mirzapur | 52 | 12:00 | 185 | Sreepur | 139 | 19:30
54 | Faridpur | 173 | 20:00 | 120 | Mithapukur | 76 | 05:00 | 186 | Srinagar | 54.9 | 22:00
55 | Fatullah | 107 | 10:00 | 121 | Modern | N/A | N/A | 187 | Sunamganj | 58 | 19:00
56 | Fenchuganj | 45 | 19:00 | 122 | Mogbazar | 104.8 | 13:00 | 188 | Sylhet | 126 | 19:00
57 | Feni | 115 | 22:00 | 123 | Mongla | 52 | 11:00 | 189 | Sylhet_(South) | 67 | 22:00
58 | GPH | 77 | 06:00 | 124 | Motijheel | 56 | 13:00 | 190 | TK | 23 | 01:00
59 | Ghatail | 79 | 19:30 | 125 | Muktagacha | 35 | 19:30 | 191 | Tangail | 188 | 12:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 119 | 23:00 | 192 | Taraganj | 31 | 20:00
61 | Ghorashal-230 | 100 | 05:00 | 127 | Muradnagar | 55 | 22:00 | 193 | Tasnim | 42 | 17:00
62 | Goalpara | 42 | 07:00 | 128 | Mymensingh | 170 | 00:00 | 194 | Thakurgaon | 108 | 19:30
63 | Gollamari | 124 | 13:00 | 129 | Nabinagar | 120 | 08:00 | 195 | Tongi | 139 | 00:00
64 | Gopalganj | 119.4 | 19:30 | 130 | Naogaon | 137 | 22:00 | 196 | Ullahpara | 40 | 19:30
65 | Gulshan | 140 | 12:00 | 131 | Narail | 61.5 | 21:00 | 197 | Ullon | 65 | 00:00
66 | Halishahar | 106 | 10:00 | 132 | Narinda | 80 | 13:00 | 198 | Uttara | 105 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 29-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15036.92 | 2799 |  | 17961.88
1:00 | 14432.56 | 2756 |  | 17312.58
2:00 | 14192.59 | 2828 |  | 17147.85
3:00 | 14068.36 | 2584 |  | 16768.64
4:00 | 14229.24 | 1263 |  | 15549.08
5:00 | 14213.52 | 1236 |  | 15505.14
6:00 | 13786.88 | 1060 |  | 14894.58
7:00 | 13577.73 | 630 |  | 14236.08
8:00 | 13732.52 | 753 |  | 14519.41
9:00 | 13960.18 | 726 |  | 14718.85
10:00 | 14122.2 | 616 |  | 14765.92
11:00 | 14254.77 | 488 |  | 14764.73
12:00 | 14669.72 | 339 |  | 15023.72
13:00 | 14500.25 | 339 |  | 14854.25
14:00 | 14363.22 | 163 |  | 14533.22
15:00 | 14100.7 | 201 |  | 14310.7
16:00 | 14454.63 | 158 |  | 14619.63
17:00 | 14268.46 | 152 |  | 14427.46
18:00 | 14221.5 | 105 |  | 14331.5
19:00 | 15661.83 | 108 |  | 15774.83
19:30 | 16082.14 | 267 |  | 16361.14
20:00 | 15879.06 | 376 |  | 16272.06
21:00 | 15913.88 | 549 |  | 16487.88
22:00 | 15821.11 | 542 |  | 16387.11
23:00 | 15990.53 | 598 |  | 16615.53
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 29-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8024 | 7012.92 | 15036.92 | DAILY GENERATION CURVE
00:30 | 7790 | 6944.74 | 14734.74
01:00 | 7556 | 6876.56 | 14432.56 | 29-06-2026
01:30 | 7448.5 | 6864.075 | 14312.575
02:00 | 7341 | 6851.59 | 14192.59
02:30 | 7232 | 6898.475 | 14130.475
03:00 | 7123 | 6945.36 | 14068.36
03:30 | 7153 | 6995.8 | 14148.8
04:00 | 7183 | 7046.24 | 14229.24
04:30 | 7166 | 7055.38 | 14221.38
05:00 | 7149 | 7064.52 | 14213.52
05:30 | 7030.6 | 6969.6 | 14000.2
06:00 | 6912.2 | 6874.68 | 13786.88
06:30 | 6830.805 | 6851.5 | 13682.305
07:00 | 6749.41 | 6828.32 | 13577.73
07:30 | 6804.28 | 6850.845 | 13655.125
08:00 | 6859.15 | 6873.37 | 13732.52
08:30 | 6963.73 | 6882.62 | 13846.35
09:00 | 7068.31 | 6891.87 | 13960.18
09:30 | 7197.265 | 6843.925 | 14041.19
10:00 | 7326.22 | 6795.98 | 14122.2
10:30 | 7504.795 | 6683.69 | 14188.485
11:00 | 7683.37 | 6571.4 | 14254.77
11:30 | 7954.16 | 6508.085 | 14462.245
12:00 | 8224.95 | 6444.77 | 14669.72
12:30 | 8111.525 | 6473.46 | 14584.985
13:00 | 7998.1 | 6502.15 | 14500.25
13:30 | 7962.285 | 6469.45 | 14431.735
14:00 | 7926.47 | 6436.75 | 14363.22
14:30 | 7893.065 | 6338.895 | 14231.96
15:00 | 7859.66 | 6241.04 | 14100.7
15:30 | 7932.24 | 6345.425 | 14277.665
16:00 | 8004.82 | 6449.81 | 14454.63
16:30 | 8004.975 | 6356.57 | 14361.545
17:00 | 8005.13 | 6263.33 | 14268.46
17:30 | 8051.915 | 6193.065 | 14244.98
18:00 | 8098.7 | 6122.8 | 14221.5
18:30 | 8454.6 | 6487.065 | 14941.665
19:00 | 8810.5 | 6851.33 | 15661.83
19:30 | 9033.5 | 7048.64 | 16082.14
20:00 | 8883.5 | 6995.56 | 15879.06
20:30 | 8874.18 | 7022.29 | 15896.47 |  | Executive Engineer
21:00 | 8864.86 | 7049.02 | 15913.88 |  | Network Operation Division
21:30 | 8843.61 | 7023.885 | 15867.495
22:00 | 8822.36 | 6998.75 | 15821.11
22:30 | 8774.93 | 7130.89 | 15905.82
23:00 | 8727.5 | 7263.03 | 15990.53

## En-Curve
QF-LDC-12
Date | 29-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3442 | 1997 | 703 | 38 | 176 | 1472.92 | 89 | 5455 | 0 | 471 | 1174 | 0 | 0 | 19 | 2799 | DAILY ENERGY CURVE
00:30 | 3438 | 1964.5 | 703 | 38 | 170 | 1483.74 | 87 | 5331.5 | 0 | 421.5 | 1078.5 | 0 | 0 | 19 | 2777.5 | 29-06-2026
01:00 | 3434 | 1932 | 703 | 38 | 164 | 1494.56 | 85 | 5208 | 0 | 372 | 983 | 0 | 0 | 19 | 2756
01:30 | 3447 | 1907.5 | 703 | 38 | 162 | 1491.075 | 85 | 5174 | 0 | 359.5 | 930 | 0 | 0 | 15.5 | 2792 | Energy Generated | 352.9664 |  | MKWHr
02:00 | 3460 | 1883 | 703 | 38 | 160 | 1487.59 | 85 | 5140 | 0 | 347 | 877 | 0 | 0 | 12 | 2828 | Energy not Served | 21.369 |  | MKWHr
02:30 | 3444.5 | 1840 | 750 | 38 | 158 | 1483.975 | 85 | 5140.5 | 0 | 306 | 866.5 | 0 | 0 | 18 | 2706 | Total Energy Requirement | 374.3354 |  | MKWHr
03:00 | 3429 | 1797 | 797 | 38 | 156 | 1480.36 | 85 | 5141 | 0 | 265 | 856 | 0 | 0 | 24 | 2584
03:30 | 3439.5 | 1852.5 | 844 | 38 | 154 | 1480.3 | 85 | 5140 | 0 | 243 | 851 | 0 | 0 | 21.5 | 1923.5
04:00 | 3450 | 1908 | 891 | 38 | 152 | 1480.24 | 85 | 5139 | 0 | 221 | 846 | 0 | 0 | 19 | 1263
04:30 | 3453 | 1901.5 | 891 | 38 | 150 | 1488.88 | 85 | 5139 | 0 | 221 | 838 | 0 | 0 | 16 | 1249.5
05:00 | 3456 | 1895 | 891 | 38 | 148 | 1497.52 | 85 | 5139 | 0 | 221 | 830 | 0 | 0 | 13 | 1236
05:30 | 3423.5 | 1798.5 | 891 | 38 | 138 | 1491.39 | 86 | 5118 | 7.81 | 220.5 | 771.5 | 0 | 0 | 16 | 1148
06:00 | 3391 | 1702 | 891 | 38 | 128 | 1485.26 | 87 | 5097 | 15.62 | 220 | 713 | 0 | 0 | 19 | 1060
06:30 | 3388 | 1634 | 891.5 | 38 | 133 | 1489.715 | 87 | 5033 | 41.59 | 220 | 710.5 | 0 | 0 | 16 | 845
07:00 | 3385 | 1566 | 892 | 38 | 138 | 1494.17 | 87 | 4969 | 67.56 | 220 | 708 | 0 | 0 | 13 | 630
07:30 | 3387 | 1614 | 892 | 38 | 139 | 1492.615 | 88 | 4954.5 | 87.51 | 235 | 710 | 0 | 0 | 17.5 | 691.5
08:00 | 3389 | 1662 | 892 | 38 | 140 | 1491.06 | 89 | 4940 | 107.46 | 250 | 712 | 0 | 0 | 22 | 753
08:30 | 3379 | 1695 | 892 | 38 | 143 | 1482.08 | 89 | 4986 | 134.27 | 281.5 | 705 | 0 | 0 | 21.5 | 739.5
09:00 | 3369 | 1728 | 892 | 38 | 146 | 1473.1 | 89 | 5032 | 161.08 | 313 | 698 | 0 | 0 | 21 | 726
09:30 | 3415 | 1709.5 | 892.5 | 38 | 145 | 1457.885 | 89 | 5080.5 | 156.305 | 331.5 | 707 | 0 | 0 | 19 | 671
10:00 | 3461 | 1691 | 893 | 38 | 144 | 1442.67 | 89 | 5129 | 151.53 | 350 | 716 | 0 | 0 | 17 | 616
10:30 | 3486.5 | 1697 | 892.5 | 38 | 144 | 1422.055 | 89 | 5213.5 | 183.43 | 336.5 | 661.5 | 0 | 0 | 24.5 | 552
11:00 | 3512 | 1703 | 892 | 38 | 144 | 1401.44 | 89 | 5298 | 215.33 | 323 | 607 | 0 | 0 | 32 | 488
11:30 | 3562 | 1785.25 | 892 | 38 | 142 | 1395.54 | 88 | 5254 | 238.955 | 341 | 709.5 | 0 | 0 | 16 | 413.5
12:00 | 3612 | 1867.5 | 892 | 38 | 140 | 1389.64 | 87 | 5210 | 262.58 | 359 | 812 | 0 | 0 | 0 | 339
12:30 | 3554.5 | 1845.5 | 892 | 38 | 146 | 1382.64 | 85 | 5127.5 | 257.845 | 360 | 895.5 | 0 | 0 | 0.5 | 339
13:00 | 3497 | 1823.5 | 892 | 38 | 152 | 1375.64 | 83 | 5045 | 253.11 | 361 | 979 | 0 | 0 | 1 | 339
13:30 | 3524.5 | 1860.75 | 892 | 38 | 150 | 1366.79 | 82 | 4978 | 200.195 | 329 | 1005.5 | 0 | 0 | 5 | 251
14:00 | 3552 | 1898 | 892 | 38 | 148 | 1357.94 | 81 | 4911 | 147.28 | 297 | 1032 | 0 | 0 | 9 | 163
14:30 | 3552 | 1908.5 | 705 | 38 | 148 | 1371.95 | 79.5 | 5031.5 | 156.01 | 272.5 | 952.5 | 0 | 0 | 16.5 | 182
15:00 | 3552 | 1919 | 518 | 38 | 148 | 1385.96 | 78 | 5152 | 164.74 | 248 | 873 | 0 | 0 | 24 | 201
15:30 | 3561 | 1932.5 | 518.5 | 38 | 151 | 1411.915 | 79.5 | 5283 | 153.75 | 248 | 887.5 | 0 | 0 | 13 | 179.5
16:00 | 3570 | 1946 | 519 | 38 | 154 | 1437.87 | 81 | 5414 | 142.76 | 248 | 902 | 0 | 0 | 2 | 158
16:30 | 3555.5 | 1920.75 | 512 | 38 | 151 | 1431.06 | 82 | 5305 | 106.235 | 313.5 | 945.5 | 0 | 0 | 1 | 155
17:00 | 3541 | 1895.5 | 505 | 38 | 148 | 1424.25 | 83 | 5196 | 69.71 | 379 | 989 | 0 | 0 | 0 | 152
17:30 | 3547 | 1904.75 | 505 | 38 | 148 | 1387.82 | 84 | 5044 | 53.41 | 462.5 | 1064.5 | 0 | 0 | 6 | 128.5
18:00 | 3553 | 1914 | 505 | 38 | 148 | 1351.39 | 85 | 4892 | 37.11 | 546 | 1140 | 0 | 0 | 12 | 105
18:30 | 3539 | 1968.5 | 693.5 | 38 | 157 | 1367.36 | 85 | 5180 | 18.555 | 592 | 1290.75 | 0 | 0 | 12 | 106.5
19:00 | 3525 | 2023 | 882 | 38 | 166 | 1383.33 | 85 | 5468 | 0 | 638 | 1441.5 | 0 | 0 | 12 | 108
19:30 | 3477 | 1998 | 892 | 38 | 156 | 1427.64 | 107 | 5563 | 0 | 617 | 1791.5 | 0 | 0 | 15 | 267
20:00 | 3353 | 1919 | 892 | 38 | 152 | 1383.56 | 97 | 5591 | 0 | 649 | 1783.5 | 0 | 0 | 21 | 376
20:30 | 3355.5 | 1901.5 | 892 | 38 | 155 | 1371.29 | 98 | 5614 | 0 | 656 | 1797.18 | 0 | 0 | 18 | 462.5
21:00 | 3358 | 1884 | 892 | 38 | 158 | 1359.02 | 99 | 5637 | 0 | 663 | 1810.86 | 0 | 0 | 15 | 549
21:30 | 3366 | 1883.75 | 892 | 38 | 158 | 1329.885 | 99 | 5637 | 0 | 655.5 | 1796.36 | 0 | 0 | 12 | 545.5
22:00 | 3374 | 1883.5 | 892 | 38 | 158 | 1300.75 | 99 | 5637 | 0 | 648 | 1781.86 | 0 | 0 | 9 | 542
22:30 | 3391.5 | 1853.75 | 892 | 38 | 158 | 1393.39 | 99.5 | 5632 | 0 | 630 | 1752.18 | 50 | 0 | 15.5 | 570
23:00 | 3409 | 1824 | 892 | 38 | 158 | 1486.03 | 100 | 5627 | 0 | 612 | 1722.5 | 100 | 0 | 22 | 598
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 29-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 134 | 43 | 496 | 99 | 1628 | 544 | Ishurdi-Ghorashal Ckt-1 | Export | 3327054.54
1:00 | 117 | 34 | 464 | 136 | 1660 | 452
2:00 | 121 | 33 | 476 | 140 | 1690 | 468 |  | Import | 0
3:00 | 135 | 25 | 520 | 160 | 1746 | 438
4:00 | 133 | 0 | 612 | 174 | 1710 | 400 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 138 | -1 | 550 | 192 | 1772 | 400
6:00 | 141 | -1 | 620 | 150 | 1806 | 388 |  | Import | 0
7:00 | 145 | -5 | 610 | 140 | 1782 | 372
8:00 | 162 | 16 | 620 | 160 | 1854 | 470 | Sirajganj-Sreepur Ckt-1 | Export | 3244000
9:00 | 175 | 28 | 646 | 182 | 1930 | 532
10:00 | 181 | 34 | 636 | 186 | 1884 | 604 |  | Import | 0
11:00 | 177 | 37 | 624 | 220 | 1698 | 624
12:00 | 143 | 22 | 548 | 220 | 1480 | 556 | Sirajganj-Sreepur Ckt-2 | Export | 3249000
13:00 | 147 | 20 | 540 | 174 | 1442 | 514
14:00 | 157 | 22 | 516 | 170 | 1506 | 508 |  | Import | 0
15:00 | 128 | 50 | 524 | 196 | 1588 | 568
16:00 | 128 | 50 | 520 | 200 | 1724 | 578 | Gopalganj-Aminbazar Ckt-1 | Export | 19660000
17:00 | 124 | 52 | 506 | 184 | 1608 | 558
18:00 | 110 | 49 | 470 | 190 | 1380 | 524 |  | Import | 0
18:30 | 131 | 35 | 504 | 182 | 1432 | 490
19:00 | 155 | 35 | 484 | 204 | 1565 | 462 | Gopalganj-Aminbazar Ckt-2 | Export | 19690000
19:30 | 119 | 8 | 452 | 180 | 1424 | 338
20:00 | 125 | 14 | 456 | 188 | 1512 | 378 |  | Import | 0
21:00 | 126 | 20 | 462 | 186 | 1516 | 430
22:00 | 118 | 8 | 460 | 180 | 1434 | 372 |  | Total Export | 49170054.54
23:00 | 133 | 4 | 520 | 188 | 1570 | 370 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 29-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 366 | 18:00 | 349 | 11:00 | Madunaghat | 389 | 02:00 | 380 | 12:00
Amtali | 407 | 18:00 | 400 | 19:30 | Meghnaghat | 370 | 01:00 | 353 | 11:00
Ashuganj | 398 | 1:00 | 379 | 11:00 | Payra | 408 | 17:00 | 403 | 23:00
Bhulta | 387 | 01:00 | 368 | 11:00 | Rahanpur | 401 | 18:00 | 390 | 23:00
Bibiana | 388 | 02:00 | 378 | 11:00 | Rampal | 386 | 18:00 | 369 | 11:00
BIPTC | 408 | 17:00 | 391 | 13:00
Bogura | 384 | 18:00 | 371 | 23:00
Gopalganj | 382 | 18:00 | 368 | 09:00
Kaliakoir | 360 | 18:00 | 341 | 11:00
Korerhat | 388 | 01:00 | 373 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 18:00 | 209 | 11:00 | Ishurdi | 233 | 18:00 | 208 | 07:00
AKSML | 226 | 01:00 | 217 | 12:00 | Jhenaidah | 220 | 18:00 | 197 | 23:00
Aminbazar | 224 | 02:00 | 210 | 11:00 | Kachua | 221 | 18:30 | 212 | 11:00
Ashuganj | 223 | 01:00 | 214 | 11:00 | Kaliakoir | 222 | 01:00 | 208 | 11:00
Ashuganj-400 | 223 | 01:00 | 214 | 11:00 | Keranigonj | 221 | 01:00 | 207 | 11:00
Baghabari | 230 | 18:00 | 218 | 12:00 | Khulna(S) | 219 | 18:00 | 201 | 07:00
Barapukuria | 225 | 06:00 | 217 | 12:00 | Korerhat | 223 | 01:00 | 212 | 11:00
Barapukuria-230 | 225 | 06:00 | 217 | 12:00 | Madunaghat | 227 | 01:00 | 220 | 12:00
Barishal | 222 | 18:00 | 213 | 19:30 | Madunaghat-400 | 229 | 02:00 | 223 | 12:00
Bheramara | 234 | 18:00 | 207 | 07:00 | Maniknagar | 225 | 03:00 | 207 | 11:00
Bhulta | 222 | 02:00 | 208 | 11:00 | Meghnaghat | 228 | 06:00 | 215 | 10:00
Bibiana | 224 | 01:00 | 218 | 11:00 | Meghnaghat-400 | 224 | 01:00 | 212 | 11:00
BIPTC | 234 | 18:00 | 206 | 07:00 | Mirsorai | 223 | 01:00 | 216 | 11:00
Bogura | 238 | 18:00 | 230 | 07:00 | Naogaon | 226 | 18:00 | 206 | 23:00
Bogura-400 | 239 | 18:00 | 230 | 12:00 | Purbasadipur | 226 | 06:00 | 215 | 12:00
Borhanuddin | 226 | 17:00 | 222 | 12:00 | Rajshahi | 233 | 18:00 | 205 | 12:00
BSRM | 220 | 01:00 | 212 | 11:00 | Rampal | 219 | 18:00 | 204 | 19:30
Charfasson | 229 | 06:00 | 221 | 19:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 220 | 09:00 | 211 | 16:00 | Rampura | 222 | 06:00 | 207 | 11:00
Cumilla(N) | 220 | 18:00 | 210 | 11:00 | Shikalbaha | 227 | 01:00 | 221 | 12:00
Faridpur | 217 | 18:00 | 207 | 19:30 | Shyampur | 222 | 01:00 | 209 | 11:00
Fenchuganj | 227 | 02:00 | 221 | 19:00 | Siddhirganj | 223 | 05:00 | 215 | 08:00
Feni | 219 | 01:00 | 211 | 11:00 | Sirajgonj | 237 | 14:00 | 224 | 02:00
Ghorashal | 225 | 07:00 | 220 | 00:00 | Sreepur | 223 | 01:00 | 209 | 12:00
Ghorashal-230 | 211 | 02:00 | 193 | 11:00 | Tongi | 214 | 04:00 | 197 | 11:00
Gopalganj | 218 | 18:00 | 209 | 19:00
GPH | 225 | 01:00 | 217 | 11:00
Haripur | 223 | 06:00 | 209 | 11:00
Hasnabad | 221 | 01:00 | 209 | 10:00
Hathazari | 224 | 04:00 | 218 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 22:00 | 123 | 11:00 | Madunaghat | 132 | 01:00 | 127 | 12:00
Agargaon | 131 | 03:00 | 120 | 11:00 | Magura | 132 | 18:00 | 105 | 07:00
Agrabad | 130 | 00:00 | 124 | 12:00 | Mahasthangarh | 134 | 17:00 | 128 | 19:00
AKS | 128 | 05:00 | 124 | 12:00 | Maijdee | 123 | 18:30 | 118 | 11:00
Aminbazar | 128 | 02:00 | 117 | 11:00 | Manikganj | 131 | 18:00 | 120 | 11:00
Amnura | 136 | 18:00 | 118 | 12:00 | Maniknagar | 129 | 02:00 | 119 | 11:00
Ashuganj | 132 | 01:00 | 127 | 11:00 | Matarbari | 118 | 00:00 | 106 | 19:00
Ashuganj-230 | 132 | 01:00 | 127 | 11:00 | Matuail | 129 | 02:00 | 120 | 12:00
Bagerhat | 123 | 18:00 | 106 | 23:00 | Metrorail_Motijheel | 129 | 02:00 | 119 | 03:00
Bajitpur | 125 | 15:00 | 117 | 12:00 | Metrorail_Uttara | 129 | 03:00 | 115 | 11:00
Bakerganj | 133 | 17:00 | 125 | 00:00 | Millgate | 131 | 02:00 | 116 | 11:00
Bakulia | 132 | 00:00 | 125 | 10:00 | Mirpur | 128 | 18:00 | 117 | 11:00
Banani | 134 | 18:30 | 120 | 11:00 | Mirzapur | 131 | 13:00 | 121 | 10:00
Bangabhaban | 131 | 05:00 | 118 | 12:00 | Mithapukur | 133 | 08:00 | 126 | 19:30
Barapukuria | 138 | 06:00 | 128 | 12:00 | MI_Cement | 130 | 01:00 | 119 | 11:00
Barguna | 132 | 17:00 | 122 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 128 | 00:00 | 122 | 11:00 | Mogbazar | 136 | 02:00 | 123 | 11:00
Barishal-230 | 128 | 01:00 | 122 | 19:30 | Mongla | 124 | 18:00 | 107 | 19:30
Baroaulia | 131 | 04:00 | 126 | 13:00 | Motijheel | 131 | 05:00 | 118 | 12:00
Baroirhat | 128 | 06:00 | 123 | 11:00 | Muktagacha | 135 | 13:00 | 113 | 00:00
Bashundhara | 134 | 02:00 | 117 | 10:00 | Munshiganj | 128 | 06:00 | 120 | 11:00
BashundharaCement | 129 | 05:00 | 121 | 10:00 | Muradnagar | 123 | 01:00 | 116 | 11:00
Beanibazar | 122 | 01:00 | 116 | 19:00 | Mymensingh | 135 | 12:00 | 108 | 12:00
Benapole | 127 | 18:00 | 108 | 23:00 | Nabinagar | 126 | 02:00 | 114 | 11:00
Bhaluka | 129 | 01:00 | 118 | 12:00 | Naogaon | 137 | 18:00 | 124 | 23:00
Bhandaria | 124 | 01:00 | 102 | 23:00 | Narail | 131 | 18:00 | 104 | 07:00
Bhangura | 133 | 18:00 | 124 | 12:00 | Narinda | 129 | 02:00 | 119 | 11:00
Bheramara | 137 | 18:00 | 120 | 07:00 | Narshingdi | 124 | 01:00 | 114 | 12:00
Bheramara(GK) | 136 | 18:00 | 119 | 07:00 | Natore | 134 | 18:00 | 120 | 07:00
Bhulta | 125 | 13:00 | 118 | 11:00 | Nawabganj | 133 | 01:00 | 124 | 11:00
Bog-Sherpur | 135 | 18:00 | 127 | 07:00 | Netrakona | 119 | 01:00 | 103 | 19:00
Bogura | 138 | 18:00 | 130 | 07:00 | New | 130 | 18:00 | 118 | 11:00
Bogura-230 | 137 | 18:00 | 131 | 07:00 | Niamatpur | 132 | 15:00 | 126 | 23:00
Brahmanbaria | 125 | 01:00 | 118 | 12:00 | Noapara | 129 | 18:00 | 113 | 19:30
Cantonment | 130 | 05:00 | 119 | 11:00 | Pabna | 134 | 18:00 | 120 | 07:00
Chandina | 126 | 01:00 | 118 | 12:00 | Palashbari | 131 | 18:00 | 124 | 00:00
Chandpur | 127 | 18:30 | 120 | 11:00 | Panchagarh | 142 | 04:00 | 128 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 132 | 00:00 | 128 | 16:00 | Patiya | 130 | 00:00 | 123 | 12:00
Chapai | 132 | 13:00 | 129 | 09:00 | Patuakhali | 134 | 18:30 | 124 | 23:00
Charsaidpur | 129 | 18:30 | 120 | 12:00 | Payra | 134 | 18:30 | 129 | 23:00
Chauddagram | 125 | 01:00 | 120 | 11:00 | PHP | 127 | 18:30 | 122 | 16:00
Chhatak | 122 | 01:00 | 113 | 19:00 | Postogola | 131 | 03:00 | 121 | 11:00
Chowmuhani | 123 | 18:30 | 119 | 19:30 | Pubail | 125 | 04:00 | 113 | 12:00
Chuadanga | 129 | 18:00 | 108 | 23:00 | Purbachal | 134 | 18:00 | 122 | 11:00
Coxsbazar | 118 | 06:00 | 109 | 19:00 | Purbasadipur | 138 | 06:00 | 129 | 12:00
Cumilla(N) | 125 | 01:00 | 121 | 10:00 | Rahanpur | 134 | 18:00 | 129 | 23:00
Cumilla(S) | 131 | 05:00 | 121 | 10:00 | Rahanpur-400 | 134 | 15:00 | 130 | 05:00
Daganbhuiyan | 125 | 18:00 | 119 | 11:00 | Rahim | 129 | 02:00 | 121 | 12:00
Daudkandi | 122 | 01:00 | 114 | 10:00 | Rajbari | 122 | 15:00 | 116 | 19:30
DhakaUniversity | 134 | 18:30 | 123 | 11:00 | Rajendrapur | 128 | 14:00 | 118 | 12:00
Dhamrai | 127 | 18:00 | 116 | 11:00 | Rajshahi | 131 | 18:00 | 116 | 07:00
Dhanmondi | 135 | 04:00 | 122 | 11:00 | Rajshahi-230 | 134 | 18:00 | 118 | 12:00
Dohazari | 127 | 00:00 | 120 | 19:00 | Ramganj | 122 | 18:30 | 116 | 16:00
Faridpur | 125 | 18:00 | 120 | 10:00 | Rampur | 130 | 06:00 | 123 | 12:00
Fatullah | 133 | 18:30 | 120 | 11:00 | Rampura | 134 | 03:00 | 122 | 11:00
Fenchuganj | 129 | 01:00 | 124 | 19:00 | Rangamati | 132 | 03:00 | 127 | 16:00
Feni | 127 | 02:00 | 120 | 11:00 | Rangpur | 134 | 05:00 | 124 | 19:30
Feni-230 | 126 | 01:00 | 121 | 11:00 | Ruppur | 134 | 02:00 | 121 | 07:00
Ghatail | 133 | 13:00 | 114 | 00:00 | Saidpur | 138 | 06:00 | 127 | 19:30
Ghorashal | 124 | 18:30 | 117 | 10:00 | Santhia | 134 | 18:00 | 123 | 06:00
Goalpara | 131 | 18:00 | 116 | 07:00 | Satkhira | 126 | 18:00 | 108 | 23:00
Gollamari | 131 | 18:00 | 117 | 19:30 | Satmasjid | 138 | 06:00 | 121 | 11:00
Gopalganj | 128 | 18:00 | 117 | 19:30 | Savar | 128 | 18:00 | 114 | 11:00
Gopalganj-400 | 129 | 18:00 | 123 | 11:00 | SevenRings | 126 | 01:00 | 115 | 12:00
Gulshan | 134 | 18:00 | 123 | 11:00 | ShahCement | 129 | 18:30 | 120 | 12:00
Halishahar | 131 | 00:00 | 123 | 16:00 | Shahjadpur | 135 | 18:00 | 128 | 07:00
Haripur | 130 | 06:00 | 121 | 11:00 | Shahjibazar | 126 | 02:00 | 120 | 12:00
HaripurSBU | 130 | 18:30 | 121 | 11:00 | Shahmirpur | 130 | 00:00 | 124 | 16:00
Hasnabad | 130 | 04:00 | 123 | 10:00 | Shariatpur | 127 | 18:00 | 118 | 19:30
Hathazari | 131 | 00:00 | 127 | 12:00 | Sherpur | 138 | 12:00 | 108 | 19:00
Hatirjheel | 135 | 06:00 | 123 | 11:00 | Shikalbaha | 123 | 02:00 | 117 | 12:00
Ishurdi | 137 | 18:00 | 122 | 07:00 | Shikalbaha-230 | 131 | 01:00 | 126 | 16:00
Jaldhaka | 137 | 06:00 | 125 | 19:30 | Shitalakhya | 130 | 01:00 | 119 | 11:00
Jamalpur | 138 | 12:00 | 113 | 00:00 | Sholosohor | 130 | 01:00 | 126 | 12:00
Jashore | 128 | 18:00 | 110 | 19:30 | Shomvuganj | 122 | 14:00 | 112 | 08:00
Jhenaidah | 134 | 18:00 | 113 | 12:00 | Shyampur | 132 | 18:00 | 124 | 11:00
Jhenaidah-230 | 132 | 18:00 | 117 | 23:00 | Shyampur-230 | 135 | 16:00 | 121 | 11:00
Joydebpur | 118 | 01:00 | 110 | 12:00 | Siddhirganj | 130 | 06:00 | 122 | 11:00
Joypurhat | 134 | 18:00 | 124 | 05:00 | Sirajganj | 131 | 18:00 | 123 | 07:00
Juldah | 131 | 00:00 | 125 | 12:00 | Sitakunda | 132 | 04:00 | 126 | 16:00
Kabirpur | 135 | 18:00 | 113 | 11:00 | Sonargaon | 127 | 06:00 | 118 | 12:00
Kachua | 126 | 18:30 | 120 | 10:00 | Sreemongol | 125 | 01:00 | 119 | 19:00
Kaliakoir | 134 | 18:00 | 121 | 11:00 | Sreepur | 131 | 01:00 | 121 | 12:00
Kaliganj | 132 | 18:00 | 116 | 23:00 | Srinagar | 133 | 06:00 | 124 | 11:00
Kallyanpur | 128 | 18:00 | 117 | 11:00 | SSM | 135 | 00:00 | 131 | 17:00
Kalurghat | 132 | 00:00 | 127 | 16:00 | Sunamganj | 120 | 01:00 | 109 | 19:00
Kamrangirchar | 134 | 01:00 | 114 | 11:00 | Sylhet | 125 | 02:00 | 119 | 19:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet_(South) | 125 | 01:00 | 119 | 19:00
Kasba | 123 | 02:00 | 116 | 11:00 | Tangail | 130 | 13:00 | 116 | 08:00
Kazla | 130 | 06:00 | 118 | 12:00 | Taraganj | 135 | 07:00 | 126 | 19:30
Keranigonj | 134 | 01:00 | 125 | 11:00 | Tasnim | 127 | 03:00 | 119 | 11:00
Khagrachori | 130 | 01:00 | 126 | 21:00 | Thakurgaon | 141 | 04:00 | 127 | 12:00
Khulna | 130 | 18:00 | 115 | 23:00 | TK | 132 | 01:00 | 128 | 11:00
Khulna(S) | 130 | 18:00 | 117 | 23:00 | Tongi | 133 | 04:00 | 123 | 09:00
Khulshi | 130 | 05:00 | 122 | 12:00 | Ullahpara | 133 | 18:00 | 124 | 19:30
Kishoreganj | 124 | 14:00 | 114 | 12:00 | Ullon | 134 | 05:00 | 122 | 11:00
Kodda | 134 | 18:00 | 122 | 10:00 | Uttara | 131 | 03:00 | 114 | 11:00
Korerhat | 129 | 01:00 | 125 | 11:00 | UttaraNew | 129 | 03:00 | 115 | 11:00
KSRM | 132 | 07:00 | 125 | 16:00 | Zigatola | 134 | 05:00 | 124 | 11:00
Kulaura | 128 | 01:00 | 122 | 19:00
Kurigram | 134 | 07:00 | 120 | 19:30
Kushtia | 135 | 18:00 | 115 | 07:00
Laksam | 125 | 18:30 | 120 | 00:00
Lakshmipur | 123 | 18:30 | 117 | 16:00
Lalbag | 132 | 18:00 | 124 | 11:00
Lalmonirhat | 132 | 07:00 | 121 | 19:30
Madanganj | 129 | 05:00 | 121 | 10:00
Madaripur | 128 | 02:00 | 120 | 19:30
Madartek | 134 | 06:00 | 123 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division