## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-06-2026 | during | 01-07-2026 | during | 01-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 393 | 330 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 168 | 168 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 12 | 15 | 55 | 55 | 30 | 30 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 324 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 112 | 147 | 149.36 | 149.36 | 15 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16.5 | 16.5 | 33 | 33 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 33 | 52.19 | 52.19 | 8 | 24 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 146 | 195 | 300 | 300 | 146 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 133 | 149 | 149 | 70 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 35 | 70 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 90 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 15 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 480 | 445 | 584 | 584 | 526 | 526 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 515 | 460 | 583 | 583 | 525 | 525 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 123 | 142 | 160 | 160 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2342.5 | 2578.5 | 5822.22 | 5792.22 | 2536 | 2937
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 13 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 1 | 6 | 50 | 50 | 6 | 6 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 99 | 97 | 99 | 99 | 99 | 99 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 17 | 17 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 8 | 8 | 8 | 8 | 8 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 20 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 7 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 30 | 78 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0.73 | 0 | 1.83 | 0 | 1.83 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 49 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 54.36 | 54.36 | 54.36 | 0 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 110 | 110 | 0 | 0 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 31 | 92 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1171 | 1170 | 1224 | 1224 | 1224 | 1224 | Coal Shortage Due to BPDB Payment Default
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 9 | 0 | 20 | 32 | 20 | 32 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1135 | 1135 | 1150 | 1150 | 1135 | 1135 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2763.73 | 3037.86 | 3801.69 | 3876.86 | 2905.83 | 3077
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 200 | 215 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 310 | 290 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 250 | 230 | 342.01 | 342.01 | 342.01 | 342.01 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 300 | 220 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 33 | 41.65 | 41.65 | 41.65 | 41.65 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 20 | 0 | 52.82 | 52.82 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 53 | 143 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 137 | 142 | 163 | 163 | 140 | 140 | Low gas pressure
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 24 | 51 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 144 | 144 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 20.83 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 47 | 87 | 114 | 114 | 17 | 17 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 18 | 8 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 14 | 89 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1694 | 1723 | 2713.77 | 2656.44 | 1743.92 | 1911.92
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-06-2026 | during | 01-07-2026 | during | 01-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 21.28 | 0 | 15 | 0 | 15 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.1 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 67 | 106 | 70 | 110 | 70 | 110 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 78 | 60 | 80 | 60 | 80 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 35.38 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 182.76 | 201 | 481.7 | 476.5 | 195.2 | 207
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 29 | 29 | 28 | 28 | 29 | 29 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 141 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 143 | 143 | 145 | 145 | 145 | 145 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 25 | 30 | 0 | 0 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 83 | 86 | 86 | 52 | 52 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 102 | 102 | 102 | 102 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 257 | 258 | 300 | 300 | 300 | 300 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1107 | 1115 | 1190 | 1190 | 1129 | 1129
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 903 | 904 | 1000 | 1000 | 550 | 1000 | Block-2 under maint.
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 12.15 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 900 | 866 | 900 | 900 | 900 | 900 | Machine Problem
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1853.15 | 1823 | 3200 | 3120 | 2143 | 2513
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 850 | 936 | 1050 | 1050 | 1050 | 1050 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 65 | 65 | 65 | 65 | 65 | 65 | GT-1 & ST under maint
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1060 | 1170 | 1244 | 1244 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 28 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 180 | 247 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.19 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2375.19 | 2698 | 3147 | 3146 | 2860 | 2859
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 50.15 | 0 | 40 | 0 | 40 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 18 | 30 | 30 | 0 | 10 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 18 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 174 | 160 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 172 | 157 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 157 | 220 | 220 | 158 | 158 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 384 | 356 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 18 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 102 | 102 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 72 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 55 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 2.53 | 0 | 0 | 0 | 0 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1242.2 | 1420.78 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 29.69 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 90 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2144.57 | 2563.78 | 3244.12 | 3043.12 | 2730.54 | 2701.54
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 38 | 39 | 40 | 40 | 40 | 40 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 210 | 182 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 101 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.1 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 90 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 17 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 191 | 0 | 187.56 | 0 | 187.56 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 457.1 | 412 | 722.56 | 502 | 589.56 | 404
System Total |  |  |  |  | 28843.2 | 29323.517 | 14920 | 16152.14 | 24323.06 | 23803.14 | 16833.05 | 17739.46
Forecast Scenario (01-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15840 |  | 1222.4 |  | 17120
|  |  |  | 1:00 | 15665 |  | 959.775 |  | 16670
|  |  |  | 2:00 | 14977 |  | 1253.915 |  | 16290
|  |  |  | 3:00 | 14595 |  | 1246.275 |  | 15900
|  |  |  | 4:00 | 14266 |  | 806.02 |  | 15110
|  |  |  | 5:00 | 14047 |  | 871.915 |  | 14960
|  |  |  | 6:00 | 13657 |  | 728.665 |  | 14420
|  |  |  | 7:00 | 13767 |  | 327.565 |  | 14110
|  |  |  | 8:00 | 13970 |  | 353.35 |  | 14340
|  |  |  | 9:00 | 14075 |  | 396.325 |  | 14490
|  |  |  | 10:00 | 14401 |  | 237.795 |  | 14650
|  |  |  | 11:00 | 14472 |  | 284.59 |  | 14770
|  |  |  | 12:00 | 14920 |  | 276.95 |  | 15210
|  |  |  | 13:00 | 15146 |  | 51.57 |  | 15200
|  |  |  | 14:00 | 14880 |  | 0 |  | 14880
|  |  |  | 15:00 | 14660 |  | 0 |  | 14660
|  |  |  | 16:00 | 14703 |  | 254.985 |  | 14970
|  |  |  | 17:00 | 14424 |  | 339.98 |  | 14780
|  |  |  | 18:00 | 14145 |  | 520.475 |  | 14690
|  |  |  | 18:30 | 14650 |  | 811.75 |  | 15500
|  |  |  | 19:00 | 15376 |  | 729.62 |  | 16140
|  |  |  | 19:30 | 16152 |  | 667 |  | 16850
|  |  |  | 20:00 | 15914 |  | 856 |  | 16810
|  |  |  | 21:00 | 15809 |  | 946 |  | 16800
|  |  |  | 22:00 | 15708 |  | 1014.21 |  | 16770
|  |  |  | 23:00 | 15613 |  | 1324.585 |  | 17000
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 15210.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 667
Probable Maximum Demand at Evening Peak: |  |  | 16850.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16152.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 355.03 MKWHr. |  | 147 | 40 | 90 | 200 | 40 | 80 | 0 | 40 | 30 | 667
*** This report is generated digitally from Operation Information System (OIS) at 11:18 hrs on 01-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 30-06-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15822.61 | 415 |  | 16256.29
1:00 | 15665.14 | 334 |  | 16014.14
2:00 | 14977.15 | 433 |  | 15429.15
3:00 | 14595.42 | 402 |  | 15015.42
4:00 | 14266.3 | 370 |  | 14653.3
5:00 | 14047.18 | 350 |  | 14413.18
6:00 | 13657.97 | 266 |  | 13935.94
7:00 | 13767.53 | 197 |  | 13973.4
8:00 | 13970.36 | 175 |  | 14153.24
9:00 | 14075.57 | 165 |  | 14248
10:00 | 14401.19 | 115 |  | 14521.37
11:00 | 14472.93 | 271 |  | 14756.13
12:00 | 14920 | 438 |  | 15378
13:00 | 15146.61 | 369 |  | 15532.61
14:00 | 15049.87 | 369 |  | 15435.87
15:00 | 15094.48 | 482 |  | 15598.48
16:00 | 14703.98 | 281 |  | 14997.98
17:00 | 14424.23 | 226 |  | 14660.23
18:00 | 14145.65 | 158 |  | 14310.76
19:00 | 15376.04 | 260 |  | 15648.04
19:30 | 16152.14 | 549 |  | 16726.14
20:00 | 15914.72 | 404 |  | 16336.72
21:00 | 15809.17 | 299 |  | 16121.17
22:00 | 15708.11 | 257 |  | 15977.11
23:00 | 15824.33 | 251 |  | 16086.33
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 30-06-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3408 | 1810 | 892 | 38 | 156 | 1425.61 | 100 | 5546 | 0 | 593 | 1745 | 100 | 0 | 9 | 415 | DAILY ENERGY CURVE
00:30 | 3420 | 1828 | 897.5 | 38 | 152 | 1389.875 | 99 | 5545.5 | 0 | 602.5 | 1664.5 | 100.5 | 0 | 6.5 | 374.5 | 30-06-2026
01:00 | 3432 | 1846 | 903 | 38 | 148 | 1354.14 | 98 | 5545 | 0 | 612 | 1584 | 101 | 0 | 4 | 334
01:30 | 3440 | 1910.5 | 903.5 | 38 | 151 | 1422.645 | 97.5 | 5557 | 0 | 526.5 | 1169.5 | 100.5 | 0 | 4.5 | 383.5 | Energy Generated | 358.0682 |  | MKWHr
02:00 | 3448 | 1975 | 904 | 38 | 154 | 1491.15 | 97 | 5569 | 0 | 441 | 755 | 100 | 0 | 5 | 433 | Energy not Served | 7.287 |  | MKWHr
02:30 | 3409.5 | 1949.5 | 903.5 | 38 | 152 | 1488.785 | 97 | 5568.5 | 0 | 425 | 697 | 50 | 0 | 7.5 | 417.5 | Total Energy Requirement | 365.3552 |  | MKWHr
03:00 | 3371 | 1924 | 903 | 38 | 150 | 1486.42 | 97 | 5568 | 0 | 409 | 639 | 0 | 0 | 10 | 402
03:30 | 3401 | 1897.25 | 903 | 38 | 149.5 | 1486.61 | 97 | 5567.5 | 0 | 396 | 487.5 | 0 | 0 | 7.5 | 386
04:00 | 3431 | 1870.5 | 903 | 38 | 149 | 1486.8 | 97 | 5567 | 0 | 383 | 336 | 0 | 0 | 5 | 370
04:30 | 3430 | 1839 | 903 | 38 | 144.5 | 1483.24 | 97 | 5542.5 | 0 | 383 | 292 | 0 | 0 | 4.5 | 360
05:00 | 3429 | 1807.5 | 903 | 38 | 140 | 1479.68 | 97 | 5518 | 0 | 383 | 248 | 0 | 0 | 4 | 350
05:30 | 3447 | 1862.25 | 903.5 | 38 | 131 | 1432.855 | 97 | 5348.5 | 16.47 | 365 | 207 | 0 | 0 | 4 | 308
06:00 | 3465 | 1917 | 904 | 38 | 122 | 1386.03 | 97 | 5179 | 32.94 | 347 | 166 | 0 | 0 | 4 | 266
06:30 | 3405 | 1889 | 903.5 | 38 | 127 | 1400.06 | 97.5 | 5249 | 68.19 | 347 | 184.5 | 0 | 0 | 4 | 231.5
07:00 | 3345 | 1861 | 903 | 38 | 132 | 1414.09 | 98 | 5319 | 103.44 | 347 | 203 | 0 | 0 | 4 | 197
07:30 | 3373 | 1840 | 903 | 38 | 134 | 1402.4 | 98.5 | 5327.5 | 158.545 | 355.5 | 233 | 0 | 0 | 5.5 | 186
08:00 | 3401 | 1819 | 903 | 38 | 136 | 1390.71 | 99 | 5336 | 213.65 | 364 | 263 | 0 | 0 | 7 | 175
08:30 | 3394.5 | 1794 | 903 | 38 | 137 | 1358.56 | 99 | 5359.5 | 285.905 | 367.5 | 276.5 | 0 | 0 | 9.5 | 170
09:00 | 3388 | 1769 | 903 | 38 | 138 | 1326.41 | 99 | 5383 | 358.16 | 371 | 290 | 0 | 0 | 12 | 165
09:30 | 3389.5 | 1830 | 903 | 38 | 141 | 1342.705 | 99.5 | 5415.5 | 405.175 | 363 | 298.5 | 0 | 0 | 12.5 | 140
10:00 | 3391 | 1891 | 903 | 38 | 144 | 1359 | 100 | 5448 | 452.19 | 355 | 307 | 0 | 0 | 13 | 115
10:30 | 3371 | 1830.75 | 903 | 38 | 146 | 1314 | 100 | 5479 | 481.81 | 360 | 401.5 | 0 | 0 | 12 | 193
11:00 | 3351 | 1770.5 | 903 | 38 | 148 | 1269 | 100 | 5510 | 511.43 | 365 | 496 | 0 | 0 | 11 | 271
11:30 | 3422 | 1830 | 903 | 38 | 146 | 1255.6 | 99.5 | 5527 | 533.865 | 344 | 587.5 | 0 | 0 | 10 | 354.5
12:00 | 3493 | 1889.5 | 903 | 38 | 144 | 1242.2 | 99 | 5544 | 556.3 | 323 | 679 | 0 | 0 | 9 | 438
12:30 | 3548.5 | 1891 | 903 | 38 | 150 | 1299.83 | 98 | 5533 | 533.475 | 331.5 | 700.5 | 0 | 0 | 6.5 | 403.5
13:00 | 3604 | 1892.5 | 903 | 38 | 156 | 1357.46 | 97 | 5522 | 510.65 | 340 | 722 | 0 | 0 | 4 | 369
13:30 | 3579.5 | 1849.5 | 903 | 38 | 153 | 1413.415 | 96 | 5509 | 478.825 | 348 | 722.5 | 0 | 0 | 7.5 | 369
14:00 | 3555 | 1806.5 | 903 | 38 | 150 | 1469.37 | 95 | 5496 | 447 | 356 | 723 | 0 | 0 | 11 | 369
14:30 | 3581 | 1819.5 | 902.5 | 38 | 149 | 1469.52 | 94 | 5513.5 | 443.655 | 372.5 | 674.5 | 0 | 0 | 14.5 | 425.5
15:00 | 3607 | 1832.5 | 902 | 38 | 148 | 1469.67 | 93 | 5531 | 440.31 | 389 | 626 | 0 | 0 | 18 | 482
15:30 | 3583 | 1805.75 | 902.5 | 38 | 145 | 1442.18 | 92.5 | 5494 | 341.8 | 389 | 647.5 | 0 | 0 | 18 | 381.5
16:00 | 3559 | 1779 | 903 | 38 | 142 | 1414.69 | 92 | 5457 | 243.29 | 389 | 669 | 0 | 0 | 18 | 281
16:30 | 3529.5 | 1755.5 | 903 | 38 | 146 | 1381.805 | 93 | 5424 | 194.3 | 389 | 692.5 | 0 | 0 | 17.5 | 253.5
17:00 | 3500 | 1732 | 903 | 38 | 150 | 1348.92 | 94 | 5391 | 145.31 | 389 | 716 | 0 | 0 | 17 | 226
17:30 | 3476 | 1682 | 903 | 38 | 146 | 1305.835 | 94.5 | 5356.5 | 89.105 | 397 | 788.5 | 0 | 0 | 8.5 | 192
18:00 | 3452 | 1632 | 903 | 38 | 142 | 1262.75 | 95 | 5322 | 32.9 | 405 | 861 | 0 | 0 | 0 | 158
18:30 | 3472.5 | 1682.75 | 903 | 38 | 153 | 1300.395 | 96 | 5443 | 16.45 | 538 | 1117.75 | 0 | 0 | 0 | 209
19:00 | 3493 | 1733.5 | 903 | 38 | 164 | 1338.04 | 97 | 5564 | 0 | 671 | 1374.5 | 0 | 0 | 0 | 260
19:30 | 3456 | 1794.5 | 904 | 38 | 144 | 1420.78 | 97 | 5745 | 0 | 687 | 1865.86 | 0 | 0 | 0 | 549
20:00 | 3475 | 1738.5 | 903 | 38 | 152 | 1338.36 | 98 | 5637 | 0 | 694 | 1840.86 | 0 | 0 | 0 | 404
20:30 | 3489.5 | 1716 | 903 | 38 | 151 | 1401.585 | 98 | 5811.5 | 0 | 646.5 | 1556.86 | 50 | 0 | 0 | 351.5
21:00 | 3504 | 1693.5 | 903 | 38 | 150 | 1464.81 | 98 | 5986 | 0 | 599 | 1272.86 | 100 | 0 | 0 | 299
21:30 | 3513 | 1737 | 903 | 38 | 153 | 1437.96 | 98.5 | 5952.5 | 0 | 583 | 1240.68 | 100 | 0 | 2 | 278
22:00 | 3522 | 1780.5 | 903 | 38 | 156 | 1411.11 | 99 | 5919 | 0 | 567 | 1208.5 | 100 | 0 | 4 | 257
22:30 | 3548.5 | 1873 | 903.5 | 38 | 156 | 1405.47 | 99.5 | 5934.5 | 0 | 553 | 1152.25 | 100 | 0 | 2.5 | 254
23:00 | 3575 | 1965.5 | 904 | 38 | 156 | 1399.83 | 100 | 5950 | 0 | 539 | 1096 | 100 | 0 | 1 | 251
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 30-06-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 128 | 3 | 492 | 172 | 1518 | 406 | Ishurdi-Ghorashal Ckt-1 | Export | 3664945.51
1:00 | 127 | 3 | 494 | 174 | 1516 | 384
2:00 | 126 | 1 | 520 | 164 | 1582 | 398 |  | Import | 0
3:00 | 123 | -1 | 526 | 172 | 1560 | 382
4:00 | 132 | 4 | 552 | 168 | 1626 | 388 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 138 | 9 | 552 | 164 | 1608 | 422
6:00 | 144 | 20 | 526 | 160 | 1498 | 460 |  | Import | 0
7:00 | 134 | 16 | 488 | 144 | 1548 | 392
8:00 | 144 | 23 | 540 | 160 | 1702 | 530 | Sirajganj-Sreepur Ckt-1 | Export | 3225000
9:00 | 175 | 46 | 592 | 192 | 1904 | 662
10:00 | 194 | 56 | 644 | 206 | 1914 | 728 |  | Import | 0
11:00 | 179 | 52 | 578 | 192 | 1806 | 734
12:00 | 163 | 37 | 550 | 200 | 1746 | 726 | Sirajganj-Sreepur Ckt-2 | Export | 3236000
13:00 | 154 | 24 | 570 | 208 | 1700 | 660
14:00 | 152 | 19 | 560 | 194 | 1744 | 686 |  | Import | 0
15:00 | 164 | 26 | 600 | 200 | 1724 | 660
16:00 | 160 | 24 | 610 | 214 | 1716 | 706 | Gopalganj-Aminbazar Ckt-1 | Export | 20220000
17:00 | 172 | 41 | 560 | 184 | 1698 | 740
18:00 | 162 | 36 | 560 | 184 | 1720 | 680 |  | Import | 0
18:30 | 168 | 40 | 550 | 190 | 1670 | 680
19:00 | 163 | 40 | 610 | 240 | 1648 | 624 | Gopalganj-Aminbazar Ckt-2 | Export | 20300000
19:30 | 126 | 7 | 490 | 172 | 1566 | 544
20:00 | 125 | 15 | 470 | 162 | 1600 | 546 |  | Import | 0
21:00 | 136 | 13 | 510 | 204 | 1850 | 574
22:00 | 135 | 12 | 490 | 190 | 1748 | 548 |  | Total Export | 50645945.51
23:00 | 129 | 4 | 470 | 194 | 1443 | 548 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 30-06-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8695 | 7127.61 | 15822.61 | DAILY GENERATION CURVE
00:30 | 8625.5 | 7118.375 | 15743.875
01:00 | 8556 | 7109.14 | 15665.14 | 30-06-2026
01:30 | 8283.5 | 7037.645 | 15321.145
02:00 | 8011 | 6966.15 | 14977.15
02:30 | 7912.5 | 6873.785 | 14786.285
03:00 | 7814 | 6781.42 | 14595.42
03:30 | 7663.25 | 6767.61 | 14430.86
04:00 | 7512.5 | 6753.8 | 14266.3
04:30 | 7436.5 | 6720.24 | 14156.74
05:00 | 7360.5 | 6686.68 | 14047.18
05:30 | 7289.82 | 6562.755 | 13852.575
06:00 | 7219.14 | 6438.83 | 13657.97
06:30 | 7245.33 | 6467.42 | 13712.75
07:00 | 7271.52 | 6496.01 | 13767.53
07:30 | 7323.29 | 6545.655 | 13868.945
08:00 | 7375.06 | 6595.3 | 13970.36
08:30 | 7400.09 | 6622.875 | 14022.965
09:00 | 7425.12 | 6650.45 | 14075.57
09:30 | 7484.135 | 6754.245 | 14238.38
10:00 | 7543.15 | 6858.04 | 14401.19
10:30 | 7611.415 | 6825.645 | 14437.06
11:00 | 7679.68 | 6793.25 | 14472.93
11:30 | 7884.835 | 6811.63 | 14696.465
12:00 | 8089.99 | 6830.01 | 14920
12:30 | 8136.09 | 6897.215 | 15033.305
13:00 | 8182.19 | 6964.42 | 15146.61
13:30 | 8132.95 | 6965.29 | 15098.24
14:00 | 8083.71 | 6966.16 | 15049.87
14:30 | 8070.115 | 7002.06 | 15072.175
15:00 | 8056.52 | 7037.96 | 15094.48
15:30 | 7971.965 | 6927.265 | 14899.23
16:00 | 7887.41 | 6816.57 | 14703.98
16:30 | 7849.895 | 6714.21 | 14564.105
17:00 | 7812.38 | 6611.85 | 14424.23
17:30 | 7777.62 | 6507.32 | 14284.94
18:00 | 7742.86 | 6402.79 | 14145.65
18:30 | 8032.93 | 6727.915 | 14760.845
19:00 | 8323 | 7053.04 | 15376.04
19:30 | 8655.36 | 7496.78 | 16152.14
20:00 | 8589.36 | 7325.36 | 15914.72
20:30 | 8374.86 | 7487.085 | 15861.945 |  | Executive Engineer
21:00 | 8160.36 | 7648.81 | 15809.17 |  | Network Operation Division
21:30 | 8137.68 | 7620.96 | 15758.64
22:00 | 8115 | 7593.11 | 15708.11
22:30 | 8151.75 | 7614.47 | 15766.22
23:00 | 8188.5 | 7635.83 | 15824.33

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 30-06-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14920 | MW | 12:00 Hr. | Energy Generated |  |  | 358.0682 |  | MKWHr.
| Day Peak Demand |  |  | 15378 | MW | 12:00 Hr. | Energy Unserverd |  |  | 7.287 |  | MKWHr.
| Evening Peak Generation |  |  | 16152.14 | MW | 19:30 Hr. | Energy Demand |  |  | 365.3552 |  | MKWHr.
| Evening Peak Demand |  |  | 16726.14 | MW | 19:30 Hr. | Maximum Temperature |  |  | 34.4 |  | °C
| Minimum Generation of the Day |  |  | 13657.97 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 933.78 |  | MMCFD
| Maximum Generation of the Day |  |  | 16152.14 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.3689 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.7261 | 0 | 16.1164 | 0 | 0 | 0.16794 | 0 | 0 | 56.0105 | Gas | 129.2275 | Gas | 429580422.2528
| Chattogram Zone |  |  | 5.4175 | 55.0618 | 3.72 | 0 | 2.3304 | 0.078736 | 0 | 0.17328 | 66.7818 | Coal | 133.7566 | Coal | 887427009.6926
| Cumilla Zone |  |  | 31.2021 | 0 | 2.9887 | 0 | 0 | 0.39163 | 3.5146 | 0 | 38.097 | HFO | 29.5223 | HFO | 522760456.348
| Mymensingh Zone |  |  | 0 | 0 | 3.0757 | 0 | 0 | 0.41849 | 0 | 0 | 3.4942 | HSD | 0.52298 | HSD | 10564155.6
| Sylhet Zone |  |  | 26.591 | 0 | 0 | 0 | 0 | 0.080553 | 0 | 0 | 26.6715 | Hydro | 2.3304 | Hydro | 8878671.6
| Khulna Zone |  |  | 0 | 17.7455 | 0.043632 | 0.52298 | 0 | 0.24768 | 21.5389 | 0 | 40.0987 | Solar | 4.0417 | Solar | 65372190.8444
| Barishal Zone |  |  | 6.9932 | 55.3179 | 0.41784 | 0 | 0 | 0.0021 | 0 | 0 | 62.731 | Import | 58.4934 | Import | 353368746.25
| Rajshahi Zone |  |  | 19.2976 | 0 | 1.9301 | 0 | 0 | 1.1292 | 33.44 | 0 | 55.7969 | Wind | 0.17328 | Wind | 2548948.8
| Rangpur Zone |  |  | 0 | 5.6314 | 1.2298 | 0 | 0 | 1.5254 | 0 | 0 | 8.3866
| Total |  |  | 129.2275 | 133.7566 | 29.5223 | 0.52298 | 2.3304 | 4.0417 | 58.4934 | 0.17328 | 358.0682
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 429580422.2528 |  | Hydro | 8878671.6
|  |  |  | Coal | 887427009.6926 |  | Solar | 65372190.8444
|  |  |  | HFO | 522760456.348 |  | Import | 353368746.25
|  |  |  | HSD | 10564155.6 |  | Wind | 2548948.8
[5 empty] | Total: | 228,05,00,601 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.6269 | Peak Hr Flow | 904.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50645945.51 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.44 | Peak Hr Flow | 1420.78 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2182 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.5146 | Peak Hr Flow | 144.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2752 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 57.5814 | Peak Hr Flow | 2468.78 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 77 |  | 5962
|  |  |  | Chattogram |  | 0 |  | 1518
|  |  |  | Cumilla |  | 96 |  | 1557
|  |  |  | Mymensingh |  | 308 |  | 1378
|  |  |  | Sylhet |  | 14 |  | 679
|  |  |  | Khulna |  | 51 |  | 1917
|  |  |  | Barishal |  | 3 |  | 467
|  |  |  | Rajshahi |  | 0 |  | 1641
|  |  |  | Rangpur |  | 0 |  | 1052
|  |  |  | Total |  | 549 |  | 16171
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Karnaphuli Hydro PP Unit-5 |  |  | 50
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 350 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 400
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:55 | 19:34 | Korerhat 400/230/132kV S/S ATR-4(7403T) LT Project Work S/D Due to Project work
| 09:05 | 14:47 | Chauddagram-Feni 132 kV Ckt-2 Project Work S/D from Feni 132/33kV end Due to For project
work at Feni 230kv grid end and from Feni 230/132kV end Due to project work
| 09:56 | 19:33 | Korerhat 400/230/132kV S/S ATR-4(7403T) HT Project Work S/D Due to Project Work
| 12:00 |  | Day Peak Generation: 14919 MW.
| 12:22 | 13:12 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-1 Scheduled S/D
| 12:23 | 13:10 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 Scheduled S/D
| 13:13 | 14:02 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 Scheduled S/D
| 13:13 | 14:04 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-2 Scheduled S/D
| 14:54 | 15:02 | Joypurhat 132/33kV S/S Patnitola Ckt.-1 Project Work S/D Due to 132 kv circuit
demarkkation
| 15:10 | 17:28 | Gallamari- Khulna (S) 132kV Ckt-1 Project Work S/D from Gollamari 132/33kV end Due to
Due to Satkhira-Rupsha line charge for trail basis
| 15:10 |  | Gopalganj 132/33kV S/S Gallamari-1 Scheduled S/D Due to project work
| 15:11 | 17:30 | Gallamari- Khulna (S) 132kV Ckt-2 Project Work S/D from Gollamari 132/33kV end Due to
Due to Satkhira-Rupsha line charge for trail basis
| 15:19 |  | Gopalganj 132/33kV S/S Gallamari-2 Scheduled S/D Due to project work
| 15:44 |  | Potnitola 132 kV bus-1 was charged by Joypurhat ckt-1 for the first time.
| 15:47 | 17:25 | Bagerhat-Bhandaria 132 kV Ckt-1 Project Work S/D from Bagerhat 132/33kV end Due to
Project work in Bhandaria. instructions from ALDC
| 15:50 |  | 132/33 kV (50/75 MVA) transformer T-1 at Potnitola grid s/s was charged from 132 kV side
for the first time.
| 17:02 |  | Jhenaidah grid s/s 230/132 kV ATR-3 (100/150 MVA) transformer was switched ON in loaded
condition for the first time.
| 17:36 | 17:52 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Tongi 230/132/33kV end showing distance
relay Z1. ph-RY, D-14 km relays Due to N/A
|  | 18:15 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT is restored.
|  | 18:15 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT is restored.
| 19:30 |  | Evening Peak Generation: 16152 MW.
| 19:31 | 19:40 | Barishal-Bhandaria 132 kV Ckt-1 Tripped from Barishal 132/33kV end showing Instt. R | [7 empty] | 52.0MW load
|  |  | phase, Time delayed E/F, Distance relays Due to The line has broken and fallen between | [7 empty] | interrup. Barishal
|  |  | tower no122 to 123, 27.1km away from Barishal 132kV SS | [7 empty] | 132/33kV end
| 19:50 | 07:17 | Barishal-Bhandaria 132 kV Ckt-1 Forced S/D from Bhandaria 132/33kV end Due to The outage
occurred due to the sanpping of the conductor on the barishal bhandaria transmission
line. and from Barishal 132/33kV end Due to Joining the broken conductor
| 19:54 | 21:21 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Forced S/D Due to Red Hot removed works
| 19:54 | 21:21 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Forced S/D Due to Red Hot removed works
| 20:26 | 20:45 | Ramganj 132/33kV S/S Transformer -02 LT Tripped showing over current relay relays Due to | [7 empty] | 54.0MW load
|  |  | PBS 5no feeder CT brust | [7 empty] | interrup.
| 20:26 | 20:45 | Ramganj 132/33kV S/S Transformer-01 LT Tripped showing over current relay relays Due to | [7 empty] | 54.0MW load
|  |  | PBS 5 no feeder CT brust | [7 empty] | interrup.
|  | 20:40 | Nabinagar 132/33kV S/S T-1 HT is restored.
|  | 20:40 | Nabinagar 132/33kV S/S T-1 LT is restored.
| 20:51 | 22:23 | Ishurdi 230/132kV S/S 230/132 kV T-02 LT Forced S/D Due to DS-826M R-phase red hor
maintenance
| 20:51 | 22:22 | Ishurdi 230/132kV S/S 230/132 kV T-02 HT Forced S/D Due to DS-826M R-phase red hot
maintenance
| 00:01 | 00:01 | Kishoreganj-Mymensingh 132kV Ckt-2 Tripped from Shomvuganj 400/132kV end showing
Siprotec relays.
| 00:28 |  | Kishoreganj-Mymensingh 132kV Ckt-2 Forced S/D from Shomvuganj 400/132kV end.
| 06:05 |  | Patuakhali-Payra 132kV Ckt-2 Scheduled S/D from Payra 400/132/33kV end Due to High
temperature maintenance
| 07:42 |  | Goalpara 132/33kV S/S T-6 HT Tripped showing PRD Relay, Breaker Failure Relay P821, Trip
Relay relays.
| 07:42 |  | Goalpara 132/33kV S/S T-6 LT Tripped showing PRD Relay relays Due to Transformer-06 PRD
TRIP.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 30-06-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 330 | 8650800 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 11375 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 334078 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 324 | 7294140 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 247320 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 147 | 3248640 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 538481 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270099 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16.5 | 415800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 504000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 612480 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 3055069 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 1837008 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1745280 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 807840 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 167938 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 99720 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 445 | 10968636.36 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 460 | 11881350 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 142 | 3320400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2578.5 | 56010454.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 129430.8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 56295 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 108480 | Liquid fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 97 | 2330360 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5151626 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 24255 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 31628 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 299527 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 20 | 231360 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 7 | 265920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 78 | 701760 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22441 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 49 | 386400 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 315484 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 427382 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 234240 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 92 | 766527 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 63564 | Under Maintenance
55 | SS Power |  | IPP | 2*660 | 1224 | 1170 | 28167270 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 173280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1135 | 26894545.46 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 3037.86 | 66781775.26
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 215 | 5033000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7695600 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 230 | 6018000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 6171000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 821016 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 316320 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1252368 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 143 | 1057163 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 1 | 61056 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 142 | 3425644 | Low gas pressure, Plant Availability Zero
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 488160 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 144 | 3514560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 469190 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 87 | 539220 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 139440 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 703680 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 391627 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1723 | 38097044
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 135187 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 106 | 1480800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1435200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 273000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 44880 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 114840 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 201 | 3494207
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 80553 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 29 | 693000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 141 | 3366572.73 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 143 | 3252200 | STG Under Maintenance
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 649248 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1469760 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2405350 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 360864 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7612000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 258 | 6782000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1115 | 26671547.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 904 | 20626909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 43632 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 247680 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 522978 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 866 | 17745453 | machine problem
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1823 | 40098652
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 936 | 23047272 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 222240 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 65 | 1556000 | GT-1 & ST under maint
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1170 | 26859636.36 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5437160 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 28 | 195600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 247 | 5411000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2100 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2698 | 62731008.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 256608 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 290841 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 18 | 48866 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 18 | 192115 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 160 | 4102364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 157 | 3661955 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 157 | 2562445 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 356 | 8970836 | AGC+Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 18 | 98789 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 648944 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 72 | 370656 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 55 | 279936 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 30720 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1420.78 | 33439951 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 259024 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 582890 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2563.78 | 55796940
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 39 | 933381 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 182 | 4698000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 101 | 521760 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 19320.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 90 | 708053 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 158210 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1347840 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 412 | 8386564.72
Eastern Grid Total |  |  |  |  | 17438.042 | 8655.36 | 191055028.35
Western Grid Total |  |  |  |  | 11885.475 | 7496.78 | 167013165.08
National Grid Total |  |  |  |  | 29323.517 | 16152.14 | 358068193.43
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 30-06-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10649.84 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5022.8 | MW
i) Dhaka area |  |  | 5885.14 |  | MW | i) Khulna area |  |  |  | 1866 | MW
ii) Chattogram area |  |  | 1568.7 |  | MW | ii) Barishal area |  |  |  | 464 | MW
iii) Cumilla area |  |  | 1461 |  | MW | iii) Rajshahi area |  |  |  | 1640.8 | MW
iv) Mymensingh area |  |  | 1070 |  | MW | iv) Rangpur area |  |  |  | 1052 | MW
v) Sylhet area |  |  | 665 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15672.64 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 130 | 07:00 | 133 | Narshingdi | 193 | 22:00 | 199 | UttaraNew | 58 | 13:00
2 | AKSML | 157.4 | 10:00 | 68 | Hasnabad | 97 | 21:00 | 134 | Natore | 169 | 19:30 | 200 | Zigatola | 97 | 13:00
3 | Aftabnagar | 48 | 13:00 | 69 | Hathazari | 101 | 22:00 | 135 | Nawabganj | 62.4 | 00:00
4 | Agargaon | 127 | 13:00 | 70 | Hatirjheel | 42 | 11:00 | 136 | Netrakona | 134 | 21:00
5 | Agrabad | 68 | 14:00 | 71 | Ishurdi | 87 | 21:00 | 137 | New | 86 | 12:00
6 | Amnura | 33 | 23:00 | 72 | Jaldhaka | 81 | 22:00 | 138 | Niamatpur | 89 | 23:00
7 | Ashuganj | 97 | 02:00 | 73 | Jamalpur | 120 | 21:00 | 139 | Noapara | 47 | 19:30
8 | BSRM | 204 | 02:00 | 74 | Jashore | 150 | 19:30 | 140 | PHP | 14 | 13:00
9 | Bagerhat | 94 | 20:00 | 75 | Jhenaidah | 95 | 21:00 | 141 | Pabna | 108 | 20:00
10 | Bajitpur | 95 | 00:00 | 76 | Joydebpur | 156 | 19:00 | 142 | Palashbari | 132 | 20:00
11 | Bakerganj | 15.2 | 21:00 | 77 | Joypurhat | 66 | 23:00 | 143 | Panchagarh | 68 | 20:00
12 | Bakulia | 97 | 20:00 | 78 | Juldah | 21 | 14:00 | 144 | Patiya | 11.6 | 20:00
13 | Banani | 73.2 | 13:00 | 79 | KSRM | 33 | 20:00 | 145 | Patuakhali | 67.5 | 23:00
14 | Bangabhaban | 22 | 10:00 | 80 | Kabirpur | 273 | 19:30 | 146 | Payra | 34 | 00:00
15 | Barapukuria | 67 | 23:00 | 81 | Kachua | 100 | 19:00 | 147 | Postogola | 64 | 13:00
16 | Barguna | 22 | 22:00 | 82 | Kaliganj | 41 | 19:30 | 148 | Pubail | 39 | 09:00
17 | Barishal | 110 | 12:00 | 83 | Kallyanpur | 132 | 00:00 | 149 | Purbachal | 34 | 13:00
18 | Barishal-230 | 110 | 00:00 | 84 | Kalurghat | 41 | 11:00 | 150 | Purbasadipur | 143 | 20:00
19 | Baroaulia | 50 | 13:00 | 85 | Kamrangirchar | 85 | 13:00 | 151 | Rahanpur | 46 | 22:00
20 | Baroirhat | 65 | 19:00 | 86 | Kaptai | N/A | N/A | 152 | Rahim | 32 | 10:00
21 | Bashundhara | 217 | 13:00 | 87 | Kasba | 41 | 19:30 | 153 | Rajbari | 91 | 19:30
22 | BashundharaCement | 1 | 00:00 | 88 | Kazla | 117 | 17:00 | 154 | Rajendrapur | 116 | 16:00
23 | Beanibazar | 92 | 23:00 | 89 | Keranigonj | 87 | 19:30 | 155 | Rajshahi | 149 | 23:00
24 | Benapole | 68 | 20:00 | 90 | Khagrachori | 34 | 01:00 | 156 | Rajshahi-230 | 86 | 00:00
25 | Bhaluka | 157 | 21:00 | 91 | Khulna | 69 | 19:00 | 157 | Ramganj | 112 | 19:00
26 | Bhandaria | 49 | 18:30 | 92 | Khulshi | 199 | 16:00 | 158 | Rampur | 42 | 00:00
27 | Bhangura | 43 | 19:30 | 93 | Kishoreganj | 122 | 00:00 | 159 | Rangamati | 16 | 11:00
28 | Bheramara(GK) | 65 | 00:00 | 94 | Kodda | 317 | 18:00 | 160 | Rangpur | 150 | 19:30
29 | Bhulta | 210 | 00:00 | 95 | Kulaura | 61 | 21:00 | 161 | Ruppur | 4.6 | 11:00
30 | Bog-Sherpur | 84 | 23:00 | 96 | Kurigram | 72 | 19:30 | 162 | SSM | 0 | 00:00
31 | Bogura | 183 | 20:00 | 97 | Kushtia | 165 | 19:00 | 163 | Saidpur | 103 | 15:00
32 | Borhanuddin | 78 | 00:00 | 98 | Laksam | 29 | 00:00 | 164 | Santhia | 38 | 19:00
33 | Brahmanbaria | 145 | 21:00 | 99 | Lakshmipur | 41 | 19:30 | 165 | Satkhira | 138 | 00:00
34 | Cantonment | 144 | 13:00 | 100 | Lalbag | 80 | 13:00 | 166 | Satmasjid | 108 | 13:00
35 | Chandina | 35 | 12:00 | 101 | Lalmonirhat | 64 | 19:30 | 167 | Savar | 224 | 18:30
36 | Chandpur | 88 | 00:00 | 102 | MI_Cement | 15.7 | 12:00 | 168 | SevenRings | 18.31 | 21:00
37 | Chandraghona | 34 | 19:00 | 103 | Madanganj | 45 | 21:00 | 169 | ShahCement | 34 | 23:00
38 | Chapai | 82 | 20:00 | 104 | Madaripur | 122 | 19:30 | 170 | Shahjadpur | 78 | 17:00
39 | Charfasson | 34 | 23:00 | 105 | Madartek | 86 | 00:00 | 171 | Shahjibazar | 131 | 00:00
40 | Charsaidpur | 40 | 09:00 | 106 | Madunaghat | 60 | 17:00 | 172 | Shahmirpur | 52 | 22:00
41 | Chauddagram | 79 | 19:00 | 107 | Magura | 66 | 19:30 | 173 | Shariatpur | 95 | 21:00
42 | Chhatak | 43 | 19:00 | 108 | Mahasthangarh | 83 | 19:30 | 174 | Sherpur | 140 | 22:00
43 | Chowmuhani | 157 | 22:00 | 109 | Maijdee | 42 | 23:00 | 175 | Shikalbaha | 31 | 19:00
44 | Chuadanga | 129 | 19:00 | 110 | Manikganj | 147 | 22:00 | 176 | Shitalakhya | 84.3 | 12:00
45 | Coxsbazar | 147 | 19:30 | 111 | Maniknagar | 86 | 14:00 | 177 | Sholosohor | 45 | 19:00
46 | Cumilla(N) | 134 | 23:00 | 112 | Matarbari | 58 | 22:00 | 178 | Shomvuganj | 42 | 00:00
47 | Cumilla(S) | 165 | 00:00 | 113 | Matuail | 80 | 10:00 | 179 | Shyampur | 162 | 11:00
48 | Daganbhuiyan | 39 | 23:00 | 114 | Metrorail_Motijheel | 47 | 18:30 | 180 | Siddhirganj | 133 | 11:00
49 | Daudkandi | 144 | 00:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Sirajganj | 116 | 19:30
50 | DhakaUniversity | 98 | 13:00 | 116 | Millgate | 114 | 15:00 | 182 | Sitakunda | 21 | 19:30
51 | Dhamrai | 112 | 19:00 | 117 | Mirpur | 162 | 13:00 | 183 | Sonargaon | 146 | 01:00
52 | Dhanmondi | 115 | 13:00 | 118 | Mirsorai | 35 | 11:00 | 184 | Sreemongol | 94 | 19:30
53 | Dohazari | 103 | 20:00 | 119 | Mirzapur | 41 | 21:00 | 185 | Sreepur | 131 | 20:00
54 | Faridpur | 178 | 00:00 | 120 | Mithapukur | 78 | 21:00 | 186 | Srinagar | 55 | 20:00
55 | Fatullah | 107 | 15:00 | 121 | Modern | N/A | N/A | 187 | Sunamganj | 61 | 20:00
56 | Fenchuganj | 48 | 19:00 | 122 | Mogbazar | 102.4 | 14:00 | 188 | Sylhet | 134 | 19:00
57 | Feni | 108 | 00:00 | 123 | Mongla | 43 | 05:00 | 189 | Sylhet_(South) | 67 | 19:00
58 | GPH | 89 | 03:00 | 124 | Motijheel | 56 | 13:00 | 190 | TK | 24.5 | 19:30
59 | Ghatail | 86 | 20:00 | 125 | Muktagacha | 40 | 11:00 | 191 | Tangail | 168 | 00:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 116 | 00:00 | 192 | Taraganj | 30 | 20:00
61 | Ghorashal-230 | 103 | 16:00 | 127 | Muradnagar | 53 | 22:00 | 193 | Tasnim | 38 | 17:00
62 | Goalpara | 39 | 13:00 | 128 | Mymensingh | 162 | 22:00 | 194 | Thakurgaon | 111 | 20:00
63 | Gollamari | 112 | 13:00 | 129 | Nabinagar | 108 | 00:00 | 195 | Tongi | 164 | 11:00
64 | Gopalganj | 117 | 21:00 | 130 | Naogaon | 144 | 22:00 | 196 | Ullahpara | 44 | 20:00
65 | Gulshan | 154 | 12:00 | 131 | Narail | 57 | 21:00 | 197 | Ullon | 60 | 00:00
66 | Halishahar | 110 | 15:00 | 132 | Narinda | 80 | 13:00 | 198 | Uttara | 105 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 30-06-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 364 | 06:00 | 352 | 11:00 | Madunaghat | 387 | 21:00 | 378 | 13:00
Amtali | 406 | 06:00 | 401 | 22:00 | Meghnaghat | 370 | 06:00 | 347 | 11:00
Ashuganj | 361 | 20:00 | 347 | 12:00 | Payra | 409 | 18:00 | 403 | 23:00
Bhulta | 390 | 06:00 | 371 | 12:00 | Rahanpur | 399 | 18:00 | 387 | 21:00
Bibiana | 386 | 05:00 | 377 | 23:00 | Rampal | 391 | 18:30 | 373 | 00:00
BIPTC | 400 | 06:00 | 391 | 00:00
Bogura | 381 | 18:30 | 365 | 23:00
Gopalganj | 382 | 18:30 | 371 | 00:00
Kaliakoir | 361 | 20:00 | 347 | 12:00
Korerhat | 381 | 06:00 | 371 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 06:00 | 211 | 13:00 | Ishurdi | 227 | 18:30 | 206 | 23:00
AKSML | 223.9 | 19:30 | 216.3 | 10:00 | Jhenaidah | 220 | 18:30 | 200 | 00:00
Aminbazar | 223 | 05:00 | 212 | 11:00 | Kachua | 215 | 06:00 | 210 | 15:00
Ashuganj | 222 | 20:00 | 215 | 10:00 | Kaliakoir | 222 | 06:00 | 212 | 11:00
Ashuganj-400 | 222 | 20:00 | 215 | 10:00 | Keranigonj | 222 | 06:00 | 209 | 13:00
Baghabari | 225 | 09:00 | 216 | 23:00 | Khulna(S) | 221 | 18:00 | 203 | 00:00
Barapukuria | 222 | 18:30 | 213 | 21:00 | Korerhat | 216 | 05:00 | 211 | 10:00
Barapukuria-230 | 222 | 18:30 | 213 | 21:00 | Madunaghat | 224 | 00:00 | 218 | 13:00
Barishal | 223 | 18:30 | 215 | 13:00 | Madunaghat-400 | 226 | 21:00 | 220 | 13:00
Bheramara | 225 | 18:30 | 205 | 21:00 | Maniknagar | 221 | 06:00 | 208 | 13:00
Bhulta | 224 | 06:00 | 210 | 12:00 | Meghnaghat | 226 | 11:00 | 221 | 14:00
Bibiana | 222 | 06:00 | 215 | 12:00 | Meghnaghat-400 | 225 | 06:00 | 210 | 12:00
BIPTC | 227 | 18:00 | 203 | 23:00 | Mirsorai | 221 | 06:00 | 215 | 13:00
Bogura | 235 | 18:00 | 224 | 23:00 | Naogaon | 221 | 19:00 | 200 | 23:00
Bogura-400 | 236 | 18:00 | 226 | 23:00 | Purbasadipur | 221 | 19:00 | 207 | 21:00
Borhanuddin | 227 | 12:00 | 222 | 01:00 | Rajshahi | 226 | 18:00 | 204 | 21:00
BSRM | 217 | 06:00 | 211 | 16:00 | Rampal | 221 | 18:00 | 206 | 00:00
Charfasson | 228 | 07:00 | 222 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 221 | 06:00 | 210 | 15:00 | Rampura | 223 | 06:00 | 207 | 13:00
Cumilla(N) | 218 | 07:00 | 211 | 12:00 | Shikalbaha | 225 | 20:00 | 218 | 10:00
Faridpur | 217 | 18:30 | 208 | 00:00 | Shyampur | 222 | 06:00 | 210 | 12:00
Fenchuganj | 223 | 06:00 | 216 | 13:00 | Siddhirganj | 224 | 06:00 | 212 | 12:00
Feni | 216 | 06:00 | 210 | 12:00 | Sirajgonj | 238 | 04:00 | 228 | 23:00
Ghorashal | 220 | 00:00 | 215 | 13:00 | Sreepur | 218 | 07:00 | 210 | 21:00
Ghorashal-230 | 206 | 06:00 | 195 | 10:00 | Tongi | 212 | 04:00 | 198 | 11:00
Gopalganj | 217 | 18:00 | 210 | 00:00
GPH | 221 | 20:00 | 215 | 12:00
Haripur | 223 | 06:00 | 210 | 13:00
Hasnabad | 222 | 04:00 | 210 | 12:00
Hathazari | 220 | 00:00 | 216 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 06:00 | 127 | 12:00 | Madunaghat | 130 | 19:30 | 112 | 17:00
Agargaon | 131 | 06:00 | 122 | 12:00 | Magura | 128 | 20:00 | 106 | 23:00
Agrabad | 128 | 00:00 | 123 | 13:00 | Mahasthangarh | 132 | 18:00 | 124 | 21:00
AKS | 126 | 00:00 | 123 | 10:00 | Maijdee | 120 | 06:00 | 117 | 02:00
Aminbazar | 127 | 01:00 | 15 | 20:00 | Manikganj | 131 | 20:00 | 122 | 22:00
Amnura | 133 | 18:30 | 120 | 02:00 | Maniknagar | 130 | 05:00 | 120 | 12:00
Ashuganj | N/A | N/A | N/A | N/A | Matarbari | 114 | 22:00 | 106 | 13:00
Ashuganj-230 | 131 | 06:00 | 127 | 13:00 | Matuail | 129 | 06:00 | 121 | 13:00
Bagerhat | 127 | 18:00 | 109 | 00:00 | Metrorail_Motijheel | 130 | 05:00 | 120 | 12:00
Bajitpur | 122 | 19:30 | 116 | 00:00 | Metrorail_Uttara | 127 | 01:00 | 117 | 15:00
Bakerganj | 131 | 18:00 | 124 | 00:00 | Millgate | 127 | 01:00 | 118 | 11:00
Bakulia | 129 | 00:00 | 123 | 10:00 | Mirpur | 126 | 01:00 | 119 | 11:00
Banani | 138 | 05:00 | 126 | 12:00 | Mirzapur | 129 | 20:00 | 120 | 23:00
Bangabhaban | 129 | 05:00 | 119 | 12:00 | Mithapukur | 133 | 19:00 | 120 | 23:00
Barapukuria | 135 | 18:30 | 125 | 21:00 | MI_Cement | 131 | 06:00 | 120 | 12:00
Barguna | 131 | 18:00 | 124 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 128 | 18:30 | 123 | 13:00 | Mogbazar | 139 | 06:00 | 13.5 | 20:00
Barishal-230 | 128 | 18:00 | 123 | 13:00 | Mongla | 126 | 18:00 | 109 | 00:00
Baroaulia | 128 | 19:30 | 123 | 12:00 | Motijheel | 129 | 05:00 | 119 | 12:00
Baroirhat | 125 | 07:00 | 122 | 12:00 | Muktagacha | 123 | 19:30 | 113 | 02:00
Bashundhara | 138 | 06:00 | 117 | 11:00 | Munshiganj | 127 | 05:00 | 120 | 11:00
BashundharaCement | 128 | 06:00 | 121 | 13:00 | Muradnagar | 122 | 06:00 | 117 | 11:00
Beanibazar | 124 | 06:00 | 117 | 23:00 | Mymensingh | 125 | 20:00 | 108 | 00:00
Benapole | 128 | 18:00 | 109 | 00:00 | Nabinagar | 125 | 05:00 | 118 | 10:00
Bhaluka | 125 | 18:00 | 117 | 13:00 | Naogaon | 133 | 18:30 | 120 | 23:00
Bhandaria | 125 | 17:00 | 105 | 00:00 | Narail | 125 | 18:00 | 103 | 21:00
Bhangura | 129 | 09:00 | 121 | 13:00 | Narinda | 130 | 05:00 | 120 | 12:00
Bheramara | 131 | 18:00 | 119 | 21:00 | Narshingdi | 123 | 07:00 | 115 | 12:00
Bheramara(GK) | 132 | 18:00 | 119 | 21:00 | Natore | 130 | 18:30 | 117 | 23:00
Bhulta | 125 | 18:00 | 119 | 11:00 | Nawabganj | 133 | 06:00 | 125 | 16:00
Bog-Sherpur | 132 | 18:00 | 124 | 23:00 | Netrakona | 115 | 11:00 | 102 | 21:00
Bogura | 136 | 18:30 | 128 | 00:00 | New | 129 | 05:00 | 119 | 10:00
Bogura-230 | 135 | 18:00 | 127 | 23:00 | Niamatpur | 131 | 18:30 | 123 | 23:00
Brahmanbaria | 125 | 06:00 | 119 | 13:00 | Noapara | 130 | 18:00 | 114 | 00:00
Cantonment | 131 | 06:00 | 122 | 11:00 | Pabna | 129 | 18:00 | 118 | 23:00
Chandina | 125 | 06:00 | 20 | 15:00 | Palashbari | 130 | 04:00 | 118 | 23:00
Chandpur | 125 | 00:00 | 118 | 09:00 | Panchagarh | 138 | 19:00 | 126 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 130 | 00:00 | 126 | 12:00 | Patiya | 127 | 21:00 | 121 | 13:00
Chapai | 130 | 01:00 | 126 | 22:00 | Patuakhali | 131 | 18:00 | 124 | 00:00
Charsaidpur | 128 | 05:00 | 121 | 12:00 | Payra | 133 | 18:00 | 130 | 22:00
Chauddagram | 123 | 05:00 | 120 | 10:00 | PHP | 125 | 06:00 | 121 | 13:00
Chhatak | 123 | 05:00 | 113 | 19:00 | Postogola | 132 | 06:00 | 123 | 12:00
Chowmuhani | 121 | 18:00 | 118 | 10:00 | Pubail | 120 | 20:00 | 113 | 12:00
Chuadanga | 127 | 18:00 | 111 | 19:00 | Purbachal | 139 | 06:00 | 125 | 13:00
Coxsbazar | 118 | 23:00 | 108 | 13:00 | Purbasadipur | 134 | 19:00 | 125 | 21:00
Cumilla(N) | 125 | 07:00 | 120 | 12:00 | Rahanpur | 133 | 18:00 | 128 | 21:00
Cumilla(S) | 132 | 06:00 | 120 | 13:00 | Rahanpur-400 | 133 | 18:00 | 129 | 02:00
Daganbhuiyan | 123 | 20:00 | 119 | 10:00 | Rahim | 129 | 06:00 | 122 | 12:00
Daudkandi | 122 | 05:00 | 113 | 13:00 | Rajbari | 122 | 18:00 | 117 | 00:00
DhakaUniversity | 138 | 05:00 | 126 | 13:00 | Rajendrapur | 124 | 17:00 | 118 | 23:00
Dhamrai | 127 | 01:00 | 120 | 16:00 | Rajshahi | 127 | 18:00 | 114 | 23:00
Dhanmondi | 139 | 06:00 | 126 | 13:00 | Rajshahi-230 | 130 | 18:00 | 112 | 03:00
Dohazari | 124 | 21:00 | 117 | 13:00 | Ramganj | 119 | 00:00 | 115 | 02:00
Faridpur | 125 | 18:30 | 120 | 00:00 | Rampur | 128 | 00:00 | 123 | 10:00
Fatullah | 133 | 06:00 | 121 | 12:00 | Rampura | 138 | 06:00 | 126 | 13:00
Fenchuganj | 131 | 06:00 | 125 | 19:00 | Rangamati | 128 | 00:00 | 124 | 12:00
Feni | 124 | 01:00 | 121 | 00:00 | Rangpur | 131 | 18:30 | 120 | 23:00
Feni-230 | 124 | 06:00 | 120 | 16:00 | Ruppur | 131 | 09:00 | 119 | 23:00
Ghatail | 123 | 18:30 | 113 | 19:00 | Saidpur | 133 | 18:30 | 125 | 23:00
Ghorashal | 123 | 08:00 | 117 | 12:00 | Santhia | 131 | 18:00 | 122 | 19:30
Goalpara | 132 | 18:00 | 119 | 00:00 | Satkhira | 128 | 18:00 | 110 | 00:00
Gollamari | 132 | 18:00 | 119 | 00:00 | Satmasjid | 130 | 06:00 | 121 | 13:00
Gopalganj | 127 | 18:00 | 118 | 23:00 | Savar | 128 | 02:00 | 118 | 10:00
Gopalganj-400 | 129 | 18:00 | 123 | 00:00 | SevenRings | 123 | 07:00 | 116 | 10:00
Gulshan | 138 | 06:00 | 126 | 13:00 | ShahCement | 128 | 05:00 | 121 | 12:00
Halishahar | 128 | 00:00 | 123 | 10:00 | Shahjadpur | 130 | 00:00 | 129 | 23:00
Haripur | 129 | 06:00 | 122 | 12:00 | Shahjibazar | 124 | 01:00 | 120 | 15:00
HaripurSBU | 129 | 06:00 | 122 | 12:00 | Shahmirpur | 129 | 00:00 | 123 | 13:00
Hasnabad | 132 | 04:00 | 123 | 11:00 | Shariatpur | 126 | 18:00 | 119 | 00:00
Hathazari | 130 | 01:00 | 126 | 17:00 | Sherpur | 123 | 20:00 | 107 | 06:00
Hatirjheel | 138 | 06:00 | 126 | 13:00 | Shikalbaha | 119 | 00:00 | 113 | 13:00
Ishurdi | 133 | 18:00 | 120 | 23:00 | Shikalbaha-230 | 132 | 00:00 | 124 | 13:00
Jaldhaka | 131 | 18:30 | 122 | 21:00 | Shitalakhya | 131 | 06:00 | 120 | 12:00
Jamalpur | 128 | 20:00 | 112 | 02:00 | Sholosohor | 129 | 00:00 | 125 | 11:00
Jashore | 129 | 18:00 | 111 | 00:00 | Shomvuganj | 119 | 11:00 | 110 | 23:00
Jhenaidah | 134 | 18:00 | 108 | 21:00 | Shyampur | 132 | 20:00 | 124 | 10:00
Jhenaidah-230 | 134 | 18:30 | 119 | 00:00 | Shyampur-230 | 132 | 01:00 | 125 | 12:00
Joydebpur | 117 | 05:00 | 110 | 10:00 | Siddhirganj | 130 | 05:00 | 121 | 12:00
Joypurhat | 131 | 18:30 | 119 | 23:00 | Sirajganj | 130 | 05:00 | 121 | 21:00
Juldah | 128 | 00:00 | 124 | 10:00 | Sitakunda | 131 | 05:00 | 124 | 13:00
Kabirpur | 133 | 18:30 | 113 | 11:00 | Sonargaon | 126 | 20:00 | 120 | 11:00
Kachua | 122 | 00:00 | 119 | 10:00 | Sreemongol | 126 | 06:00 | 120 | 13:00
Kaliakoir | 133 | 18:30 | 15 | 22:00 | Sreepur | 127 | 07:00 | 121 | 21:00
Kaliganj | 133 | 18:00 | 117 | 00:00 | Srinagar | 135 | 05:00 | 126 | 12:00
Kallyanpur | 127 | 01:00 | 118 | 12:00 | SSM | 131 | 00:00 | 129 | 12:00
Kalurghat | 129 | 00:00 | 126 | 10:00 | Sunamganj | 120 | 04:00 | 112 | 20:00
Kamrangirchar | 133 | 05:00 | 116 | 13:00 | Sylhet | 125 | 05:00 | 119 | 19:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet_(South) | 126 | 07:00 | 120 | 13:00
Kasba | 122 | 07:00 | 115 | 12:00 | Tangail | 126 | 20:00 | 117 | 09:00
Kazla | 130 | 06:00 | 119 | 13:00 | Taraganj | 131 | 18:30 | 122 | 23:00
Keranigonj | 134 | 06:00 | 126 | 13:00 | Tasnim | 126 | 05:00 | 120 | 11:00
Khagrachori | 127 | 01:00 | 123 | 12:00 | Thakurgaon | 137 | 19:00 | 124 | 21:00
Khulna | 131 | 18:00 | 117 | 00:00 | TK | 130 | 00:00 | 125 | 12:00
Khulna(S) | 133 | 18:00 | 119 | 00:00 | Tongi | 132 | 04:00 | 122 | 11:00
Khulshi | 127 | 00:00 | 122 | 10:00 | Ullahpara | 131 | 01:00 | 121 | 23:00
Kishoreganj | 121 | 20:00 | 114 | 00:00 | Ullon | 138 | 05:00 | 126 | 13:00
Kodda | 135 | 20:00 | 125 | 23:00 | Uttara | 129 | 05:00 | 116 | 11:00
Korerhat | 128 | 20:00 | 125 | 10:00 | UttaraNew | 127 | 01:00 | 117 | 12:00
KSRM | 130 | 01:00 | 124 | 11:00 | Zigatola | 133 | 05:00 | 126 | 13:00
Kulaura | 129 | 06:00 | 124 | 19:00
Kurigram | 130 | 00:00 | 118 | 13:00
Kushtia | 129 | 18:00 | 113 | 23:00
Laksam | 122 | 00:00 | 118 | 10:00
Lakshmipur | 119 | 07:00 | 116 | 02:00
Lalbag | 134 | 06:00 | 126 | 11:00
Lalmonirhat | 128 | 19:00 | 117 | 23:00
Madanganj | 128 | 06:00 | 121 | 13:00
Madaripur | 128 | 18:30 | 122 | 00:00
Madartek | 138 | 06:00 | 126 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 30-06-2026 | [28 empty] | Date: | 30-06-2026 | [28 empty] | Date: | 30-06-2026 | [28 empty] | Date: | 30-06-2026 | [28 empty] | Date: | 30-06-2026 | [18 empty] | Date: | 30-06-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [18 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 35 | 17 | 113 | 146 | 195 | 12 | 35 | 108 | 0 | 0 | 0 | 435 | 0 | 0 | 302 | 0 | 0 | 0 | 142 | 17 | 21 | 0 | 450 | 107 | 16 | 79 | 0 | 9 | 33 | 0 | 18 | 12 | 12 | 0 | 100 | 50 | 24 | 1135 | 0 | 0 | 31 | 8 | 17 | 220 | 0 | 0 | 0 | 1224 | 0 | 140 | 0 | 230 | 290 | 220 | 51 | 20 | 216 | 40 | 66 | 139 | 100 | 28 | 19 | 17 | 156 | 0 | 0 | 0 | 315 | 0 | 295 | 29 | 0 | 138 | 0 | 17 | 0 | 83 | 28 | 143 | 0 | 101 | 17 | 79 | 0 | 107 | 0 | 0 | 0 | 0 | 8695 | 892 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 100 | 0 | 0 | 0 | 460 | 0 | 0 | 0 | 1425.61 | 0 | 32 | 0 | 57 | 70 | 0 | 102 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 10 | 0 | 164 | 0 | 370 | 0 | 0 | 181 | 40 | 95 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 256 | 65 | 220 | 0 | 1050 | 1200 | 17 | 7127.61 | 15822.61 | 76.33
01:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 17 | 78 | 146 | 195 | 11 | 35 | 108 | 0 | 0 | 0 | 445 | 0 | 0 | 297 | 0 | 0 | 0 | 142 | 17 | 21 | 0 | 470 | 70 | 16 | 78 | 0 | 4 | 33 | 0 | 18 | 12 | 12 | 0 | 98 | 51 | 25 | 1135 | 0 | 0 | 6 | 8 | 17 | 219 | 0 | 0 | 0 | 1224 | 0 | 140 | 0 | 230 | 290 | 220 | 51 | 20 | 216 | 40 | 51 | 139 | 95 | 27 | 19 | 17 | 148 | 0 | 0 | 0 | 315 | 0 | 295 | 29 | 0 | 143 | 0 | 17 | 0 | 83 | 28 | 143 | 0 | 101 | 17 | 79 | 0 | 107 | 0 | 0 | 0 | 0 | 8556 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 101 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 1354.14 | 0 | 33 | 0 | 57 | 70 | 0 | 102 | 26 | 0 | 0 | 0 | 18 | 0 | 0 | 170 | 0 | 16 | 0 | 164 | 0 | 394 | 0 | 0 | 181 | 41 | 95 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 249 | 65 | 220 | 0 | 1050 | 1215 | 17 | 7109.14 | 15665.14 | 76.33
02:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 58 | 146 | 145 | 11 | 35 | 0 | 0 | 0 | 0 | 535 | 0 | 0 | 298 | 0 | 0 | 0 | 142 | 17 | 14 | 0 | 505 | 77 | 16 | 27 | 0 | 5 | 0 | 0 | 18 | 12 | 12 | 0 | 97 | 29 | 25 | 1135 | 0 | 0 | 6 | 8 | 0 | 219 | 0 | 0 | 0 | 1224 | 0 | 55 | 0 | 230 | 310 | 220 | 51 | 22 | 216 | 40 | 0 | 139 | 27 | 0 | 19 | 17 | 154 | 0 | 0 | 0 | 315 | 0 | 295 | 29 | 0 | 152 | 0 | 17 | 0 | 83 | 28 | 143 | 0 | 101 | 17 | 48 | 0 | 9 | 0 | 0 | 0 | 0 | 8011 | 904 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 100 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 1491.15 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 18 | 0 | 164 | 0 | 400 | 0 | 0 | 181 | 41 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 275 | 65 | 220 | 0 | 1050 | 1213 | 17 | 6966.15 | 14977.15 | 76.33
03:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 52 | 147 | 145 | 11 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 297 | 0 | 0 | 0 | 142 | 17 | 14 | 0 | 485 | 92 | 16 | 0 | 0 | 10 | 0 | 0 | 18 | 12 | 12 | 0 | 97 | 28 | 25 | 1135 | 0 | 0 | 6 | 8 | 0 | 219 | 0 | 0 | 0 | 1224 | 0 | 20 | 0 | 230 | 310 | 220 | 51 | 20 | 199 | 40 | 0 | 139 | 17 | 0 | 19 | 17 | 150 | 0 | 0 | 0 | 310 | 0 | 295 | 29 | 0 | 149 | 0 | 17 | 0 | 52 | 28 | 143 | 0 | 101 | 0 | 48 | 0 | 9 | 0 | 0 | 0 | 0 | 7814 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 1486.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 33 | 0 | 130 | 0 | 373 | 0 | 0 | 181 | 41 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 65 | 220 | 0 | 1050 | 1210 | 17 | 6781.42 | 14595.42 | 76.32
04:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 52 | 147 | 80 | 11 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 17.5 | 21 | 0 | 435 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 18 | 0 | 12 | 0 | 97 | 17 | 25 | 1135 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1224 | 0 | 20 | 0 | 230 | 310 | 220 | 51 | 20 | 198 | 40 | 0 | 142 | 0 | 0 | 19 | 0 | 149 | 0 | 0 | 0 | 310 | 0 | 295 | 29 | 0 | 139 | 0 | 16 | 0 | 52 | 28 | 141 | 0 | 101 | 0 | 49 | 0 | 9 | 0 | 0 | 0 | 0 | 7512.5 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 1486.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 85 | 0 | 130 | 0 | 380 | 0 | 0 | 181 | 40 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 65 | 220 | 0 | 1050 | 1210 | 17 | 6753.8 | 14266.3 | 76.32
05:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 52 | 147 | 45 | 11 | 0 | 0 | 0 | 0 | 0 | 535 | 0 | 0 | 300 | 0 | 0 | 0 | 142 | 17.5 | 21 | 0 | 390 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 18 | 0 | 12 | 0 | 97 | 16 | 25 | 1135 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1196 | 0 | 20 | 0 | 230 | 310 | 220 | 51 | 20 | 190 | 39 | 0 | 142 | 0 | 0 | 19 | 0 | 140 | 0 | 0 | 0 | 310 | 0 | 295 | 29 | 0 | 131 | 0 | 16 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 49 | 0 | 9 | 0 | 0 | 0 | 0 | 7360.5 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 1479.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 132 | 0 | 130 | 0 | 346 | 0 | 0 | 181 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 267 | 65 | 220 | 0 | 1037 | 1212 | 0 | 6686.68 | 14047.18 | 76.32
06:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 52 | 130 | 45 | 11 | 0 | 0 | 0 | 0 | 0 | 498 | 0 | 0 | 300 | 0 | 0 | 1 | 123 | 18 | 21 | 0 | 515 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.2 | 97 | 0 | 28 | 1050 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1150 | 1 | 0 | 0 | 230 | 310 | 220 | 51 | 20 | 201 | 37 | 0 | 142 | 0 | 0 | 19 | 0 | 122 | 0 | 4 | 0 | 315 | 0 | 295 | 29 | 0 | 144 | 1 | 16 | 0 | 52 | 30 | 142 | 0 | 100 | 0 | 49 | 1.2 | 9 | 0 | 0.1 | 2.64 | 0 | 7219.14 | 904 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 450 | 0 | 0 | 0 | 1386.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.81 | 5 | 0 | 0 | 1.77 | 170 | 0 | 147 | 0 | 130 | 0 | 378 | 0 | 0.19 | 181 | 40 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 9 | 0.03 | 0 | 238 | 65 | 220 | 0 | 950 | 1120 | 0 | 6438.83 | 13657.97 | 76.31
07:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 52 | 130 | 45 | 11 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 300 | 0 | 0 | 2 | 123 | 18 | 21 | 0 | 455 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1.27 | 98 | 0 | 25 | 1050 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1160 | 3 | 0 | 0 | 230 | 310 | 220 | 51 | 20 | 207 | 40 | 0 | 142 | 0 | 0 | 19 | 0 | 132 | 0 | 24 | 0 | 315 | 0 | 307 | 27 | 0 | 149 | 2 | 16 | 0 | 52 | 30 | 140 | 0 | 100 | 0 | 49 | 1 | 46 | 0 | 0.4 | 11.85 | 0 | 7271.52 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5 | 450 | 0 | 0 | 0 | 1414.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1 | 5 | 0 | 0 | 6.84 | 169 | 0 | 152 | 0 | 0 | 0 | 368 | 0 | 0.82 | 181 | 40 | 0 | 4 | 0 | 0 | 0 | 0 | 0.1 | 32 | 0.06 | 0 | 278 | 65 | 220 | 0 | 1050 | 1110 | 0 | 6496.01 | 13767.53 | 76.3
08:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 52 | 147 | 105 | 11 | 0 | 0 | 0 | 0 | 0 | 495 | 0 | 0 | 302 | 0 | 0 | 2 | 123 | 18 | 21 | 0 | 440 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1.63 | 99 | 0 | 7 | 1050 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1153 | 3 | 0 | 0 | 230 | 310 | 220 | 51 | 20 | 201 | 40 | 0 | 139 | 0 | 0 | 19 | 0 | 136 | 0 | 35 | 0 | 320 | 0 | 320 | 29 | 0 | 140 | 5 | 16 | 0 | 52 | 30 | 140 | 0 | 102 | 0 | 49 | 8.8 | 46 | 0 | 0.7 | 14.93 | 0 | 7375.06 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29 | 535 | 0 | 0 | 0 | 1390.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.09 | 17 | 0 | 0 | 10.03 | 173 | 0 | 164 | 0 | 0 | 0 | 366 | 0 | 1.05 | 180 | 40 | 0 | 8 | 0 | 0 | 0 | 0 | 0.3 | 67 | 0.12 | 0 | 220 | 65 | 220 | 0 | 1050 | 1108 | 0 | 6595.3 | 13970.36 | 76.3
09:00 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 52 | 146 | 113 | 11 | 0 | 17 | 0 | 0 | 0 | 490 | 0 | 0 | 295 | 0 | 0 | 21 | 123 | 17 | 21 | 0 | 410 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 3 | 99 | 0 | 2 | 1050 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1160 | 6 | 0 | 0 | 230 | 310 | 220 | 51 | 20 | 201 | 37 | 0 | 138 | 0 | 0 | 19 | 0 | 138 | 0 | 41 | 0 | 315 | 0 | 320 | 29 | 0 | 136 | 10 | 16 | 0 | 52 | 28 | 142 | 0 | 101 | 0 | 49 | 10.04 | 48 | 0 | 0.9 | 38.18 | 0 | 7425.12 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44.78 | 635 | 0 | 0 | 0 | 1326.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.97 | 45 | 0 | 0 | 10.53 | 174 | 0 | 169 | 0 | 0 | 0 | 354 | 0 | 1.19 | 202 | 40 | 0 | 8 | 0 | 0 | 0 | 0 | 1.4 | 93 | 0.17 | 0 | 218 | 65 | 220 | 0 | 968 | 1110 | 0 | 6650.45 | 14075.57 | 76.3
10:00 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 52 | 130 | 113 | 11 | 17 | 17 | 0 | 0 | 0 | 495 | 0 | 0 | 300 | 0 | 0 | 26 | 123 | 17 | 21 | 0 | 515 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 2.6 | 100 | 0 | 2 | 1100 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1150 | 7 | 0 | 0 | 230 | 310 | 220 | 51 | 20 | 200 | 37 | 0 | 139 | 0 | 0 | 19 | 0 | 144 | 0 | 31 | 0 | 320 | 0 | 294 | 29 | 0 | 143 | 10 | 16 | 0 | 52 | 25 | 141 | 0 | 101 | 0 | 49 | 20.17 | 48 | 0 | 1 | 4.38 | 0 | 7543.15 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41.54 | 840 | 0 | 0 | 0 | 1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.44 | 62 | 0 | 0 | 38.91 | 173 | 0 | 171 | 0 | 0 | 0 | 381 | 0 | 4.64 | 202 | 40 | 0 | 20 | 0 | 0 | 0 | 0 | 1.3 | 159 | 0.21 | 0 | 186 | 65 | 220 | 0 | 850 | 1080 | 0 | 6858.04 | 14401.19 | 76.3
11:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 52 | 130 | 125 | 11 | 17 | 17 | 0 | 0 | 0 | 490 | 0 | 0 | 303 | 0 | 0 | 28 | 123 | 16.5 | 21 | 0 | 405 | 23 | 16 | 5 | 0 | 11 | 0 | 0 | 0 | 10 | 12 | 4.53 | 100 | 8 | 2 | 1135 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1150 | 7 | 25 | 0 | 230 | 310 | 250 | 51 | 20 | 196 | 37 | 0 | 137 | 12 | 15 | 19 | 51 | 148 | 0 | 48 | 0 | 325 | 0 | 254 | 29 | 0 | 133 | 12 | 16 | 0 | 52 | 25 | 143 | 0 | 101 | 0 | 49 | 21.15 | 48 | 0 | 1.7 | 23.8 | 0 | 7679.68 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 37.17 | 885 | 0 | 0 | 0 | 1269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.24 | 71 | 0 | 0 | 42.82 | 173 | 0 | 171 | 0 | 0 | 0 | 364 | 0 | 4.9 | 210 | 39 | 0 | 6 | 0 | 0 | 0 | 0 | 0.9 | 186 | 0.22 | 0 | 181 | 65 | 220 | 0 | 850 | 1060 | 0 | 6793.25 | 14472.93 | 76.29
12:00 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 17 | 0 | 52 | 112 | 146 | 12 | 35 | 17 | 0 | 0 | 0 | 515 | 0 | 0 | 300 | 0 | 0 | 15 | 123 | 16.5 | 21 | 0 | 480 | 31 | 16 | 30 | 0 | 9 | 0 | 0 | 0 | 12 | 12 | 0.73 | 99 | 17 | 2 | 1135 | 0 | 0 | 1 | 0 | 0 | 215 | 0 | 0 | 0 | 1171 | 13 | 53 | 0 | 300 | 310 | 250 | 51 | 20 | 200 | 39 | 14 | 137 | 24 | 18 | 19 | 47 | 144 | 0 | 68 | 0 | 325 | 0 | 257 | 29 | 0 | 152 | 8 | 16 | 0 | 52 | 25 | 143 | 0 | 100 | 0 | 58 | 21.28 | 67 | 0 | 1.1 | 35.38 | 0 | 8089.99 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12.15 | 900 | 0 | 0 | 0 | 1242.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.15 | 90 | 0 | 0 | 29.69 | 174 | 0 | 172 | 0 | 0 | 0 | 384 | 0 | 2.53 | 210 | 38 | 0 | 17 | 0 | 0 | 0 | 0 | 1.1 | 191 | 0.19 | 0 | 180 | 65 | 220 | 0 | 850 | 1060 | 0 | 6830.01 | 14920 | 76.29
13:00 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 0 | 52 | 129 | 146 | 15 | 35 | 17 | 0 | 0 | 0 | 545 | 0 | 0 | 296 | 0 | 0 | 25 | 123 | 16.5 | 21 | 0 | 465 | 28 | 16 | 31 | 0 | 4 | 0 | 0 | 0 | 12 | 12 | 1.82 | 97 | 17 | 7 | 1135 | 0 | 0 | 6 | 0 | 0 | 215 | 0 | 0 | 0 | 1151 | 6 | 53 | 0 | 381 | 310 | 250 | 51 | 20 | 198 | 39 | 34 | 135 | 45 | 17 | 19 | 44 | 156 | 0 | 9 | 0 | 320 | 0 | 258 | 29 | 0 | 141 | 5 | 16 | 0 | 51 | 25 | 143 | 0 | 100 | 0 | 58 | 21.23 | 67 | 0 | 1 | 52.64 | 0 | 8182.19 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 23.49 | 900 | 0 | 0 | 0 | 1357.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.92 | 50 | 0 | 0 | 41.51 | 175 | 0 | 176 | 0 | 10 | 0 | 395 | 0 | 4.42 | 210 | 37 | 0 | 30 | 0 | 0 | 0 | 0 | 2.4 | 186 | 0.22 | 0 | 179 | 65 | 220 | 0 | 850 | 1060 | 0 | 6964.42 | 15146.61 | 76.28
14:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 0 | 52 | 128 | 146 | 18 | 35 | 17 | 0 | 0 | 0 | 535 | 0 | 0 | 280 | 0 | 0 | 22 | 123 | 16.5 | 21 | 0 | 390 | 70 | 16 | 30 | 0 | 11 | 0 | 0 | 0 | 12 | 12 | 3.3 | 95 | 17 | 3 | 1135 | 0 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 1136 | 3 | 53 | 8 | 330 | 310 | 300 | 51 | 20 | 184 | 36 | 34 | 137 | 17 | 0 | 19 | 44 | 150 | 0 | 36 | 0 | 320 | 0 | 258 | 29 | 0 | 136 | 12 | 16 | 0 | 51 | 25 | 143 | 0 | 100 | 0 | 59 | 20.35 | 68 | 0 | 0.4 | 45.16 | 0 | 8083.71 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30.1 | 900 | 0 | 0 | 0 | 1469.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.84 | 53 | 0 | 0 | 41.42 | 176 | 0 | 180 | 0 | 40 | 0 | 345 | 0 | 4.49 | 210 | 38 | 0 | 28 | 0 | 0 | 0 | 0 | 2.8 | 117 | 0.14 | 0 | 167 | 65 | 220 | 0 | 850 | 1060 | 0 | 6966.16 | 15049.87 | 76.28
15:00 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 0 | 0 | 52 | 128 | 146 | 15 | 35 | 17 | 0 | 0 | 0 | 520 | 0 | 0 | 298 | 0 | 0 | 16 | 123 | 16.5 | 21 | 0 | 470 | 17 | 16 | 22 | 0 | 18 | 0 | 0 | 0 | 12 | 12 | 0.47 | 93 | 17 | 2 | 1135 | 15 | 0 | 6 | 0 | 0 | 214 | 0 | 0 | 0 | 1170 | 2 | 51 | 0 | 290 | 310 | 300 | 51 | 0 | 198 | 32 | 34 | 141 | 17 | 0 | 19 | 15 | 148 | 0 | 54 | 0 | 315 | 0 | 258 | 29 | 0 | 132 | 6 | 16 | 0 | 50 | 25 | 143 | 0 | 102 | 0 | 59 | 19 | 68 | 0 | 0.1 | 36.45 | 0 | 8056.52 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7.04 | 900 | 0 | 0 | 0 | 1469.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.28 | 64 | 0 | 0 | 32.44 | 177 | 0 | 180 | 0 | 92 | 0 | 362 | 0 | 3.71 | 200 | 40 | 0 | 17 | 0 | 0 | 0 | 0 | 3.7 | 140 | 0.12 | 0 | 180 | 65 | 220 | 0 | 881 | 1025 | 0 | 7037.96 | 15094.48 | 76.27
16:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 52 | 144 | 146 | 15 | 35 | 17 | 0 | 0 | 0 | 500 | 0 | 17 | 295 | 0 | 0 | 13 | 142 | 16 | 21 | 0 | 435 | 17 | 32 | 23 | 0 | 18 | 0 | 0 | 0 | 12 | 12 | 0.72 | 92 | 17 | 2 | 1135 | 15 | 0 | 6 | 0 | 0 | 217 | 0 | 0 | 0 | 1160 | 4 | 53 | 0 | 280 | 310 | 300 | 51 | 0 | 196 | 10 | 34 | 141 | 17 | 0 | 19 | 15 | 142 | 0 | 34 | 0 | 310 | 0 | 257 | 29 | 0 | 139 | 4 | 16 | 0 | 50 | 25 | 142 | 0 | 101 | 0 | 59 | 10.88 | 68 | 0 | 0.2 | 7.61 | 7 | 7887.41 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.32 | 900 | 0 | 0 | 0 | 1414.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.32 | 45 | 0 | 0 | 5.31 | 176 | 0 | 178 | 0 | 116 | 0 | 375 | 0 | 0.58 | 200 | 40 | 0 | 4 | 0 | 0 | 0 | 0 | 2.1 | 85 | 0.25 | 0 | 180 | 65 | 220 | 0 | 882 | 960 | 0 | 6816.57 | 14703.98 | 76.27
17:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 3 | 64 | 144 | 146 | 15 | 35 | 17 | 0 | 0 | 0 | 440 | 0 | 35 | 300 | 0 | 0 | 5 | 142 | 16 | 21 | 0 | 450 | 15 | 32 | 29 | 0 | 17 | 0 | 0 | 0 | 15 | 12 | 0.61 | 94 | 17 | 2 | 1135 | 17 | 0 | 6 | 0 | 0 | 217 | 0 | 0 | 0 | 1165 | 3 | 51 | 0 | 230 | 310 | 290 | 51 | 0 | 203 | 10 | 34 | 141 | 17 | 2 | 19 | 15 | 150 | 0 | 22 | 0 | 310 | 0 | 258 | 29 | 0 | 135 | 1 | 16 | 0 | 52 | 25 | 142 | 0 | 99 | 0 | 59 | 5.32 | 68 | 0 | 0.2 | 5.25 | 12 | 7812.38 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3.81 | 900 | 0 | 0 | 0 | 1348.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 30 | 0 | 0 | 2.31 | 176 | 0 | 171 | 0 | 140 | 0 | 356 | 0 | 0.22 | 200 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 1.7 | 59 | 0.19 | 0 | 181 | 65 | 220 | 0 | 860 | 910 | 0 | 6611.85 | 14424.23 | 76.26
18:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 35 | 17 | 92 | 145 | 185 | 15 | 35 | 17 | 0 | 0 | 0 | 385 | 0 | 35 | 292 | 0 | 0 | 2 | 142 | 16 | 21 | 0 | 405 | 13 | 49 | 35 | 0 | 0 | 0 | 0 | 13 | 16 | 12 | 0.15 | 95 | 17 | 2 | 1135 | 0 | 0 | 6 | 2 | 0 | 217 | 0 | 0 | 0 | 1160 | 1 | 55 | 0 | 230 | 310 | 270 | 51 | 0 | 195 | 10 | 34 | 142 | 17 | 8 | 19 | 14 | 142 | 0 | 5 | 0 | 315 | 0 | 258 | 29 | 0 | 130 | 0 | 16 | 0 | 52 | 30 | 141 | 0 | 101 | 0 | 59 | 1.09 | 68 | 0 | 0.1 | 1.52 | 12 | 7742.86 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.68 | 900 | 0 | 0 | 0 | 1262.75 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 11 | 0 | 1.21 | 8 | 0 | 0 | 0.74 | 173 | 0 | 167 | 0 | 165 | 0 | 345 | 0 | 0.07 | 182 | 40 | 0 | 3 | 0 | 0 | 0 | 0 | 0.3 | 7 | 0.04 | 0 | 179 | 65 | 220 | 0 | 851 | 875 | 0 | 6402.79 | 14145.65 | 76.3
19:00 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 35 | 17 | 118 | 147 | 195 | 15 | 35 | 90 | 0 | 0 | 0 | 385 | 0 | 35 | 311 | 0 | 0 | 0 | 142 | 16.5 | 21 | 0 | 540 | 13 | 49 | 50 | 0 | 0 | 36 | 8 | 20 | 19 | 12 | 0 | 97 | 17 | 5 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 217 | 0 | 0 | 0 | 1170 | 0 | 115 | 0 | 220 | 290 | 230 | 51 | 0 | 213 | 10 | 44 | 142 | 21 | 8 | 19 | 52 | 164 | 0 | 0 | 1 | 315 | 0 | 258 | 29 | 0 | 133 | 0 | 16 | 0 | 52 | 30 | 143 | 0 | 100 | 1 | 68 | 0 | 86 | 0 | 0 | 0 | 12 | 8323 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 867 | 0 | 0 | 0 | 1338.04 | 0 | 40 | 0 | 5 | 3 | 18 | 92 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 153 | 0 | 150 | 0 | 151 | 0 | 401 | 0 | 0 | 182 | 39 | 91 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 194 | 65 | 180 | 0 | 957 | 1020 | 0 | 7053.04 | 0 | 76.25
19:30 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 35 | 17 | 133 | 147 | 195 | 15 | 35 | 90 | 0 | 0 | 0 | 460 | 0 | 35 | 324 | 0 | 0 | 0 | 142 | 16.5 | 21 | 0 | 445 | 92 | 49 | 78 | 0 | 0 | 50 | 8 | 54.36 | 20 | 12 | 0 | 97 | 17 | 7 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 217 | 0 | 0 | 0 | 1170 | 0 | 143 | 0 | 220 | 290 | 230 | 51 | 0 | 215 | 33 | 89 | 142 | 51 | 8 | 19 | 87 | 144 | 0 | 0 | 1 | 315 | 0 | 258 | 29 | 0 | 141 | 0 | 16 | 0 | 83 | 30 | 143 | 0 | 100 | 17 | 78 | 0 | 106 | 0 | 0 | 0 | 0 | 8655.36 | 904 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 866 | 0 | 0 | 0 | 1420.78 | 0 | 40 | 0 | 55 | 72 | 18 | 92 | 18 | 0 | 0 | 0 | 18 | 0 | 0 | 160 | 0 | 157 | 0 | 157 | 0 | 356 | 0 | 0 | 182 | 39 | 90 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 247 | 65 | 220 | 0 | 936 | 1170 | 28 | 7496.78 | 15376.04
20:00 | 0 | 105 | 33 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 35 | 17 | 133 | 147 | 195 | 15 | 35 | 90 | 0 | 0 | 0 | 460 | 0 | 35 | 326 | 0 | 0 | 0 | 142 | 16.5 | 21 | 0 | 395 | 74 | 16 | 78 | 0 | 0 | 50 | 8 | 54.36 | 20 | 12 | 0 | 98 | 17 | 12 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 218 | 0 | 0 | 0 | 1165 | 0 | 142 | 0 | 220 | 290 | 230 | 51 | 0 | 216 | 40 | 85 | 142 | 51 | 9 | 19 | 97 | 152 | 0 | 0 | 8 | 310 | 0 | 258 | 29 | 0 | 135 | 0 | 16 | 0 | 83 | 30 | 141 | 0 | 100 | 17 | 77 | 0 | 106 | 0 | 0 | 0 | 0 | 8589.36 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 900 | 0 | 0 | 0 | 1338.36 | 0 | 41 | 0 | 90 | 65 | 17 | 92 | 18 | 0 | 0 | 0 | 18 | 0 | 0 | 161 | 0 | 158 | 0 | 158 | 0 | 347 | 0 | 0 | 183 | 40 | 90 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 65 | 220 | 0 | 845 | 1140 | 54 | 7325.36 | 16152.14 | 76.25
21:00 | 0 | 35 | 33 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 35 | 17 | 133 | 112 | 95 | 15 | 35 | 108 | 0 | 0 | 0 | 400 | 0 | 35 | 327 | 0 | 0 | 0 | 142 | 16.5 | 21 | 0 | 420 | 15 | 16 | 72 | 0 | 0 | 50 | 8 | 54.36 | 23 | 12 | 0 | 98 | 17 | 3 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 218 | 0 | 0 | 0 | 1224 | 0 | 40 | 0 | 250 | 290 | 230 | 51 | 0 | 216 | 40 | 82 | 139 | 17 | 9 | 19 | 17 | 150 | 0 | 0 | 16 | 310 | 0 | 258 | 29 | 0 | 133 | 0 | 16 | 0 | 84 | 30 | 141 | 0 | 100 | 17 | 79 | 0 | 106 | 0 | 0 | 0 | 0 | 8160.36 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 100 | 0 | 15 | 0 | 900 | 0 | 0 | 0 | 1464.81 | 0 | 40 | 0 | 35 | 35 | 17 | 92 | 19 | 0 | 0 | 0 | 20 | 0 | 0 | 162 | 0 | 160 | 0 | 159 | 0 | 355 | 0 | 0 | 182 | 39 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 65 | 220 | 0 | 1050 | 1220 | 17 | 7648.81 | 15914.72 | 76.24
22:00 | 0 | 35 | 33 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 35 | 0 | 133 | 112 | 95 | 15 | 35 | 108 | 0 | 0 | 0 | 415 | 0 | 35 | 300 | 0 | 0 | 0 | 142 | 16.5 | 21 | 0 | 480 | 15 | 16 | 76 | 0 | 4 | 50 | 8 | 18 | 25 | 12 | 0 | 99 | 17 | 15 | 1135 | 0 | 0 | 6 | 25.5 | 0 | 218 | 0 | 0 | 0 | 1162 | 0 | 12 | 0 | 250 | 290 | 260 | 51 | 0 | 217 | 40 | 72 | 140 | 17 | 8 | 19 | 17 | 156 | 0 | 0 | 16 | 315 | 0 | 258 | 29 | 0 | 135 | 0 | 8 | 0 | 85 | 28 | 142 | 0 | 100 | 17 | 79 | 0 | 106 | 0 | 0 | 0 | 0 | 8115 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 100 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 1411.11 | 0 | 40 | 0 | 35 | 35 | 0 | 92 | 19 | 0 | 0 | 0 | 20 | 0 | 0 | 161 | 0 | 160 | 0 | 161 | 0 | 367 | 0 | 0 | 183 | 40 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 239 | 65 | 220 | 0 | 1050 | 1210 | 17 | 7593.11 | 15809.17 | 76.24
23:00 | 0 | 35 | 33 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 26 | 0 | 133 | 112 | 95 | 15 | 35 | 54 | 0 | 0 | 10 | 515 | 0 | 35 | 300 | 0 | 0 | 0 | 142 | 16.5 | 21 | 0 | 530 | 15 | 16 | 56 | 0 | 1 | 50 | 0 | 18 | 12 | 12 | 0 | 100 | 17 | 21 | 1135 | 0 | 0 | 6 | 0 | 0 | 219 | 0 | 0 | 0 | 1164 | 0 | 12 | 0 | 250 | 290 | 260 | 51 | 0 | 214 | 37 | 72 | 140 | 17 | 8 | 19 | 16 | 156 | 0 | 0 | 16 | 315 | 0 | 257 | 29 | 0 | 146 | 0 | 16 | 0 | 85 | 25 | 143 | 0 | 101 | 17 | 79 | 0 | 106 | 0 | 0 | 0 | 0 | 8188.5 | 904 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 100 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 1399.83 | 0 | 40 | 0 | 35 | 35 | 0 | 92 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 159 | 0 | 161 | 0 | 403 | 0 | 0 | 183 | 39 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 279 | 65 | 220 | 0 | 1050 | 1200 | 17 | 7635.83 | 15708.11 | 76.23
Total KWH | 0 | 1745280 | 612480 | 0 | 0 | 0 | 0 | 0 | 8650800 | 0 | 0 | 247320 | 99720 | 1837008 | 3248640 | 3055069 | 334078 | 538481 | 807840 | 0 | 0 | 11375 | 11881350 | 0 | 270099 | 7294140 | 0 | 0 | 167938 | 3320400 | 415800 | 504000 | 0 | 10968636.36 | 766527 | 386400 | 701760 | 0 | 173280 | 299527 | 31628 | 315484 | 231360 | 234240 | 22441 | 2330360 | 427382 | 265920 | 26894545.46 | 63564 | 0 | 108480 | 129430.8 | 24255 | 5151626 | 0 | 0 | 0 | 28167270 | 56295 | 1057163 | 0 | 6171000 | 7695600 | 6018000 | 1252368 | 316320 | 5033000 | 821016 | 703680 | 3425644 | 488160 | 139440 | 469190 | 539220 | 3514560 | 0 | 391627 | 61056 | 7612000 | 0 | 6782000 | 693000 | 0 | 3366572.73 | 80553 | 360864 | 0 | 1469760 | 649248 | 3252200 | 0 | 2405350 | 114840 | 1435200 | 135187 | 1480800 | 0 | 10300 | 273000 | 44880 | 191055028.35 | 20626909 | 0 | 0 | 0 | 0 | 912000 | 0 | 0 | 522978 | 0 | 43632 | 247680 | 17745453 | 0 | 0 | 0 | 33439951 | 0 | 290841 | 0 | 279936 | 370656 | 48866 | 648944 | 192115 | 0 | 256608 | 582890 | 98789 | 0 | 259024 | 4102364 | 0 | 3661955 | 0 | 2562445 | 0 | 8970836 | 0 | 30720 | 4698000 | 933381 | 708053 | 158210 | 521760 | 0 | 0 | 0 | 19320.72 | 1347840 | 2100 | 222240 | 5411000 | 1556000 | 5437160 | 0 | 23047272 | 26859636.36 | 195600 | 167013165.08 | 358068193.43