## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 03-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-07-2026 | during | 03-07-2026 | during | 03-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 396 | 355 | 412 | 412 | 412 | 412 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 303 | 291 | 335 | 335 | 305 | 305 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 324 | 293 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 36 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 144 | 144 | 149.36 | 149.36 | 149.36 | 149.36 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15.5 | 15.5 | 33 | 33 | 17 | 17 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 25 | 52.19 | 52.19 | 33 | 33 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 112 | 146 | 300 | 300 | 146 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 79 | 115 | 149 | 149 | 70 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 51 | 105 | 105 | 35 | 70 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 17 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 15 | 28 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 385 | 430 | 584 | 584 | 526 | 526 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 565 | 435 | 583 | 583 | 525 | 525 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 51 | 143 | 143 | 143 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2536.5 | 2686.5 | 5805.22 | 5775.22 | 2813.36 | 3088.36
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 8 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 13 | 0 | 13 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 95 | 96 | 99 | 99 | 99 | 99 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 215 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 30 | 24 | 56 | 8 | 8 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 8 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 28 | 30 | 40 | 30 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 25 | 70 | 108 | 108 | 18 | 30 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.5 | 0 | 3.54 | 0 | 3.54 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 54.36 | 54.36 | 54.36 | 0 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 68 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 17 | 0 | 163 | 163 | 17 | 17 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1165 | 1158 | 1224 | 1224 | 1200 | 1200 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 29 | 5 | 48 | 41 | 48 | 41 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1120 | 1115 | 720 | 1150 | 1135 | 1135 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2707.5 | 3036.36 | 3608.4 | 4112.86 | 3170.54 | 3279
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 190 | 204 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 290 | 350.01 | 350.01 | 290 | 290 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 240 | 220 | 342.01 | 342.01 | 240 | 240 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 220 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 40 | 40 | 41.65 | 41.65 | 41.65 | 41.65 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 25 | 5 | 52.82 | 52.82 | 25 | 25 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 3 | 150 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 23 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 138 | 163 | 163 | 140 | 140 | Low gas pressure
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 11 | 68 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 168 | 164 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 24.5 | 24.5 | 17 | 17 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 32 | 62 | 114 | 114 | 17 | 17 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 6 | 89 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 62 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1523 | 1758 | 2749.44 | 2688.44 | 1646.1 | 1837.1
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-07-2026 | during | 03-07-2026 | during | 03-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 12.3 | 0 | 10 | 0 | 10 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.6 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 156 | 120 | 160 | 70 | 110 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 68 | 60 | 70 | 60 | 80 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 15.76 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 18 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 204.66 | 259 | 526.5 | 516.5 | 190 | 207
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 29 | 29 | 28 | 28 | 29 | 29 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 150 | 138 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 142 | 142 | 145 | 145 | 145 | 145 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 25 | 25 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 83 | 83 | 83 | 52 | 84 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 98 | 102 | 102 | 102 | 102 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 330 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 217 | 76 | 300 | 300 | 245 | 245 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1059 | 937 | 1247 | 1247 | 1074 | 1106
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 878 | 879 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 103 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 152 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1057 | 1190 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2076 | 2259 | 3539.2 | 3454.2 | 2932.2 | 2847.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 1035 | 1050 | 1050 | 1050 | 1050 | 1050 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 80 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 65 | 63 | 65 | 65 | 65 | 65 | GT-1 Normal Shutdown Due to Major inspection(MI)
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1050 | 1190 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 25 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 280 | 276 | 307 | 307 | 307 | 307 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.2 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2650.2 | 2904 | 3147 | 3146 | 2920 | 2919
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 17.95 | 0 | 0 | 0 | 0 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 156 | 138 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 145 | 125 | 220 | 220 | 145 | 145 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 143 | 125 | 220 | 220 | 145 | 145 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 384 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 3.23 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1145.18 | 1479.81 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 44.54 | 0 | 55 | 0 | 55 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 49 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2117.9 | 2502.81 | 3203.72 | 3043.12 | 2548.14 | 2564.54
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 39 | 37 | 40 | 40 | 40 | 40 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 200 | 138 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 104 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.7 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 95 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 194 | 0 | 185.9 | 0 | 185.9 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 452.7 | 374 | 720.9 | 502 | 587.9 | 404
System Total |  |  |  |  | 28843.2 | 29323.517 | 15327.46 | 16716.67 | 24547.38 | 24485.34 | 17882.24 | 18252.2
Forecast Scenario (03-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15972.64 |  | 820 |  | 16792.64
|  |  |  | 1:00 | 15696.64 |  | 790 |  | 16486.64
|  |  |  | 2:00 | 15475.64 |  | 730 |  | 16205.64
|  |  |  | 3:00 | 15446.64 |  | 590 |  | 16036.64
|  |  |  | 4:00 | 15310 |  | 470 |  | 15780
|  |  |  | 5:00 | 14770 |  | 450 |  | 15220
|  |  |  | 6:00 | 13550 |  | 340 |  | 13890
|  |  |  | 7:00 | 13360 |  | 0 |  | 13360
|  |  |  | 8:00 | 13200 |  | 0 |  | 13200
|  |  |  | 9:00 | 13200 |  | 0 |  | 13200
|  |  |  | 10:00 | 13020 |  | 0 |  | 13020
|  |  |  | 11:00 | 13150 |  | 0 |  | 13150
|  |  |  | 12:00 | 13730 |  | 0 |  | 13730
|  |  |  | 13:00 | 14630 |  | 0 |  | 14630
|  |  |  | 14:00 | 14290 |  | 0 |  | 14290
|  |  |  | 15:00 | 14440 |  | 0 |  | 14440
|  |  |  | 16:00 | 13940 |  | 0 |  | 13940
|  |  |  | 17:00 | 13710 |  | 0 |  | 13710
|  |  |  | 18:00 | 13360 |  | 0 |  | 13360
|  |  |  | 18:30 | 13900 |  | 0 |  | 13900
|  |  |  | 19:00 | 14520 |  | 0 |  | 14520
|  |  |  | 19:30 | 15660 |  | 0 |  | 15660
|  |  |  | 20:00 | 15830 |  | 0 |  | 15830
|  |  |  | 21:00 | 16340 |  | 0 |  | 16340
|  |  |  | 22:00 | 16377.64 |  | 11.8038 |  | 16390
|  |  |  | 23:00 | 16365.64 |  | 519.8638 |  | 16910
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 13730.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16340.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16340.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 349.68484 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:52 hrs on 03-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 02-07-2026 | [28 empty] | Date: | 02-07-2026 | [28 empty] | Date: | 02-07-2026 | [28 empty] | Date: | 02-07-2026 | [28 empty] | Date: | 02-07-2026 | [18 empty] | Date: | 02-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [18 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 15.8 | 17 | 115 | 147 | 95 | 15 | 35 | 66 | 0 | 0 | 309 | 450 | 0 | 17 | 300 | 0 | 0 | 0 | 143 | 15.5 | 21 | 0 | 450 | 13 | 16 | 60 | 0 | 32 | 50 | 0 | 38 | 12 | 12 | 0 | 98 | 107 | 34 | 1135 | 0 | 0 | 50 | 8 | 90 | 218 | 0 | 0 | 0 | 1160 | 0 | 30 | 0 | 230 | 290 | 240 | 51 | 25 | 203 | 40 | 47 | 139 | 38 | 0 | 17 | 46 | 158 | 16 | 0 | 24 | 320 | 0 | 229 | 29 | 0 | 131 | 0 | 16 | 0 | 83 | 25 | 142 | 0 | 98 | 17 | 78 | 0 | 107 | 0 | 0 | 0 | 0 | 8727.3 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1418.7 | 0 | 40 | 0 | 35 | 35 | 0 | 42 | 18 | 0 | 0 | 0 | 21 | 0 | 0 | 156 | 0 | 144 | 0 | 142 | 0 | 414 | 0 | 0 | 180 | 37 | 95 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 241 | 65 | 220 | 0 | 881 | 1190 | 17 | 7547.7 | 16275 | 76.04
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 0 | 59 | 147 | 95 | 15 | 35 | 72 | 0 | 0 | 292 | 470 | 0 | 0 | 300 | 0 | 0 | 0 | 123 | 15.5 | 21 | 0 | 460 | 15 | 16 | 30 | 0 | 16 | 50 | 0 | 0 | 12 | 12 | 0 | 99 | 106 | 34 | 1135 | 0 | 0 | 50 | 0 | 101 | 219 | 0 | 0 | 0 | 1165 | 0 | 50 | 0 | 230 | 290 | 240 | 51 | 25 | 203 | 40 | 49 | 139 | 71 | 0 | 17 | 62 | 154 | 25 | 0 | 23 | 315 | 0 | 229 | 29 | 0 | 134 | 0 | 16 | 0 | 52 | 25 | 143 | 0 | 100 | 0 | 68 | 0 | 88 | 0 | 0 | 0 | 0 | 8460.5 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1339.56 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 20 | 0 | 0 | 0 | 21 | 0 | 0 | 154 | 0 | 145 | 0 | 141 | 0 | 414 | 0 | 0 | 180 | 36 | 95 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 222 | 65 | 220 | 0 | 905 | 1125 | 17 | 7363.56 | 15824.06 | 76
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 35 | 147 | 95 | 15 | 0 | 0 | 0 | 0 | 298 | 460 | 0 | 0 | 300 | 0 | 0 | 0 | 123 | 15.5 | 21 | 0 | 480 | 0 | 0 | 24 | 0 | 20 | 0 | 0 | 0 | 12 | 12 | 0 | 97 | 107 | 34 | 1135 | 0 | 0 | 50 | 0 | 51 | 218 | 0 | 0 | 0 | 1163 | 0 | 60 | 0 | 230 | 290 | 240 | 51 | 25 | 203 | 40 | 0 | 139 | 84 | 0 | 17 | 62 | 154 | 25 | 0 | 23 | 310 | 0 | 229 | 29 | 0 | 137 | 0 | 16 | 0 | 50 | 25 | 140 | 0 | 100 | 0 | 49 | 0 | 9 | 0 | 0 | 0 | 0 | 8027.5 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1269.99 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 145 | 0 | 141 | 0 | 414 | 0 | 0 | 180 | 38 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 220 | 65 | 220 | 0 | 893 | 1050 | 17 | 7093.99 | 15121.49 | 75.99
03:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 34 | 147 | 45 | 15 | 0 | 0 | 0 | 0 | 298 | 505 | 0 | 0 | 280 | 0 | 0 | 0 | 123 | 16 | 21 | 0 | 500 | 0 | 0 | 24 | 0 | 21 | 0 | 0 | 0 | 12 | 12 | 0 | 95 | 68 | 34 | 1135 | 0 | 0 | 15 | 0 | 17 | 220 | 0 | 0 | 0 | 1165 | 0 | 60 | 0 | 230 | 290 | 240 | 51 | 25 | 207 | 40 | 0 | 139 | 17 | 0 | 17 | 0 | 146 | 25 | 0 | 23 | 310 | 0 | 229 | 29 | 0 | 144 | 0 | 16 | 0 | 52 | 25 | 143 | 0 | 100 | 0 | 49 | 0 | 9 | 0 | 0 | 0 | 0 | 7793 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1237.47 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 145 | 0 | 141 | 0 | 414 | 0 | 0 | 180 | 37 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 230 | 65 | 220 | 0 | 941 | 1015 | 17 | 7003.47 | 14796.47 | 75.98
04:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 34 | 147 | 0 | 15 | 0 | 0 | 0 | 0 | 298 | 510 | 0 | 0 | 281 | 0 | 0 | 0 | 123 | 15 | 21 | 0 | 475 | 0 | 0 | 25 | 0 | 24 | 0 | 0 | 0 | 0 | 12 | 0 | 93 | 67 | 35 | 1135 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1163 | 0 | 40 | 0 | 230 | 290 | 240 | 51 | 25 | 202 | 37 | 0 | 140 | 0 | 0 | 17 | 0 | 144 | 0 | 0 | 23 | 315 | 0 | 244 | 29 | 0 | 142 | 0 | 16 | 0 | 50 | 25 | 141 | 0 | 100 | 0 | 49 | 0 | 9 | 0 | 0 | 0 | 0 | 7628 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 0 | 0 | 0 | 1223.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 145 | 0 | 143 | 0 | 414 | 0 | 0 | 180 | 37 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 65 | 220 | 0 | 909 | 1015 | 0 | 6807.31 | 14435.31 | 75.97
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 34 | 147 | 0 | 15 | 0 | 0 | 0 | 0 | 291 | 495 | 0 | 0 | 282 | 0 | 0 | 0 | 123 | 15.5 | 21 | 0 | 450 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 12 | 0 | 93 | 34 | 37 | 1135 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1168 | 0 | 30 | 0 | 230 | 290 | 240 | 51 | 25 | 201 | 40 | 0 | 140 | 0 | 0 | 17 | 0 | 142 | 0 | 0 | 23 | 320 | 0 | 244 | 29 | 0 | 139 | 0 | 16 | 0 | 53 | 25 | 141 | 0 | 101 | 0 | 49 | 0 | 9 | 0 | 0 | 0 | 0 | 7541.5 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 1225.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 145 | 0 | 143 | 0 | 414 | 0 | 0 | 180 | 37 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 65 | 220 | 0 | 872 | 1008 | 0 | 6759.54 | 14301.04 | 75.96
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 34 | 147 | 0 | 15 | 0 | 0 | 0 | 0 | 285 | 450 | 0 | 0 | 280 | 0 | 0 | 1 | 123 | 15.5 | 21 | 0 | 430 | 0 | 0 | 24 | 0 | 31 | 0 | 0 | 0 | 0 | 12 | 0.28 | 94 | 0 | 37 | 1050 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1070 | 1 | 12 | 0 | 230 | 290 | 240 | 51 | 25 | 196 | 40 | 0 | 140 | 0 | 0 | 17 | 0 | 138 | 0 | 5 | 23 | 315 | 0 | 244 | 29 | 0 | 131 | 1 | 8 | 0 | 53 | 30 | 141 | 0 | 100 | 0 | 48 | 1.24 | 47 | 0 | 0 | 1.24 | 0 | 7245.26 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5.99 | 1030 | 0 | 0 | 0 | 1226.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.72 | 4 | 0 | 0 | 2.86 | 155 | 0 | 145 | 0 | 143 | 0 | 350 | 0 | 0.3 | 180 | 37 | 0 | 1 | 34 | 0 | 0 | 0 | 0 | 9 | 0.03 | 0 | 208 | 65 | 220 | 0 | 869 | 1002 | 0 | 6607.14 | 13852.4 | 75.95
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 147 | 0 | 15 | 0 | 0 | 0 | 0 | 297 | 485 | 0 | 0 | 281 | 0 | 0 | 6 | 123 | 16 | 21 | 0 | 470 | 0 | 0 | 21 | 0 | 21 | 0 | 0 | 0 | 0 | 12 | 1.09 | 95 | 0 | 33 | 1050 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1007 | 4 | 12 | 0 | 230 | 290 | 240 | 51 | 25 | 200 | 40 | 0 | 140 | 0 | 0 | 17 | 0 | 128 | 0 | 19 | 23 | 320 | 0 | 244 | 29 | 0 | 140 | 2 | 8 | 0 | 53 | 30 | 140 | 0 | 100 | 0 | 49 | 2.2 | 46 | 0 | 0.1 | 0.66 | 0 | 7302.05 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.19 | 1017 | 0 | 0 | 0 | 1223.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.45 | 17 | 0 | 0 | 10.46 | 156 | 0 | 145 | 0 | 143 | 0 | 350 | 0 | 0 | 180 | 37 | 0 | 2 | 34 | 0 | 0 | 0 | 0.9 | 50 | 0.05 | 0 | 222 | 65 | 220 | 0 | 897 | 1008 | 0 | 6711.21 | 14013.26 | 75.94
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 34 | 147 | 0 | 15 | 0 | 0 | 0 | 0 | 300 | 475 | 0 | 0 | 281 | 0 | 0 | 10 | 123 | 16 | 21 | 0 | 460 | 0 | 0 | 22 | 0 | 23 | 0 | 0 | 0 | 0 | 12 | 2.23 | 95 | 0 | 10 | 1050 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 1005 | 8 | 0 | 0 | 230 | 290 | 240 | 51 | 25 | 205 | 40 | 0 | 138 | 0 | 0 | 17 | 0 | 134 | 0 | 36 | 23 | 315 | 0 | 244 | 29 | 0 | 135 | 4 | 16 | 0 | 53 | 30 | 141 | 0 | 100 | 0 | 49 | 2.65 | 46 | 0 | 0.5 | 2.3 | 0 | 7278.68 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21.03 | 1050 | 0 | 0 | 0 | 1213.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.78 | 45 | 0 | 0 | 15 | 156 | 0 | 145 | 0 | 143 | 0 | 350 | 0 | 1.52 | 180 | 38 | 0 | 11 | 34 | 0 | 0 | 0 | 2.2 | 71 | 0.14 | 0 | 216 | 65 | 220 | 0 | 884 | 992 | 0 | 6782.65 | 14061.33 | 75.93
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 34 | 145 | 15 | 15 | 0 | 17 | 0 | 0 | 291 | 495 | 0 | 0 | 281 | 0 | 0 | 27 | 51 | 16 | 21 | 0 | 440 | 0 | 0 | 24 | 0 | 17 | 0 | 0 | 0 | 0 | 12 | 3.21 | 97 | 0 | 3 | 1050 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1000 | 8 | 0 | 0 | 230 | 290 | 240 | 51 | 25 | 200 | 40 | 0 | 138 | 0 | 0 | 17 | 0 | 140 | 0 | 36 | 23 | 315 | 0 | 224 | 29 | 0 | 138 | 5 | 16 | 0 | 53 | 30 | 141 | 0 | 100 | 0 | 49 | 4.49 | 48 | 0 | 1.1 | 8.34 | 0 | 7232.14 | 878 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 76.62 | 1050 | 0 | 0 | 0 | 1212.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.42 | 65 | 0 | 0 | 21.2 | 155 | 0 | 145 | 0 | 143 | 0 | 350 | 0 | 3.74 | 201 | 38 | 0 | 9 | 34 | 0 | 0 | 0 | 5.7 | 108 | 0.24 | 0 | 218 | 65 | 220 | 0 | 871 | 1000 | 0 | 6937.57 | 14169.71 | 75.92
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 0 | 34 | 145 | 15 | 15 | 17 | 17 | 0 | 0 | 305 | 510 | 0 | 0 | 303 | 0 | 0 | 15 | 51 | 16 | 21 | 0 | 535 | 0 | 0 | 25 | 0 | 19 | 0 | 0 | 0 | 0 | 12 | 4.08 | 97 | 0 | 4 | 1050 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 1005 | 16 | 0 | 0 | 230 | 290 | 240 | 51 | 25 | 202 | 35 | 0 | 136 | 0 | 0 | 17 | 0 | 148 | 0 | 63 | 23 | 320 | 0 | 228 | 29 | 0 | 145 | 9 | 16 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 49 | 11 | 48 | 0 | 1.3 | 22.21 | 0 | 7493.59 | 878 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 94.09 | 1050 | 0 | 0 | 0 | 1152.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.71 | 49 | 0 | 0 | 9.31 | 155 | 0 | 145 | 0 | 143 | 0 | 350 | 0 | 2.12 | 201 | 40 | 0 | 13 | 0 | 0 | 0 | 0 | 3.1 | 126 | 0.26 | 0 | 237 | 65 | 220 | 0 | 942 | 990 | 0 | 6949.69 | 14443.28 | 75.9
11:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 17 | 0 | 61 | 95 | 95 | 15 | 35 | 17 | 0 | 0 | 304 | 495 | 0 | 0 | 313 | 0 | 0 | 7 | 51 | 15.5 | 21 | 0 | 530 | 0 | 0 | 25 | 0 | 34 | 0 | 0 | 0 | 0 | 12 | 3.85 | 97 | 0 | 2 | 1120 | 13 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 1150 | 15 | 0 | 0 | 230 | 290 | 240 | 51 | 25 | 209 | 37 | 0 | 134 | 0 | 0 | 17 | 0 | 138 | 0 | 70 | 23 | 320 | 0 | 228 | 29 | 0 | 153 | 8 | 16 | 0 | 52 | 27 | 142 | 0 | 101 | 0 | 58 | 10.42 | 62 | 0 | 2.4 | 30.65 | 0 | 7859.82 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 68 | 1050 | 0 | 0 | 0 | 1107.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.77 | 65 | 0 | 0 | 41.33 | 156 | 0 | 145 | 0 | 143 | 0 | 414 | 0 | 2.07 | 201 | 40 | 0 | 6 | 0 | 0 | 0 | 0 | 4.1 | 200 | 0.1 | 0 | 238 | 65 | 220 | 0 | 950 | 1030 | 0 | 7089.93 | 14949.75 | 75.9
12:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 17 | 15 | 79 | 144 | 112 | 15 | 35 | 17 | 0 | 0 | 303 | 565 | 0 | 0 | 324 | 0 | 0 | 17 | 51 | 15.5 | 21 | 0 | 385 | 0 | 0 | 25 | 0 | 29 | 0 | 0 | 0 | 8 | 12 | 4.5 | 95 | 0 | 2 | 1120 | 17 | 0 | 0 | 1 | 0 | 212 | 0 | 0 | 0 | 1165 | 17 | 3 | 0 | 230 | 290 | 240 | 51 | 25 | 190 | 40 | 6 | 136 | 11 | 0 | 17 | 32 | 168 | 0 | 62 | 22 | 320 | 0 | 217 | 29 | 0 | 150 | 8 | 16 | 0 | 52 | 25 | 142 | 0 | 100 | 0 | 59 | 12.3 | 115 | 0 | 2.6 | 15.76 | 0 | 8030.66 | 878 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 103 | 1057 | 0 | 0 | 0 | 1145.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.95 | 49 | 0 | 0 | 44.54 | 156 | 0 | 145 | 0 | 143 | 0 | 414 | 0 | 3.23 | 200 | 39 | 0 | 16 | 0 | 0 | 0 | 0 | 3.7 | 194 | 0.2 | 0 | 280 | 65 | 220 | 0 | 1035 | 1050 | 0 | 7296.8 | 15327.46 | 75.89
13:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 17 | 28 | 71 | 143 | 112 | 15 | 35 | 17 | 0 | 0 | 296 | 530 | 0 | 0 | 324 | 0 | 0 | 18 | 51 | 15.5 | 0 | 0 | 480 | 0 | 0 | 24 | 0 | 19 | 0 | 0 | 0 | 12 | 12 | 3.95 | 97 | 56 | 2 | 1120 | 17 | 0 | 33 | 6 | 0 | 211 | 0 | 0 | 0 | 1155 | 8 | 45 | 0 | 230 | 290 | 240 | 51 | 25 | 177 | 40 | 34 | 138 | 65 | 0 | 17 | 80 | 164 | 12 | 75 | 22 | 315 | 0 | 218 | 29 | 0 | 147 | 9 | 16 | 0 | 52 | 25 | 141 | 0 | 100 | 0 | 59 | 17.1 | 117 | 0 | 2.6 | 20.14 | 5 | 8346.29 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 83 | 1007 | 0 | 0 | 0 | 1153.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.56 | 62 | 0 | 0 | 23.46 | 153 | 0 | 139 | 0 | 141 | 0 | 414 | 0 | 2.12 | 200 | 39 | 0 | 18 | 0 | 0 | 0 | 0 | 4.8 | 193 | 0.23 | 0 | 280 | 63 | 220 | 0 | 1038 | 1085 | 0 | 7250.3 | 15596.59 | 75.88
14:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 27 | 70 | 95 | 112 | 15 | 35 | 17 | 0 | 0 | 308 | 480 | 0 | 0 | 322 | 0 | 0 | 33 | 51 | 15.5 | 21 | 0 | 455 | 0 | 0 | 24 | 0 | 26 | 0 | 0 | 0 | 12 | 12 | 1.32 | 95 | 103 | 2 | 1110 | 0 | 0 | 45 | 8 | 0 | 212 | 0 | 0 | 0 | 1155 | 18 | 51 | 0 | 220 | 290 | 240 | 51 | 19 | 176 | 40 | 34 | 135 | 63 | 0 | 17 | 94 | 174 | 52.2 | 65 | 22 | 315 | 0 | 218 | 29 | 0 | 144 | 11 | 16 | 0 | 51 | 25 | 142 | 0 | 101 | 0 | 59 | 19.2 | 117 | 0 | 0.8 | 23.49 | 12 | 8368.51 | 878 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29 | 1002 | 0 | 0 | 0 | 1213.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.56 | 50 | 0 | 0 | 27.14 | 145 | 0 | 131 | 0 | 133 | 0 | 414 | 0 | 2.41 | 200 | 38 | 0 | 13 | 0 | 0 | 0 | 0 | 4.9 | 187 | 0.31 | 0 | 255 | 63 | 220 | 0 | 995 | 1090 | 0 | 7142.64 | 15511.15 | 75.87
15:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 17 | 22 | 70 | 95 | 112 | 15 | 35 | 17 | 0 | 0 | 299 | 485 | 0 | 5 | 326 | 0 | 0 | 15 | 51 | 15.5 | 21 | 0 | 455 | 0 | 0 | 25 | 0 | 26 | 0 | 0 | 0 | 12 | 12 | 1.78 | 92 | 106 | 2 | 1110 | 0 | 0 | 45 | 8 | 0 | 211 | 0 | 0 | 0 | 1160 | 4 | 53 | 0 | 220 | 290 | 240 | 51 | 5 | 179 | 40 | 34 | 135 | 66 | 0 | 11 | 91 | 172 | 52.2 | 53 | 23 | 315 | 0 | 210 | 29 | 0 | 144 | 7 | 16 | 0 | 81 | 25 | 135 | 0 | 100 | 0 | 59 | 8 | 117 | 0 | 0.8 | 38.05 | 12 | 8348.33 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 43 | 1004 | 0 | 0 | 0 | 1261.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.19 | 45 | 0 | 0 | 18.44 | 141 | 0 | 126 | 0 | 127 | 0 | 414 | 0 | 1.65 | 200 | 37 | 0 | 20 | 0 | 0 | 0 | 0 | 7.8 | 122 | 0.26 | 0 | 250 | 63 | 220 | 0 | 991 | 1100 | 0 | 7152.31 | 15500.64 | 75.86
16:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 17 | 28 | 70 | 95 | 112 | 15 | 35 | 17 | 0 | 0 | 305 | 485 | 0 | 17 | 320 | 0 | 0 | 8 | 51 | 15.5 | 21 | 0 | 470 | 0 | 0 | 24 | 0 | 23 | 0 | 14 | 0 | 12 | 12 | 2.92 | 90 | 68 | 2 | 1105 | 0 | 0 | 48 | 8 | 0 | 211 | 0 | 0 | 0 | 1160 | 5 | 51 | 0 | 220 | 290 | 240 | 51 | 5 | 180 | 40 | 34 | 134 | 34 | 0 | 11 | 95 | 164 | 25 | 27 | 23 | 320 | 0 | 0 | 29 | 0 | 145 | 7 | 16 | 0 | 80 | 25 | 136 | 0 | 100 | 0 | 59 | 4 | 116 | 0 | 0.6 | 25.65 | 12 | 8040.67 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 1035 | 0 | 0 | 0 | 1282.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.64 | 47 | 0 | 0 | 17.45 | 141 | 0 | 128 | 0 | 127 | 0 | 414 | 0 | 1.5 | 178 | 36 | 0 | 17 | 0 | 0 | 0 | 0 | 6.4 | 76 | 0.23 | 0 | 258 | 63 | 220 | 0 | 1004 | 1100 | 0 | 7116.78 | 15157.45 | 75.85
17:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 28 | 70 | 95 | 112 | 15 | 35 | 17 | 0 | 0 | 303 | 465 | 0 | 17 | 320 | 0 | 0 | 10 | 51 | 15.5 | 21 | 0 | 440 | 0 | 0 | 27 | 0 | 55 | 0 | 22 | 0 | 12 | 12 | 0.29 | 89 | 67 | 7 | 1105 | 0 | 0 | 50 | 8 | 0 | 212 | 0 | 0 | 0 | 1170 | 4 | 53 | 0 | 220 | 290 | 240 | 51 | 5 | 190 | 40 | 34 | 135 | 30 | 2 | 17 | 93 | 166 | 25 | 18 | 23 | 325 | 0 | 0 | 29 | 0 | 144 | 3 | 16 | 0 | 81 | 25 | 136 | 0 | 100 | 0 | 59 | 3.7 | 116 | 0 | 0.6 | 9.81 | 12 | 8043.9 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 1000 | 0 | 0 | 0 | 1316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.77 | 35 | 0 | 0 | 5.86 | 140 | 0 | 128 | 0 | 126 | 0 | 396 | 0 | 0.55 | 180 | 36 | 0 | 9 | 0 | 0 | 0 | 0 | 1.3 | 36 | 0.23 | 0 | 216 | 63 | 220 | 0 | 911 | 1090 | 0 | 6859.71 | 14903.61 | 75.84
18:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 28 | 70 | 95 | 146 | 15 | 35 | 35 | 0 | 0 | 303 | 445 | 0 | 35 | 323 | 0 | 0 | 2 | 51 | 15.5 | 21 | 0 | 465 | 0 | 0 | 38 | 0 | 41 | 0 | 30 | 0 | 12 | 12 | 0.18 | 90 | 68 | 14 | 1050 | 0 | 0 | 50 | 8 | 0 | 213 | 0 | 0 | 0 | 1116 | 1 | 53 | 0 | 220 | 290 | 240 | 51 | 5 | 195 | 40 | 34 | 135 | 29 | 8 | 17 | 64 | 146 | 25 | 4 | 23 | 330 | 0 | 0 | 29 | 0 | 134 | 1 | 16 | 0 | 80 | 30 | 134 | 0 | 100 | 0 | 59 | 2.01 | 117 | 0 | 0.3 | 3.1 | 16 | 7956.09 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 988 | 0 | 0 | 0 | 1314.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.94 | 6 | 0 | 0 | 3.21 | 140 | 0 | 127 | 0 | 126 | 0 | 391 | 0 | 0.4 | 180 | 36 | 0 | 2 | 0 | 0 | 0 | 0 | 1.6 | 15 | 0.05 | 0 | 223 | 63 | 220 | 0 | 896 | 1030 | 0 | 6686.96 | 14643.05 | 75.84
19:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 36 | 28 | 91 | 145 | 146 | 15 | 35 | 108 | 0 | 0 | 307 | 450 | 0 | 35 | 320 | 0 | 0 | 0 | 86 | 15.5 | 21 | 0 | 490 | 3 | 16 | 51 | 0 | 17 | 40 | 30 | 2 | 12 | 12 | 0 | 94 | 71 | 16 | 1080 | 0 | 0 | 50 | 10 | 1 | 213 | 0 | 0 | 0 | 1160 | 0 | 58 | 0 | 220 | 290 | 220 | 51 | 5 | 206 | 40 | 34 | 135 | 32 | 9 | 17 | 63 | 174 | 25 | 0 | 23 | 330 | 0 | 0 | 29 | 0 | 137 | 0 | 16 | 0 | 81 | 25 | 141 | 0 | 100 | 1 | 59 | 0 | 126 | 0 | 0 | 0 | 18 | 8352.5 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1008 | 0 | 0 | 0 | 1431.79 | 0 | 0 | 0 | 35 | 1 | 0 | 100 | 19 | 0 | 0 | 0 | 21 | 0 | 0 | 140 | 0 | 125 | 0 | 126 | 0 | 383 | 0 | 0 | 180 | 37 | 55 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 223 | 63 | 220 | 0 | 906 | 1020 | 4 | 7159.79 | 15512.29 | 75.83
19:30 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 36 | 28 | 114 | 144 | 146 | 15 | 35 | 108 | 0 | 0 | 285 | 418 | 0 | 35 | 324 | 0 | 0 | 0 | 143 | 15.5 | 21 | 0 | 400 | 15 | 16 | 65 | 0 | 17 | 50 | 30 | 54.36 | 12 | 12 | 0 | 95 | 85 | 20 | 1125 | 0 | 0 | 50 | 25.5 | 87 | 213 | 0 | 0 | 0 | 1105 | 0 | 120 | 0 | 220 | 290 | 220 | 51 | 5 | 206 | 40 | 90 | 136 | 118 | 9 | 17 | 75 | 168 | 30 | 0 | 23 | 330 | 0 | 7 | 29 | 0 | 146 | 0 | 16 | 0 | 81 | 25 | 142 | 0 | 100 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 18 | 8780.36 | 878 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1142 | 0 | 0 | 0 | 1477.68 | 0 | 0 | 0 | 70 | 50 | 0 | 100 | 19 | 0 | 0 | 0 | 21 | 0 | 0 | 139 | 0 | 123 | 0 | 124 | 0 | 383 | 0 | 0 | 163 | 37 | 90 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 226 | 63 | 220 | 0 | 1050 | 1120 | 40 | 7731.68 | 16512.04
20:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 36 | 28 | 115 | 144 | 146 | 15 | 35 | 108 | 0 | 0 | 287 | 450 | 0 | 35 | 300 | 0 | 0 | 0 | 143 | 15.5 | 21 | 0 | 400 | 15 | 16 | 65 | 0 | 21 | 50 | 30 | 54.36 | 12 | 12 | 0 | 95 | 105 | 24 | 1125 | 0 | 0 | 50 | 25.5 | 81 | 214 | 0 | 0 | 0 | 1130 | 0 | 150 | 0 | 220 | 290 | 220 | 51 | 5 | 202 | 40 | 72 | 136 | 108 | 9 | 17 | 73 | 170 | 30 | 0 | 23 | 330 | 0 | 9 | 29 | 0 | 146 | 0 | 16 | 0 | 82 | 25 | 140 | 0 | 100 | 17 | 68 | 0 | 155 | 0 | 0 | 0 | 18 | 8810.36 | 878 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1174 | 0 | 0 | 0 | 1483.66 | 0 | 39 | 0 | 70 | 60 | 0 | 100 | 20 | 0 | 0 | 0 | 21 | 0 | 0 | 138 | 0 | 123 | 0 | 124 | 0 | 300 | 0 | 0 | 160 | 37 | 90 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 210 | 63 | 180 | 0 | 1050 | 1160 | 54 | 7778.66 | 16589.02 | 75.8
21:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 36 | 28 | 115 | 144 | 146 | 15 | 0 | 108 | 0 | 0 | 291 | 435 | 0 | 35 | 293 | 0 | 0 | 0 | 143 | 15.5 | 21 | 0 | 430 | 15 | 16 | 70 | 0 | 5 | 50 | 30 | 54.36 | 12 | 12 | 0 | 96 | 68 | 28 | 1115 | 0 | 0 | 50 | 8 | 34 | 215 | 0 | 0 | 0 | 1158 | 0 | 150 | 0 | 220 | 290 | 220 | 51 | 5 | 204 | 40 | 89 | 138 | 68 | 9 | 17 | 62 | 164 | 8 | 0 | 23 | 330 | 0 | 76 | 29 | 0 | 138 | 0 | 16 | 0 | 83 | 25 | 142 | 0 | 98 | 17 | 68 | 0 | 156 | 0 | 0 | 0 | 18 | 8676.86 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 152 | 0 | 0 | 0 | 1190 | 0 | 0 | 0 | 1479.81 | 0 | 40 | 0 | 35 | 35 | 0 | 100 | 20 | 0 | 0 | 0 | 21 | 0 | 0 | 138 | 0 | 125 | 0 | 125 | 0 | 384 | 0 | 0 | 138 | 37 | 95 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 276 | 63 | 220 | 0 | 1050 | 1190 | 25 | 8039.81 | 16716.67 | 75.8
22:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 36 | 28 | 115 | 127 | 146 | 15 | 0 | 108 | 0 | 0 | 302 | 425 | 0 | 35 | 298 | 0 | 0 | 0 | 143 | 15.5 | 21 | 0 | 433 | 15 | 16 | 72 | 0 | 15 | 50 | 23 | 17 | 12 | 12 | 0 | 96 | 51 | 30 | 1115 | 0 | 0 | 40 | 0 | 28 | 216 | 0 | 0 | 0 | 1165 | 0 | 33 | 0 | 220 | 290 | 220 | 51 | 5 | 202 | 40 | 86 | 138 | 17 | 10 | 17 | 50 | 162 | 8 | 0 | 23 | 330 | 0 | 76 | 29 | 0 | 152 | 0 | 16 | 0 | 83 | 20 | 139 | 0 | 99 | 17 | 69 | 0 | 156 | 0 | 0 | 0 | 18 | 8419.5 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 130 | 0 | 0 | 0 | 1185 | 0 | 0 | 0 | 1481.61 | 0 | 39 | 0 | 35 | 35 | 0 | 100 | 20 | 0 | 0 | 0 | 21 | 0 | 0 | 138 | 0 | 126 | 0 | 125 | 0 | 388 | 0 | 0 | 180 | 37 | 95 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 275 | 63 | 220 | 0 | 1050 | 1190 | 17 | 8037.61 | 16457.11 | 75.79
23:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 28 | 75 | 95 | 136 | 15 | 17 | 72 | 0 | 0 | 308 | 485 | 0 | 35 | 302 | 0 | 0 | 0 | 143 | 15.5 | 21 | 0 | 510 | 13 | 16 | 48 | 0 | 22 | 50 | 23 | 17 | 12 | 12 | 0 | 97 | 34 | 31 | 1115 | 0 | 0 | 32 | 0 | 17 | 216 | 0 | 0 | 0 | 1162 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 5 | 199 | 40 | 66 | 138 | 17 | 9 | 17 | 49 | 174 | 8 | 0 | 23 | 330 | 0 | 74 | 29 | 0 | 148 | 0 | 16 | 0 | 83 | 20 | 141 | 0 | 98 | 17 | 69 | 0 | 146 | 0 | 0 | 0 | 18 | 8336.5 | 979 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 130 | 0 | 0 | 0 | 1190 | 0 | 0 | 0 | 1482.1 | 0 | 39 | 0 | 35 | 35 | 0 | 100 | 20 | 0 | 0 | 0 | 21 | 0 | 0 | 138 | 0 | 126 | 0 | 125 | 0 | 383 | 0 | 0 | 180 | 36 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 277 | 65 | 220 | 0 | 1050 | 1190 | 17 | 8053.1 | 16389.6 | 75.78
Total KWH | 0 | 825600 | 195245 | 0 | 0 | 0 | 0 | 0 | 9061200 | 0 | 0 | 264240 | 360360 | 1493712 | 3047520 | 2021825 | 379511 | 465188 | 789120 | 0 | 0 | 7243578 | 11663845 | 0 | 270458 | 7301249 | 0 | 0 | 176086 | 2422800 | 378600 | 488160 | 0 | 10949545.45 | 107891 | 102873 | 821760 | 0 | 581760 | 342547 | 207340 | 215050 | 187200 | 290880 | 28559 | 2274760 | 1350727 | 438720 | 26472727.27 | 53527 | 0 | 702720 | 94033.8 | 501818 | 5077382 | 0 | 0 | 0 | 27043634 | 115830 | 1006981 | 0 | 5566500 | 7321400 | 5760000 | 1244072 | 409440 | 4840000 | 944640 | 697920 | 3320911 | 810240 | 57120 | 392330 | 1059060 | 3738240 | 363706 | 527536 | 556176 | 7737000 | 0 | 3957000 | 693000 | 0 | 3428672.73 | 74153 | 373296 | 0 | 1547520 | 617280 | 3246000 | 0 | 2395730 | 95400 | 1352400 | 91170 | 2030400 | 0 | 12900 | 216060 | 181440 | 193475275.25 | 21305455 | 0 | 0 | 0 | 0 | 912000 | 0 | 0 | 462258 | 0 | 26208 | 586080 | 25709090 | 0 | 0 | 0 | 30496000 | 0 | 230271 | 0 | 287520 | 371520 | 0 | 577840 | 119928 | 0 | 269384 | 551611 | 134000 | 0 | 288688 | 3581727 | 0 | 3488073 | 0 | 3480800 | 0 | 9322109 | 0 | 27420 | 4564000 | 893236 | 851518 | 156529 | 1001443 | 0 | 0 | 0 | 47517.6 | 1323360 | 2172 | 458400 | 5781000 | 1533000 | 5386940 | 0 | 23061818 | 26286545.45 | 186000 | 173761461.05 | 367236736.3

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 02-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 15327.46 | MW | 12:00 Hr. | Energy Generated |  |  | 367.2367 |  | MKWHr.
| Day Peak Demand |  |  | 15659.46 | MW | 12:00 Hr. | Energy Unserverd |  |  | 8.511 |  | MKWHr.
| Evening Peak Generation |  |  | 16716.67 | MW | 21:00 Hr. | Energy Demand |  |  | 375.7477 |  | MKWHr.
| Evening Peak Demand |  |  | 17232.67 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.5 |  | °C
| Minimum Generation of the Day |  |  | 13852.4 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 950.18 |  | MMCFD
| Maximum Generation of the Day |  |  | 16716.67 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.3748 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 47.0862 | 0 | 12.5356 | 0 | 0 | 0.17609 | 0 | 0 | 59.7978 | Gas | 133.1897 | Gas | 448444258.9181
| Chattogram Zone |  |  | 5.5161 | 53.5164 | 4.9784 | 0 | 2.2748 | 0.14439 | 0 | 0.58176 | 67.0117 | Coal | 139.8121 | Coal | 931113962.0116
| Cumilla Zone |  |  | 29.7993 | 0 | 4.5512 | 0 | 0 | 0.52754 | 3.7382 | 0 | 38.6163 | HFO | 29.9694 | HFO | 525913730.798
| Mymensingh Zone |  |  | 0 | 0 | 3.6596 | 0 | 0 | 0.32013 | 0 | 0 | 3.9798 | HSD | 0.46226 | HSD | 9337611.6
| Sylhet Zone |  |  | 23.9955 | 0 | 0 | 0 | 0 | 0.074153 | 0 | 0 | 24.0697 | Hydro | 2.2748 | Hydro | 8666835.6
| Khulna Zone |  |  | 0 | 25.7091 | 0.026208 | 0.46226 | 0 | 0.58608 | 22.2175 | 0 | 49.0011 | Solar | 4.4951 | Solar | 72064121.112
| Barishal Zone |  |  | 6.9199 | 55.1294 | 0.6444 | 0 | 0 | 0.002172 | 0 | 0 | 62.6959 | Import | 56.4517 | Import | 336952498
| Rajshahi Zone |  |  | 19.8727 | 0 | 1.7211 | 0 | 0 | 1.1371 | 30.496 | 0 | 53.2269 | Wind | 0.58176 | Wind | 8557689.6
| Rangpur Zone |  |  | 0 | 5.4572 | 1.853 | 0 | 0 | 1.5274 | 0 | 0 | 8.8376
| Total |  |  | 133.1897 | 139.8121 | 29.9694 | 0.46226 | 2.2748 | 4.4951 | 56.4517 | 0.58176 | 367.2367
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 448444258.9181 |  | Hydro | 8666835.6
|  |  |  | Coal | 931113962.0116 |  | Solar | 72064121.112
|  |  |  | HFO | 525913730.798 |  | Import | 336952498
|  |  |  | HSD | 9337611.6 |  | Wind | 8557689.6
[5 empty] | Total: | 234,10,50,707 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.3055 | Peak Hr Flow | 879.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50918509.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.496 | Peak Hr Flow | 1479.81 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2455 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.7382 | Peak Hr Flow | 164.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2759 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 55.5397 | Peak Hr Flow | 2522.81 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 67 |  | 5836
|  |  |  | Chattogram |  | 0 |  | 1579
|  |  |  | Cumilla |  | 14 |  | 1585
|  |  |  | Mymensingh |  | 280 |  | 1489
|  |  |  | Sylhet |  | 34 |  | 719
|  |  |  | Khulna |  | 99 |  | 1987
|  |  |  | Barishal |  | 0 |  | 526
|  |  |  | Rajshahi |  | 0 |  | 1685
|  |  |  | Rangpur |  | 0 |  | 1148
|  |  |  | Total |  | 494 |  | 16554
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Karnaphuli Hydro PP Unit-5 |  |  | 50
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 350 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 400
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:09 | Jashore 132/33kV S/S T-1 HT is restored.
|  | 08:10 | Jashore 132/33kV S/S T-1 LT is restored.
|  | 09:28 | Hasnabad 230/132kV S/S AUTO TR-1 HT is restored.
|  | 09:29 | Hasnabad 230/132kV S/S AUTO TR-1 LT is restored.
|  | 10:28 | BIPTC S/S 20D10A 20MVA HT is restored.
|  | 10:28 | BIPTC S/S 20D10A 20MVA LT is restored.
|  | 10:28 | BIPTC S/S Block-01, Trafo-02 HT is restored.
|  | 10:28 | BIPTC S/S Block-01, Trafo-02 LT is restored.
|  | 10:28 | BIPTC S/S Block-02, Trafo-02 HT is restored.
|  | 10:28 | BIPTC S/S Block-02, Trafo-02 LT is restored.
| 10:46 |  | BSRM 230/33kV S/S 230/33 kV Transformer-2 (125/140 MVA) HT Scheduled S/D Due to Annual
Maintenance
| 11:04 | 12:51 | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to
Suspension clamp maintenance work.
| 11:57 | 16:24 | Haripur 230/132kV S/S 132kV Reserve Bus Sec-2 Scheduled S/D Due to Busbar Protection
Work.
| 12:10 | 21:05 | Hasnabad 230/132kV S/S AUTO TR-1 HT Tripped showing 86T1,86T2,86L1,86L2 relays.
| 13:10 | 21:05 | Hasnabad 230/132kV S/S AUTO TR-1 LT Tripped showing 86T1,86T2,86L1,86L2 relays.
| 13:20 | 16:04 | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Bajitpur 132/33kV end Due to Due to
high temperature reduce maintenance at line DS
| 13:20 |  | Bhandaria-Barishal North 132KV CKT-1,2 S/D.
| 14:41 | 17:37 | Chhatak 132/33kV S/S T-1 LT Scheduled S/D Due to 33KV Doarabazar PBS Feeder DS | [7 empty] | 15.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 14:44 | 17:36 | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to 33KV Doarabazar PBS Feeder DS | [7 empty] | 15.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 15:31 |  | Bibiyana-III 400 MW CCPP Tripped with remarks:- GT
| 16:20 | 17:11 | Maijdee 132/33kV S/S Tr-02 LT Scheduled S/D Due to Maintanance the Red Hot condition at
the source side of the 33kv ABS of BREB.
| 16:20 | 17:11 | Maijdee 132/33kV S/S Tr-02 HT Scheduled S/D Due to Maintanance the Red Hot condition at
the source side of the 33kv ABS of BREB.
| 19:13 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- GT
| 04:26 | 04:47 | Chattak-Sylhet 132 kV Ckt-2 Tripped from Chhatak 132/33kV end showing Main 1 Protection | [7 empty] | 52.0MW load
|  |  | at 132 kv sunamganj-1 relays Due to Trip at sylhet end and from Sylhet 132/33kV end | [7 empty] | interrup. Chhatak
|  |  | showing 21 relays Due to Distance Protection Operated | [7 empty] | 132/33kV end and
50.0MW load
interrup. Sylhet
132/33kV end
| 04:26 | 04:40 | Chattak-Sylhet 132 kV Ckt-1 Tripped from Chhatak 132/33kV end showing no relay signal | [7 empty] | 34.0MW load
|  |  | relays Due to trip at sylhet end and from Sylhet 132/33kV end showing 21 relays Due to | [7 empty] | interrup. Chhatak
|  |  | Distance Protection Operated | [7 empty] | 132/33kV end and
35.0MW load
interrup. Sylhet
132/33kV end
| 05:57 |  | Hasnabad-Sitalakhya 132kV Ckt-1 Scheduled S/D from Hasnabad 132/33kV end Due to Red hot
maintenance work.
| 06:00 |  | Minimum generation 14097 MW
| 06:18 |  | Hasnabad 230/132kV S/S AUTO TR-1 HT Scheduled S/D Due to 132 kv main bus D/S mainance by
132kv S/S.
| 06:18 |  | Hasnabad 230/132kV S/S AUTO TR-1 LT Scheduled S/D Due to 132 kv main bus D/S mainance by
132kv S/S.
| 06:25 |  | Hasnabad 132/33kV S/S 132kV Main Bus Scheduled S/D Due to Red hot maintenance work of
Shitalakkhya ckt main bus D/S & ATR-1 main bus D/S.
| 06:43 | 06:53 | Chattak-Sylhet 132 kV Ckt-2 Tripped from Chhatak 132/33kV end showing Main 1 Protection | [7 empty] | 50.0MW load
|  |  | of 132 kv sunamganj ckt-1 relays Due to Trip at Sylhet end and from Sylhet 132/33kV end | [7 empty] | interrup. Chhatak
|  |  | showing 21 relays Due to Distance protection operated | [7 empty] | 132/33kV end and
40.0MW load
interrup. Sylhet
132/33kV end
| 07:21 |  | Aminbazar 400/230/132kV S/S Gopalganj-1 Scheduled S/D Due to Setting change by SPMD
| 07:23 |  | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 02-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 355 | 9061200 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 291 | 7243578 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 379511 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 293 | 7301249 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 36 | 264240 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 144 | 3047520 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 465188 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270458 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15.5 | 378600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 488160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 195245 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 146 | 2021825 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 1493712 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 51 | 825600 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 789120 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 176086 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 28 | 360360 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 430 | 10949545.45 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 435 | 11663845 | AGC+Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143 | 2422800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2686.5 | 59797842.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 94033.8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 115830 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 702720 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 96 | 2274760 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 215 | 5077382 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 501818 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 30 | 207340 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 342547 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 187200 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 28 | 438720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 70 | 821760 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 28559 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 102873 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 215050 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 68 | 1350727 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 290880 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 107891 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 53527 | Under Maintenance
55 | SS Power |  | IPP | 2*660 | 1224 | 1158 | 27043634 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 5 | 581760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1115 | 26472727.27 | machine problem
Chattogram Area Total |  |  |  |  | 4898.863 | 3036.36 | 67011739.07
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 204 | 4840000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7321400 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 220 | 5760000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5566500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 944640 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 409440 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1244072 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1006981 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 556176 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 138 | 3320911 | Low gas pressure
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 68 | 810240 | -
| Import (Tripura) |  | Import | 0 | 160 | 164 | 3738240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 363706 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 392330 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 62 | 1059060 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 57120 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 697920 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 527536 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1758 | 38616272
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 91170 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 156 | 2030400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1352400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 216060 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 181440 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 95400 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 259 | 3979770
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 74153 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 29 | 693000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 138 | 3428672.73 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 3246000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 25 | 617280 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1547520 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 2395730 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 373296 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 330 | 7737000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 76 | 3957000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 937 | 24069651.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 879 | 21305455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 26208 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 586080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 152 | 462258 | Liquid fuel shortage
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1190 | 25709090 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2259 | 49001091
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1050 | 23061818 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 80 | 458400 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 63 | 1533000 | GT-1 & ST under maint
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1190 | 26286545.45 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5386940 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 25 | 186000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 5781000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2172 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2904 | 62695875.45
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 269384 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 230271 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 119928 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 138 | 3581727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 125 | 3488073 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 125 | 3480800 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 384 | 9322109 | AGC
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 134000 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 577840 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 371520 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 287520 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 27420 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1479.81 | 30496000 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 288688 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 551611 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2502.81 | 53226891
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 37 | 893236 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 138 | 4564000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 104 | 1001443 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47517.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 851518 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 156529 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1323360 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 374 | 8837603.6
Eastern Grid Total |  |  |  |  | 17438.042 | 8676.86 | 193475275.25
Western Grid Total |  |  |  |  | 11885.475 | 8039.81 | 173761461.05
National Grid Total |  |  |  |  | 29323.517 | 16716.67 | 367236736.3
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 02-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10870.59 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5246.6 | MW
i) Dhaka area |  |  | 5769.29 |  | MW | i) Khulna area |  |  |  | 1888 | MW
ii) Chattogram area |  |  | 1636.3 |  | MW | ii) Barishal area |  |  |  | 526 | MW
iii) Cumilla area |  |  | 1571 |  | MW | iii) Rajshahi area |  |  |  | 1684.6 | MW
iv) Mymensingh area |  |  | 1209 |  | MW | iv) Rangpur area |  |  |  | 1148 | MW
v) Sylhet area |  |  | 685 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 16117.19 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 145 | 11:00 | 133 | Narshingdi | 193 | 00:00 | 199 | UttaraNew | 56 | 23:00
2 | AKSML | 143.2 | 03:00 | 68 | Hasnabad | 94 | 19:00 | 134 | Natore | 162 | 21:00 | 200 | Zigatola | 94 | 13:00
3 | Aftabnagar | 46 | 00:00 | 69 | Hathazari | 99 | 19:30 | 135 | Nawabganj | 65 | 22:00
4 | Agargaon | 119 | 14:00 | 70 | Hatirjheel | 49 | 12:00 | 136 | Netrakona | 125 | 07:00
5 | Agrabad | 80 | 13:00 | 71 | Ishurdi | 85 | 19:30 | 137 | New | 86 | 09:00
6 | Amnura | 32 | 22:00 | 72 | Jaldhaka | 93 | 22:00 | 138 | Niamatpur | 87 | 23:00
7 | Ashuganj | 108 | 00:00 | 73 | Jamalpur | 122 | 21:00 | 139 | Noapara | 49 | 21:00
8 | BSRM | 203 | 04:00 | 74 | Jashore | 161 | 19:30 | 140 | PHP | 8 | 00:00
9 | Bagerhat | 89 | 01:00 | 75 | Jhenaidah | 99 | 20:00 | 141 | Pabna | 102 | 19:30
10 | Bajitpur | 96 | 21:00 | 76 | Joydebpur | 157 | 11:00 | 142 | Palashbari | 138 | 23:00
11 | Bakerganj | 16 | 21:00 | 77 | Joypurhat | 72 | 00:00 | 143 | Panchagarh | 73 | 19:30
12 | Bakulia | 102 | 15:00 | 78 | Juldah | 22 | 12:00 | 144 | Patiya | 11.9 | 19:30
13 | Banani | 72 | 13:00 | 79 | KSRM | 26 | 19:30 | 145 | Patuakhali | 74 | 22:00
14 | Bangabhaban | 21 | 11:00 | 80 | Kabirpur | 269 | 19:00 | 146 | Payra | 38 | 23:00
15 | Barapukuria | 72 | 21:00 | 81 | Kachua | 104 | 22:00 | 147 | Postogola | 64 | 00:00
16 | Barguna | 24 | 19:30 | 82 | Kaliganj | 41 | 19:30 | 148 | Pubail | 40 | 06:00
17 | Barishal | 106 | 12:00 | 83 | Kallyanpur | 129 | 23:00 | 149 | Purbachal | 33 | 13:00
18 | Barishal-230 | 112 | 22:00 | 84 | Kalurghat | 42 | 15:00 | 150 | Purbasadipur | 152 | 00:00
19 | Baroaulia | 53 | 00:00 | 85 | Kamrangirchar | 80 | 12:00 | 151 | Rahanpur | 45 | 22:00
20 | Baroirhat | 71 | 19:00 | 86 | Kaptai | N/A | N/A | 152 | Rahim | 40 | 11:00
21 | Bashundhara | 216 | 19:30 | 87 | Kasba | 43 | 22:00 | 153 | Rajbari | 94 | 19:30
22 | BashundharaCement | 12 | 00:00 | 88 | Kazla | 121 | 13:00 | 154 | Rajendrapur | 114 | 09:00
23 | Beanibazar | 86 | 19:00 | 89 | Keranigonj | 89 | 19:30 | 155 | Rajshahi | 129 | 21:00
24 | Benapole | 74 | 22:00 | 90 | Khagrachori | 36 | 19:30 | 156 | Rajshahi-230 | 86 | 13:00
25 | Bhaluka | 144 | 21:00 | 91 | Khulna | 66 | 13:00 | 157 | Ramganj | 120 | 20:00
26 | Bhandaria | 62 | 22:00 | 92 | Khulshi | 180 | 17:00 | 158 | Rampur | 44 | 15:00
27 | Bhangura | 42 | 19:30 | 93 | Kishoreganj | 133 | 04:00 | 159 | Rangamati | 20 | 19:00
28 | Bheramara(GK) | 70 | 19:30 | 94 | Kodda | 315 | 19:00 | 160 | Rangpur | 148 | 20:00
29 | Bhulta | 230 | 17:00 | 95 | Kulaura | 62 | 19:00 | 161 | Ruppur | 4.6 | 11:00
30 | Bog-Sherpur | 88 | 22:00 | 96 | Kurigram | 76 | 19:30 | 162 | SSM | 3 | 04:00
31 | Bogura | 183 | 23:00 | 97 | Kushtia | 156 | 20:00 | 163 | Saidpur | 116 | 19:30
32 | Borhanuddin | 82 | 00:00 | 98 | Laksam | 30 | 23:00 | 164 | Santhia | 36 | 19:30
33 | Brahmanbaria | 136 | 00:00 | 99 | Lakshmipur | 44 | 00:00 | 165 | Satkhira | 145 | 22:00
34 | Cantonment | 138 | 13:00 | 100 | Lalbag | 82 | 13:00 | 166 | Satmasjid | 107 | 13:00
35 | Chandina | 45 | 21:00 | 101 | Lalmonirhat | 70 | 20:00 | 167 | Savar | 226 | 12:00
36 | Chandpur | 90 | 00:00 | 102 | MI_Cement | 14.7 | 00:00 | 168 | SevenRings | 15.31 | 10:00
37 | Chandraghona | 35 | 21:00 | 103 | Madanganj | 36 | 12:00 | 169 | ShahCement | 37 | 16:00
38 | Chapai | 80 | 21:00 | 104 | Madaripur | 129 | 23:00 | 170 | Shahjadpur | 90 | 21:00
39 | Charfasson | 34 | 00:00 | 105 | Madartek | 86 | 00:00 | 171 | Shahjibazar | 131 | 22:00
40 | Charsaidpur | 31 | 12:00 | 106 | Madunaghat | 60 | 19:00 | 172 | Shahmirpur | 53 | 19:00
41 | Chauddagram | 84 | 23:00 | 107 | Magura | 64 | 19:00 | 173 | Shariatpur | 101 | 22:00
42 | Chhatak | 43 | 21:00 | 108 | Mahasthangarh | 85 | 00:00 | 174 | Sherpur | 152 | 21:00
43 | Chowmuhani | 172 | 20:00 | 109 | Maijdee | 45 | 22:00 | 175 | Shikalbaha | 24 | 00:00
44 | Chuadanga | 117 | 13:00 | 110 | Manikganj | 152 | 22:00 | 176 | Shitalakhya | 80.8 | 17:00
45 | Coxsbazar | 154 | 19:00 | 111 | Maniknagar | 76 | 13:00 | 177 | Sholosohor | 48 | 15:00
46 | Cumilla(N) | 137 | 01:00 | 112 | Matarbari | 57 | 21:00 | 178 | Shomvuganj | 45 | 21:00
47 | Cumilla(S) | 174 | 23:00 | 113 | Matuail | 82 | 12:00 | 179 | Shyampur | 188 | 12:00
48 | Daganbhuiyan | 39 | 23:00 | 114 | Metrorail_Motijheel | 39 | 17:00 | 180 | Siddhirganj | 133 | 12:00
49 | Daudkandi | 150 | 03:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Sirajganj | 122 | 19:30
50 | DhakaUniversity | 100 | 13:00 | 116 | Millgate | 117 | 15:00 | 182 | Sitakunda | 22 | 19:30
51 | Dhamrai | 108 | 01:00 | 117 | Mirpur | 157 | 15:00 | 183 | Sonargaon | 143 | 11:00
52 | Dhanmondi | 124 | 13:00 | 118 | Mirsorai | 34 | 09:00 | 184 | Sreemongol | 97 | 22:00
53 | Dohazari | 112 | 23:00 | 119 | Mirzapur | 54 | 19:30 | 185 | Sreepur | 127 | 10:00
54 | Faridpur | 190 | 23:00 | 120 | Mithapukur | 80 | 20:00 | 186 | Srinagar | 53.2 | 22:00
55 | Fatullah | 109 | 15:00 | 121 | Modern | N/A | N/A | 187 | Sunamganj | 64 | 22:00
56 | Fenchuganj | 49 | 19:00 | 122 | Mogbazar | 97.3 | 14:00 | 188 | Sylhet | 135 | 14:00
57 | Feni | 122 | 19:30 | 123 | Mongla | 40 | 11:00 | 189 | Sylhet_(South) | 84 | 22:00
58 | GPH | 82 | 01:00 | 124 | Motijheel | 51 | 13:00 | 190 | TK | 28 | 19:30
59 | Ghatail | 89 | 19:30 | 125 | Muktagacha | 42 | 19:00 | 191 | Tangail | 188 | 20:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 123 | 23:00 | 192 | Taraganj | 30 | 19:30
61 | Ghorashal-230 | 101 | 14:00 | 127 | Muradnagar | 54 | 21:00 | 193 | Tasnim | 40 | 18:30
62 | Goalpara | 36 | 00:00 | 128 | Mymensingh | 169 | 21:00 | 194 | Thakurgaon | 123 | 20:00
63 | Gollamari | 118 | 19:30 | 129 | Nabinagar | 106 | 09:00 | 195 | Tongi | 161 | 11:00
64 | Gopalganj | 124 | 21:00 | 130 | Naogaon | 152 | 21:00 | 196 | Ullahpara | 43 | 19:30
65 | Gulshan | 124 | 13:00 | 131 | Narail | 59 | 20:00 | 197 | Ullon | 60 | 00:00
66 | Halishahar | 116 | 15:00 | 132 | Narinda | 78 | 13:00 | 198 | Uttara | 106 | 16:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 02-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 16275 | 532 |  | 16830.94
1:00 | 15824.06 | 387 |  | 16228.48
2:00 | 15121.49 | 505 |  | 15649.22
3:00 | 14796.47 | 479 |  | 15297.03
4:00 | 14435.31 | 280 |  | 14727.91
5:00 | 14301.04 | 230 |  | 14541.04
6:00 | 13852.4 | 170 |  | 14030.4
7:00 | 14013.26 | 146 |  | 14166.26
8:00 | 14061.33 | 148 |  | 14216.33
9:00 | 14169.71 | 196 |  | 14374.71
10:00 | 14443.28 | 195 |  | 14647.28
11:00 | 14949.75 | 230 |  | 15189.75
12:00 | 15327.46 | 318 |  | 15659.46
13:00 | 15596.59 | 347 |  | 15959.59
14:00 | 15511.15 | 379 |  | 15907.15
15:00 | 15500.64 | 570 |  | 16096.64
16:00 | 15157.45 | 469 |  | 15647.45
17:00 | 14903.61 | 399 |  | 15320.61
18:00 | 14643.05 | 257 |  | 14912.05
19:00 | 15512.29 | 310 |  | 15836.29
19:30 | 16512.04 | 361 |  | 16889.04
20:00 | 16589.02 | 402 |  | 17009.02
21:00 | 16716.67 | 494 |  | 17232.67
22:00 | 16457.11 | 437 |  | 16914.11
23:00 | 16389.6 | 631 |  | 17048.6
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 02-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8727.3 | 7547.7 | 16275 | DAILY GENERATION CURVE
00:30 | 8593.9 | 7455.63 | 16049.53
01:00 | 8460.5 | 7363.56 | 15824.06 | 02-07-2026
01:30 | 8244 | 7228.775 | 15472.775
02:00 | 8027.5 | 7093.99 | 15121.49
02:30 | 7910.25 | 7048.73 | 14958.98
03:00 | 7793 | 7003.47 | 14796.47
03:30 | 7710.5 | 6905.39 | 14615.89
04:00 | 7628 | 6807.31 | 14435.31
04:30 | 7584.75 | 6783.425 | 14368.175
05:00 | 7541.5 | 6759.54 | 14301.04
05:30 | 7393.38 | 6683.34 | 14076.72
06:00 | 7245.26 | 6607.14 | 13852.4
06:30 | 7273.655 | 6659.175 | 13932.83
07:00 | 7302.05 | 6711.21 | 14013.26
07:30 | 7290.365 | 6746.93 | 14037.295
08:00 | 7278.68 | 6782.65 | 14061.33
08:30 | 7255.41 | 6860.11 | 14115.52
09:00 | 7232.14 | 6937.57 | 14169.71
09:30 | 7362.865 | 6943.63 | 14306.495
10:00 | 7493.59 | 6949.69 | 14443.28
10:30 | 7676.705 | 7019.81 | 14696.515
11:00 | 7859.82 | 7089.93 | 14949.75
11:30 | 7945.24 | 7193.365 | 15138.605
12:00 | 8030.66 | 7296.8 | 15327.46
12:30 | 8188.475 | 7273.55 | 15462.025
13:00 | 8346.29 | 7250.3 | 15596.59
13:30 | 8357.4 | 7196.47 | 15553.87
14:00 | 8368.51 | 7142.64 | 15511.15
14:30 | 8358.42 | 7147.475 | 15505.895
15:00 | 8348.33 | 7152.31 | 15500.64
15:30 | 8194.5 | 7134.545 | 15329.045
16:00 | 8040.67 | 7116.78 | 15157.45
16:30 | 8042.285 | 6988.245 | 15030.53
17:00 | 8043.9 | 6859.71 | 14903.61
17:30 | 7999.995 | 6773.335 | 14773.33
18:00 | 7956.09 | 6686.96 | 14643.05
18:30 | 8154.295 | 6923.375 | 15077.67
19:00 | 8352.5 | 7159.79 | 15512.29
19:30 | 8780.36 | 7731.68 | 16512.04
20:00 | 8810.36 | 7778.66 | 16589.02
20:30 | 8743.61 | 7909.235 | 16652.845 |  | Executive Engineer
21:00 | 8676.86 | 8039.81 | 16716.67 |  | Network Operation Division
21:30 | 8548.18 | 8038.71 | 16586.89
22:00 | 8419.5 | 8037.61 | 16457.11
22:30 | 8378 | 8045.355 | 16423.355
23:00 | 8336.5 | 8053.1 | 16389.6

## En-Curve
QF-LDC-12
Date | 02-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3515 | 2142.5 | 903 | 38 | 158 | 1418.7 | 98 | 5919 | 0 | 588 | 1462.8 | 0 | 0 | 32 | 532 | DAILY ENERGY CURVE
00:30 | 3516 | 2132.5 | 903 | 38 | 156 | 1379.13 | 98.5 | 5891 | 0 | 514.5 | 1396.9 | 0 | 0 | 24 | 459.5 | 02-07-2026
01:00 | 3517 | 2122.5 | 903 | 38 | 154 | 1339.56 | 99 | 5863 | 0 | 441 | 1331 | 0 | 0 | 16 | 387
01:30 | 3489.5 | 2128.5 | 903 | 38 | 154 | 1304.775 | 98 | 5818.5 | 0 | 375.5 | 1145 | 0 | 0 | 18 | 446 | Energy Generated | 367.2367 |  | MKWHr
02:00 | 3462 | 2134.5 | 903 | 38 | 154 | 1269.99 | 97 | 5774 | 0 | 310 | 959 | 0 | 0 | 20 | 505 | Energy not Served | 8.511 |  | MKWHr
02:30 | 3455 | 2171.75 | 891 | 38 | 150 | 1253.73 | 96 | 5788.5 | 0 | 310 | 784.5 | 0 | 0 | 20.5 | 492 | Total Energy Requirement | 375.7477 |  | MKWHr
03:00 | 3448 | 2209 | 879 | 38 | 146 | 1237.47 | 95 | 5803 | 0 | 310 | 610 | 0 | 0 | 21 | 479
03:30 | 3453.5 | 2199.5 | 879 | 38 | 145 | 1230.39 | 94 | 5779 | 0 | 310 | 465 | 0 | 0 | 22.5 | 379.5
04:00 | 3459 | 2190 | 879 | 38 | 144 | 1223.31 | 93 | 5755 | 0 | 310 | 320 | 0 | 0 | 24 | 280
04:30 | 3455.5 | 2170.25 | 879 | 38 | 143 | 1224.425 | 93 | 5732 | 0 | 310 | 298.5 | 0 | 0 | 24.5 | 255
05:00 | 3452 | 2150.5 | 879 | 38 | 142 | 1225.54 | 93 | 5709 | 0 | 310 | 277 | 0 | 0 | 25 | 230
05:30 | 3410.5 | 2104.5 | 879 | 38 | 140 | 1225.89 | 93.5 | 5577.5 | 18.33 | 310 | 251.5 | 0 | 0 | 28 | 200
06:00 | 3369 | 2058.5 | 879 | 38 | 138 | 1226.24 | 94 | 5446 | 36.66 | 310 | 226 | 0 | 0 | 31 | 170
06:30 | 3379.5 | 2107.25 | 879 | 38 | 133 | 1224.7 | 94.5 | 5432 | 84.38 | 310 | 224.5 | 0 | 0 | 26 | 158
07:00 | 3390 | 2156 | 879 | 38 | 128 | 1223.16 | 95 | 5418 | 132.1 | 310 | 223 | 0 | 0 | 21 | 146
07:30 | 3386.5 | 2135 | 879 | 38 | 131 | 1218.57 | 95 | 5416.5 | 188.225 | 310 | 217.5 | 0 | 0 | 22 | 147
08:00 | 3383 | 2114 | 879 | 38 | 134 | 1213.98 | 95 | 5415 | 244.35 | 310 | 212 | 0 | 0 | 23 | 148
08:30 | 3372.5 | 2107.5 | 878.5 | 38 | 137 | 1213.315 | 96 | 5421.5 | 328.205 | 273 | 230 | 0 | 0 | 20 | 172
09:00 | 3362 | 2101 | 878 | 38 | 140 | 1212.65 | 97 | 5428 | 412.06 | 236 | 248 | 0 | 0 | 17 | 196
09:30 | 3375.5 | 2169 | 878 | 38 | 144 | 1182.375 | 97 | 5471.5 | 448.62 | 236 | 248.5 | 0 | 0 | 18 | 195.5
10:00 | 3389 | 2237 | 878 | 38 | 148 | 1152.1 | 97 | 5515 | 485.18 | 236 | 249 | 0 | 0 | 19 | 195
10:30 | 3440 | 2229.25 | 878.5 | 38 | 143 | 1129.83 | 97 | 5647 | 522.935 | 215 | 329.5 | 0 | 0 | 26.5 | 212.5
11:00 | 3491 | 2221.5 | 879 | 38 | 138 | 1107.56 | 97 | 5779 | 560.69 | 194 | 410 | 0 | 0 | 34 | 230
11:30 | 3492.5 | 2182 | 878.5 | 38 | 153 | 1126.37 | 96 | 5862.5 | 565.735 | 218 | 494.5 | 0 | 0 | 31.5 | 274
12:00 | 3494 | 2142.5 | 878 | 38 | 168 | 1145.18 | 95 | 5946 | 570.78 | 242 | 579 | 0 | 0 | 29 | 318
12:30 | 3482.5 | 2154.5 | 878.5 | 38 | 166 | 1149.155 | 96 | 5935 | 562.87 | 250 | 725.5 | 0 | 0 | 24 | 332.5
13:00 | 3471 | 2166.5 | 879 | 38 | 164 | 1153.13 | 97 | 5924 | 554.96 | 258 | 872 | 0 | 0 | 19 | 347
13:30 | 3455 | 2140.5 | 878.5 | 38 | 169 | 1183.225 | 96 | 5884.5 | 527.045 | 242.5 | 917.1 | 0 | 0 | 22.5 | 363
14:00 | 3439 | 2114.5 | 878 | 38 | 174 | 1213.32 | 95 | 5845 | 499.13 | 227 | 962.2 | 0 | 0 | 26 | 379
14:30 | 3428.5 | 2117.5 | 878.5 | 38 | 173 | 1237.645 | 93.5 | 5848.5 | 463.55 | 227.5 | 973.7 | 0 | 0 | 26 | 474.5
15:00 | 3418 | 2120.5 | 879 | 38 | 172 | 1261.97 | 92 | 5852 | 427.97 | 228 | 985.2 | 0 | 0 | 26 | 570
15:30 | 3312 | 2133.5 | 879 | 38 | 168 | 1272.265 | 91 | 5864 | 360.68 | 239 | 947.1 | 0 | 0 | 24.5 | 519.5
16:00 | 3206 | 2146.5 | 879 | 38 | 164 | 1282.56 | 90 | 5876 | 293.39 | 250 | 909 | 0 | 0 | 23 | 469
16:30 | 3200 | 2128.5 | 879 | 38 | 165 | 1299.28 | 89.5 | 5792 | 231.75 | 258.5 | 910 | 0 | 0 | 39 | 434
17:00 | 3194 | 2110.5 | 879 | 38 | 166 | 1316 | 89 | 5708 | 170.11 | 267 | 911 | 0 | 0 | 55 | 399
17:30 | 3197.5 | 2113.5 | 879 | 38 | 156 | 1315.38 | 89.5 | 5613.5 | 109.45 | 271 | 942.5 | 0 | 0 | 48 | 328
18:00 | 3201 | 2116.5 | 879 | 38 | 146 | 1314.76 | 90 | 5519 | 48.79 | 275 | 974 | 0 | 0 | 41 | 257
18:30 | 3191 | 2136.5 | 879 | 38 | 160 | 1373.275 | 92 | 5566.5 | 24.395 | 415 | 1173 | 0 | 0 | 29 | 283.5
19:00 | 3181 | 2156.5 | 879 | 38 | 174 | 1431.79 | 94 | 5614 | 0 | 555 | 1372 | 0 | 0 | 17 | 310
19:30 | 3193 | 2025.5 | 878 | 38 | 168 | 1477.68 | 95 | 5968 | 0 | 621 | 2030.86 | 0 | 0 | 17 | 361
20:00 | 3053 | 2024.5 | 878 | 38 | 170 | 1483.66 | 95 | 6046 | 0 | 661 | 2118.86 | 0 | 0 | 21 | 402
20:30 | 3116.5 | 2052.5 | 878.5 | 38 | 167 | 1481.735 | 95.5 | 6100 | 0 | 654 | 1980.11 | 76 | 0 | 13 | 448
21:00 | 3180 | 2080.5 | 879 | 38 | 164 | 1479.81 | 96 | 6154 | 0 | 647 | 1841.36 | 152 | 0 | 5 | 494
21:30 | 3177 | 2090.5 | 879 | 38 | 163 | 1480.71 | 96 | 6175.5 | 0 | 634.5 | 1701.68 | 141 | 0 | 10 | 465.5
22:00 | 3174 | 2100.5 | 879 | 38 | 162 | 1481.61 | 96 | 6197 | 0 | 622 | 1562 | 130 | 0 | 15 | 437
22:30 | 3182 | 2170.5 | 929 | 38 | 168 | 1481.855 | 96.5 | 6198.5 | 0 | 593.5 | 1417 | 130 | 0 | 18.5 | 534
23:00 | 3190 | 2240.5 | 979 | 38 | 174 | 1482.1 | 97 | 6200 | 0 | 565 | 1272 | 130 | 0 | 22 | 631
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 02-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 127 | 9 | 480 | 176 | 1558 | 482 | Ishurdi-Ghorashal Ckt-1 | Export | 3360509.09
1:00 | 115 | 5 | 450 | 184 | 1508 | 460
2:00 | 112 | 8 | 430 | 164 | 1478 | 498 |  | Import | 0
3:00 | 116 | 13 | 440 | 160 | 1532 | 494
4:00 | 123 | 20 | 440 | 160 | 1536 | 527 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 125 | 23 | 450 | 158 | 1530 | 526
6:00 | 132 | 31 | 450 | 152 | 1516 | 540 |  | Import | 0
7:00 | 127 | 26 | 440 | 162 | 1570 | 538
8:00 | 151 | 39 | 490 | 176 | 1686 | 614 | Sirajganj-Sreepur Ckt-1 | Export | 2992000
9:00 | 185 | 61 | 590 | 210 | 1866 | 698
10:00 | 182 | 62 | 590 | 230 | 1960 | 730 |  | Import | 0
11:00 | 178 | 54 | 600 | 246 | 1880 | 740
12:00 | 179 | 58 | 610 | 264 | 1970 | 756 | Sirajganj-Sreepur Ckt-2 | Export | 2996000
13:00 | 150 | 36 | 500 | 216 | 1740 | 630
14:00 | 151 | 38 | 520 | 220 | 1784 | 656 |  | Import | 0
15:00 | 136 | 23 | 510 | 196 | 1794 | 640
16:00 | 146 | 32 | 540 | 208 | 1894 | 714 | Gopalganj-Aminbazar Ckt-1 | Export | 20770000
17:00 | 165 | 47 | 520 | 204 | 1792 | 738
18:00 | 161 | 48 | 520 | 202 | 1742 | 740 |  | Import | 0
18:30 | 168 | 49 | 540 | 192 | 1832 | 702
19:00 | 154 | 35 | 530 | 214 | 1836 | 702 | Gopalganj-Aminbazar Ckt-2 | Export | 20800000
19:30 | 118 | 8 | 446 | 170 | 1834 | 566
20:00 | 114 | 4 | 438 | 166 | 1816 | 526 |  | Import | 0
21:00 | 115 | 3 | 460 | 184 | 1880 | 544
22:00 | 118 | 2 | 492 | 184 | 1860 | 514 |  | Total Export | 50918509.09
23:00 | 123 | 3 | 480 | 180 | 1868 | 520 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 02-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 367 | 05:00 | 352 | 23:00 | Madunaghat | 388 | 07:00 | 379 | 12:00
Amtali | 407 | 06:00 | 400 | 22:00 | Meghnaghat | 374 | 06:00 | 357 | 12:00
Ashuganj | 400 | 6:00 | 377 | 12:00 | Payra | 410 | 06:00 | 403 | 13:00
Bhulta | 392 | 06:00 | 368 | 12:00 | Rahanpur | 400 | 09:00 | 384 | 21:00
Bibiana | 385 | 05:00 | 363 | 17:00 | Rampal | 391 | 06:00 | 373 | 19:30
BIPTC | 402 | 05:00 | 394 | 00:00
Bogura | 383 | 09:00 | 363 | 23:00
Gopalganj | 384 | 06:00 | 368 | 21:00
Kaliakoir | 360 | 05:00 | 341 | 12:00
Korerhat | 385 | 06:00 | 373 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 06:00 | 210 | 12:00 | Ishurdi | 229 | 06:00 | 209 | 21:00
AKSML | 229 | 20:00 | 216 | 11:00 | Jhenaidah | 220 | 06:00 | 200 | 21:00
Aminbazar | 226 | 05:00 | 214 | 10:00 | Kachua | 218 | 06:00 | 211 | 11:00
Ashuganj | 224 | 05:00 | 213 | 12:00 | Kaliakoir | 222 | 05:00 | 208 | 12:00
Ashuganj-400 | 224 | 05:00 | 213 | 12:00 | Keranigonj | 225 | 06:00 | 208 | 12:00
Baghabari | 229 | 05:00 | 216 | 23:00 | Khulna(S) | 220 | 06:00 | 204 | 20:00
Barapukuria | 221 | 08:00 | 211 | 23:00 | Korerhat | 219 | 06:00 | 211 | 11:00
Barapukuria-230 | 221 | 08:00 | 211 | 23:00 | Madunaghat | 233 | 19:30 | 219 | 11:00
Barishal | 223 | 06:00 | 213 | 23:00 | Madunaghat-400 | 233 | 19:00 | 220 | 12:00
Bheramara | 227 | 06:00 | 205 | 21:00 | Maniknagar | 224 | 06:00 | 207 | 12:00
Bhulta | 225 | 06:00 | 208 | 12:00 | Meghnaghat | 232 | 05:00 | 218 | 12:00
Bibiana | 222 | 06:00 | 210 | 19:00 | Meghnaghat-400 | 228 | 06:00 | 214 | 12:00
BIPTC | 230 | 06:00 | 207 | 21:00 | Mirsorai | 223 | 06:00 | 216 | 12:00
Bogura | 236 | 09:00 | 224 | 21:00 | Naogaon | 220 | 09:00 | 198 | 21:00
Bogura-400 | 237 | 09:00 | 225 | 21:00 | Purbasadipur | 219 | 19:00 | 207 | 23:00
Borhanuddin | 227 | 07:00 | 219 | 23:00 | Rajshahi | 225 | 09:00 | 204 | 21:00
BSRM | 219 | 06:00 | 212 | 11:00 | Rampal | 221 | 06:00 | 205 | 19:30
Charfasson | 228 | 07:00 | 219 | 23:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 218 | 04:00 | 210 | 11:00 | Rampura | 223 | 06:00 | 206 | 12:00
Cumilla(N) | 220 | 05:00 | 211 | 12:00 | Shikalbaha | 232 | 20:00 | 218 | 11:00
Faridpur | 217 | 06:00 | 205 | 23:00 | Shyampur | 225 | 06:00 | 210 | 12:00
Fenchuganj | 223 | 07:00 | 212 | 19:00 | Siddhirganj | 224 | 01:00 | 213 | 10:00
Feni | 218 | 06:00 | 210 | 11:00 | Sirajgonj | 236 | 06:00 | 228 | 23:00
Ghorashal | 230 | 03:00 | 215 | 13:00 | Sreepur | 219 | 06:00 | 210 | 12:00
Ghorashal-230 | 209 | 05:00 | 193 | 13:00 | Tongi | 211 | 07:00 | 193 | 13:00
Gopalganj | 218 | 06:00 | 208 | 22:00
GPH | 226 | 18:00 | 216 | 11:00
Haripur | 225 | 06:00 | 209 | 12:00
Hasnabad | 231 | 15:00 | 209 | 13:00
Hathazari | 228 | 18:00 | 216 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 06:00 | 125 | 12:00 | Madunaghat | 134 | 18:30 | 126 | 11:00
Agargaon | 133 | 06:00 | 121 | 12:00 | Magura | 125 | 06:00 | 109 | 21:00
Agrabad | 132 | 19:00 | 123 | 11:00 | Mahasthangarh | 132 | 08:00 | 121 | 23:00
AKS | 130 | 18:30 | 122 | 11:00 | Maijdee | 122 | 06:00 | 118 | 12:00
Aminbazar | 129 | 05:00 | 120 | 11:00 | Manikganj | 128 | 00:00 | 120 | 11:00
Amnura | 132 | 18:30 | 121 | 13:00 | Maniknagar | 131 | 04:00 | 119 | 12:00
Ashuganj | 131 | 06:00 | 124.7 | 12:00 | Matarbari | 117 | 17:00 | 109 | 21:00
Ashuganj-230 | 132 | 06:00 | 126 | 12:00 | Matuail | 129 | 03:00 | 120 | 12:00
Bagerhat | 126 | 09:00 | 110 | 19:30 | Metrorail_Motijheel | 131 | 04:00 | 119 | 12:00
Bajitpur | 124 | 03:00 | 117 | 12:00 | Metrorail_Uttara | 129 | 05:00 | 114 | 12:00
Bakerganj | 128 | 08:00 | 123 | 21:00 | Millgate | 130 | 4:00 | 115 | 12:00
Bakulia | 132 | 18:00 | 122 | 11:00 | Mirpur | 128 | 05:00 | 118 | 11:00
Banani | 137 | 03:00 | 123 | 12:00 | Mirzapur | 127 | 03:00 | 119 | 21:00
Bangabhaban | 131 | 07:00 | 118 | 12:00 | Mithapukur | 129 | 08:00 | 118 | 22:00
Barapukuria | 134 | 08:00 | 123 | 23:00 | MI_Cement | 132 | 05:00 | 118 | 12:00
Barguna | 129 | 07:00 | 121 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 127 | 07:00 | 122 | 00:00 | Mogbazar | 138 | 06:00 | 125 | 12:00
Barishal-230 | 128 | 06:00 | 122 | 22:00 | Mongla | 127 | 07:00 | 110 | 19:30
Baroaulia | 133 | 20:00 | 125 | 11:00 | Motijheel | 131 | 06:00 | 118 | 12:00
Baroirhat | 126 | 07:00 | 122 | 11:00 | Muktagacha | 126 | 11:00 | 113 | 10:00
Bashundhara | 137 | 03:00 | 114 | 10:00 | Munshiganj | 128 | 04:00 | 120 | 13:00
BashundharaCement | 129 | 01:00 | 120 | 12:00 | Muradnagar | 124 | 05:00 | 117 | 12:00
Beanibazar | 123 | 07:00 | 115 | 19:00 | Mymensingh | 125 | 11:00 | 108 | 21:00
Benapole | 127 | 09:00 | 110 | 21:00 | Nabinagar | 125 | 03:00 | 114 | 12:00
Bhaluka | 125 | 08:00 | 117 | 12:00 | Naogaon | 133 | 09:00 | 120 | 21:00
Bhandaria | 123 | 08:00 | 114 | 23:00 | Narail | 124 | 06:00 | 105 | 21:00
Bhangura | 131 | 06:00 | 123 | 21:00 | Narinda | 131 | 04:00 | 119 | 12:00
Bheramara | 133 | 06:00 | 120 | 21:00 | Narshingdi | 125 | 06:00 | 114 | 12:00
Bheramara(GK) | 132 | 05:00 | 120 | 21:00 | Natore | 131 | 09:00 | 118 | 22:00
Bhulta | 126 | 08:00 | 118 | 12:00 | Nawabganj | 135 | 06:00 | 124 | 12:00
Bog-Sherpur | 132 | 06:00 | 124 | 21:00 | Netrakona | 115 | 04:00 | 107 | 19:30
Bogura | 136 | 19:00 | 126 | 23:00 | New | 130 | 05:00 | 115 | 11:00
Bogura-230 | 135 | 06:00 | 127 | 23:00 | Niamatpur | 131 | 09:00 | 122 | 21:00
Brahmanbaria | 125 | 06:00 | 119 | 23:00 | Noapara | 130 | 09:00 | 115 | 21:00
Cantonment | 132 | 04:00 | 121 | 12:00 | Pabna | 131 | 06:00 | 119 | 21:00
Chandina | 126 | 06:00 | 120 | 12:00 | Palashbari | 128 | 09:00 | 117 | 23:00
Chandpur | 126 | 20:00 | 119 | 11:00 | Panchagarh | 135 | 19:00 | 126 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 134 | 19:00 | 126 | 11:00 | Patiya | 132 | 19:00 | 123 | 11:00
Chapai | 131 | 12:00 | 125 | 00:00 | Patuakhali | 129 | 09:00 | 123 | 22:00
Charsaidpur | 129 | 06:00 | 120 | 12:00 | Payra | 134 | 15:00 | 130 | 00:00
Chauddagram | 125 | 06:00 | 120 | 11:00 | PHP | 127 | 06:00 | 122 | 11:00
Chhatak | 120 | 03:00 | 111 | 20:00 | Postogola | 133 | 05:00 | 121 | 12:00
Chowmuhani | 122 | 04:00 | 118 | 11:00 | Pubail | 121 | 05:00 | 113 | 10:00
Chuadanga | 130 | 06:00 | 114 | 21:00 | Purbachal | 138 | 06:00 | 124 | 12:00
Coxsbazar | 121 | 12:00 | 110 | 19:00 | Purbasadipur | 132 | 19:00 | 123 | 23:00
Cumilla(N) | 127 | 06:00 | 121 | 10:00 | Rahanpur | 133 | 05:00 | 128 | 21:00
Cumilla(S) | 128 | 03:00 | 120 | 14:00 | Rahanpur-400 | 134 | 09:00 | 128 | 21:00
Daganbhuiyan | 124 | 06:00 | 120 | 11:00 | Rahim | 130 | 06:00 | 120 | 12:00
Daudkandi | 123 | 05:00 | 115 | 12:00 | Rajbari | 124 | 06:00 | 114 | 23:00
DhakaUniversity | 137 | 04:00 | 124 | 12:00 | Rajendrapur | 125 | 06:00 | 118 | 12:00
Dhamrai | 127 | 05:00 | 116 | 12:00 | Rajshahi | 128 | 09:00 | 116 | 21:00
Dhanmondi | 138 | 06:00 | 124 | 12:00 | Rajshahi-230 | 129 | 06:00 | 117 | 21:00
Dohazari | 127 | 18:00 | 119 | 10:00 | Ramganj | 120 | 18:00 | 116 | 11:00
Faridpur | 126 | 06:00 | 118 | 23:00 | Rampur | 132 | 19:00 | 123 | 11:00
Fatullah | 134 | 06:00 | 120 | 12:00 | Rampura | 138 | 06:00 | 124 | 12:00
Fenchuganj | 131 | 07:00 | 123 | 19:30 | Rangamati | 132 | 18:00 | 124 | 12:00
Feni | 125 | 10:00 | 122 | 03:00 | Rangpur | 128 | 09:00 | 117 | 23:00
Feni-230 | 126 | 06:00 | 121 | 11:00 | Ruppur | 133 | 06:00 | 121 | 21:00
Ghatail | 121 | 04:00 | 111 | 19:00 | Saidpur | 131 | 09:00 | 121 | 23:00
Ghorashal | 124 | 03:00 | 116 | 12:00 | Santhia | 131 | 04:00 | 122 | 21:00
Goalpara | 131 | 06:00 | 118 | 21:00 | Satkhira | 126 | 09:00 | 109 | 21:00
Gollamari | 131 | 06:00 | 118 | 20:00 | Satmasjid | 132 | 06:00 | 121 | 13:00
Gopalganj | 127 | 06:00 | 118 | 21:00 | Savar | 126 | 01:00 | 116 | 12:00
Gopalganj-400 | 129 | 06:00 | 122 | 21:00 | SevenRings | 124 | 03:00 | 116 | 12:00
Gulshan | 137 | 06:00 | 124 | 12:00 | ShahCement | 129 | 06:00 | 119 | 12:00
Halishahar | 132 | 18:00 | 124 | 11:00 | Shahjadpur | 134 | 06:00 | 126 | 00:00
Haripur | 131 | 06:00 | 121 | 12:00 | Shahjibazar | 126 | 06:00 | 120 | 12:00
HaripurSBU | 130 | 06:00 | 121 | 12:00 | Shahmirpur | 132 | 18:00 | 125 | 10:00
Hasnabad | 132 | 04:00 | 119 | 13:00 | Shariatpur | 126 | 06:00 | 117 | 23:00
Hathazari | 133 | 20:00 | 127 | 11:00 | Sherpur | 127 | 11:00 | 110 | 10:00
Hatirjheel | 137 | 04:00 | 124 | 12:00 | Shikalbaha | 121 | 17:00 | 118 | 10:00
Ishurdi | 134 | 06:00 | 122 | 21:00 | Shikalbaha-230 | 133 | 19:00 | 125 | 11:00
Jaldhaka | 129 | 09:00 | 119 | 23:00 | Shitalakhya | 132 | 05:00 | 118 | 12:00
Jamalpur | 128 | 11:00 | 114 | 02:00 | Sholosohor | 133 | 18:00 | 124 | 12:00
Jashore | 129 | 06:00 | 112 | 21:00 | Shomvuganj | 120 | 05:00 | 110 | 01:00
Jhenaidah | 134 | 08:00 | 110 | 21:00 | Shyampur | 132 | 05:00 | 125 | 12:00
Jhenaidah-230 | 134 | 06:00 | 118 | 19:30 | Shyampur-230 | 134 | 05:00 | 122 | 12:00
Joydebpur | 118 | 03:00 | 109 | 12:00 | Siddhirganj | 131 | 06:00 | 121 | 12:00
Joypurhat | 130 | 09:00 | 119 | 23:00 | Sirajganj | 129 | 09:00 | 121 | 22:00
Juldah | 132 | 19:00 | 124 | 11:00 | Sitakunda | 132 | 18:00 | 125 | 11:00
Kabirpur | 131 | 00:00 | 111 | 12:00 | Sonargaon | 126 | 05:00 | 118 | 12:00
Kachua | 124 | 18:30 | 120 | 11:00 | Sreemongol | 127 | 07:00 | 118 | 21:00
Kaliakoir | 132 | 03:00 | 121 | 10:00 | Sreepur | 128 | 06:00 | 121 | 12:00
Kaliganj | 132 | 09:00 | 118 | 19:30 | Srinagar | 135 | 06:00 | 125 | 12:00
Kallyanpur | 128 | 03:00 | 118 | 13:00 | SSM | 138 | 20:00 | 130 | 00:00
Kalurghat | 133 | 17:00 | 126 | 12:00 | Sunamganj | 119 | 06:00 | 109 | 19:00
Kamrangirchar | 134 | 07:00 | 115 | 12:00 | Sylhet | 124 | 05:00 | 118 | 21:00
Kaptai | 135 | 18:00 | 130 | 11:00 | Sylhet_(South) | 125 | 07:00 | 116 | 21:00
Kasba | 124 | 06:00 | 116 | 12:00 | Tangail | 122 | 00:00 | 113 | 22:00
Kazla | 131 | 06:00 | 118 | 13:00 | Taraganj | 130 | 19:00 | 120 | 23:00
Keranigonj | 136 | 06:00 | 125 | 12:00 | Tasnim | 127 | 06:00 | 118 | 12:00
Khagrachori | 132 | 23:00 | 125 | 11:00 | Thakurgaon | 135 | 19:00 | 126 | 23:00
Khulna | 130 | 08:00 | 118 | 21:00 | TK | 133 | 17:00 | 126 | 11:00
Khulna(S) | 131 | 06:00 | 120 | 19:30 | Tongi | 132 | 04:00 | 118 | 13:00
Khulshi | 130 | 18:30 | 122 | 11:00 | Ullahpara | 130 | 05:00 | 122 | 21:00
Kishoreganj | 122 | 15:00 | 115 | 12:00 | Ullon | 137 | 05:00 | 124 | 12:00
Kodda | 132 | 00:00 | 122 | 11:00 | Uttara | 127 | 05:00 | 112 | 12:00
Korerhat | 129 | 06:00 | 125 | 11:00 | UttaraNew | 129 | 05:00 | 114 | 12:00
KSRM | 134 | 19:00 | 124 | 11:00 | Zigatola | 135 | 06:00 | 125 | 12:00
Kulaura | 129 | 06:00 | 122 | 19:00
Kurigram | 127 | 09:00 | 115 | 23:00
Kushtia | 130 | 06:00 | 114 | 21:00
Laksam | 123 | 06:00 | 118 | 11:00
Lakshmipur | 122 | 06:00 | 117 | 11:00
Lalbag | 135 | 05:00 | 125 | 12:00
Lalmonirhat | 127 | 09:00 | 117 | 20:00
Madanganj | 129 | 01:00 | 120 | 12:00
Madaripur | 128 | 07:00 | 120 | 22:00
Madartek | 137 | 06:00 | 124 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division