## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 04-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-07-2026 | during | 04-07-2026 | during | 04-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 380 | 356 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 298 | 305 | 335 | 335 | 305 | 305 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 30 | 15 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 309 | 300 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 110 | 149.36 | 149.36 | 149.36 | 149.36 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15 | 18 | 33 | 33 | 17 | 17 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 8 | 52.19 | 52.19 | 33 | 33 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 195 | 300 | 300 | 146 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 50 | 115 | 149 | 149 | 70 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 17 | 105 | 105 | 35 | 70 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 72 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 24 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 28 | 55 | 55 | 0 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 525 | 450 | 584 | 584 | 526 | 526 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 520 | 465 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 51 | 143 | 143 | 143 | 142 | 142 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2274 | 2670 | 5805.22 | 5775.22 | 2813.06 | 3088.06
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 8 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 20 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 0 | 60 | 99 | 99 | 99 | 99 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 210 | 212 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 71 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 30 | 24 | 56 | 8 | 8 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 14 | 27 | 5 | 24 | 30 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 71 | 108 | 108 | 18 | 30 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 5.25 | 0 | 5.25 | 0 | 5.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 0 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 98 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 10 | 163 | 163 | 17 | 17 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1224 | 1224 | 1224 | 1200 | 1200 | Coal Shortage Due to BPDB Payment Default
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 50 | 60 | 35 | 28 | 35 | 28 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 675 | 680 | 1150 | 1150 | 1135 | 1135 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2132.25 | 2699.36 | 4006.11 | 4083.86 | 3163.25 | 3266
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 204 | 211 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 290 | 350.01 | 350.01 | 290 | 290 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 220 | 250 | 342.01 | 342.01 | 240 | 240 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 220 | 220 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 40 | 40 | 41.65 | 41.65 | 41.65 | 41.65 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 5 | 21 | 52.82 | 52.82 | 25 | 25 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 142 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 15 | 24 | 24 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 134 | 141 | 163 | 163 | 140 | 140 | Low gas pressure
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 17 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 156 | 160 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 17 | 17 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 16 | 114 | 114 | 17 | 17 | Liquid fuel shortage
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 51 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1408 | 1705.2 | 2741.44 | 2680.44 | 1646.1 | 1837.1
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-07-2026 | during | 04-07-2026 | during | 04-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 21.29 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.3 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 154 | 120 | 160 | 70 | 110 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 68 | 60 | 70 | 60 | 80 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 16.63 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 24 | 22 | 22 | 0 | 0 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 227.22 | 263 | 536.7 | 516.5 | 200.2 | 207
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 29 | 29 | 0 | 0 | 29 | 29 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 148 | 131 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 142 | 141 | 145 | 145 | 145 | 145 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 28 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 52 | 84 | Gas Restrction
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 100 | 100 | 100 | 102 | 102 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 171 | 224 | 300 | 300 | 245 | 245 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1058 | 1074 | 1210 | 1210 | 1074 | 1106
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 900 | 900 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 50 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 105.64 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 890 | 1195 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1933.64 | 2133 | 3544.2 | 3504.2 | 2707.2 | 2617.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 763 | 1050 | 1050 | 1050 | 1050 | 1050 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 63 | 64 | 65 | 65 | 65 | 65 | GT-1 Normal Shutdown Due to Major inspection(MI)
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1010 | 1135 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.82 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2306.82 | 2809 | 3147 | 3146 | 2920 | 2919
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 50.42 | 0 | 40 | 0 | 40 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 38 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 17 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 142 | 150 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 136 | 143 | 220 | 220 | 145 | 145 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 135 | 144 | 220 | 220 | 145 | 145 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 45 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.57 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1122.27 | 1495.89 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.46 | 0 | 53 | 0 | 53 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 116 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2178.72 | 2622.89 | 3241.72 | 3043.12 | 2586.14 | 2564.54
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 37 | 38 | 40 | 40 | 40 | 40 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.9 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 95 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 205 | 0 | 185.89 | 0 | 185.89 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 461.9 | 383 | 723.89 | 502 | 590.89 | 404
System Total |  |  |  |  | 28843.2 | 29323.517 | 13980.55 | 16359.45 | 24956.28 | 24461.34 | 17700.84 | 18008.9
Forecast Scenario (04-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 16110 |  | 57.3 |  | 16170
|  |  |  | 1:00 | 15660 |  | 0 |  | 15660
|  |  |  | 2:00 | 15470 |  | 0 |  | 15470
|  |  |  | 3:00 | 15150 |  | 0 |  | 15150
|  |  |  | 4:00 | 14500 |  | 0 |  | 14500
|  |  |  | 5:00 | 13800 |  | 0 |  | 13800
|  |  |  | 6:00 | 13140 |  | 0 |  | 13140
|  |  |  | 7:00 | 13360 |  | 0 |  | 13360
|  |  |  | 8:00 | 13220 |  | 0 |  | 13220
|  |  |  | 9:00 | 13246 |  | 137.52 |  | 13390
|  |  |  | 10:00 | 13165 |  | 300.825 |  | 13480
|  |  |  | 11:00 | 13436 |  | 366.72 |  | 13820
|  |  |  | 12:00 | 13980 |  | 458.4 |  | 14460
|  |  |  | 13:00 | 14524 |  | 339.98 |  | 14880
|  |  |  | 14:00 | 14302 |  | 561.54 |  | 14890
|  |  |  | 15:00 | 14491 |  | 428.795 |  | 14940
|  |  |  | 16:00 | 14189 |  | 459.355 |  | 14670
|  |  |  | 17:00 | 13765 |  | 405.875 |  | 14190
|  |  |  | 18:00 | 13246 |  | 729.62 |  | 14010
|  |  |  | 18:30 | 13600 |  | 1241.5 |  | 14900
|  |  |  | 19:00 | 14146 |  | 1694.17 |  | 15920
|  |  |  | 19:30 | 15913 |  | 398.235 |  | 16330
|  |  |  | 20:00 | 15905 |  | 510.925 |  | 16440
|  |  |  | 21:00 | 16359 |  | 526.205 |  | 16910
|  |  |  | 22:00 | 16308 |  | 145.16 |  | 16460
|  |  |  | 23:00 | 16343 |  | 503.285 |  | 16870
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 14460.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 16910.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16359.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 347.815 MKWHr. |  | 150 | 40 | 76 | 180 | 50 | 30 |  |  |  | 526
*** This report is generated digitally from Operation Information System (OIS) at 09:55 hrs on 04-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 03-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13980.55 | MW | 12:00 Hr. | Energy Generated |  |  | 356.6671 |  | MKWHr.
| Day Peak Demand |  |  | 14240.55 | MW | 12:00 Hr. | Energy Unserverd |  |  | 8.176 |  | MKWHr.
| Evening Peak Generation |  |  | 16359.45 | MW | 21:00 Hr. | Energy Demand |  |  | 364.8431 |  | MKWHr.
| Evening Peak Demand |  |  | 16653.45 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.2 |  | °C
| Minimum Generation of the Day |  |  | 13165.71 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 904.08 |  | MMCFD
| Maximum Generation of the Day |  |  | 16359.45 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.2748 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 47.3295 | 0 | 9.0588 | 0 | 0 | 0.2068 | 0 | 0 | 56.5951 | Gas | 133.5733 | Gas | 450439223.0484
| Chattogram Zone |  |  | 5.5774 | 45.12 | 5.4091 | 0 | 2.2872 | 0.098461 | 0 | 0.8784 | 59.3705 | Coal | 128.7251 | Coal | 858486815.6844
| Cumilla Zone |  |  | 29.4334 | 0 | 3.0298 | 0 | 0 | 0.53757 | 3.6374 | 0 | 36.6383 | HFO | 27.078 | HFO | 469574355.982
| Mymensingh Zone |  |  | 0 | 0 | 4.027 | 0 | 0 | 0.49388 | 0 | 0 | 4.5208 | HSD | 0.30402 | HSD | 6141163.6
| Sylhet Zone |  |  | 24.6355 | 0 | 0 | 0 | 0 | 0.065785 | 0 | 0 | 24.7013 | Hydro | 2.2872 | Hydro | 8714079.6
| Khulna Zone |  |  | 0 | 25.7964 | 0.022464 | 0.30402 | 0 | 0.63504 | 22.4116 | 0 | 49.1695 | Solar | 4.9637 | Solar | 78513121.3244
| Barishal Zone |  |  | 6.8683 | 52.5149 | 1.0277 | 0 | 0 | 0.003945 | 0 | 0 | 60.4148 | Import | 58.8574 | Import | 353238495.49
| Rajshahi Zone |  |  | 19.7292 | 0 | 2.4671 | 0 | 0 | 1.569 | 32.8084 | 0 | 56.5736 | Wind | 0.8784 | Wind | 12921264
| Rangpur Zone |  |  | 0 | 5.2938 | 2.0362 | 0 | 0 | 1.3532 | 0 | 0 | 8.6832
| Total |  |  | 133.5733 | 128.7251 | 27.078 | 0.30402 | 2.2872 | 4.9637 | 58.8574 | 0.8784 | 356.6671
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 450439223.0484 |  | Hydro | 8714079.6
|  |  |  | Coal | 858486815.6844 |  | Solar | 78513121.3244
|  |  |  | HFO | 469574355.982 |  | Import | 353238495.49
|  |  |  | HSD | 6141163.6 |  | Wind | 12921264
[5 empty] | Total: | 223,80,28,518 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4996 | Peak Hr Flow | 900.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 52499200 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.8084 | Peak Hr Flow | 1495.89 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2391 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.6374 | Peak Hr Flow | 160.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2787 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 57.9454 | Peak Hr Flow | 2555.89 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 45 |  | 5476
|  |  |  | Chattogram |  | 0 |  | 1543
|  |  |  | Cumilla |  | 0 |  | 1588
|  |  |  | Mymensingh |  | 215 |  | 1427
|  |  |  | Sylhet |  | 21 |  | 752
|  |  |  | Khulna |  | 0 |  | 1914
|  |  |  | Barishal |  | 0 |  | 507
|  |  |  | Rajshahi |  | 0 |  | 1666
|  |  |  | Rangpur |  | 0 |  | 1124
|  |  |  | Total |  | 281 |  | 15997
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Karnaphuli Hydro PP Unit-5 |  |  | 50
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 350 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 400
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:14 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 is restored.
|  | 08:16 | Aminbazar 400/230/132kV S/S Gopalganj-1 is restored.
| 08:20 | 08:57 | Aminbazar 400/230/132kV S/S Gopalganj-2 Scheduled S/D Due to Setting change by SPMD
| 08:21 | 08:55 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 Scheduled S/D Due to SPMD work
|  | 08:27 | Hasnabad 230/132kV S/S AUTO TR-1 HT is restored.
|  | 08:28 | Hasnabad 230/132kV S/S AUTO TR-1 LT is restored.
| 08:35 | 16:21 | Hasnabad 230/132kV S/S AUTO TR-3 LT Scheduled S/D Due to maintenance work.
| 08:35 | 16:21 | Hasnabad 230/132kV S/S AUTO TR-3 HT Scheduled S/D Due to maintenance work.
| 08:40 | 12:36 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) LT Scheduled S/D Due to O/C & E/F
Relay Replacement
| 08:41 | 12:34 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) HT Scheduled S/D Due to O/C & E/F
Relay Replacement
| 08:44 | 17:33 | Goalpara 132/33kV S/S Goalpara-NWPGCL Scheduled S/D Due to Maintanance works.
| 08:53 | 12:16 | Ashuganj-Brahmanbaria 132kV Ckt-1 Forced S/D from Brahmanbaria 132/33kV end.
|  | 08:57 | Aminbazar 400/230/132kV S/S Gopalganj-2 is restored.
| 08:58 | 17:30 | Goalpara 132/33kV S/S Bus 1 Scheduled S/D Due to Maintenance works.
| 09:14 | 17:08 | Chandina 132/33kV S/S TR-3 LT Scheduled S/D Due to 132/33 kV TR-2 HT Scheduled S/D due to
Due to cumilla pbs-1 has their maintenance work in the switchyard.
| 09:16 | 17:08 | Chandina 132/33kV S/S TR-3 HT Scheduled S/D Due to 132/33 kV TR-2 HT Scheduled S/D due to
Due to cumilla pbs-1 has their maintenance work in the switchyard.
| 09:41 | 15:43 | Chandina 132/33kV S/S TR-2 LT Scheduled S/D Due to 132/33 kV TR-2 HT Scheduled S/D due to
Due to cumilla pbs-1 has their maintenance work in the switchyard.
| 09:43 | 15:43 | Chandina 132/33kV S/S TR-2 HT Scheduled S/D Due to Due to cumilla pbs-1 has their
maintenance work in the switchyard.
| 10:17 | 11:12 | Kushtia 132/33kV S/S T-3 LT Forced S/D Due to 33kv Kumarkhali feeder source side red hot | [7 empty] | 15.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 10:18 | 11:11 | Kushtia 132/33kV S/S T-1 HT Forced S/D Due to 33 kv kumarkhali feeder red hot maintenance | [7 empty] | 15.0MW load
interrup.
| 11:24 | 15:19 | Mithapukur 132/33kV S/S TR-2 (414T) LT Forced S/D Due to 33 kv TR-2 isolator er insulator | [7 empty] | 20.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 11:26 | 15:19 | Mithapukur 132/33kV S/S TR-2 (414T) HT Forced S/D Due to 33 kv TR-2 isolator er insulator | [7 empty] | 20.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 11:32 | 12:40 | Barishal 230/132kV S/S T-4 LT Tripped showing Micon P142 relays Due to 33kv korapur | [7 empty] | 34.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 11:32 | 11:56 | Barishal 230/132kV S/S T-5 LT Tripped showing Micon P142 relays Due to 33Kv korapur | [7 empty] | 34.0MW load
|  |  | feeder fault | [7 empty] | interrup.
|  | 11:52 | Hasnabad-Sitalakhya 132kV Ckt-1 is restored.
| 12:00 |  | Day Peak Generation: 13981 MW.
|  | 12:31 | Hasnabad 132/33kV S/S 132kV Main Bus is restored.
| 12:35 |  | Hasnabad 132/33kV S/S 132kV Reserve Bus Scheduled S/D Due to AutoTR-3 Reserve Bus D/S red
hot maintenance work.
| 13:08 |  | Lalmonirhat-Rangpur 132 kV Ckt-2 Tripped from Rangpur 132/33kV end showing Quadramho 21 | [7 empty] | and 30.0MW load
|  |  | relays Due to Trip Circuit Supervision RY and from Lalmonirhat 132/33kV end showing NA | [7 empty] | interrup.
|  |  | relays Due to রংপুর - লালমনিরহাট ১৩২ কেভি লাইন রংপুর প্রান্তে ট্রিপ করে কিন্তু লালমনিরহাট | [7 empty] | Lalmonirhat
|  |  | প্রান্তে ব্রেকার চালু ছিল। পরবর্তীতে ALDC, Bogura পরামর্শে CB OFF করা হয়। | [7 empty] | 132/33kV end
| 13:11 | 13:42 | Lalmonirhat 132/33kV S/S Kurigram-Lalmonirhat Tripped showing 86-Lockout-1 86-Lockout-2
relays.
| 14:46 | 17:05 | Bhulta 132/33kV S/S GT2 HT Scheduled S/D Due to GT- 2 transformer HT bushing top terminal | [7 empty] | 50.0MW load
|  |  | & LT side link cable maintenance for Hot spot. | [7 empty] | interrup.
| 16:37 |  | Hasnabad 132/33kV S/S Keraniganj-2 (Pre- Aourahati) Scheduled S/D
| 17:56 | 19:21 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to Due to keranihut | [7 empty] | 62.0MW load
|  |  | 33kv red hot Maintenance | [7 empty] | interrup.
| 17:56 | 19:22 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to Due to keranihut | [7 empty] | 62.0MW load
|  |  | 33kv red hot Maintenance | [7 empty] | interrup.
| 18:59 | 19:15 | Mongla 132/33kV S/S T-1 LT Tripped showing K81 Relay relays. | [7 empty] | 7.0MW load
interrup.
| 21:00 |  | Evening peak generation: 16359 MW
| 04:15 |  | Ashuganj Network 230 kV bus coupler tripped at 04:15 hrs showing O/C relay. During the
first trial at 04:50 hrs, it tripped again. As a result, load on Ashuganj (S)–Ashuganj
Network 230 kV Ckt-1 and Ckt-2 became unbalanced. Due to overloading of Ashuganj
(S)–Ashuganj Network 230 kV Ckt-2, forced load shedding is occurring under Ashuganj, B.
Baria, Bajitpur, and Kishoreganj Grid Substations.
| 06:00 |  | Minimum generation: 14369 MW
| 07:44 |  | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D Due to 33kv LDS change | [7 empty] | 25.0MW load
interrup.
| 07:44 |  | Kodda 132/33kV S/S Tr-2 (416T) LT Scheduled S/D Due to 33kv LDS change | [7 empty] | 25.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 03-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 356 | 8812800 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 305 | 7052887 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 623722 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7162203 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 129600 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 110 | 1068000 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 158541 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 137651 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 412200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 452160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 231360 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 1263578 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 1160352 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 728429 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 407520 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 206804 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 28 | 356400 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 11640000 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 465 | 11797299 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143 | 2793600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2670 | 56595106
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 63997.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 71820 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 20 | 584160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 60 | 2287160 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 212 | 5060927 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 71 | 856436 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 30 | 173305 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 426359 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 185280 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 27 | 516480 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 71 | 547200 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 26641 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 150545 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 497277 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 98 | 1349048 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 260160 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 278509 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 10 | 36800 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 27665452 | Coal Shortage Due to BPDB Payment Default
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 60 | 878400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 680 | 17454545.46 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 2699.36 | 59370501.66
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 211 | 5100000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 290 | 7335000 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 250 | 5556000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5424000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 950760 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 21 | 137280 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1230128 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 142 | 777818 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 15 | 264240 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 141 | 3311349 | Low gas pressure
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 600480 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 160 | 3637440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 346118 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 388890 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 16 | 619020 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 55440 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 366720 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 537573 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1705.2 | 36638256
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 149472 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 154 | 2215200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1329600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 330810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 387840 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 94320 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 263 | 4520842
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 65785 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 29 | 692000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 131 | 3319527.27 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 141 | 3199100 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 630240 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1957440 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2403380 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 215808 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7638000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 224 | 4580000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1074 | 24701280.27
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 900 | 21499636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 22464 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 635040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 304018 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1195 | 25796360 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2133 | 49169518
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1050 | 19912727 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 794880 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 64 | 1539000 | GT-1 Normal Shutdown Due to Major inspection(MI)
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1135 | 26602181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5329280 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 232800 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6000000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3945 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2809 | 60414813.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 391376 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 276309 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 17 | 42668 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 149076 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 150 | 3483455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 143 | 3478027 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 144 | 3502455 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9265236 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 112730 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 96053 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 574192 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 45 | 845280 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 370752 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 37680 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1495.89 | 32808363 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 414000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 725981 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2622.89 | 56573633
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 38 | 833818 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4460000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 871555 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 55203.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1164623 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 204277 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1093680 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 383 | 8683156.72
Eastern Grid Total |  |  |  |  | 17438.042 | 8411.56 | 181825985.93
Western Grid Total |  |  |  |  | 11885.475 | 7947.89 | 174841121.54
National Grid Total |  |  |  |  | 29323.517 | 16359.45 | 356667107.47
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 03-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10558.66 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5209.7 | MW
i) Dhaka area |  |  | 5430.66 |  | MW | i) Khulna area |  |  |  | 1913.5 | MW
ii) Chattogram area |  |  | 1597 |  | MW | ii) Barishal area |  |  |  | 506.6 | MW
iii) Cumilla area |  |  | 1588 |  | MW | iii) Rajshahi area |  |  |  | 1665.6 | MW
iv) Mymensingh area |  |  | 1212 |  | MW | iv) Rangpur area |  |  |  | 1124 | MW
v) Sylhet area |  |  | 731 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15768.36 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 135 | 07:00 | 133 | Narshingdi | 196 | 20:00 | 199 | Uttara | 101 | 20:00
2 | AKSML | 154.1 | 04:00 | 68 | Hasnabad | 96 | 00:00 | 134 | Natore | 163 | 21:00 | 200 | UttaraNew | 57 | 23:00
3 | Aftabnagar | 46 | 00:00 | 69 | Hathazari | 99 | 21:00 | 135 | Nawabganj | 70 | 22:00 | 201 | Zigatola | 92 | 13:00
4 | Agargaon | 107 | 15:00 | 70 | Hatirjheel | 38 | 16:00 | 136 | Netrakona | 143 | 18:30
5 | Agrabad | 58 | 19:30 | 71 | Ishurdi | 84 | 20:00 | 137 | New | 74.8 | 00:00
6 | Amnura | 34 | 22:00 | 72 | Jaldhaka | 99 | 23:00 | 138 | Niamatpur | 93 | 22:00
7 | Ashuganj | 83 | 01:00 | 73 | Jamalpur | 125 | 14:00 | 139 | Noapara | 42 | 03:00
8 | BSRM | 187 | 16:00 | 74 | Jashore | 164 | 23:00 | 140 | PHP | 13 | 11:00
9 | Bagerhat | 91 | 23:00 | 75 | Jhenaidah | 102 | 19:30 | 141 | Pabna | 101 | 20:00
10 | Bajitpur | 104 | 19:30 | 76 | Joydebpur | 152 | 21:00 | 142 | Palashbari | 142 | 20:00
11 | Bakerganj | 16 | 22:00 | 77 | Joypurhat | 76 | 23:00 | 143 | Panchagarh | 71 | 20:00
12 | Bakulia | 95 | 20:00 | 78 | Juldah | 16 | 23:00 | 144 | Patiya | 12 | 21:00
13 | Banani | 65 | 19:30 | 79 | KSRM | 28 | 13:00 | 145 | Patnitala | N/A | N/A
14 | Bangabhaban | 4 | 00:00 | 80 | Kabirpur | 228 | 00:00 | 146 | Patuakhali | 72.7 | 23:00
15 | Barapukuria | 72 | 23:00 | 81 | Kachua | 106 | 22:00 | 147 | Payra | 38 | 23:00
16 | Barguna | 24 | 00:00 | 82 | Kaliganj | 40 | 19:30 | 148 | Postogola | 63 | 00:00
17 | Barishal | 114 | 13:00 | 83 | Kallyanpur | 156 | 12:00 | 149 | Pubail | 39 | 02:00
18 | Barishal-230 | 112 | 23:00 | 84 | Kalurghat | 34 | 00:00 | 150 | Purbachal | 31 | 21:00
19 | Baroaulia | 48 | 08:00 | 85 | Kamrangirchar | 74 | 01:00 | 151 | Purbasadipur | 155 | 23:00
20 | Baroirhat | 66 | 22:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 49 | 23:00
21 | Bashundhara | 206 | 13:00 | 87 | Kasba | 44 | 20:00 | 153 | Rahim | 33 | 02:00
22 | BashundharaCement | 12 | 00:00 | 88 | Kazla | 115 | 00:00 | 154 | Rajbari | 90 | 23:00
23 | Beanibazar | 90 | 19:30 | 89 | Keranigonj | 86 | 23:00 | 155 | Rajendrapur | 118 | 22:00
24 | Benapole | 70 | 20:00 | 90 | Khagrachori | 36 | 19:00 | 156 | Rajshahi | 138 | 23:00
25 | Bhaluka | 152 | 19:30 | 91 | Khulna | 65 | 13:00 | 157 | Rajshahi-230 | 95 | 23:00
26 | Bhandaria | 64 | 00:00 | 92 | Khulshi | 190 | 20:00 | 158 | Ramganj | 120 | 00:00
27 | Bhangura | 43 | 19:30 | 93 | Kishoreganj | 154 | 22:00 | 159 | Rampur | 46 | 00:00
28 | Bheramara(GK) | 69 | 21:00 | 94 | Kodda | 257 | 07:00 | 160 | Rangamati | 18 | 09:00
29 | Bhulta | 224 | 00:00 | 95 | Kulaura | 62 | 19:00 | 161 | Rangpur | 136 | 21:00
30 | Bog-Sherpur | 88 | 00:00 | 96 | Kurigram | 76 | 19:30 | 162 | Ruppur | 4.2 | 10:00
31 | Bogura | 187 | 22:00 | 97 | Kushtia | 145 | 19:30 | 163 | SSM | 9 | 23:00
32 | Borhanuddin | 83 | 23:00 | 98 | Laksam | 31 | 23:00 | 164 | Saidpur | 108 | 00:00
33 | Brahmanbaria | 157 | 19:30 | 99 | Lakshmipur | 47 | 22:00 | 165 | Santhia | 39 | 19:30
34 | Cantonment | 112 | 19:00 | 100 | Lalbag | 71 | 00:00 | 166 | Satkhira | 143 | 20:00
35 | Chandina | 47 | 22:00 | 101 | Lalmonirhat | 76 | 19:30 | 167 | Satmasjid | 101 | 19:30
36 | Chandpur | 90 | 00:00 | 102 | MI_Cement | 15.1 | 16:00 | 168 | Savar | 176 | 00:00
37 | Chandraghona | 36 | 19:00 | 103 | Madanganj | 37 | 21:00 | 169 | SevenRings | 5.9 | 08:00
38 | Chapai | 81 | 21:00 | 104 | Madaripur | 133 | 23:00 | 170 | ShahCement | 36 | 00:00
39 | Charfasson | 34 | 00:00 | 105 | Madartek | 90 | 23:00 | 171 | Shahjadpur | 82 | 19:00
40 | Charsaidpur | 31 | 12:00 | 106 | Madunaghat | 57 | 23:00 | 172 | Shahjibazar | 139 | 20:00
41 | Chauddagram | 86 | 23:00 | 107 | Magura | 68 | 20:00 | 173 | Shahmirpur | 50 | 00:00
42 | Chhatak | 46 | 19:00 | 108 | Mahasthangarh | 90 | 23:00 | 174 | Shariatpur | 102 | 23:00
43 | Chowmuhani | 167 | 23:00 | 109 | Maijdee | 46 | 23:00 | 175 | Sherpur | 152 | 20:00
44 | Chuadanga | 125 | 21:00 | 110 | Manikganj | 148 | 21:00 | 176 | Shikalbaha | 30 | 01:00
45 | Coxsbazar | 139 | 00:00 | 111 | Maniknagar | 76 | 13:00 | 177 | Shitalakhya | 61 | 00:00
46 | Cumilla(N) | 129 | 02:00 | 112 | Matarbari | 56 | 19:30 | 178 | Sholosohor | 45 | 00:00
47 | Cumilla(S) | 173 | 00:00 | 113 | Matuail | 72 | 00:00 | 179 | Shomvuganj | 44 | 19:30
48 | Daganbhuiyan | 41 | 23:00 | 114 | Metrorail_Motijheel | 35 | 19:00 | 180 | Shyampur | 160 | 00:00
49 | Daudkandi | 152 | 19:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 116 | 00:00
50 | DhakaUniversity | 48 | 00:00 | 116 | Millgate | 82 | 00:00 | 182 | Sirajganj | 116 | 00:00
51 | Dhamrai | 110 | 21:00 | 117 | Mirpur | 190 | 13:00 | 183 | Sitakunda | 22 | 19:30
52 | Dhanmondi | 99.2 | 19:00 | 118 | Mirsorai | 37 | 02:00 | 184 | Sonargaon | 136 | 01:00
53 | Dohazari | 118 | 20:00 | 119 | Mirzapur | 42 | 23:00 | 185 | Sreemongol | 99 | 22:00
54 | Faridpur | 188 | 00:00 | 120 | Mithapukur | 81 | 19:30 | 186 | Sreepur | 119 | 20:00
55 | Fatullah | 94 | 00:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 55.5 | 22:00
56 | Fenchuganj | 48 | 23:00 | 122 | Mogbazar | 78.6 | 20:00 | 188 | Sunamganj | 64 | 21:00
57 | Feni | 121 | 22:00 | 123 | Mongla | 34 | 01:00 | 189 | Sylhet | 119 | 21:00
58 | GPH | 73 | 05:00 | 124 | Motijheel | 42 | 00:00 | 190 | Sylhet_(South) | 81 | 21:00
59 | Ghatail | 90 | 18:30 | 125 | Muktagacha | 44 | 15:00 | 191 | TK | 28 | 19:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 119 | 22:00 | 192 | Tangail | 206 | 20:00
61 | Ghorashal-230 | 85 | 02:00 | 127 | Muradnagar | 58 | 22:00 | 193 | Taraganj | 27 | 00:00
62 | Goalpara | 36 | 01:00 | 128 | Mymensingh | 171 | 21:00 | 194 | Tasnim | 40 | 22:00
63 | Gollamari | 114 | 21:00 | 129 | Nabinagar | 88 | 00:00 | 195 | Thakurgaon | 126 | 20:00
64 | Gopalganj | 125 | 23:00 | 130 | Naogaon | 156 | 21:00 | 196 | Tongi | 144 | 11:00
65 | Gulshan | 92 | 15:00 | 131 | Narail | 62 | 20:00 | 197 | Ullahpara | 41 | 20:00
66 | Halishahar | 78 | 19:00 | 132 | Narinda | 54 | 00:00 | 198 | Ullon | 63 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 03-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 16108.87 | 790 |  | 16934.87
1:00 | 15826.75 | 784 |  | 16645.75
2:00 | 15687.41 | 728 |  | 16448.41
3:00 | 15388.28 | 586 |  | 16000.28
4:00 | 15065.69 | 467 |  | 15553.69
5:00 | 14783.6 | 442 |  | 15245.6
6:00 | 14097.49 | 337 |  | 14449.49
7:00 | 14006.45 | 295 |  | 14314.45
8:00 | 13581.37 | 355 |  | 13952.37
9:00 | 13246.33 | 317 |  | 13577.33
10:00 | 13165.71 | 317 |  | 13496.71
11:00 | 13496.77 | 281 |  | 13790.42
12:00 | 13980.55 | 249 |  | 14240.55
13:00 | 14524.53 | 250 |  | 14785.53
14:00 | 14302.81 | 141 |  | 14449.81
15:00 | 14491.98 | 108 |  | 14604.98
16:00 | 14189.89 | 132 |  | 14327.89
17:00 | 13765.17 | 102 |  | 13872.17
18:00 | 13246.06 | 72 |  | 13321.06
19:00 | 14146.83 | 146 |  | 14299.83
19:30 | 15913.25 | 155 |  | 16075.25
20:00 | 15905.09 | 187 |  | 16100.51
21:00 | 16359.45 | 281 |  | 16653.45
22:00 | 16308.3 | 264 |  | 16584.18
23:00 | 16114.68 | 545 |  | 16684.21
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 03-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 130 | 9 | 488 | 178 | 1900 | 578 | Ishurdi-Ghorashal Ckt-1 | Export | 3551200
1:00 | 128 | 12 | 484 | 188 | 1902 | 564
2:00 | 124 | 11 | 486 | 174 | 1800 | 534 |  | Import | 0
3:00 | 125 | 12 | 492 | 174 | 1770 | 536
4:00 | 127 | 11 | 500 | 162 | 1806 | 526 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 132 | 17 | 520 | 164 | 1844 | 544
6:00 | 127 | 22 | 450 | 140 | 1604 | 514 |  | Import | 0
7:00 | 120 | 22 | 410 | 130 | 1502 | 516
8:00 | 163 | 37 | 520 | 152 | 1313 | 478 | Sirajganj-Sreepur Ckt-1 | Export | 3125000
9:00 | 154 | 40 | 490 | 152 | 1524 | 584
10:00 | 171 | 40 | 520 | 160 | 1654 | 602 |  | Import | 0
11:00 | 179 | 44 | 564 | 184 | 1702 | 646
12:00 | 174 | 34 | 580 | 196 | 1850 | 686 | Sirajganj-Sreepur Ckt-2 | Export | 3133000
13:00 | 159 | 32 | 524 | 190 | 1872 | 616
14:00 | 187 | 39 | 608 | 162 | 1918 | 658 |  | Import | 0
15:00 | 189 | 43 | 638 | 202 | 1960 | 662
16:00 | 179 | 42 | 600 | 188 | 1898 | 662 | Gopalganj-Aminbazar Ckt-1 | Export | 21140000
17:00 | 181 | 43 | 602 | 186 | 1882 | 632
18:00 | 162 | 36 | 528 | 166 | 1798 | 352 |  | Import | 0
18:30 | 162 | 34 | 540 | 176 | 1742 | 602
19:00 | 165 | 31 | 400 | 94 | 1626 | 488 | Gopalganj-Aminbazar Ckt-2 | Export | 21550000
19:30 | 113 | -1 | 444 | 156 | 1650 | 376
20:00 | 117 | -5 | 456 | 124 | 1762 | 414 |  | Import | 0
21:00 | 111 | -17 | 468 | 134 | 1812 | 366
22:00 | 110 | -23 | 472 | 116 | 1798 | 352 |  | Total Export | 52499200
23:00 | 137 | 2 | 502 | 122 | 1854 | 436 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 03-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8148.5 | 7960.37 | 16108.87 | DAILY GENERATION CURVE
00:30 | 8043 | 7924.81 | 15967.81
01:00 | 7937.5 | 7889.25 | 15826.75 | 03-07-2026
01:30 | 7939 | 7818.08 | 15757.08
02:00 | 7940.5 | 7746.91 | 15687.41
02:30 | 7867 | 7670.845 | 15537.845
03:00 | 7793.5 | 7594.78 | 15388.28
03:30 | 7662.5 | 7564.485 | 15226.985
04:00 | 7531.5 | 7534.19 | 15065.69
04:30 | 7428.5 | 7496.145 | 14924.645
05:00 | 7325.5 | 7458.1 | 14783.6
05:30 | 7255.04 | 7185.505 | 14440.545
06:00 | 7184.58 | 6912.91 | 14097.49
06:30 | 7247.75 | 6804.22 | 14051.97
07:00 | 7310.92 | 6695.53 | 14006.45
07:30 | 7209.185 | 6584.725 | 13793.91
08:00 | 7107.45 | 6473.92 | 13581.37
08:30 | 6951.975 | 6461.875 | 13413.85
09:00 | 6796.5 | 6449.83 | 13246.33
09:30 | 6764 | 6442.02 | 13206.02
10:00 | 6731.5 | 6434.21 | 13165.71
10:30 | 6826.135 | 6505.105 | 13331.24
11:00 | 6920.77 | 6576 | 13496.77
11:30 | 7010.12 | 6728.54 | 13738.66
12:00 | 7099.47 | 6881.08 | 13980.55
12:30 | 7260.865 | 6991.675 | 14252.54
13:00 | 7422.26 | 7102.27 | 14524.53
13:30 | 7228.855 | 7184.815 | 14413.67
14:00 | 7035.45 | 7267.36 | 14302.81
14:30 | 7095.855 | 7301.54 | 14397.395
15:00 | 7156.26 | 7335.72 | 14491.98
15:30 | 7131.24 | 7209.695 | 14340.935
16:00 | 7106.22 | 7083.67 | 14189.89
16:30 | 7028.555 | 6948.975 | 13977.53
17:00 | 6950.89 | 6814.28 | 13765.17
17:30 | 6898.25 | 6607.365 | 13505.615
18:00 | 6845.61 | 6400.45 | 13246.06
18:30 | 7121.305 | 6575.14 | 13696.445
19:00 | 7397 | 6749.83 | 14146.83
19:30 | 8378.36 | 7534.89 | 15913.25
20:00 | 8215.36 | 7689.73 | 15905.09
20:30 | 8313.46 | 7818.81 | 16132.27 |  | Executive Engineer
21:00 | 8411.56 | 7947.89 | 16359.45 |  | Network Operation Division
21:30 | 8358.06 | 7975.815 | 16333.875
22:00 | 8304.56 | 8003.74 | 16308.3
22:30 | 8225.38 | 7986.11 | 16211.49
23:00 | 8146.2 | 7968.48 | 16114.68

## En-Curve
QF-LDC-12
Date | 03-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3232 | 2335.5 | 879 | 38 | 172 | 1494.37 | 97 | 6159 | 0 | 508 | 1055 | 131 | 0 | 8 | 790 | DAILY ENERGY CURVE
00:30 | 3254 | 2317.5 | 879 | 38 | 168 | 1490.81 | 96.5 | 6069 | 0 | 452 | 1067 | 130.5 | 0 | 5.5 | 787 | 03-07-2026
01:00 | 3276 | 2299.5 | 879 | 38 | 164 | 1487.25 | 96 | 5979 | 0 | 396 | 1079 | 130 | 0 | 3 | 784
01:30 | 3298 | 2192 | 879 | 38 | 161 | 1487.58 | 96.5 | 5845 | 0 | 396.5 | 1226.5 | 130 | 0 | 7 | 756 | Energy Generated | 356.6671 |  | MKWHr
02:00 | 3320 | 2084.5 | 879 | 38 | 158 | 1487.91 | 97 | 5711 | 0 | 397 | 1374 | 130 | 0 | 11 | 728 | Energy not Served | 8.176 |  | MKWHr
02:30 | 3317 | 2092 | 879 | 38 | 156 | 1489.345 | 96 | 5677 | 0 | 377.5 | 1337.5 | 65 | 0 | 13.5 | 657 | Total Energy Requirement | 364.8431 |  | MKWHr
03:00 | 3314 | 2099.5 | 879 | 38 | 154 | 1490.78 | 95 | 5643 | 0 | 358 | 1301 | 0 | 0 | 16 | 586
03:30 | 3326.5 | 2099 | 879 | 38 | 152 | 1487.985 | 95 | 5596.5 | 0 | 308 | 1227.5 | 0 | 0 | 17.5 | 526.5
04:00 | 3339 | 2098.5 | 879 | 38 | 150 | 1485.19 | 95 | 5550 | 0 | 258 | 1154 | 0 | 0 | 19 | 467
04:30 | 3336 | 2101.5 | 879 | 38 | 136 | 1479.145 | 94 | 5538 | 0 | 258 | 1043.5 | 0 | 0 | 21.5 | 454.5
05:00 | 3333 | 2104.5 | 879 | 38 | 122 | 1473.1 | 93 | 5526 | 0 | 258 | 933 | 0 | 0 | 24 | 442
05:30 | 3291 | 2117 | 879 | 38 | 125 | 1443.405 | 93 | 5458 | 16.14 | 258 | 696.5 | 0 | 0 | 25.5 | 389.5
06:00 | 3249 | 2129.5 | 879 | 38 | 128 | 1413.71 | 93 | 5390 | 32.28 | 258 | 460 | 0 | 0 | 27 | 337
06:30 | 3253.5 | 2193.75 | 879 | 38 | 123 | 1367.17 | 93.5 | 5286 | 83.55 | 258 | 450 | 0 | 0 | 26.5 | 316
07:00 | 3258 | 2258 | 879 | 38 | 118 | 1320.63 | 94 | 5182 | 134.82 | 258 | 440 | 0 | 0 | 26 | 295
07:30 | 3268.5 | 2200 | 879 | 38 | 138 | 1271.245 | 94.5 | 5038 | 235.665 | 199.5 | 406.5 | 0 | 0 | 25 | 325
08:00 | 3279 | 2142 | 879 | 38 | 158 | 1221.86 | 95 | 4894 | 336.51 | 141 | 373 | 0 | 0 | 24 | 355
08:30 | 3270.5 | 2111.5 | 878.5 | 38 | 148 | 1197.71 | 95.5 | 4787.5 | 396.64 | 112 | 349 | 0 | 0 | 29 | 336
09:00 | 3262 | 2081 | 878 | 38 | 138 | 1173.56 | 96 | 4681 | 456.77 | 83 | 325 | 0 | 0 | 34 | 317
09:30 | 3270 | 2102 | 878 | 38 | 142 | 1137.78 | 48 | 4623.5 | 556.74 | 83 | 288 | 0 | 0 | 39 | 317
10:00 | 3278 | 2123 | 878 | 38 | 146 | 1102 | 0 | 4566 | 656.71 | 83 | 251 | 0 | 0 | 44 | 317
10:30 | 3315 | 2175 | 878 | 38 | 147 | 1086.095 | 30 | 4621 | 654.645 | 83 | 259 | 0 | 0 | 44.5 | 299
11:00 | 3352 | 2227 | 878 | 38 | 148 | 1070.19 | 60 | 4676 | 652.58 | 83 | 267 | 0 | 0 | 45 | 281
11:30 | 3361 | 2243.5 | 889 | 38 | 152 | 1096.23 | 30 | 4820.5 | 692.43 | 92.5 | 276 | 0 | 0 | 47.5 | 265
12:00 | 3370 | 2260 | 900 | 38 | 156 | 1122.27 | 0 | 4965 | 732.28 | 102 | 285 | 0 | 0 | 50 | 249
12:30 | 3360 | 2277.5 | 900 | 38 | 163 | 1150.75 | 0 | 5128.5 | 630.79 | 102 | 454 | 0 | 0 | 48 | 249.5
13:00 | 3350 | 2295 | 900 | 38 | 170 | 1179.23 | 0 | 5292 | 529.3 | 102 | 623 | 0 | 0 | 46 | 250
13:30 | 3330 | 2198 | 899.5 | 38 | 169 | 1309.395 | 0 | 5221.5 | 505.775 | 104 | 597 | 0 | 0 | 41.5 | 195.5
14:00 | 3310 | 2101 | 899 | 38 | 168 | 1439.56 | 0 | 5151 | 482.25 | 106 | 571 | 0 | 0 | 37 | 141
14:30 | 3324 | 2158.25 | 899.5 | 38 | 169 | 1449.945 | 0 | 5201 | 471.2 | 119 | 531.5 | 0 | 0 | 36 | 124.5
15:00 | 3338 | 2215.5 | 900 | 38 | 170 | 1460.33 | 0 | 5251 | 460.15 | 132 | 492 | 0 | 0 | 35 | 108
15:30 | 3368 | 2206.75 | 900 | 38 | 170 | 1430.04 | 0 | 5213.5 | 377.645 | 133.5 | 462.5 | 0 | 0 | 41 | 120
16:00 | 3398 | 2198 | 900 | 38 | 170 | 1399.75 | 0 | 5176 | 295.14 | 135 | 433 | 0 | 0 | 47 | 132
16:30 | 3386.5 | 2157 | 899.5 | 38 | 165 | 1367.705 | 0 | 5133 | 244.825 | 144 | 391 | 0 | 0 | 51 | 117
17:00 | 3375 | 2116 | 899 | 38 | 160 | 1335.66 | 0 | 5090 | 194.51 | 153 | 349 | 0 | 0 | 55 | 102
17:30 | 3323 | 2032.5 | 899.5 | 38 | 156 | 1272.31 | 30 | 5010 | 116.805 | 172.5 | 400.5 | 0 | 0 | 54.5 | 87
18:00 | 3271 | 1949 | 900 | 38 | 152 | 1208.96 | 60 | 4930 | 39.1 | 192 | 452 | 0 | 0 | 54 | 72
18:30 | 3312.5 | 1978.5 | 899.5 | 38 | 154 | 1212.395 | 60 | 4986 | 19.55 | 359 | 630.5 | 0 | 0 | 46.5 | 109
19:00 | 3354 | 2008 | 899 | 38 | 156 | 1215.83 | 60 | 5042 | 0 | 526 | 809 | 0 | 0 | 39 | 146
19:30 | 3473 | 2259 | 900 | 38 | 156 | 1370.89 | 60 | 5597 | 0 | 573 | 1464.36 | 0 | 0 | 22 | 155
20:00 | 3397 | 2137 | 900 | 38 | 158 | 1480.73 | 60 | 5632 | 0 | 579 | 1482.36 | 0 | 0 | 41 | 187
20:30 | 3427 | 2143 | 900 | 38 | 159 | 1488.31 | 60 | 5720.5 | 0 | 574 | 1571.96 | 0 | 0 | 50.5 | 234
21:00 | 3457 | 2149 | 900 | 38 | 160 | 1495.89 | 60 | 5809 | 0 | 569 | 1661.56 | 0 | 0 | 60 | 281
21:30 | 3444 | 2109.5 | 899.5 | 38 | 161 | 1492.315 | 60 | 5834.5 | 0 | 574 | 1660.56 | 0 | 0 | 60.5 | 272.5
22:00 | 3431 | 2070 | 899 | 38 | 162 | 1488.74 | 60 | 5860 | 0 | 579 | 1659.56 | 0 | 0 | 61 | 264
22:30 | 3438.5 | 2147 | 899.5 | 38 | 157 | 1484.01 | 60 | 5846 | 0 | 575.5 | 1506.98 | 0 | 0 | 59 | 404.5
23:00 | 3446 | 2224 | 900 | 38 | 152 | 1479.28 | 60 | 5832 | 0 | 572 | 1354.4 | 0 | 0 | 57 | 545
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 03-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 374 | 18:00 | 351 | 00:00 | Madunaghat | 390 | 19:00 | 380 | 00:00
Amtali | 413 | 09:00 | 403 | 00:00 | Meghnaghat | 378 | 18:30 | 359 | 00:00
Ashuganj | 391 | 08:00 | 367 | 00:00 | Payra | 414 | 09:00 | 403 | 00:00
Bhulta | 396 | 07:00 | 375 | 00:00 | Rahanpur | 406 | 18:30 | 384 | 00:00
Bibiana | 378 | 18:30 | 363 | 00:00 | Rampal | 396 | 10:00 | 374 | 00:00
BIPTC | 402 | 06:00 | 392 | 21:00
Bogura | 388 | 10:00 | 363 | 00:00
Gopalganj | 391 | 08:00 | 367 | 00:00
Kaliakoir | 364 | 18:00 | 338 | 00:00
Korerhat | 391 | 18:30 | 374 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 18:30 | 214 | 00:00 | Ishurdi | 235 | 10:00 | 208 | 22:00
AKSML | 233 | 06:00 | 222 | 00:00 | Jhenaidah | 228 | 18:30 | 197 | 22:00
Aminbazar | 230 | 18:00 | 214 | 00:00 | Kachua | 222 | 10:00 | 211 | 00:00
Ashuganj | 227 | 09:00 | 214 | 00:00 | Kaliakoir | 227 | 18:30 | 210 | 00:00
Ashuganj-400 | 227 | 09:00 | 214 | 00:00 | Keranigonj | 228 | 18:30 | 212 | 00:00
Baghabari | 232 | 08:00 | 216 | 00:00 | Khulna(S) | 226 | 10:00 | 202 | 22:00
Barapukuria | 224 | 18:30 | 210 | 00:00 | Korerhat | 223 | 18:30 | 212 | 00:00
Barapukuria-230 | 224 | 18:30 | 210 | 00:00 | Madunaghat | 236 | 09:00 | 228 | 00:00
Barishal | 226 | 18:00 | 214 | 00:00 | Madunaghat-400 | 237 | 19:00 | 230 | 00:00
Bheramara | 234 | 18:30 | 206 | 22:00 | Maniknagar | 226 | 07:00 | 213 | 00:00
Bhulta | 228 | 09:00 | 214 | 00:00 | Meghnaghat | 236 | 07:00 | 223 | 00:00
Bibiana | 220 | 10:00 | 210 | 00:00 | Meghnaghat-400 | 230 | 10:00 | 218 | 00:00
BIPTC | 236 | 10:00 | 206 | 22:00 | Mirsorai | 227 | 18:30 | 217 | 00:00
Bogura | 240 | 18:00 | 223 | 00:00 | Naogaon | 226 | 18:00 | 200 | 22:00
Bogura-400 | 240 | 10:00 | 224 | 00:00 | Purbasadipur | 222 | 18:00 | 206 | 00:00
Borhanuddin | 230 | 18:30 | 220 | 00:00 | Rajshahi | 233 | 18:30 | 203 | 22:00
BSRM | 224 | 18:30 | 214 | 00:00 | Rampal | 225 | 09:00 | 205 | 22:00
Charfasson | 232 | 18:00 | 220 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 222 | 09:00 | 210 | 00:00 | Rampura | 226 | 07:00 | 213 | 00:00
Cumilla(N) | 224 | 07:00 | 212 | 00:00 | Shikalbaha | 235 | 18:30 | 228 | 12:00
Faridpur | 222 | 18:30 | 205 | 00:00 | Shyampur | 228 | 10:00 | 214 | 00:00
Fenchuganj | 222 | 09:00 | 211 | 00:00 | Siddhirganj | 229 | 09:00 | 216 | 00:00
Feni | 222 | 18:30 | 21 | 03:00 | Sirajgonj | 239 | 18:30 | 228 | 00:00
Ghorashal | 230 | 07:00 | 220 | 00:00 | Sreepur | 225 | 19:00 | 211 | 01:00
Ghorashal-230 | 215 | 18:30 | 196 | 00:00 | Tongi | 216 | 18:30 | 126 | 19:00
Gopalganj | 222 | 08:00 | 208 | 00:00
GPH | 231 | 09:00 | 222 | 00:00
Haripur | 228 | 07:00 | 215 | 00:00
Hasnabad | 234 | 09:00 | 213 | 00:00
Hathazari | 232 | 07:00 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 07:00 | 130 | 00:00 | Madunaghat | 136 | 09:00 | 117 | 15:00
Agargaon | 134 | 07:00 | 125 | 00:00 | Magura | 131 | 18:30 | 105 | 22:00
Agrabad | 135 | 18:00 | 129 | 00:00 | Mahasthangarh | 136 | 18:30 | 121 | 00:00
AKS | 132 | 18:30 | 127 | 12:00 | Maijdee | 124 | 09:00 | 117 | 00:00
Aminbazar | 150 | 00:00 | 120 | 00:00 | Manikganj | 130 | 19:30 | 118 | 00:00
Amnura | 138 | 18:30 | 119 | 01:00 | Maniknagar | 133 | 06:00 | 125 | 00:00
Ashuganj | 133 | 09:00 | 125 | 00:00 | Matarbari | 123 | 18:00 | 108 | 00:00
Ashuganj-230 | 136 | 09:00 | 127 | 00:00 | Matuail | 132 | 09:00 | 124 | 00:00
Bagerhat | 131 | 18:30 | 110 | 22:00 | Metrorail_Motijheel | 133 | 06:00 | 125 | 00:00
Bajitpur | 124 | 11:00 | 116 | 19:30 | Metrorail_Uttara | 131 | 18:30 | 118 | 00:00
Bakerganj | 132 | 10:00 | 123 | 23:00 | Millgate | 132 | 18:30 | 120 | 00:00
Bakulia | 134 | 07:00 | 129 | 12:00 | Mirpur | 130 | 07:00 | 121 | 13:00
Banani | 138 | 06:00 | 130 | 00:00 | Mirzapur | 130 | 19:00 | 120 | 01:00
Bangabhaban | 133 | 07:00 | 124 | 00:00 | Mithapukur | 133 | 18:00 | 117 | 00:00
Barapukuria | 136 | 18:00 | 122 | 00:00 | MI_Cement | 134 | 18:30 | 124 | 00:00
Barguna | 132 | 18:30 | 122 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 132 | 18:30 | 122 | 22:00 | Mogbazar | 140 | 07:00 | 131 | 13:00
Barishal-230 | 132 | 18:30 | 123 | 22:00 | Mongla | 130 | 10:00 | 111 | 21:00
Baroaulia | 135 | 09:00 | 130 | 00:00 | Motijheel | 133 | 07:00 | 124 | 00:00
Baroirhat | 130 | 19:30 | 124 | 00:00 | Muktagacha | 128 | 10:00 | 113 | 00:00
Bashundhara | 138 | 06:00 | 120 | 00:00 | Munshiganj | 131 | 18:30 | 123 | 00:00
BashundharaCement | 132 | 18:00 | 125 | 00:00 | Muradnagar | 126 | 09:00 | 118 | 00:00
Beanibazar | 124 | 07:00 | 115 | 22:00 | Mymensingh | 127 | 10:00 | 108 | 19:00
Benapole | 133 | 18:30 | 109 | 22:00 | Nabinagar | 130 | 18:30 | 116 | 00:00
Bhaluka | 130 | 19:00 | 119 | 00:00 | Naogaon | 136 | 18:00 | 120 | 22:00
Bhandaria | 127 | 18:30 | 112 | 23:00 | Narail | 130 | 09:00 | 100 | 22:00
Bhangura | 134 | 09:00 | 123 | 22:00 | Narinda | 133 | 06:00 | 125 | 00:00
Bheramara | 137 | 18:30 | 119 | 22:00 | Narshingdi | 128 | 09:00 | 117 | 00:00
Bheramara(GK) | 137 | 18:30 | 118 | 22:00 | Natore | 135 | 18:30 | 118 | 00:00
Bhulta | 129 | 10:00 | 121 | 00:00 | Nawabganj | 137 | 18:30 | 126 | 00:00
Bog-Sherpur | 136 | 18:00 | 123 | 00:00 | Netrakona | 118 | 08:00 | 109 | 00:00
Bogura | 138 | 18:00 | 126 | 00:00 | New | 134 | 18:30 | 122 | 00:00
Bogura-230 | 138 | 10:00 | 126 | 00:00 | Niamatpur | 134 | 18:00 | 122 | 22:00
Brahmanbaria | 129 | 09:00 | 119 | 00:00 | Noapara | 135 | 18:00 | 113 | 22:00
Cantonment | 134 | 07:00 | 125 | 00:00 | Pabna | 135 | 10:00 | 120 | 00:00
Chandina | 129 | 09:00 | 121 | 00:00 | Palashbari | 131 | 18:30 | 116 | 00:00
Chandpur | 126 | 19:30 | 120 | 00:00 | Panchagarh | 137 | 05:00 | 125 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 18:30 | 14 | 21:00 | Patiya | 133 | 09:00 | 128 | 00:00
Chapai | 133 | 10:00 | 126 | 00:00 | Patnitala | N/A | N/A | N/A | N/A
Charsaidpur | 132 | 18:30 | 124 | 00:00 | Patuakhali | 131 | 09:00 | 124 | 00:00
Chauddagram | 127 | 09:00 | 120 | 00:00 | Payra | 135 | 10:00 | 33 | 20:00
Chhatak | 124 | 07:00 | 111 | 00:00 | PHP | 129 | 10:00 | 123 | 00:00
Chowmuhani | 124 | 09:00 | 119 | 00:00 | Postogola | 136 | 06:00 | 126 | 00:00
Chuadanga | 135 | 18:30 | 111 | 22:00 | Pubail | 126 | 18:00 | 116 | 00:00
Coxsbazar | 125 | 18:30 | 110 | 00:00 | Purbachal | 139 | 07:00 | 130 | 00:00
Cumilla(N) | 128 | 07:00 | 121 | 00:00 | Purbasadipur | 133 | 17:00 | 123 | 00:00
Cumilla(S) | 129 | 18:00 | 119 | 15:00 | Rahanpur | 136 | 18:30 | 127 | 22:00
Daganbhuiyan | 127 | 18:00 | 120 | 00:00 | Rahanpur-400 | 136 | 18:30 | 128 | 00:00
Daudkandi | 125 | 10:00 | 116 | 00:00 | Rahim | 132 | 10:00 | 124 | 00:00
DhakaUniversity | 139 | 06:00 | 130 | 00:00 | Rajbari | 126 | 10:00 | 114 | 00:00
Dhamrai | 131 | 18:30 | 120 | 00:00 | Rajendrapur | 130 | 19:00 | 119 | 01:00
Dhanmondi | 139.6 | 09:00 | 131 | 00:00 | Rajshahi | 133 | 18:30 | 117 | 00:00
Dohazari | 133 | 18:30 | 122 | 00:00 | Rajshahi-230 | 134 | 18:30 | 117 | 00:00
Faridpur | 128 | 08:00 | 118 | 00:00 | Ramganj | 123 | 18:30 | 116 | 00:00
Fatullah | 138 | 18:30 | 125 | 00:00 | Rampur | 134 | 18:30 | 128 | 12:00
Fenchuganj | 131 | 09:00 | 123 | 00:00 | Rampura | 139 | 07:00 | 131 | 00:00
Feni | 128 | 10:00 | 124 | 00:00 | Rangamati | 134 | 05:00 | 129 | 12:00
Feni-230 | 128 | 09:00 | 122 | 00:00 | Rangpur | 130 | 17:00 | 116 | 00:00
Ghatail | 126 | 10:00 | 113 | 00:00 | Ruppur | 137 | 09:00 | 121 | 00:00
Ghorashal | 128 | 07:00 | 119 | 00:00 | Saidpur | 134 | 19:00 | 121 | 00:00
Goalpara | 136 | 18:00 | 118 | 22:00 | Santhia | 135 | 10:00 | 122 | 00:00
Gollamari | 136 | 18:30 | 121 | 00:00 | Satkhira | 131 | 18:00 | 108 | 22:00
Gopalganj | 131 | 18:30 | 117 | 22:00 | Satmasjid | 134 | 18:30 | 124 | 00:00
Gopalganj-400 | 132 | 18:30 | 122 | 00:00 | Savar | 131 | 18:00 | 118 | 01:00
Gulshan | 138 | 07:00 | 130 | 00:00 | SevenRings | 128 | 18:30 | 118 | 00:00
Halishahar | 135 | 18:30 | 129 | 12:00 | ShahCement | 132 | 18:30 | 124 | 00:00
Haripur | 133 | 10:00 | 125 | 00:00 | Shahjadpur | 139 | 09:00 | 126 | 00:00
HaripurSBU | 133 | 10:00 | 124 | 01:00 | Shahjibazar | 130 | 08:00 | 120 | 00:00
Hasnabad | 136 | 09:00 | 126 | 00:00 | Shahmirpur | 135 | 18:30 | 129 | 12:00
Hathazari | 135 | 06:00 | 131 | 00:00 | Shariatpur | 130 | 18:30 | 117 | 00:00
Hatirjheel | 139 | 07:00 | 131 | 00:00 | Sherpur | 128 | 19:30 | 110 | 00:00
Ishurdi | 138 | 09:00 | 122 | 00:00 | Shikalbaha | 124 | 18:00 | 119 | 00:00
Jaldhaka | 131 | 18:00 | 118 | 00:00 | Shikalbaha-230 | 136 | 18:30 | 131 | 11:00
Jamalpur | 131 | 19:30 | 112 | 00:00 | Shitalakhya | 134 | 18:30 | 125 | 00:00
Jashore | 134 | 18:30 | 111 | 22:00 | Sholosohor | 135 | 07:00 | 130 | 13:00
Jhenaidah | 139 | 18:30 | 110 | 00:00 | Shomvuganj | 122 | 19:00 | 109 | 19:30
Jhenaidah-230 | 139 | 18:30 | 118 | 22:00 | Shyampur | 136 | 18:30 | 127 | 00:00
Joydebpur | 124 | 18:00 | 114 | 00:00 | Shyampur-230 | 137 | 10:00 | 126 | 00:00
Joypurhat | 133 | 18:00 | 118 | 00:00 | Siddhirganj | 133 | 10:00 | 125 | 00:00
Juldah | 134 | 08:00 | 129 | 13:00 | Sirajganj | 134 | 18:30 | 120 | 00:00
Kabirpur | 134 | 19:00 | 116 | 00:00 | Sitakunda | 135 | 18:00 | 128 | 02:00
Kachua | 126 | 18:00 | 120 | 00:00 | Sonargaon | 130 | 18:30 | 121 | 00:00
Kaliakoir | 134 | 18:00 | 122 | 00:00 | Sreemongol | 128 | 09:00 | 119 | 00:00
Kaliganj | 137 | 18:00 | 116 | 22:00 | Sreepur | 134 | 19:00 | 122 | 00:00
Kallyanpur | 131 | 18:30 | 120 | 12:00 | Srinagar | 137 | 10:00 | 127 | 00:00
Kalurghat | 136 | 06:00 | 132 | 00:00 | SSM | 140 | 08:00 | 132 | 12:00
Kamrangirchar | 138 | 18:30 | 118 | 00:00 | Sunamganj | 121 | 07:00 | 109 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 125 | 09:00 | 118 | 00:00
Kasba | 125 | 09:00 | 117 | 00:00 | Sylhet_(South) | 125 | 07:00 | 17 | 01:00
Kazla | 133 | 07:00 | 124 | 00:00 | Tangail | 126 | 09:00 | 115 | 00:00
Keranigonj | 138 | 18:30 | 127 | 00:00 | Taraganj | 132 | 18:00 | 120 | 00:00
Khagrachori | 134 | 18:30 | 128 | 12:00 | Tasnim | 130 | 18:30 | 121 | 00:00
Khulna | 135 | 18:30 | 116 | 22:00 | Thakurgaon | 136 | 19:00 | 125 | 00:00
Khulna(S) | 136 | 18:00 | 118 | 22:00 | TK | 137 | 18:30 | 132 | 00:00
Khulshi | 133 | 18:30 | 128 | 00:00 | Tongi | 133 | 21:00 | 125 | 00:00
Kishoreganj | 125 | 19:00 | 115 | 00:00 | Ullahpara | 135 | 18:30 | 122 | 00:00
Kodda | 134 | 19:30 | 119 | 00:00 | Ullon | 138 | 06:00 | 130 | 00:00
Korerhat | 131 | 09:00 | 125 | 00:00 | Uttara | 131 | 18:30 | 118 | 00:00
KSRM | 135 | 18:30 | 128 | 01:00 | UttaraNew | 131 | 18:30 | 118 | 00:00
Kulaura | 130 | 09:00 | 122 | 00:00 | Zigatola | 138 | 18:30 | 127 | 00:00
Kurigram | 129 | 18:00 | 114 | 00:00
Kushtia | 134 | 10:00 | 113 | 22:00
Laksam | 126 | 18:30 | 119 | 00:00
Lakshmipur | 124 | 18:30 | 116 | 00:00
Lalbag | 138 | 18:30 | 128 | 00:00
Lalmonirhat | 127 | 15:00 | 116 | 22:00
Madanganj | 132 | 18:00 | 124 | 00:00
Madaripur | 131 | 18:00 | 120 | 00:00
Madartek | 138 | 07:00 | 131 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 03-07-2026 | [28 empty] | Date: | 03-07-2026 | [28 empty] | Date: | 03-07-2026 | [28 empty] | Date: | 03-07-2026 | [28 empty] | Date: | 03-07-2026 | [18 empty] | Date: | 03-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 28 | 38 | 45 | 146 | 15 | 17 | 35 | 0 | 0 | 308 | 525 | 0 | 0 | 317 | 0 | 0 | 0 | 143 | 15.5 | 21 | 0 | 560 | 15 | 16 | 44 | 0 | 8 | 50 | 15 | 17 | 12 | 12 | 0 | 97 | 36 | 33 | 1115 | 0 | 0 | 32 | 0 | 16 | 216 | 0 | 0 | 0 | 1170 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 5 | 207 | 39 | 51 | 138 | 17 | 0 | 17 | 48 | 172 | 8 | 0 | 23 | 330 | 0 | 74 | 29 | 0 | 151 | 0 | 16 | 0 | 83 | 20 | 143 | 0 | 98 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 18 | 8148.5 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 131 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 1494.37 | 0 | 39 | 0 | 35 | 35 | 0 | 100 | 20 | 0 | 0 | 0 | 21 | 0 | 0 | 138 | 0 | 126 | 0 | 125 | 0 | 383 | 0 | 0 | 180 | 37 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 277 | 65 | 220 | 0 | 1050 | 1190 | 17 | 7960.37 | 16108.87 | 75.77
01:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 0 | 17 | 35 | 30 | 130 | 15 | 0 | 0 | 0 | 0 | 287 | 540 | 0 | 0 | 302 | 0 | 0 | 0 | 143 | 15.5 | 21 | 0 | 535 | 25 | 16 | 30 | 0 | 3 | 50 | 15 | 17 | 12 | 12 | 0 | 96 | 60 | 33 | 925 | 0 | 0 | 32 | 0 | 32 | 217 | 0 | 0 | 0 | 1163 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 5 | 207 | 39 | 50 | 139 | 35 | 0 | 17 | 90 | 164 | 8 | 0 | 23 | 325 | 0 | 119 | 29 | 0 | 151 | 0 | 16 | 0 | 83 | 20 | 140 | 0 | 98 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7937.5 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 130 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 1487.25 | 0 | 39 | 0 | 35 | 50 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 126 | 0 | 125 | 0 | 390 | 0 | 0 | 180 | 40 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 276 | 65 | 220 | 0 | 1050 | 1205 | 17 | 7889.25 | 15826.75 | 75.76
02:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 17 | 35 | 30 | 130 | 32 | 0 | 0 | 0 | 0 | 290 | 470 | 0 | 0 | 290 | 0 | 0 | 0 | 143 | 15.5 | 21 | 0 | 415 | 60 | 16 | 24 | 0 | 11 | 50 | 15 | 17 | 12 | 12 | 0 | 97 | 107 | 30 | 835 | 0 | 0 | 45 | 0 | 102 | 217 | 0 | 0 | 0 | 1163 | 0 | 11 | 0 | 220 | 290 | 220 | 51 | 5 | 214 | 40 | 35 | 139 | 128 | 0 | 17 | 96 | 158 | 25 | 0 | 23 | 320 | 0 | 183 | 29 | 0 | 131 | 0 | 16 | 0 | 83 | 20 | 140 | 0 | 99 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7940.5 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 130 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 1487.91 | 0 | 39 | 0 | 35 | 70 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 127 | 0 | 125 | 0 | 404 | 0 | 0 | 180 | 36 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 274 | 65 | 220 | 0 | 878 | 1205 | 17 | 7746.91 | 15687.41 | 75.75
03:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 17 | 35 | 15 | 64 | 41 | 0 | 0 | 0 | 0 | 295 | 465 | 0 | 0 | 292 | 0 | 0 | 0 | 143 | 15.5 | 21 | 0 | 440 | 58 | 16 | 23 | 0 | 16 | 50 | 15 | 17 | 12 | 12 | 0 | 95 | 106 | 30 | 780 | 0 | 0 | 50 | 0 | 96 | 218 | 0 | 0 | 0 | 1160 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 5 | 213 | 40 | 0 | 139 | 151 | 0 | 17 | 95 | 154 | 25 | 0 | 23 | 310 | 0 | 183 | 29 | 0 | 131 | 0 | 16 | 0 | 83 | 20 | 141 | 0 | 98 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7793.5 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 1490.78 | 0 | 32 | 0 | 35 | 70 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 130 | 0 | 128 | 0 | 406 | 0 | 0 | 180 | 35 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 276 | 65 | 220 | 0 | 867 | 1205 | 17 | 7594.78 | 15388.28 | 75.74
04:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 17 | 35 | 15 | 64 | 41 | 0 | 0 | 0 | 0 | 295 | 465 | 0 | 0 | 300 | 0 | 0 | 0 | 143 | 15.5 | 21 | 0 | 450 | 17 | 16 | 23 | 0 | 19 | 0 | 0 | 17 | 12 | 12 | 0 | 95 | 105 | 30 | 715 | 0 | 0 | 50 | 0 | 68 | 217 | 0 | 0 | 0 | 1165 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 5 | 213 | 40 | 0 | 139 | 100 | 0 | 17 | 69 | 150 | 25 | 0 | 23 | 315 | 0 | 183 | 29 | 0 | 131 | 0 | 0 | 0 | 83 | 20 | 141 | 0 | 98 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7531.5 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 1485.19 | 0 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 132 | 0 | 132 | 0 | 414 | 0 | 0 | 180 | 35 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 224 | 65 | 220 | 0 | 886 | 1205 | 17 | 7534.19 | 15065.69 | 75.73
05:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 21 | 35 | 15 | 15 | 41 | 0 | 0 | 0 | 0 | 296 | 465 | 0 | 0 | 300 | 0 | 0 | 0 | 143 | 15.5 | 21 | 0 | 455 | 15 | 16 | 23 | 0 | 24 | 0 | 0 | 17 | 12 | 12 | 0 | 93 | 106 | 25 | 720 | 0 | 0 | 35 | 0 | 64 | 218 | 0 | 0 | 0 | 1166 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 5 | 215 | 40 | 0 | 138 | 36 | 0 | 17 | 30 | 122 | 8 | 0 | 23 | 320 | 0 | 183 | 29 | 0 | 131 | 0 | 0 | 0 | 83 | 20 | 140 | 0 | 100 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 7325.5 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 1473.1 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 132 | 0 | 132 | 0 | 414 | 0 | 0 | 180 | 35 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 214 | 65 | 220 | 0 | 866 | 1205 | 17 | 7458.1 | 14783.6 | 75.72
06:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 28 | 35 | 15 | 0 | 41 | 0 | 0 | 0 | 0 | 293 | 475 | 0 | 0 | 297 | 0 | 0 | 1 | 143 | 16.5 | 21 | 0 | 465 | 15 | 16 | 25 | 0 | 27 | 0 | 0 | 17 | 12 | 12 | 0.39 | 93 | 51 | 32 | 720 | 0 | 0 | 19 | 0 | 34 | 217 | 0 | 0 | 0 | 1165 | 0 | 13 | 0 | 220 | 290 | 220 | 51 | 5 | 217 | 40 | 0 | 139 | 0 | 0 | 17 | 0 | 128 | 0 | 5 | 23 | 315 | 0 | 182 | 29 | 0 | 136 | 0 | 0 | 0 | 83 | 20 | 140 | 0 | 101 | 0 | 48 | 0.8 | 48 | 0 | 0.1 | 0.79 | 12 | 7184.58 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 1110 | 0 | 0 | 0 | 1413.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 8 | 0 | 0 | 1.81 | 140 | 0 | 132 | 0 | 132 | 0 | 330 | 0 | 0.18 | 180 | 36 | 0 | 1 | 34 | 0 | 0 | 0 | 0.5 | 9 | 0.03 | 0 | 232 | 65 | 220 | 0 | 807 | 1140 | 0 | 6912.91 | 14097.49 | 75.71
07:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 28 | 35 | 15 | 0 | 41 | 0 | 0 | 0 | 0 | 306 | 510 | 0 | 0 | 303 | 0 | 0 | 5 | 143 | 18 | 21 | 0 | 550 | 15 | 16 | 24 | 0 | 26 | 0 | 0 | 0 | 12 | 12 | 0.52 | 94 | 50 | 14 | 720 | 0 | 0 | 19 | 0 | 32 | 217 | 0 | 0 | 0 | 1170 | 2 | 13 | 0 | 220 | 290 | 220 | 51 | 5 | 216 | 40 | 0 | 138 | 0 | 0 | 17 | 0 | 118 | 0 | 10 | 23 | 315 | 0 | 181 | 29 | 0 | 148 | 0 | 0 | 0 | 83 | 20 | 140 | 0 | 101 | 0 | 49 | 3.1 | 48 | 0 | 0.6 | 5.7 | 12 | 7310.92 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 996 | 0 | 0 | 0 | 1320.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.51 | 24 | 0 | 0 | 9.7 | 140 | 0 | 135 | 0 | 134 | 0 | 330 | 0 | 0.96 | 180 | 36 | 0 | 7 | 34 | 0 | 0 | 0 | 1.7 | 52 | 0.03 | 0 | 262 | 65 | 220 | 0 | 778 | 1040 | 0 | 6695.53 | 14006.45 | 75.7
08:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 17 | 35 | 15 | 0 | 41 | 0 | 0 | 0 | 0 | 296 | 505 | 0 | 0 | 301 | 0 | 0 | 8 | 51 | 15 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 12 | 12 | 2.16 | 95 | 51 | 14 | 720 | 0 | 0 | 19 | 0 | 31 | 215 | 0 | 0 | 0 | 1165 | 4 | 12 | 0 | 220 | 290 | 220 | 51 | 5 | 215 | 40 | 0 | 138 | 0 | 0 | 17 | 0 | 158 | 0 | 37 | 23 | 320 | 0 | 181 | 29 | 0 | 145 | 1 | 0 | 0 | 83 | 25 | 141 | 0 | 101 | 0 | 49 | 13.62 | 48 | 0 | 0.7 | 5.97 | 12 | 7107.45 | 879 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58 | 897 | 0 | 0 | 0 | 1221.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.61 | 40 | 0 | 0 | 22.98 | 143 | 0 | 135 | 0 | 135 | 0 | 330 | 0 | 2.46 | 180 | 36 | 0 | 14 | 34 | 0 | 0 | 0 | 3.9 | 99 | 0.11 | 0 | 214 | 65 | 220 | 0 | 702 | 980 | 0 | 6473.92 | 13581.37 | 75.69
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 17 | 34 | 15 | 0 | 41 | 0 | 0 | 0 | 0 | 302 | 455 | 0 | 0 | 300 | 0 | 0 | 15 | 51 | 15 | 21 | 0 | 470 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 12 | 12 | 4.57 | 96 | 45 | 14 | 700 | 0 | 0 | 19 | 0 | 27 | 213 | 0 | 0 | 0 | 1015 | 9 | 0 | 0 | 220 | 290 | 220 | 51 | 5 | 201 | 40 | 0 | 137 | 0 | 0 | 5 | 0 | 138 | 0 | 23 | 0 | 315 | 0 | 186 | 29 | 0 | 125 | 3 | 0 | 0 | 83 | 30 | 140 | 0 | 101 | 0 | 49 | 16.3 | 57 | 0 | 1 | 17.63 | 12 | 6796.5 | 878 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 54 | 878 | 0 | 0 | 0 | 1173.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.52 | 57 | 0 | 0 | 35.11 | 142 | 0 | 135 | 0 | 135 | 0 | 330 | 0 | 3.99 | 180 | 38 | 0 | 24 | 0 | 0 | 0 | 0 | 5.3 | 145 | 0.35 | 0 | 219 | 65 | 220 | 0 | 691 | 960 | 0 | 6449.83 | 13246.33 | 75.69
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 41 | 0 | 0 | 0 | 0 | 299 | 475 | 0 | 0 | 301 | 0 | 0 | 26 | 51 | 15 | 21 | 0 | 475 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 4.28 | 0 | 0 | 9 | 670 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 1000 | 7 | 0 | 0 | 220 | 290 | 220 | 51 | 5 | 204 | 40 | 0 | 135 | 0 | 0 | 14 | 0 | 146 | 0 | 64 | 0 | 320 | 0 | 186 | 29 | 0 | 136 | 2 | 0 | 0 | 83 | 30 | 142 | 0 | 100 | 0 | 59 | 21.33 | 105 | 0 | 2 | 37.89 | 12 | 6731.5 | 878 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 78 | 828 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.02 | 89 | 0 | 0 | 50.41 | 143 | 0 | 135 | 0 | 135 | 0 | 330 | 0 | 4.48 | 180 | 37 | 0 | 30 | 0 | 0 | 0 | 0 | 4.8 | 178 | 0.5 | 0 | 221 | 65 | 220 | 0 | 680 | 950 | 0 | 6434.21 | 13165.71 | 75.68
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 30 | 0 | 0 | 0 | 0 | 298 | 510 | 0 | 0 | 298 | 0 | 0 | 12 | 51 | 15 | 21 | 0 | 530 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 17 | 0 | 0 | 5.15 | 60 | 0 | 14 | 670 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 1025 | 5 | 0 | 0 | 220 | 290 | 220 | 51 | 5 | 204 | 40 | 0 | 135 | 0 | 0 | 17 | 0 | 148 | 0 | 70 | 0 | 320 | 0 | 170 | 29 | 0 | 145 | 6 | 0 | 0 | 81 | 30 | 140 | 0 | 101 | 0 | 59 | 21.31 | 115 | 0 | 2.3 | 34.01 | 12 | 6920.77 | 878 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 104.21 | 812 | 0 | 0 | 0 | 1070.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.79 | 92 | 0 | 0 | 47.76 | 143 | 0 | 135 | 0 | 135 | 0 | 414 | 0 | 5.02 | 180 | 38 | 0 | 30 | 0 | 0 | 0 | 0 | 4.7 | 190 | 0.33 | 0 | 247 | 65 | 220 | 0 | 744 | 960 | 0 | 6576 | 13496.77 | 75.68
12:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 298 | 520 | 0 | 0 | 309 | 0 | 0 | 24 | 51 | 15 | 21 | 0 | 525 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 17 | 0 | 0 | 5.25 | 0 | 0 | 14 | 675 | 0 | 0 | 0 | 1 | 0 | 210 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 220 | 290 | 220 | 51 | 5 | 204 | 40 | 0 | 134 | 0 | 0 | 17 | 0 | 156 | 0 | 71 | 0 | 325 | 0 | 171 | 29 | 0 | 148 | 11 | 16 | 0 | 85 | 30 | 142 | 0 | 101 | 0 | 59 | 21.29 | 116 | 0 | 2.3 | 16.63 | 12 | 7099.47 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 105.64 | 890 | 0 | 0 | 0 | 1122.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.42 | 116 | 0 | 0 | 57.46 | 142 | 0 | 136 | 0 | 135 | 0 | 414 | 0 | 5.57 | 180 | 37 | 0 | 33 | 0 | 0 | 0 | 0 | 6.9 | 205 | 0.82 | 0 | 250 | 63 | 220 | 0 | 763 | 1010 | 0 | 6881.08 | 13980.55 | 75.67
13:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 52 | 0 | 45 | 30 | 0 | 0 | 0 | 0 | 303 | 530 | 0 | 0 | 309 | 0 | 0 | 34 | 51 | 15 | 21 | 0 | 545 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 17 | 0 | 12 | 4.5 | 0 | 25 | 14 | 675 | 0 | 0 | 8 | 7 | 8 | 211 | 0 | 0 | 0 | 1224 | 9 | 33 | 0 | 220 | 290 | 220 | 51 | 5 | 204 | 35 | 0 | 134 | 0 | 0 | 17 | 43 | 170 | 0 | 69 | 0 | 325 | 0 | 154 | 29 | 0 | 149 | 12 | 16 | 0 | 84 | 30 | 140 | 0 | 101 | 0 | 59 | 18 | 116 | 0 | 1.2 | 55.56 | 12 | 7422.26 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58.99 | 1085 | 0 | 0 | 0 | 1179.23 | 0 | 0 | 0 | 35 | 22 | 0 | 0 | 0 | 0 | 59.96 | 99 | 0 | 0 | 46.73 | 143 | 0 | 135 | 0 | 135 | 0 | 414 | 0 | 2.36 | 180 | 36 | 50 | 15 | 33 | 0 | 0 | 0 | 7.7 | 36 | 0.3 | 16 | 247 | 63 | 220 | 0 | 765 | 1080 | 0 | 7102.27 | 14524.53 | 75.67
14:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 300 | 475 | 0 | 0 | 284 | 0 | 0 | 26 | 55 | 15 | 21 | 0 | 425 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 17 | 0 | 12 | 3.83 | 0 | 46 | 14 | 675 | 0 | 0 | 18 | 0 | 34 | 211 | 0 | 0 | 0 | 1125 | 0 | 40 | 0 | 220 | 290 | 220 | 51 | 5 | 203 | 36 | 0 | 134 | 0 | 0 | 17 | 15 | 168 | 0 | 66 | 0 | 325 | 0 | 153 | 29 | 0 | 134 | 11 | 16 | 0 | 83 | 30 | 142 | 0 | 101 | 0 | 59 | 13 | 116 | 0 | 2.3 | 48.32 | 12 | 7035.45 | 899 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 72.18 | 1195 | 0 | 0 | 0 | 1439.56 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 49.17 | 95 | 0 | 0 | 51.99 | 143 | 0 | 135 | 0 | 135 | 0 | 414 | 0 | 4.56 | 180 | 35 | 35 | 25 | 32 | 0 | 0 | 0 | 7.2 | 6 | 0.7 | 16 | 203 | 63 | 220 | 0 | 678 | 1060 | 0 | 7267.36 | 14302.81 | 75.67
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 52 | 10 | 0 | 15 | 0 | 0 | 0 | 0 | 296 | 505 | 0 | 0 | 298 | 0 | 0 | 18 | 105 | 17.5 | 0 | 0 | 520 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 0 | 12 | 2.58 | 0 | 16 | 17 | 720 | 0 | 0 | 18 | 0 | 17 | 210 | 0 | 0 | 0 | 1140 | 7 | 25 | 0 | 220 | 290 | 220 | 51 | 0 | 201 | 39 | 0 | 138 | 0 | 0 | 17 | 14 | 170 | 0 | 45 | 0 | 330 | 0 | 164 | 29 | 0 | 143 | 9 | 16 | 0 | 83 | 30 | 135 | 0 | 101 | 0 | 59 | 20 | 116 | 0 | 1.7 | 40.48 | 12 | 7156.26 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 60.77 | 1146 | 0 | 0 | 0 | 1460.33 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 44.13 | 88 | 0 | 0 | 43.89 | 143 | 0 | 136 | 0 | 135 | 0 | 414 | 0 | 4.63 | 180 | 35 | 35 | 28 | 35 | 0 | 0 | 0 | 6.4 | 40 | 0.57 | 14 | 234 | 63 | 220 | 0 | 791 | 1005 | 0 | 7335.72 | 14491.98 | 75.68
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 49 | 30 | 0 | 15 | 0 | 0 | 0 | 0 | 291 | 505 | 0 | 0 | 290 | 0 | 0 | 17 | 105 | 18 | 0 | 0 | 510 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 17 | 0 | 12 | 1.53 | 0 | 16 | 17 | 675 | 0 | 0 | 19 | 0 | 16 | 210 | 0 | 0 | 0 | 1160 | 6 | 25 | 0 | 220 | 290 | 220 | 51 | 0 | 212 | 39 | 0 | 138 | 0 | 0 | 14 | 14 | 170 | 0 | 33 | 0 | 330 | 0 | 218 | 29 | 0 | 143 | 6 | 16 | 0 | 83 | 30 | 135 | 0 | 101 | 0 | 48 | 10 | 87 | 0 | 1.1 | 29.59 | 12 | 7106.22 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 57.11 | 1110 | 0 | 0 | 0 | 1399.75 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 28.19 | 9 | 0 | 0 | 27.47 | 143 | 0 | 136 | 0 | 135 | 0 | 414 | 0 | 2.68 | 180 | 34 | 35 | 11 | 33 | 0 | 0 | 0 | 4.3 | 51 | 0.17 | 0 | 220 | 63 | 220 | 0 | 787 | 1010 | 0 | 7083.67 | 14189.89 | 75.67
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17 | 0 | 34 | 48 | 0 | 15 | 17 | 0 | 0 | 0 | 251 | 490 | 0 | 0 | 270 | 0 | 0 | 9 | 105 | 21 | 21 | 0 | 465 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 17 | 0 | 12 | 0.82 | 0 | 15 | 19 | 675 | 0 | 0 | 19 | 0 | 0 | 211 | 0 | 0 | 0 | 1160 | 4 | 12 | 0 | 220 | 290 | 220 | 51 | 0 | 211 | 39 | 0 | 139 | 0 | 2 | 14 | 0 | 160 | 0 | 17 | 0 | 325 | 0 | 218 | 29 | 0 | 140 | 3 | 16 | 0 | 83 | 30 | 135 | 0 | 101 | 0 | 48 | 6.16 | 86 | 0 | 0.2 | 13.71 | 20 | 6950.89 | 899 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.98 | 1122 | 0 | 0 | 0 | 1335.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.81 | 32 | 0 | 0 | 12.79 | 143 | 0 | 136 | 0 | 135 | 0 | 414 | 0 | 0.64 | 180 | 35 | 0 | 11 | 35 | 0 | 0 | 0 | 3.3 | 62 | 0.1 | 0 | 217 | 63 | 220 | 0 | 721 | 980 | 0 | 6814.28 | 13765.17 | 75.67
18:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 0 | 35 | 48 | 45 | 15 | 30 | 17 | 0 | 0 | 250 | 460 | 0 | 0 | 262 | 0 | 0 | 2 | 131 | 19 | 21 | 0 | 430 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 17 | 0 | 12 | 0.36 | 60 | 15 | 19 | 615 | 0 | 0 | 19 | 0 | 0 | 211 | 0 | 0 | 0 | 1160 | 0 | 12 | 0 | 220 | 290 | 220 | 51 | 0 | 195 | 39 | 0 | 138 | 0 | 9 | 17 | 0 | 152 | 0 | 3 | 0 | 300 | 0 | 218 | 29 | 0 | 128 | 0 | 16 | 0 | 58 | 30 | 135 | 0 | 100 | 0 | 48 | 0.82 | 86 | 0 | 0.1 | 3.33 | 24 | 6845.61 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.86 | 1097 | 0 | 0 | 0 | 1208.96 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 2.47 | 7 | 0 | 0 | 2.31 | 145 | 0 | 137 | 0 | 137 | 0 | 350 | 0 | 0.21 | 180 | 35 | 0 | 3 | 51 | 0 | 0 | 0 | 0.6 | 11 | 0.04 | 0 | 210 | 64 | 180 | 0 | 678 | 955 | 0 | 6400.45 | 13246.06 | 75.66
19:00 | 0 | 19 | 8 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 17 | 9 | 49 | 117 | 45 | 15 | 17 | 72 | 0 | 0 | 297 | 455 | 0 | 17 | 278 | 0 | 0 | 0 | 143 | 19 | 0 | 0 | 505 | 6 | 15 | 28 | 0 | 39 | 50 | 14 | 21 | 12 | 12 | 0 | 60 | 15 | 20 | 675 | 0 | 0 | 20 | 3 | 10 | 212 | 0 | 0 | 0 | 1160 | 0 | 12 | 0 | 220 | 290 | 220 | 51 | 0 | 200 | 39 | 10 | 139 | 9 | 9 | 19 | 15 | 156 | 8 | 0 | 4 | 260 | 0 | 218 | 29 | 0 | 126 | 0 | 16 | 0 | 60 | 30 | 136 | 0 | 100 | 1 | 57 | 0 | 114 | 0 | 0 | 0 | 22 | 7397 | 899 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1012 | 0 | 0 | 0 | 1215.83 | 0 | 0 | 0 | 0 | 0 | 17 | 100 | 18 | 8 | 0 | 0 | 21 | 0 | 0 | 147 | 0 | 141 | 0 | 138 | 0 | 380 | 0 | 0 | 180 | 35 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 239 | 64 | 180 | 0 | 731 | 1010 | 17 | 6749.83 | 14146.83 | 75.65
19:30 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 17 | 28 | 110 | 143 | 50 | 15 | 17 | 72 | 0 | 0 | 303 | 530 | 0 | 17 | 320 | 0 | 0 | 0 | 143 | 22 | 21 | 0 | 520 | 35 | 16 | 55 | 0 | 22 | 50 | 14 | 54.36 | 12 | 12 | 0 | 60 | 20 | 14 | 720 | 0 | 0 | 49 | 9 | 51 | 212 | 0 | 0 | 0 | 1224 | 0 | 62 | 0 | 220 | 290 | 250 | 51 | 10 | 211 | 39 | 52 | 139 | 62 | 9 | 19 | 80 | 156 | 16 | 0 | 8 | 310 | 0 | 221 | 29 | 0 | 140 | 0 | 16 | 0 | 83 | 28 | 141 | 0 | 100 | 17 | 67 | 0 | 152 | 0 | 0 | 0 | 24 | 8378.36 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1115 | 0 | 0 | 0 | 1370.89 | 0 | 0 | 0 | 30 | 10 | 17 | 100 | 20 | 8 | 0 | 0 | 21 | 0 | 0 | 149 | 0 | 141 | 0 | 141 | 0 | 400 | 0 | 0 | 180 | 35 | 94 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 65 | 220 | 0 | 906 | 1110 | 40 | 7534.89 | 15913.25
20:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 17 | 28 | 113 | 110 | 130 | 15 | 17 | 72 | 0 | 0 | 300 | 500 | 0 | 17 | 300 | 0 | 0 | 0 | 143 | 23 | 21 | 0 | 460 | 15 | 16 | 69 | 0 | 41 | 50 | 30 | 54.36 | 12 | 12 | 0 | 60 | 27 | 17 | 720 | 0 | 0 | 35 | 13 | 60 | 212 | 0 | 0 | 0 | 1180 | 0 | 58 | 0 | 220 | 290 | 250 | 51 | 10 | 211 | 37 | 51 | 140 | 17 | 9 | 19 | 30 | 158 | 29 | 0 | 15 | 315 | 0 | 221 | 29 | 0 | 140 | 0 | 16 | 0 | 85 | 28 | 142 | 0 | 100 | 17 | 67 | 0 | 152 | 0 | 0 | 0 | 24 | 8215.36 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1153 | 0 | 0 | 0 | 1480.73 | 0 | 32 | 0 | 35 | 12 | 17 | 101 | 20 | 8 | 0 | 0 | 21 | 0 | 0 | 150 | 0 | 141 | 0 | 142 | 0 | 350 | 0 | 0 | 180 | 36 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 278 | 64 | 180 | 0 | 955 | 1130 | 54 | 7689.73 | 15905.09 | 75.68
21:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 28 | 115 | 110 | 195 | 15 | 17 | 72 | 0 | 0 | 305 | 465 | 0 | 35 | 300 | 0 | 0 | 0 | 143 | 18 | 21 | 0 | 450 | 0 | 0 | 71 | 0 | 60 | 50 | 30 | 54.36 | 12 | 12 | 0 | 60 | 98 | 27 | 680 | 10 | 0 | 20 | 8 | 71 | 212 | 0 | 0 | 0 | 1224 | 0 | 142 | 0 | 220 | 290 | 250 | 51 | 21 | 211 | 40 | 51 | 141 | 17 | 9 | 19 | 16 | 160 | 52.2 | 0 | 15 | 320 | 0 | 224 | 29 | 0 | 131 | 0 | 16 | 0 | 85 | 28 | 141 | 0 | 100 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 24 | 8411.56 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1195 | 0 | 0 | 0 | 1495.89 | 0 | 38 | 0 | 35 | 45 | 17 | 100 | 20 | 0 | 0 | 0 | 21 | 0 | 0 | 150 | 0 | 143 | 0 | 144 | 0 | 414 | 0 | 0 | 180 | 38 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 1050 | 1135 | 17 | 7947.89 | 16359.45 | 75.62
22:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 28 | 85 | 144 | 195 | 15 | 17 | 72 | 0 | 0 | 291 | 455 | 0 | 35 | 285 | 0 | 0 | 0 | 143 | 18 | 21 | 0 | 415 | 0 | 0 | 71 | 0 | 61 | 50 | 30 | 54.36 | 12 | 12 | 0 | 60 | 101 | 34 | 705 | 15 | 0 | 19 | 8 | 17 | 214 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 220 | 290 | 250 | 51 | 10 | 201 | 40 | 52 | 140 | 17 | 9 | 19 | 14 | 162 | 52.2 | 0 | 16 | 315 | 0 | 222 | 29 | 0 | 128 | 0 | 8 | 0 | 85 | 28 | 141 | 0 | 98 | 17 | 68 | 0 | 155 | 0 | 0 | 0 | 24 | 8304.56 | 899 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 1488.74 | 0 | 38 | 0 | 35 | 70 | 0 | 100 | 20 | 25 | 0 | 0 | 21 | 0 | 0 | 151 | 0 | 147 | 0 | 144 | 0 | 414 | 0 | 0 | 180 | 38 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 303 | 64 | 220 | 0 | 1050 | 1160 | 17 | 8003.74 | 16308.3 | 75.6
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 17 | 28 | 34 | 144 | 95 | 15 | 17 | 72 | 0 | 0 | 307 | 495 | 0 | 35 | 307 | 0 | 0 | 0 | 143 | 18 | 21 | 0 | 505 | 0 | 0 | 59 | 0 | 57 | 50 | 30 | 17 | 12 | 12 | 0 | 60 | 105 | 27 | 760 | 16 | 0 | 19 | 8 | 15 | 214 | 0 | 0 | 0 | 1160 | 0 | 50 | 0 | 220 | 290 | 250 | 51 | 10 | 191 | 40 | 51 | 136 | 17 | 9 | 19 | 16 | 152 | 52.2 | 0 | 16 | 315 | 0 | 202 | 29 | 0 | 141 | 0 | 10 | 0 | 85 | 28 | 143 | 0 | 100 | 17 | 68 | 0 | 155 | 0 | 0 | 0 | 24 | 8146.2 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1199 | 0 | 0 | 0 | 1479.28 | 0 | 38 | 0 | 35 | 70 | 0 | 93 | 20 | 52.2 | 0 | 0 | 21 | 0 | 0 | 154 | 0 | 152 | 0 | 144 | 0 | 414 | 0 | 0 | 180 | 38 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 275 | 64 | 220 | 0 | 1050 | 1170 | 17 | 7968.48 | 16114.68 | 75.58
Total KWH | 0 | 728429 | 231360 | 0 | 0 | 0 | 0 | 0 | 8812800 | 0 | 0 | 129600 | 356400 | 1160352 | 1068000 | 1263578 | 623722 | 158541 | 407520 | 0 | 0 | 7052887 | 11797299 | 0 | 137651 | 7162203 | 0 | 0 | 206804 | 2793600 | 412200 | 452160 | 0 | 11640000 | 278509 | 150545 | 547200 | 0 | 878400 | 426359 | 173305 | 497277 | 185280 | 260160 | 26641 | 2287160 | 1349048 | 516480 | 17454545.46 | 36800 | 0 | 584160 | 63997.2 | 856436 | 5060927 | 0 | 0 | 0 | 27665452 | 71820 | 777818 | 0 | 5424000 | 7335000 | 5556000 | 1230128 | 137280 | 5100000 | 950760 | 366720 | 3311349 | 600480 | 55440 | 388890 | 619020 | 3637440 | 346118 | 537573 | 264240 | 7638000 | 0 | 4580000 | 692000 | 0 | 3319527.27 | 65785 | 215808 | 0 | 1957440 | 630240 | 3199100 | 0 | 2403380 | 94320 | 1329600 | 149472 | 2215200 | 0 | 13600 | 330810 | 387840 | 181825985.93 | 21499636 | 0 | 0 | 0 | 0 | 912000 | 0 | 0 | 304018 | 0 | 22464 | 635040 | 25796360 | 0 | 0 | 0 | 32808363 | 0 | 276309 | 0 | 370752 | 845280 | 42668 | 574192 | 149076 | 96053 | 391376 | 725981 | 112730 | 0 | 414000 | 3483455 | 0 | 3478027 | 0 | 3502455 | 0 | 9265236 | 0 | 37680 | 4460000 | 833818 | 1164623 | 204277 | 871555 | 0 | 0 | 0 | 55203.72 | 1093680 | 3945 | 794880 | 6000000 | 1539000 | 5329280 | 0 | 19912727 | 26602181.82 | 232800 | 174841121.54 | 356667107.47