## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-07-2026 | during | 06-07-2026 | during | 06-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 404 | 375 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 289 | 287 | 335 | 335 | 305 | 305 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 45 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 301 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 28 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 46 | 108 | 149.36 | 149.36 | 149.36 | 149.36 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15.5 | 15 | 33 | 33 | 17 | 17 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 64 | 130 | 300 | 300 | 146 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 98 | 149 | 149 | 70 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 51 | 105 | 105 | 17 | 51 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 19 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 28 | 55 | 55 | 17 | 28 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 470 | 584 | 584 | 526 | 526 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 465 | 430 | 583 | 583 | 524.7 | 524.7 | AGC+Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 123 | 143 | 143 | 143 | 143 | 143 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2389.5 | 2733 | 5801.22 | 5775.22 | 2801.06 | 3073.06
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 2 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 70 | 70 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 217 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 24 | 56 | 24 | 56 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 25 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 18 | 30 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0.3 | 0 | 1.43 | 0 | 1.43 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 0 | 54.36 | 54.36 | 0 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 17 | 17 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1160 | 1224 | 1224 | 1194 | 1194 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 52 | 41 | 56 | 56 | 56 | 56 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1080 | 1135 | 1150 | 1150 | 1135 | 1135 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2584.3 | 2745 | 3987.29 | 4082.86 | 3129.43 | 3291
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 197 | 215 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 280 | 280 | 350.01 | 350.01 | 280 | 280 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 240 | 240 | 342.01 | 342.01 | 260 | 260 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 240 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 20 | 41.65 | 41.65 | 10 | 10 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 15 | 31 | 24 | 24 | 24 | 24 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 94 | 93 | 163 | 163 | 95 | 95 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 32 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 144 | 134 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 30 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 47 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 16 | 0 | 55 | 0 | 55 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1309 | 1441 | 2741.44 | 2680.44 | 1634.45 | 1825.45
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-07-2026 | during | 06-07-2026 | during | 06-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 16.58 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.7 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 155 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 57.79 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 18 | 22 | 22 | 12 | 22 | From 00:00-17:00 hrs 12MW&18:00-24:00 hrs 24MW dis
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 251.07 | 276 | 536.6 | 516.5 | 262.1 | 269
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 30 | 29 | 28 | 28 | 29 | 29 | Plant availability less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 30 | 0 | 0 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 138 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 141 | 144 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 23 | 20 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 63 | 64 | 64 | 61 | 61 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 102 | 100 | 100 | 100 | 100 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 16 | 16 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 320 | 320 | Machine Problem
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 244 | 254 | 250 | 250 | 250 | 250 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1024 | 1111 | 1161 | 1161 | 1093 | 1093
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 902 | 902 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 50 | 0 | 100 | 0 | 100 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 900 | 1130 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1890 | 2102 | 3642.2 | 3542.2 | 2723.2 | 2623.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1244 | 955 | 1050 | 1050 | 1050 | 1050 | 1050 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 65 | 65 | 65 | 65 | 65 | 65 | GT-1 & ST under maint
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 800 | 1050 | 1244 | 1244 | 1184 | 1184 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 275 | 307 | 307 | 307 | 307 | 307 | AGC
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.26 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3481.04 | 2315.26 | 2692 | 3147 | 3146 | 2860 | 2859
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 13.24 | 0 | 50 | 0 | 50 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 18 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 144 | 137 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 131 | 220 | 220 | 150 | 150 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 133 | 132 | 220 | 220 | 140 | 140 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 385 | 370 | 413.79 | 413.79 | 380 | 380 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 3.09 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1117.21 | 1489.76 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 42.32 | 0 | 53 | 0 | 53 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 42 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2009.86 | 2312.76 | 3243.72 | 3035.12 | 2611.73 | 2580.13
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 39 | 40 | 40 | 40 | 40 | 40 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 200 | 180 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 94 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.2 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 95 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 18 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 116 | 0 | 131.48 | 0 | 131.48 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 377.2 | 409 | 655.48 | 488 | 522.48 | 390
System Total |  |  |  |  | 28843.2 | 29323.517 | 14150.19 | 15821.76 | 24915.95 | 24427.34 | 17637.45 | 18003.84
Forecast Scenario (06-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 16000 |  | 143.25 |  | 16150
|  |  |  | 1:00 | 15950 |  | 143.25 |  | 16100
|  |  |  | 2:00 | 15570 |  | 66.85 |  | 15640
|  |  |  | 3:00 | 15150 |  | 133.7 |  | 15290
|  |  |  | 4:00 | 14600 |  | 114.6 |  | 14720
|  |  |  | 5:00 | 14410 |  | 124.15 |  | 14540
|  |  |  | 6:00 | 13920 |  | 105.05 |  | 14030
|  |  |  | 7:00 | 14047 |  | 107.915 |  | 14160
|  |  |  | 8:00 | 13960 |  | 238.75 |  | 14210
|  |  |  | 9:00 | 14038 |  | 317.06 |  | 14370
|  |  |  | 10:00 | 14256 |  | 366.72 |  | 14640
|  |  |  | 11:00 | 14675 |  | 491.825 |  | 15190
|  |  |  | 12:00 | 15150 |  | 477.5 |  | 15650
|  |  |  | 13:00 | 15291 |  | 638.895 |  | 15960
|  |  |  | 14:00 | 15300 |  | 573 |  | 15900
|  |  |  | 15:00 | 15500 |  | 563.45 |  | 16090
|  |  |  | 16:00 | 15102 |  | 513.79 |  | 15640
|  |  |  | 17:00 | 14663 |  | 627.435 |  | 15320
|  |  |  | 18:00 | 14408 |  | 479.41 |  | 14910
|  |  |  | 18:30 | 15000 |  | 334.25 |  | 15350
|  |  |  | 19:00 | 15604 |  | 215.83 |  | 15830
|  |  |  | 19:30 | 16118 |  | 727.71 |  | 16880
|  |  |  | 20:00 | 16480 |  | 496.6 |  | 17000
|  |  |  | 21:00 | 16521 |  | 677.095 |  | 17230
|  |  |  | 22:00 | 16553 |  | 340.935 |  | 16910
|  |  |  | 23:00 | 16500 |  | 515.7 |  | 17040
Probable Maximum Temperature: |  |  | 31.8 °C
Probable Maximum Demand at Day Peak: |  |  | 15650.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 667
Probable Maximum Demand at Evening Peak: |  |  | 17230.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16521.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 363.648 MKWHr. |  | 140 | 80 | 110 | 180 | 50 | 50 | 0 | 40 | 27 | 677
*** This report is generated digitally from Operation Information System (OIS) at 11:10 hrs on 06-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14150.19 | MW | 12:00 Hr. | Energy Generated |  |  | 354.6524 |  | MKWHr.
| Day Peak Demand |  |  | 14228.19 | MW | 12:00 Hr. | Energy Unserverd |  |  | 4.677 |  | MKWHr.
| Evening Peak Generation |  |  | 15821.76 | MW | 21:00 Hr. | Energy Demand |  |  | 359.3294 |  | MKWHr.
| Evening Peak Demand |  |  | 16130.76 | MW | 21:00 Hr. | Maximum Temperature |  |  | 31.8 |  | °C
| Minimum Generation of the Day |  |  | 13556.81 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 930.91 |  | MMCFD
| Maximum Generation of the Day |  |  | 16057.69 | MW | 01:00 Hr. | Production Cost per KWHr |  |  | 6.165 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 45.7203 | 0 | 12.143 | 0 | 0 | 0.13387 | 0 | 0 | 57.9971 | Gas | 132.339 | Gas | 443389442.6218
| Chattogram Zone |  |  | 5.6216 | 49.3727 | 2.5713 | 0 | 1.7421 | 0.021094 | 0 | 1.1059 | 60.4348 | Coal | 132.9959 | Coal | 887400423.0635
| Cumilla Zone |  |  | 29.0844 | 0 | 2.4179 | 0 | 0 | 0.12274 | 3.5261 | 0 | 35.1511 | HFO | 24.6849 | HFO | 423942401.056
| Mymensingh Zone |  |  | 0 | 0 | 3.9383 | 0 | 0 | 0.43284 | 0 | 0 | 4.3711 | HSD | 0.23326 | HSD | 4711888.764
| Sylhet Zone |  |  | 25.3419 | 0 | 0 | 0 | 0 | 0.056836 | 0 | 0 | 25.3988 | Hydro | 1.7421 | Hydro | 6637401
| Khulna Zone |  |  | 0 | 26.0145 | 0.33941 | 0.23326 | 0 | 0.27864 | 22.7258 | 0 | 49.5917 | Solar | 3.4449 | Solar | 57438749.2372
| Barishal Zone |  |  | 6.9198 | 52.0874 | 0.30125 | 0 | 0 | 0.001402 | 0 | 0 | 59.3098 | Import | 58.1064 | Import | 346660433.03
| Rajshahi Zone |  |  | 19.651 | 0 | 1.0601 | 0 | 0 | 0.94079 | 31.8545 | 0 | 53.5064 | Wind | 1.1059 | Wind | 16268083.2
| Rangpur Zone |  |  | 0 | 5.5213 | 1.9136 | 0 | 0 | 1.4567 | 0 | 0 | 8.8916
| Total |  |  | 132.339 | 132.9959 | 24.6849 | 0.23326 | 1.7421 | 3.4449 | 58.1064 | 1.1059 | 354.6524
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 443389442.6218 |  | Hydro | 6637401
|  |  |  | Coal | 887400423.0635 |  | Solar | 57438749.2372
|  |  |  | HFO | 423942401.056 |  | Import | 346660433.03
|  |  |  | HSD | 4711888.764 |  | Wind | 16268083.2
[5 empty] | Total: | 218,64,48,821 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8138 | Peak Hr Flow | 902.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 54212345.45 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.8545 | Peak Hr Flow | 1489.76 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2310 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.5261 | Peak Hr Flow | 134.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2634 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 57.1944 | Peak Hr Flow | 2525.76 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 65 |  | 5660
|  |  |  | Chattogram |  | 0 |  | 1385
|  |  |  | Cumilla |  | 0 |  | 1462
|  |  |  | Mymensingh |  | 206 |  | 1396
|  |  |  | Sylhet |  | 0 |  | 679
|  |  |  | Khulna |  | 25 |  | 1833
|  |  |  | Barishal |  | 0 |  | 447
|  |  |  | Rajshahi |  | 0 |  | 1598
|  |  |  | Rangpur |  | 0 |  | 1109
|  |  |  | Total |  | 296 |  | 15569
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Karnaphuli Hydro PP Unit-5 |  |  | 50
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 350 |  |  |  | Total | 50
|  |  |  | Total Unavailable Capacity |  |  |  | 400
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:22 | 08:53 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing zone2,ph-B relays.
| 09:09 | 12:33 | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Feni 230/132kV end Due to Installation
OPGW TT to gantry and from Feni 132/33kV end Due to 230 KV grid side project Work
| 09:21 | 12:17 | Chowmuhani-Feni 132 kV Ckt-2 Project Work S/D from Daganbhuiyan 132/33kV end Due to Feni
230 KV S/S project work. and from Feni 230/132kV end Due to Installation OPGW TT to
gantry
| 09:25 | 10:07 | Kushtia 132/33kV S/S T-1 LT Forced S/D Due to Old power cable remove from auxiliary
transformer
| 09:25 | 10:06 | Kushtia 132/33kV S/S T-1 HT Forced S/D Due to Old power cable remove from auxiliary
transformer
| 09:25 | 15:28 | Shahjibazar 132/33kV S/S SPCL 86 MW Scheduled S/D Due to 86MW plant maitenance work.
|  | 09:28 | Madaripur 132/33kV S/S T1-405T LT is restored.
|  | 09:28 | Madaripur 132/33kV S/S T1-405T HT is restored.
| 09:58 | 12:31 | Cumilla(S) 132/33kV S/S Cumilla North-2 Tripped showing REL 670 & REC 650 relays.
| 10:44 |  | At benapole SS,132 kv Bus coupler CB is open.
| 10:53 |  | At Jashore SS,132 kv Bus coupler CB is open.
| 12:00 |  | Day Peak Generation: 14150 MW.
| 12:37 | 15:22 | Chowmuhani-Feni 132 kV Ckt-2 Project Work S/D from Feni 230/132kV end Due to OPGW
Earthing installation. and from Feni 132/33kV end Due to 230kv grid end project work
| 12:46 | 15:07 | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Feni 230/132kV end Due to OPGW
Earthing installation. and from Daganbhuiyan 132/33kV end Due to project work at feni
230kv s/s.
| 14:42 | 16:41 | Khulna(C )-Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end Due to ALDC | [7 empty] | and 27.0MW load
|  |  | Instruction and from Khulna (C) end Due to Hot spot maint. Work. | [7 empty] | interrup. Khulna
(C) end
| 15:52 | 17:35 | Shahjadpur 132/33kV S/S T-3(425T) LT Forced S/D Due to Maintenance work for nesco | [7 empty] | 35.0MW load
interrup.
| 15:52 | 17:34 | Shahjadpur 132/33kV S/S T-3(425T) HT Forced S/D Due to Maintenance work for nesco | [7 empty] | 35.0MW load
interrup.
| 19:04 | 20:09 | Sitakunda 132/33kV S/S TRAFO-2 HT Tripped showing Trafo differential Prot. Relay F87T2 | [7 empty] | 26.0MW load
|  |  | relays Due to Over Current , EARTH Fault | [7 empty] | interrup.
| 20:00 | 20:00 | Shahjadpur 132/33kV S/S T-3(425T) HT Forced S/D Due to Red hot maintenance work. | [7 empty] | 20.0MW load
interrup.
| 20:00 | 20:30 | Shahjadpur 132/33kV S/S T-3(425T) LT Forced S/D Due to Red hot maintenance work. | [7 empty] | 20.0MW load
interrup.
| 21:06 | 21:43 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to Red hot
| 21:07 | 21:43 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to Red hot 33 kv breaker y phase
| 22:22 | 04:09 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Forced S/D from Brahmanbaria 132/33kV end Due to
None
| 22:25 | 04:09 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end.
| 05:48 |  | Rangpur 132/33kV S/S T-2 (404T) LT Scheduled S/D | [7 empty] | 25.0MW load
interrup.
| 05:48 |  | Rangpur 132/33kV S/S T-2 (404T) HT Scheduled S/D | [7 empty] | 25.0MW load
interrup.
| 06:00 |  | Minimum Generation: 13528 MW.
| 07:39 |  | Palashbari 132/33kV S/S TR2-404T LT Forced S/D Due to Red hot Maintenance
| 07:40 |  | Palashbari 132/33kV S/S TR2-404T HT Forced S/D Due to Red hot Maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 375 | 9136800 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 287 | 7178676 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 45 | 571030 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 301 | 7399312 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 28 | 188280 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 108 | 1496640 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 539136 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270456 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 274200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 474480 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 236640 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 130 | 2078782 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 98 | 1464624 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 51 | 816000 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 792000 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 133869 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 28 | 552600 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 470 | 10731818.18 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 430 | 10525000 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143 | 3136800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2733 | 57997143.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 75954.6 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 12285 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 374400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1742100 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5248657 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 549490 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 38784 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 308419 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 113280 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 372960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 77760 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 8809 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 82800 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 0 | 41045 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 635633 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 203520 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 70255 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 26623634 | Coal Shortage Due to BPDB Payment Default
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 41 | 1105920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1135 | 22749090.91 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 2745 | 60434796.51
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 215 | 5051000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 280 | 7081600 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 240 | 5746000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 240 | 6166000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 724392 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 88297 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 16727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1219088 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 341236 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 524208 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 93 | 2559166 | Low gas pressure
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 32 | 582720 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 134 | 3526080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 30346 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 432100 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 30 | 534660 | Liquid fuel shortage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 63000 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 47 | 341760 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 122736 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1441 | 35151116
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 123566 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 155 | 2244000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1347600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 296970 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 151200 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 195480 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 276 | 4371116
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 56836 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 29 | 694000 | Plant availability less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 290520 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 138 | 3328936.36 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 144 | 3245800 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 578688 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 63 | 1049280 | Gas Restrction
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 2411500 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 248208 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7520000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 254 | 5975000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1111 | 25398768.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 902 | 21813818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 339408 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 278640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 233261.82 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1130 | 26014550 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2102 | 49591677.82
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1244 | 1050 | 22160000 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 135648 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 65 | 1554000 | GT-1 Normal Shutdown Due to Major inspection(MI)
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1050 | 23316363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5365830 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 165600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6611000 | AGC
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1402 | -
Barishal Area Total |  |  |  |  | 3481.04 | 2692 | 59309843.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 232368 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 81285 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 18 | 76857 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 137 | 3535727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 131 | 3423927 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 132 | 3481264 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 370 | 9210036 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 23978 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 89323 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 556704 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 231936 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 28740 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1489.76 | 31854545 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 296368 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 383310 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2312.76 | 53506368
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 40 | 903272 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4618000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 94 | 792614 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 37071.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1121015 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 172562 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1247040 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 409 | 8891574.36
Eastern Grid Total |  |  |  |  | 17438.042 | 8306 | 183352940.05
Western Grid Total |  |  |  |  | 11885.475 | 7515.76 | 171299463.82
National Grid Total |  |  |  |  | 29323.517 | 15821.76 | 354652403.87
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10345.82 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4961.7 | MW
i) Dhaka area |  |  | 5595.12 |  | MW | i) Khulna area |  |  |  | 1808 | MW
ii) Chattogram area |  |  | 1419.7 |  | MW | ii) Barishal area |  |  |  | 447.1 | MW
iii) Cumilla area |  |  | 1462 |  | MW | iii) Rajshahi area |  |  |  | 1597.6 | MW
iv) Mymensingh area |  |  | 1190 |  | MW | iv) Rangpur area |  |  |  | 1109 | MW
v) Sylhet area |  |  | 679 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15307.52 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 144 | 17:00 | 133 | Narshingdi | 181 | 22:00 | 199 | Uttara | 100 | 13:00
2 | AKSML | 152.1 | 11:00 | 68 | Hasnabad | 101 | 00:00 | 134 | Natore | 148 | 21:00 | 200 | UttaraNew | 55 | 00:00
3 | Aftabnagar | 44 | 00:00 | 69 | Hathazari | 94 | 01:00 | 135 | Nawabganj | 66.4 | 00:00 | 201 | Zigatola | 94 | 00:00
4 | Agargaon | 125 | 13:00 | 70 | Hatirjheel | 48 | 12:00 | 136 | Netrakona | 138 | 07:00
5 | Agrabad | 64 | 14:00 | 71 | Ishurdi | 82 | 20:00 | 137 | New | 84.9 | 12:00
6 | Amnura | 31 | 23:00 | 72 | Jaldhaka | 101 | 00:00 | 138 | Niamatpur | 86 | 00:00
7 | Ashuganj | 86 | 00:00 | 73 | Jamalpur | 120 | 19:30 | 139 | Noapara | 40 | 21:00
8 | BSRM | 200 | 23:00 | 74 | Jashore | 163 | 00:00 | 140 | PHP | 13 | 17:00
9 | Bagerhat | 87.5 | 19:30 | 75 | Jhenaidah | 97 | 00:00 | 141 | Pabna | 98 | 19:30
10 | Bajitpur | 95 | 19:30 | 76 | Joydebpur | 150 | 20:00 | 142 | Palashbari | 142 | 00:00
11 | Bakerganj | 14.6 | 21:00 | 77 | Joypurhat | 76 | 00:00 | 143 | Panchagarh | 73 | 20:00
12 | Bakulia | 93 | 01:00 | 78 | Juldah | 16 | 00:00 | 144 | Patiya | 11.8 | 00:00
13 | Banani | 70 | 13:00 | 79 | KSRM | 26 | 06:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 20 | 10:00 | 80 | Kabirpur | 273 | 19:00 | 146 | Patuakhali | 63 | 01:00
15 | Barapukuria | 75 | 00:00 | 81 | Kachua | 102 | 00:00 | 147 | Payra | 36 | 00:00
16 | Barguna | 22 | 00:00 | 82 | Kaliganj | 38 | 02:00 | 148 | Postogola | 67 | 00:00
17 | Barishal | 101 | 13:00 | 83 | Kallyanpur | 132 | 00:00 | 149 | Pubail | 38 | 05:00
18 | Barishal-230 | 104 | 01:00 | 84 | Kalurghat | 41 | 11:00 | 150 | Purbachal | 29 | 18:30
19 | Baroaulia | 65 | 21:00 | 85 | Kamrangirchar | 82 | 13:00 | 151 | Purbasadipur | 159 | 00:00
20 | Baroirhat | 64 | 00:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 45 | 00:00
21 | Bashundhara | 209 | 13:00 | 87 | Kasba | 40 | 00:00 | 153 | Rahim | 31 | 11:00
22 | BashundharaCement | 1 | 10:00 | 88 | Kazla | 105 | 00:00 | 154 | Rajbari | 89 | 00:00
23 | Beanibazar | 88 | 00:00 | 89 | Keranigonj | 87 | 19:30 | 155 | Rajendrapur | 116 | 19:00
24 | Benapole | 70 | 03:00 | 90 | Khagrachori | 34 | 19:30 | 156 | Rajshahi | 136 | 23:00
25 | Bhaluka | 149 | 20:00 | 91 | Khulna | 64 | 13:00 | 157 | Rajshahi-230 | 91 | 13:00
26 | Bhandaria | 60 | 00:00 | 92 | Khulshi | 189 | 16:00 | 158 | Ramganj | 118 | 00:00
27 | Bhangura | 40 | 22:00 | 93 | Kishoreganj | 122 | 19:00 | 159 | Rampur | 48 | 00:00
28 | Bheramara(GK) | 69 | 00:00 | 94 | Kodda | 305 | 19:30 | 160 | Rangamati | 16 | 12:00
29 | Bhulta | 221 | 16:00 | 95 | Kulaura | 54 | 00:00 | 161 | Rangpur | 152 | 20:00
30 | Bog-Sherpur | 82 | 22:00 | 96 | Kurigram | 80 | 19:30 | 162 | Ruppur | 4.8 | 09:00
31 | Bogura | 195 | 00:00 | 97 | Kushtia | 168 | 03:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 81 | 00:00 | 98 | Laksam | 38 | 00:00 | 164 | Saidpur | 115 | 00:00
33 | Brahmanbaria | 140 | 21:00 | 99 | Lakshmipur | 48 | 02:00 | 165 | Santhia | 38 | 19:30
34 | Cantonment | 132 | 13:00 | 100 | Lalbag | 81 | 14:00 | 166 | Satkhira | 140 | 00:00
35 | Chandina | 35 | 15:00 | 101 | Lalmonirhat | 76 | 19:30 | 167 | Satmasjid | 106 | 13:00
36 | Chandpur | 94 | 00:00 | 102 | MI_Cement | 16.3 | 00:00 | 168 | Savar | 220 | 15:00
37 | Chandraghona | 35 | 00:00 | 103 | Madanganj | 35 | 01:00 | 169 | SevenRings | 17.65 | 11:00
38 | Chapai | 78 | 05:00 | 104 | Madaripur | 129 | 00:00 | 170 | ShahCement | 34 | 00:00
39 | Charfasson | 33 | 23:00 | 105 | Madartek | 94 | 00:00 | 171 | Shahjadpur | 79 | 22:00
40 | Charsaidpur | 39 | 17:00 | 106 | Madunaghat | 57 | 00:00 | 172 | Shahjibazar | 145 | 23:00
41 | Chauddagram | 83 | 00:00 | 107 | Magura | 66 | 01:00 | 173 | Shahmirpur | 55 | 00:00
42 | Chhatak | 46 | 00:00 | 108 | Mahasthangarh | 91 | 00:00 | 174 | Shariatpur | 96 | 00:00
43 | Chowmuhani | 153 | 22:00 | 109 | Maijdee | 39 | 22:00 | 175 | Sherpur | 158 | 21:00
44 | Chuadanga | 121 | 00:00 | 110 | Manikganj | 144 | 22:00 | 176 | Shikalbaha | 30 | 00:00
45 | Coxsbazar | 141 | 00:00 | 111 | Maniknagar | 80 | 13:00 | 177 | Shitalakhya | 79.7 | 13:00
46 | Cumilla(N) | 151 | 22:00 | 112 | Matarbari | 56 | 00:00 | 178 | Sholosohor | 45 | 00:00
47 | Cumilla(S) | 179 | 01:00 | 113 | Matuail | 80 | 00:00 | 179 | Shomvuganj | 40 | 10:00
48 | Daganbhuiyan | 44 | 00:00 | 114 | Metrorail_Motijheel | 43 | 10:00 | 180 | Shyampur | 174 | 11:00
49 | Daudkandi | 145 | 00:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 130 | 11:00
50 | DhakaUniversity | 100 | 13:00 | 116 | Millgate | 116 | 12:00 | 182 | Sirajganj | 120 | 21:00
51 | Dhamrai | 100 | 00:00 | 117 | Mirpur | 153 | 12:00 | 183 | Sitakunda | 32 | 22:00
52 | Dhanmondi | 126.3 | 13:00 | 118 | Mirsorai | 43 | 03:00 | 184 | Sonargaon | 159 | 12:00
53 | Dohazari | 112 | 00:00 | 119 | Mirzapur | 42 | 19:00 | 185 | Sreemongol | 101 | 00:00
54 | Faridpur | 190 | 00:00 | 120 | Mithapukur | 82 | 02:00 | 186 | Sreepur | 130 | 22:00
55 | Fatullah | 108 | 12:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 53.4 | 00:00
56 | Fenchuganj | 47 | 23:00 | 122 | Mogbazar | 97.8 | 13:00 | 188 | Sunamganj | 64 | 21:00
57 | Feni | 117 | 00:00 | 123 | Mongla | 47 | 09:00 | 189 | Sylhet | 126 | 17:00
58 | GPH | 18 | 00:00 | 124 | Motijheel | 53 | 13:00 | 190 | Sylhet_(South) | 81 | 19:30
59 | Ghatail | 101 | 19:30 | 125 | Muktagacha | 42 | 21:00 | 191 | TK | 23.5 | 00:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 127 | 00:00 | 192 | Tangail | 169 | 19:00
61 | Ghorashal-230 | 96 | 23:00 | 127 | Muradnagar | 50 | 22:00 | 193 | Taraganj | 30 | 19:30
62 | Goalpara | 39 | 01:00 | 128 | Mymensingh | 174 | 19:00 | 194 | Tasnim | 44 | 18:30
63 | Gollamari | 120 | 00:00 | 129 | Nabinagar | 108 | 12:00 | 195 | Thakurgaon | 126 | 00:00
64 | Gopalganj | 121 | 00:00 | 130 | Naogaon | 147 | 01:00 | 196 | Tongi | 159 | 11:00
65 | Gulshan | 122 | 11:00 | 131 | Narail | 57 | 01:00 | 197 | Ullahpara | 41 | 19:30
66 | Halishahar | 100 | 11:00 | 132 | Narinda | 77 | 13:00 | 198 | Ullon | 61 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15985.78 | 539 |  | 16549.04
1:00 | 16057.69 | 320 |  | 16391.69
2:00 | 15667.84 | 238 |  | 15916.84
3:00 | 15353.06 | 228 |  | 15591.06
4:00 | 15019.35 | 213 |  | 15242.35
5:00 | 14674.58 | 193 |  | 14876.58
6:00 | 14242.19 | 214 |  | 14465.82
7:00 | 14047.69 | 224 |  | 14281.69
8:00 | 13861.5 | 211 |  | 14081.5
9:00 | 13638.73 | 256 |  | 13906.73
10:00 | 13556.81 | 123 |  | 13685.81
11:00 | 13875.5 | 35 |  | 13912.5
12:00 | 14150.19 | 75 |  | 14228.19
13:00 | 14191.73 | 139 |  | 14336.73
14:00 | 14205.69 | 113 |  | 14323.69
15:00 | 14299.97 | 187 |  | 14494.97
16:00 | 14102.24 | 162 |  | 14271.24
17:00 | 13663 | 102 |  | 13770
18:00 | 13408.91 | 94 |  | 13507.14
19:00 | 14804.23 | 105 |  | 14914.23
19:30 | 15718.76 | 203 |  | 15930.76
20:00 | 15779.02 | 207 |  | 15995.02
21:00 | 15821.76 | 296 |  | 16130.76
22:00 | 15753.18 | 208 |  | 15970.18
23:00 | 15698.83 | 195 |  | 15902.83
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 05-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 128 | 10 | 428 | 144 | 2078 | 460 | Ishurdi-Ghorashal Ckt-1 | Export | 3499345.45
1:00 | 112 | 5 | 412 | 142 | 2078 | 470
2:00 | 118 | 12 | 400 | 156 | 2110 | 490 |  | Import | 0
3:00 | 111 | 6 | 408 | 150 | 2048 | 462
4:00 | 112 | 4 | 404 | 136 | 1938 | 464 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 122 | 15 | 422 | 144 | 1950 | 472
6:00 | 139 | 28 | 450 | 146 | 1954 | 520 |  | Import | 0
7:00 | 121 | 27 | 362 | 152 | 1902 | 560
8:00 | 142 | 44 | 406 | 168 | 1990 | 610 | Sirajganj-Sreepur Ckt-1 | Export | 2763000
9:00 | 173 | 67 | 466 | 196 | 1966 | 704
10:00 | 176 | 73 | 496 | 216 | 1862 | 730 |  | Import | 0
11:00 | 174 | 67 | 500 | 220 | 1732 | 700
12:00 | 167 | 67 | 460 | 216 | 1882 | 740 | Sirajganj-Sreepur Ckt-2 | Export | 2770000
13:00 | 160 | 43 | 466 | 160 | 1710 | 710
14:00 | 152 | 50 | 452 | 172 | 1818 | 750 |  | Import | 0
15:00 | 185 | 60 | 544 | 210 | 1810 | 810
16:00 | 193 | 69 | 550 | 196 | 1810 | 806 | Gopalganj-Aminbazar Ckt-1 | Export | 22560000
17:00 | 201 | 69 | 540 | 182 | 1742 | 788
18:00 | 158 | 47 | 480 | 180 | 1526 | 672 |  | Import | 0
18:30 | 163 | 48 | 486 | 170 | 1668 | 654
19:00 | 168 | 50 | 508 | 210 | 1780 | 1048 | Gopalganj-Aminbazar Ckt-2 | Export | 22620000
19:30 | 123 | 15 | 430 | 170 | 1778 | 576
20:00 | 121 | 14 | 440 | 162 | 1744 | 514 |  | Import | 0
21:00 | 122 | 12 | 442 | 168 | 1746 | 500
22:00 | 109 | 2 | 412 | 142 | 1640 | 460 |  | Total Export | 54212345.45
23:00 | 117 | 2 | 444 | 156 | 1810 | 446 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8061 | 7924.78 | 15985.78 | DAILY GENERATION CURVE
00:30 | 8046 | 7975.735 | 16021.735
01:00 | 8031 | 8026.69 | 16057.69 | 05-07-2026
01:30 | 7893 | 7969.765 | 15862.765
02:00 | 7755 | 7912.84 | 15667.84
02:30 | 7682.5 | 7827.95 | 15510.45
03:00 | 7610 | 7743.06 | 15353.06
03:30 | 7565.5 | 7620.705 | 15186.205
04:00 | 7521 | 7498.35 | 15019.35
04:30 | 7410 | 7436.965 | 14846.965
05:00 | 7299 | 7375.58 | 14674.58
05:30 | 7154.615 | 7303.77 | 14458.385
06:00 | 7010.23 | 7231.96 | 14242.19
06:30 | 7004.11 | 7140.83 | 14144.94
07:00 | 6997.99 | 7049.7 | 14047.69
07:30 | 6936.295 | 7018.3 | 13954.595
08:00 | 6874.6 | 6986.9 | 13861.5
08:30 | 6896.195 | 6853.92 | 13750.115
09:00 | 6917.79 | 6720.94 | 13638.73
09:30 | 6978.575 | 6619.195 | 13597.77
10:00 | 7039.36 | 6517.45 | 13556.81
10:30 | 7229.61 | 6486.545 | 13716.155
11:00 | 7419.86 | 6455.64 | 13875.5
11:30 | 7488.865 | 6523.98 | 14012.845
12:00 | 7557.87 | 6592.32 | 14150.19
12:30 | 7510.785 | 6660.175 | 14170.96
13:00 | 7463.7 | 6728.03 | 14191.73
13:30 | 7496.29 | 6702.42 | 14198.71
14:00 | 7528.88 | 6676.81 | 14205.69
14:30 | 7547.38 | 6705.45 | 14252.83
15:00 | 7565.88 | 6734.09 | 14299.97
15:30 | 7583.395 | 6617.71 | 14201.105
16:00 | 7600.91 | 6501.33 | 14102.24
16:30 | 7517.11 | 6365.51 | 13882.62
17:00 | 7433.31 | 6229.69 | 13663
17:30 | 7443.16 | 6092.795 | 13535.955
18:00 | 7453.01 | 5955.9 | 13408.91
18:30 | 7731.505 | 6375.065 | 14106.57
19:00 | 8010 | 6794.23 | 14804.23
19:30 | 8345 | 7373.76 | 15718.76
20:00 | 8331 | 7448.02 | 15779.02
20:30 | 8318.5 | 7481.89 | 15800.39 |  | Executive Engineer
21:00 | 8306 | 7515.76 | 15821.76 |  | Network Operation Division
21:30 | 8278.2 | 7509.27 | 15787.47
22:00 | 8250.4 | 7502.78 | 15753.18
22:30 | 8177.95 | 7548.055 | 15726.005
23:00 | 8105.5 | 7593.33 | 15698.83

## En-Curve
QF-LDC-12
Date | 05-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3441 | 2168 | 900 | 38 | 176 | 1495.78 | 65 | 5757 | 0 | 467 | 1277 | 150 | 0 | 51 | 539 | DAILY ENERGY CURVE
00:30 | 3421.5 | 2169 | 900 | 38 | 179 | 1495.735 | 65 | 5757 | 0 | 467 | 1333.5 | 150.5 | 0 | 45.5 | 429.5 | 05-07-2026
01:00 | 3402 | 2170 | 900 | 38 | 182 | 1495.69 | 65 | 5757 | 0 | 467 | 1390 | 151 | 0 | 40 | 320
01:30 | 3401.5 | 2107 | 900.5 | 38 | 179 | 1487.265 | 65 | 5758 | 0 | 423 | 1356.5 | 100.5 | 0 | 46.5 | 279 | Energy Generated | 354.6524 |  | MKWHr
02:00 | 3401 | 2044 | 901 | 38 | 176 | 1478.84 | 65 | 5759 | 0 | 379 | 1323 | 50 | 0 | 53 | 238 | Energy not Served | 4.677 |  | MKWHr
02:30 | 3411 | 2016 | 901.5 | 38 | 163 | 1481.85 | 65 | 5740 | 0 | 354 | 1264.1 | 25 | 0 | 51 | 233 | Total Energy Requirement | 359.3294 |  | MKWHr
03:00 | 3421 | 1988 | 902 | 38 | 150 | 1484.86 | 65 | 5721 | 0 | 329 | 1205.2 | 0 | 0 | 49 | 228
03:30 | 3440 | 1977.5 | 902 | 38 | 159 | 1482.105 | 65 | 5631 | 0 | 329 | 1110.6 | 0 | 0 | 52 | 220.5
04:00 | 3459 | 1967 | 902 | 38 | 168 | 1479.35 | 65 | 5541 | 0 | 329 | 1016 | 0 | 0 | 55 | 213
04:30 | 3467 | 2049 | 902 | 38 | 162 | 1461.965 | 65 | 5542.5 | 0 | 313 | 791 | 0 | 0 | 55.5 | 203
05:00 | 3475 | 2131 | 902 | 38 | 156 | 1444.58 | 65 | 5544 | 0 | 297 | 566 | 0 | 0 | 56 | 193
05:30 | 3473.5 | 2048 | 902 | 38 | 154 | 1394.475 | 65 | 5529.5 | 10.91 | 260 | 523.5 | 0 | 0 | 59.5 | 203.5
06:00 | 3472 | 1965 | 902 | 38 | 152 | 1344.37 | 65 | 5515 | 21.82 | 223 | 481 | 0 | 0 | 63 | 214
06:30 | 3474 | 1996.5 | 902 | 38 | 152 | 1321.22 | 65 | 5467.5 | 61.22 | 223 | 381 | 0 | 0 | 63.5 | 219
07:00 | 3476 | 2028 | 902 | 38 | 152 | 1298.07 | 65 | 5420 | 100.62 | 223 | 281 | 0 | 0 | 64 | 224
07:30 | 3443 | 1985.75 | 902 | 38 | 146 | 1243.685 | 64.5 | 5415.5 | 178.16 | 223 | 264 | 0 | 0 | 51 | 217.5
08:00 | 3410 | 1943.5 | 902 | 38 | 140 | 1189.3 | 64 | 5411 | 255.7 | 223 | 247 | 0 | 0 | 38 | 211
08:30 | 3369 | 1962 | 902 | 38 | 141 | 1151.645 | 64.5 | 5387 | 270.97 | 213 | 220 | 0 | 0 | 31 | 233.5
09:00 | 3328 | 1980.5 | 902 | 38 | 142 | 1113.99 | 65 | 5363 | 286.24 | 203 | 193 | 0 | 0 | 24 | 256
09:30 | 3323.5 | 1943.5 | 902 | 38 | 128 | 1084.085 | 67.5 | 5317 | 305.185 | 203 | 246.5 | 0 | 0 | 39.5 | 189.5
10:00 | 3319 | 1906.5 | 902 | 38 | 114 | 1054.18 | 70 | 5271 | 324.13 | 203 | 300 | 0 | 0 | 55 | 123
10:30 | 3340.5 | 1989.5 | 901.5 | 38 | 128 | 1055.855 | 70 | 5268.5 | 375.3 | 199 | 310 | 0 | 0 | 40 | 79
11:00 | 3362 | 2072.5 | 901 | 38 | 142 | 1057.53 | 70 | 5266 | 426.47 | 195 | 320 | 0 | 0 | 25 | 35
11:30 | 3392.5 | 2058.5 | 901.5 | 38 | 143 | 1087.37 | 70 | 5337.5 | 418.475 | 198 | 329.5 | 0 | 0 | 38.5 | 55
12:00 | 3423 | 2044.5 | 902 | 38 | 144 | 1117.21 | 70 | 5409 | 410.48 | 201 | 339 | 0 | 0 | 52 | 75
12:30 | 3404 | 2004.75 | 902 | 38 | 145 | 1219.245 | 70 | 5395 | 409.465 | 187 | 339 | 0 | 0 | 57.5 | 107
13:00 | 3385 | 1965 | 902 | 38 | 146 | 1321.28 | 70 | 5381 | 408.45 | 173 | 339 | 0 | 0 | 63 | 139
13:30 | 3407.5 | 2007 | 902 | 38 | 144 | 1297.415 | 70 | 5391.5 | 358.795 | 175 | 343.5 | 0 | 0 | 64 | 126
14:00 | 3430 | 2049 | 902 | 38 | 142 | 1273.55 | 70 | 5402 | 309.14 | 177 | 348 | 0 | 0 | 65 | 113
14:30 | 3427 | 2061 | 901.5 | 38 | 142 | 1282.015 | 70 | 5419 | 323.315 | 177.5 | 357 | 0 | 0 | 54.5 | 150
15:00 | 3424 | 2073 | 901 | 38 | 142 | 1290.48 | 70 | 5436 | 337.49 | 178 | 366 | 0 | 0 | 44 | 187
15:30 | 3451.5 | 2046 | 901.5 | 38 | 151 | 1281.25 | 70 | 5393 | 257.355 | 178.5 | 397.5 | 0 | 0 | 35.5 | 174.5
16:00 | 3479 | 2019 | 902 | 38 | 160 | 1272.02 | 70 | 5350 | 177.22 | 179 | 429 | 0 | 0 | 27 | 162
16:30 | 3484 | 1991.5 | 902 | 38 | 156 | 1223.73 | 70 | 5178 | 166.89 | 179 | 457.5 | 0 | 0 | 36 | 132
17:00 | 3489 | 1964 | 902 | 38 | 152 | 1175.44 | 70 | 5006 | 156.56 | 179 | 486 | 0 | 0 | 45 | 102
17:30 | 3453.5 | 1951.25 | 902 | 38 | 152 | 1128.705 | 69 | 4972.5 | 102.5 | 181.5 | 538.5 | 0 | 0 | 46.5 | 98
18:00 | 3418 | 1938.5 | 902 | 38 | 152 | 1081.97 | 68 | 4939 | 48.44 | 184 | 591 | 0 | 0 | 48 | 94
18:30 | 3409.5 | 1983.25 | 902 | 38 | 149 | 1230.6 | 68 | 5275.5 | 24.22 | 267 | 717 | 0 | 0 | 42.5 | 99.5
19:00 | 3401 | 2028 | 902 | 38 | 146 | 1379.23 | 68 | 5612 | 0 | 350 | 843 | 0 | 0 | 37 | 105
19:30 | 3417 | 2075 | 902 | 38 | 142 | 1489.76 | 70 | 5933 | 0 | 425 | 1162 | 0 | 0 | 65 | 203
20:00 | 3424 | 2057 | 902 | 38 | 148 | 1486.02 | 70 | 5995 | 0 | 451 | 1162 | 0 | 0 | 46 | 207
20:30 | 3409.5 | 2063.5 | 902 | 38 | 141 | 1487.89 | 70 | 6023.5 | 0 | 446.5 | 1175 | 0 | 0 | 43.5 | 251.5
21:00 | 3395 | 2070 | 902 | 38 | 134 | 1489.76 | 70 | 6052 | 0 | 442 | 1188 | 0 | 0 | 41 | 296
21:30 | 3381.5 | 2060 | 902 | 38 | 133 | 1489.27 | 88 | 6041 | 0 | 443 | 1177.7 | 0 | 0 | 34 | 252
22:00 | 3368 | 2050 | 902 | 38 | 132 | 1488.78 | 106 | 6030 | 0 | 444 | 1167.4 | 0 | 0 | 27 | 208
22:30 | 3384.5 | 2124 | 902 | 38 | 135 | 1492.055 | 106 | 5894 | 0 | 434 | 1186.45 | 0 | 0 | 30 | 201.5
23:00 | 3401 | 2198 | 902 | 38 | 138 | 1495.33 | 106 | 5758 | 0 | 424 | 1205.5 | 0 | 0 | 33 | 195
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 369 | 18:00 | 354 | 11:00 | Madunaghat | 389 | 04:00 | 381 | 13:00
Amtali | 410 | 17:00 | 403 | 19:30 | Meghnaghat | 373 | 05:00 | 364 | 12:00
Ashuganj | 388 | 18:00 | 371 | 00:00 | Payra | 413 | 09:00 | 405 | 21:00
Bhulta | 393 | 06:00 | 376 | 12:00 | Rahanpur | 405 | 11:00 | 382 | 23:00
Bibiana | 375 | 18:30 | 369 | 15:00 | Rampal | 394 | 18:00 | 377 | 00:00
BIPTC | 403 | 10:00 | 389 | 00:00
Bogura | 387 | 11:00 | 363 | 23:00
Gopalganj | 388 | 18:00 | 371 | 00:00
Kaliakoir | 360 | 18:00 | 345 | 11:00
Korerhat | 387 | 04:00 | 378 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 04:00 | 215 | 12:00 | Ishurdi | 234 | 18:00 | 211 | 19:30
AKSML | 233.1 | 08:00 | 223.9 | 15:00 | Jhenaidah | 227 | 18:00 | 201 | 23:00
Aminbazar | 225 | 18:00 | 214 | 11:00 | Kachua | 221 | 07:00 | 214 | 15:00
Ashuganj | 225 | 06:00 | 218 | 19:30 | Kaliakoir | 223 | 18:00 | 210 | 11:00
Ashuganj-400 | 225 | 06:00 | 218 | 19:30 | Keranigonj | 222 | 04:00 | 214 | 12:00
Baghabari | 233 | 11:00 | 218 | 21:00 | Khulna(S) | 224 | 18:00 | 205 | 21:00
Barapukuria | 223 | 10:00 | 211 | 00:00 | Korerhat | 222 | 08:00 | 215 | 15:00
Barapukuria-230 | 223 | 10:00 | 211 | 00:00 | Madunaghat | 235 | 01:00 | 228 | 13:00
Barishal | 225 | 18:00 | 214 | 00:00 | Madunaghat-400 | 237 | 04:00 | 230 | 13:00
Bheramara | 232 | 18:00 | 208 | 19:30 | Maniknagar | 223 | 05:00 | 214 | 12:00
Bhulta | 225 | 05:00 | 214 | 12:00 | Meghnaghat | 235 | 01:00 | 223 | 13:00
Bibiana | 219 | 18:00 | 213 | 00:00 | Meghnaghat-400 | 227 | 05:00 | 219 | 10:00
BIPTC | 235 | 18:00 | 208 | 19:30 | Mirsorai | 225 | 08:00 | 219 | 15:00
Bogura | 241 | 10:00 | 226 | 21:00 | Naogaon | 231 | 14:00 | 200 | 21:00
Bogura-400 | 241 | 11:00 | 227 | 23:00 | Purbasadipur | 221 | 17:00 | 206 | 00:00
Borhanuddin | 228 | 09:00 | 220 | 01:00 | Rajshahi | 230 | 18:00 | 205 | 19:30
BSRM | 223 | 18:30 | 217 | 13:00 | Rampal | 225 | 18:00 | 208 | 23:00
Charfasson | 231 | 09:00 | 220 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 221 | 08:00 | 215 | 21:00 | Rampura | 224 | 04:00 | 212 | 12:00
Cumilla(N) | 222 | 18:00 | 215 | 12:00 | Shikalbaha | 235 | 04:00 | 227 | 14:00
Faridpur | 220 | 18:00 | 206 | 00:00 | Shyampur | 224 | 04:00 | 215 | 13:00
Fenchuganj | 221 | 18:00 | 214 | 00:00 | Siddhirganj | 224 | 07:00 | 220 | 20:00
Feni | 220 | 06:00 | 214 | 13:00 | Sirajgonj | 239 | 11:00 | 230 | 21:00
Ghorashal | 225 | 18:00 | 220 | 00:00 | Sreepur | 222 | 13:00 | 216 | 19:30
Ghorashal-230 | 212 | 18:00 | 197 | 21:00 | Tongi | 211 | 18:00 | 198 | 11:00
Gopalganj | 221 | 18:00 | 210 | 00:00
GPH | 230 | 03:00 | 22 | 15:00
Haripur | 225 | 04:00 | 215 | 13:00
Hasnabad | 224 | 18:00 | 214 | 12:00
Hathazari | 232 | 00:00 | 225 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 06:00 | 125 | 13:00 | Madunaghat | 136 | 05:00 | 131 | 13:00
Agargaon | 132 | 06:00 | 125 | 12:00 | Magura | 130 | 18:00 | 108 | 01:00
Agrabad | 133 | 00:00 | 128 | 13:00 | Mahasthangarh | 135 | 17:00 | 123 | 23:00
AKS | 131 | 00:00 | 127 | 12:00 | Maijdee | 124 | 08:00 | 119 | 15:00
Aminbazar | 128 | 04:00 | 120 | 15:00 | Manikganj | 128 | 18:00 | 120 | 16:00
Amnura | 133 | 10:00 | 118 | 19:30 | Maniknagar | 132 | 06:00 | 123 | 12:00
Ashuganj | 128 | 05:00 | 124 | 19:30 | Matarbari | 128 | 08:00 | 115 | 00:00
Ashuganj-230 | 132 | 18:00 | 129 | 15:00 | Matuail | 131 | 06:00 | 124 | 12:00
Bagerhat | 128 | 10:00 | 110 | 22:00 | Metrorail_Motijheel | 132 | 06:00 | 123 | 12:00
Bajitpur | 124 | 13:00 | 119 | 19:00 | Metrorail_Uttara | 128 | 04:00 | 116 | 12:00
Bakerganj | 131 | 17:00 | 123 | 00:00 | Millgate | 129 | 04:00 | 117 | 12:00
Bakulia | 134 | 08:00 | 128 | 13:00 | Mirpur | 127 | 05:00 | 119 | 15:00
Banani | 134 | 05:00 | 125 | 12:00 | Mirzapur | 128 | 18:00 | 119 | 19:30
Bangabhaban | 131 | 06:00 | 123 | 12:00 | Mithapukur | 132 | 17:00 | 112 | 08:00
Barapukuria | 136 | 17:00 | 122 | 00:00 | MI_Cement | 131 | 04:00 | 123 | 12:00
Barguna | 131 | 18:00 | 123 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 130 | 18:00 | 122 | 00:00 | Mogbazar | 135 | 04:00 | 126 | 12:00
Barishal-230 | 130 | 09:00 | 122 | 00:00 | Mongla | 127 | 18:00 | 110 | 19:30
Baroaulia | 135 | 22:00 | 130 | 12:00 | Motijheel | 131 | 06:00 | 123 | 12:00
Baroirhat | 128 | 03:00 | 125 | 13:00 | Muktagacha | 127 | 13:00 | 113 | 19:30
Bashundhara | 135 | 06:00 | 116 | 12:00 | Munshiganj | 130 | 05:00 | 123 | 14:00
BashundharaCement | 130 | 05:00 | 124 | 12:00 | Muradnagar | 125 | 18:00 | 119 | 21:00
Beanibazar | 124 | 18:00 | 116 | 00:00 | Mymensingh | 130 | 15:00 | 110 | 19:00
Benapole | 135 | 17:00 | 112 | 19:30 | Nabinagar | 125 | 04:00 | 116 | 12:00
Bhaluka | 130 | 05:00 | 120 | 19:00 | Naogaon | 136 | 10:00 | 120 | 21:00
Bhandaria | 125 | 09:00 | 112 | 00:00 | Narail | 131 | 17:00 | 108 | 02:00
Bhangura | 134 | 09:00 | 124 | 19:30 | Narinda | 132 | 06:00 | 123 | 12:00
Bheramara | 136 | 18:00 | 121 | 19:30 | Narshingdi | 127 | 18:00 | 116 | 15:00
Bheramara(GK) | 137 | 18:00 | 121 | 19:30 | Natore | 133 | 10:00 | 120 | 19:30
Bhulta | 126 | 06:00 | 120 | 15:00 | Nawabganj | 134 | 06:00 | 128 | 12:00
Bog-Sherpur | 136 | 10:00 | 124 | 23:00 | Netrakona | 119 | 14:00 | 108 | 19:30
Bogura | 138 | 17:00 | 127 | 22:00 | New | 129 | 00:00 | 120 | 12:00
Bogura-230 | 138 | 10:00 | 128 | 21:00 | Niamatpur | 133 | 08:00 | 123 | 21:00
Brahmanbaria | 126 | 08:00 | 121 | 19:30 | Noapara | 132 | 09:00 | 117 | 19:30
Cantonment | 131 | 04:00 | 125 | 12:00 | Pabna | 134 | 11:00 | 121 | 19:30
Chandina | 128 | 06:00 | 123 | 15:00 | Palashbari | 132 | 17:00 | 116 | 00:00
Chandpur | 127 | 00:00 | 119 | 13:00 | Panchagarh | 138 | 05:00 | 128 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 135 | 00:00 | 131 | 12:00 | Patiya | 134 | 08:00 | 128 | 15:00
Chapai | 133 | 18:00 | 125 | 22:00 | Patnitala | 132 | 09:00 | 118 | 23:00
Charsaidpur | 130 | 05:00 | 124 | 12:00 | Patuakhali | 130 | 17:00 | 125 | 00:00
Chauddagram | 126 | 03:00 | 123 | 12:00 | Payra | 134 | 14:00 | 130 | 23:00
Chhatak | 120 | 06:00 | 112 | 15:00 | PHP | 128 | 03:00 | 123 | 14:00
Chowmuhani | 125 | 18:00 | 120 | 14:00 | Postogola | 133 | 05:00 | 125 | 12:00
Chuadanga | 136 | 18:00 | 114 | 23:00 | Pubail | 123 | 18:00 | 114 | 21:00
Coxsbazar | 127 | 07:00 | 116 | 00:00 | Purbachal | 135 | 05:00 | 125 | 12:00
Cumilla(N) | 128 | 07:00 | 123 | 15:00 | Purbasadipur | 133 | 06:00 | 124 | 00:00
Cumilla(S) | 136 | 09:00 | 123 | 00:00 | Rahanpur | 135 | 09:00 | 127 | 20:00
Daganbhuiyan | 126 | 06:00 | 121 | 15:00 | Rahanpur-400 | 135 | 10:00 | 127 | 23:00
Daudkandi | 124 | 05:00 | 117 | 21:00 | Rahim | 131 | 06:00 | 123 | 13:00
DhakaUniversity | 134 | 04:00 | 126 | 12:00 | Rajbari | 125 | 10:00 | 114 | 00:00
Dhamrai | 126 | 04:00 | 118 | 14:00 | Rajendrapur | 127 | 14:00 | 121 | 21:00
Dhanmondi | 135 | 05:00 | 125 | 12:00 | Rajshahi | 132 | 18:00 | 117 | 23:00
Dohazari | 131 | 06:00 | 126 | 13:00 | Rajshahi-230 | 132 | 18:00 | 118 | 19:30
Faridpur | 127 | 17:00 | 119 | 00:00 | Ramganj | 123 | 08:00 | 117 | 13:00
Fatullah | 138 | 17:00 | 124 | 12:00 | Rampur | 134 | 03:00 | 128 | 13:00
Fenchuganj | 129 | 18:00 | 124 | 00:00 | Rampura | 134 | 04:00 | 125 | 12:00
Feni | 129 | 06:00 | 123 | 12:00 | Rangamati | 134 | 04:00 | 130 | 12:00
Feni-230 | 127 | 03:00 | 124 | 13:00 | Rangpur | 129 | 17:00 | 116 | 00:00
Ghatail | 128 | 15:00 | 110 | 19:30 | Ruppur | 136 | 09:00 | 122 | 21:00
Ghorashal | 125 | 18:00 | 119 | 21:00 | Saidpur | 133 | 17:00 | 121 | 00:00
Goalpara | 134 | 18:00 | 121 | 01:00 | Santhia | 135 | 18:00 | 123 | 21:00
Gollamari | 135 | 10:00 | 120 | 19:30 | Satkhira | 130 | 09:00 | 113 | 00:00
Gopalganj | 130 | 18:00 | 120 | 00:00 | Satmasjid | 132 | 04:00 | 123 | 13:00
Gopalganj-400 | 131 | 18:00 | 123 | 01:00 | Savar | 127 | 18:00 | 117 | 15:00
Gulshan | 134 | 05:00 | 125 | 12:00 | SevenRings | 124 | 18:00 | 117 | 21:00
Halishahar | 134 | 01:00 | 128 | 15:00 | ShahCement | 130 | 05:00 | 124 | 12:00
Haripur | 131 | 04:00 | 125 | 12:00 | Shahjadpur | 137 | 17:00 | 128 | 21:00
HaripurSBU | 131 | 04:00 | 125 | 12:00 | Shahjibazar | 126 | 18:00 | 119 | 15:00
Hasnabad | 132 | 03:00 | 125 | 12:00 | Shahmirpur | 135 | 07:00 | 129 | 15:00
Hathazari | 136 | 00:00 | 131 | 13:00 | Shariatpur | 129 | 18:00 | 119 | 00:00
Hatirjheel | 135 | 05:00 | 125 | 13:00 | Sherpur | 128 | 15:00 | 108 | 06:00
Ishurdi | 137 | 09:00 | 123 | 19:30 | Shikalbaha | 126 | 04:00 | 119 | 14:00
Jaldhaka | 130 | 06:00 | 118 | 00:00 | Shikalbaha-230 | 135 | 01:00 | 130 | 14:00
Jamalpur | 130 | 10:00 | 112 | 00:00 | Shitalakhya | 131 | 04:00 | 123 | 12:00
Jashore | 136 | 18:00 | 114 | 19:30 | Sholosohor | 135 | 03:00 | 130 | 15:00
Jhenaidah | 138 | 17:00 | 111 | 01:00 | Shomvuganj | 120 | 13:00 | 112 | 19:30
Jhenaidah-230 | 140 | 18:00 | 122 | 01:00 | Shyampur | 133 | 18:00 | 125 | 13:00
Joydebpur | 120 | 13:00 | 113 | 16:00 | Shyampur-230 | 137 | 12:00 | 127 | 13:00
Joypurhat | 133 | 18:00 | 119 | 23:00 | Siddhirganj | 132 | 06:00 | 124 | 15:00
Juldah | 134 | 01:00 | 128 | 15:00 | Sirajganj | 133 | 10:00 | 120 | 21:00
Kabirpur | 130 | 03:00 | 114 | 12:00 | Sitakunda | 134 | 02:00 | 129 | 15:00
Kachua | 126 | 09:00 | 121 | 13:00 | Sonargaon | 128 | 05:00 | 122 | 12:00
Kaliakoir | 133 | 18:00 | 122 | 11:00 | Sreemongol | 126 | 18:30 | 119 | 21:00
Kaliganj | 138 | 18:00 | 120 | 01:00 | Sreepur | 130 | 06:00 | 125 | 19:00
Kallyanpur | 127 | 18:00 | 120 | 12:00 | Srinagar | 135 | 18:00 | 128 | 12:00
Kalurghat | 135 | 00:00 | 131 | 13:00 | SSM | 140 | 23:00 | 135 | 12:00
Kamrangirchar | 134 | 05:00 | 117 | 12:00 | Sunamganj | 117 | 18:00 | 109 | 23:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 123 | 06:00 | 118 | 23:00
Kasba | 124 | 07:00 | 118 | 21:00 | Sylhet_(South) | 124 | 18:30 | 118 | 00:00
Kazla | 131 | 04:00 | 122 | 13:00 | Tangail | 127 | 13:00 | 113 | 19:30
Keranigonj | 135 | 06:00 | 129 | 12:00 | Taraganj | 131 | 17:00 | 120 | 00:00
Khagrachori | 133 | 04:00 | 129 | 13:00 | Tasnim | 128 | 04:00 | 122 | 11:00
Khulna | 133 | 18:00 | 120 | 00:00 | Thakurgaon | 138 | 06:00 | 126 | 00:00
Khulna(S) | 134 | 18:00 | 120 | 19:30 | TK | 135 | 00:00 | 131 | 12:00
Khulshi | 133 | 03:00 | 127 | 15:00 | Tongi | 130 | 05:00 | 121 | 19:00
Kishoreganj | 123 | 14:00 | 116 | 19:30 | Ullahpara | 134 | 11:00 | 122 | 19:30
Kodda | 129 | 22:00 | 119 | 12:00 | Ullon | 135 | 06:00 | 124 | 13:00
Korerhat | 134 | 08:00 | 127 | 12:00 | Uttara | 130 | 04:00 | 116 | 12:00
KSRM | 135 | 03:00 | 130 | 13:00 | UttaraNew | 128 | 04:00 | 116 | 12:00
Kulaura | 129 | 18:00 | 123 | 00:00 | Zigatola | 135 | 05:00 | 34 | 19:00
Kurigram | 126 | 06:00 | 110 | 00:00
Kushtia | 133 | 17:00 | 117 | 01:00
Laksam | 125 | 08:00 | 120 | 15:00
Lakshmipur | 124 | 18:30 | 118 | 15:00
Lalbag | 134 | 05:00 | 128 | 12:00
Lalmonirhat | 127 | 17:00 | 110 | 02:00
Madanganj | 130 | 06:00 | 124 | 12:00
Madaripur | 130 | 09:00 | 121 | 00:00
Madartek | 134 | 02:00 | 125 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-07-2026 | [28 empty] | Date: | 05-07-2026 | [28 empty] | Date: | 05-07-2026 | [28 empty] | Date: | 05-07-2026 | [28 empty] | Date: | 05-07-2026 | [18 empty] | Date: | 05-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [18 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 35 | 28 | 70 | 62 | 142 | 15 | 35 | 126 | 0 | 0 | 298 | 525 | 0 | 0 | 292 | 0 | 0 | 0 | 143 | 16 | 21 | 0 | 450 | 15 | 15 | 14 | 0 | 51 | 67 | 15 | 17 | 12 | 12 | 0 | 65 | 47 | 21 | 720 | 0 | 0 | 12 | 8 | 49 | 216 | 0 | 0 | 0 | 1160 | 0 | 31 | 0 | 230 | 280 | 220 | 51 | 10 | 213 | 40 | 55 | 138 | 99 | 6 | 19 | 65 | 176 | 8 | 0 | 15 | 310 | 0 | 256 | 29 | 0 | 150 | 0 | 16 | 0 | 61 | 25 | 141 | 0 | 100 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 8061 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 150 | 0 | 32 | 0 | 1182 | 0 | 0 | 0 | 1495.78 | 0 | 35 | 0 | 30 | 78 | 0 | 0 | 0 | 8 | 0 | 0 | 21 | 0 | 0 | 154 | 0 | 137 | 0 | 139 | 0 | 414 | 0 | 0 | 180 | 38 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 307 | 64 | 220 | 0 | 1050 | 1120 | 2 | 7924.78 | 15985.78 | 75.44
01:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 28 | 70 | 62 | 145 | 15 | 35 | 35 | 0 | 0 | 299 | 505 | 0 | 0 | 293 | 0 | 0 | 0 | 143 | 16 | 21 | 0 | 475 | 16 | 15 | 12 | 0 | 40 | 67 | 15 | 0 | 12 | 12 | 0 | 65 | 103 | 26 | 720 | 0 | 0 | 50 | 8 | 99 | 217 | 0 | 0 | 0 | 1160 | 0 | 50 | 0 | 230 | 280 | 220 | 51 | 10 | 210 | 39 | 51 | 136 | 97 | 0 | 19 | 65 | 182 | 8 | 0 | 15 | 305 | 0 | 256 | 29 | 0 | 146 | 0 | 16 | 0 | 61 | 25 | 142 | 0 | 100 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 8031 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 151 | 0 | 32 | 0 | 1192 | 0 | 0 | 0 | 1495.69 | 0 | 35 | 0 | 50 | 113 | 0 | 0 | 0 | 8 | 0 | 0 | 21 | 0 | 0 | 153 | 0 | 137 | 0 | 138 | 0 | 414 | 0 | 0 | 180 | 38 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 64 | 220 | 0 | 1050 | 1110 | 35 | 8026.69 | 16057.69 | 75.47
02:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 28 | 70 | 62 | 145 | 15 | 35 | 0 | 0 | 0 | 299 | 465 | 0 | 0 | 295 | 0 | 0 | 0 | 143 | 16 | 21 | 0 | 390 | 15 | 15 | 13 | 0 | 53 | 0 | 15 | 0 | 12 | 12 | 0 | 65 | 104 | 30 | 720 | 0 | 0 | 50 | 8 | 97 | 217 | 0 | 0 | 0 | 1160 | 0 | 50 | 0 | 230 | 280 | 220 | 51 | 10 | 210 | 36 | 0 | 138 | 98 | 0 | 19 | 65 | 176 | 8 | 0 | 15 | 310 | 0 | 256 | 29 | 0 | 136 | 0 | 16 | 0 | 61 | 25 | 143 | 0 | 101 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7755 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 50 | 0 | 32 | 0 | 1193 | 0 | 0 | 0 | 1478.84 | 0 | 35 | 0 | 50 | 113 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 137 | 0 | 139 | 0 | 414 | 0 | 0 | 181 | 38 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 1050 | 1110 | 54 | 7912.84 | 15667.84 | 75.5
03:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 28 | 70 | 62 | 145 | 15 | 0 | 0 | 0 | 0 | 299 | 415 | 0 | 0 | 292 | 0 | 0 | 0 | 143 | 17 | 21 | 0 | 390 | 13 | 15 | 12 | 0 | 49 | 0 | 0 | 0 | 12 | 12 | 0 | 65 | 103 | 28 | 720 | 0 | 0 | 50 | 8 | 97 | 219 | 0 | 0 | 0 | 1160 | 0 | 50 | 0 | 230 | 280 | 220 | 51 | 10 | 215 | 36 | 0 | 137 | 93 | 0 | 19 | 61 | 150 | 8 | 0 | 15 | 310 | 0 | 256 | 29 | 0 | 131 | 0 | 16 | 0 | 61 | 25 | 142 | 0 | 101 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7610 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1193 | 0 | 0 | 0 | 1484.86 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 137 | 0 | 139 | 0 | 414 | 0 | 0 | 180 | 39 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 1012 | 1110 | 35 | 7743.06 | 15353.06 | 75.5
04:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 28 | 70 | 62 | 145 | 15 | 0 | 0 | 0 | 0 | 306 | 390 | 0 | 0 | 300 | 0 | 0 | 0 | 143 | 17 | 21 | 0 | 395 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 12 | 0 | 65 | 105 | 29 | 720 | 0 | 0 | 50 | 0 | 93 | 219 | 0 | 0 | 0 | 1160 | 0 | 50 | 0 | 230 | 280 | 220 | 51 | 10 | 217 | 36 | 0 | 138 | 34 | 0 | 19 | 60 | 168 | 0 | 0 | 15 | 305 | 0 | 256 | 29 | 0 | 127 | 0 | 16 | 0 | 61 | 25 | 142 | 0 | 101 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7521 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1192 | 0 | 0 | 0 | 1479.35 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 137 | 0 | 139 | 0 | 414 | 0 | 0 | 180 | 39 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 833 | 1110 | 35 | 7498.35 | 15019.35 | 75.56
05:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 28 | 70 | 62 | 45 | 15 | 0 | 0 | 0 | 0 | 298 | 435 | 0 | 0 | 293 | 0 | 0 | 0 | 143 | 17 | 21 | 0 | 505 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 12 | 0 | 65 | 16 | 34 | 720 | 0 | 0 | 24 | 0 | 17 | 220 | 0 | 0 | 0 | 1160 | 0 | 12 | 0 | 230 | 280 | 220 | 51 | 10 | 216 | 36 | 0 | 138 | 17 | 0 | 19 | 17 | 156 | 0 | 0 | 15 | 305 | 0 | 256 | 29 | 0 | 139 | 0 | 16 | 0 | 61 | 25 | 144 | 0 | 100 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7299 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1196 | 0 | 0 | 0 | 1444.58 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 140 | 0 | 138 | 0 | 414 | 0 | 0 | 180 | 38 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 833 | 1110 | 17 | 7375.58 | 14674.58 | 75.59
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 28 | 60 | 48 | 45 | 15 | 0 | 0 | 0 | 0 | 303 | 410 | 0 | 0 | 293 | 0 | 0 | 1 | 143 | 17 | 21 | 0 | 380 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 12 | 0.19 | 65 | 15 | 22 | 720 | 0 | 0 | 19 | 0 | 15 | 217 | 0 | 0 | 0 | 1160 | 0 | 12 | 0 | 230 | 280 | 220 | 51 | 10 | 217 | 36 | 0 | 138 | 0 | 0 | 19 | 0 | 152 | 0 | 2 | 15 | 305 | 0 | 256 | 29 | 0 | 130 | 0 | 16 | 0 | 61 | 25 | 143 | 0 | 100 | 0 | 48 | 0.82 | 48 | 0 | 0.1 | 1.12 | 0 | 7010.23 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 1205 | 0 | 0 | 0 | 1344.37 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 2.08 | 1 | 0 | 0 | 1.9 | 153 | 0 | 141 | 0 | 139 | 0 | 414 | 0 | 0.19 | 180 | 40 | 95 | 1 | 34 | 0 | 0 | 0 | 0.4 | 4 | 0.02 | 0 | 307 | 65 | 220 | 0 | 833 | 1070 | 0 | 7231.96 | 14242.19 | 75.62
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 28 | 34 | 48 | 15 | 15 | 0 | 0 | 0 | 0 | 295 | 415 | 0 | 0 | 301 | 0 | 0 | 3 | 143 | 17 | 21 | 0 | 435 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 12 | 0.21 | 65 | 0 | 21 | 720 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1160 | 0 | 12 | 0 | 230 | 280 | 220 | 51 | 10 | 216 | 36 | 0 | 137 | 0 | 0 | 19 | 0 | 152 | 0 | 10 | 15 | 310 | 0 | 256 | 29 | 0 | 137 | 2 | 16 | 0 | 61 | 28 | 142 | 0 | 100 | 0 | 48 | 6.9 | 48 | 0 | 0.3 | 10.58 | 0 | 6997.99 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18.18 | 1204 | 0 | 0 | 0 | 1298.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.74 | 7 | 0 | 0 | 11.28 | 154 | 0 | 143 | 0 | 139 | 0 | 414 | 0 | 0.71 | 181 | 39 | 35 | 5 | 34 | 0 | 0 | 0 | 3.7 | 16 | 0.02 | 0 | 307 | 65 | 220 | 0 | 833 | 976 | 0 | 7049.7 | 14047.69 | 75.65
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 28 | 34 | 48 | 15 | 15 | 0 | 0 | 0 | 0 | 295 | 410 | 0 | 0 | 293 | 0 | 0 | 8 | 143 | 16.5 | 21 | 0 | 375 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 12 | 0.7 | 64 | 0 | 7 | 770 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1150 | 0 | 12 | 0 | 230 | 280 | 220 | 51 | 10 | 216 | 36 | 0 | 93 | 0 | 0 | 19 | 0 | 140 | 0 | 9 | 15 | 310 | 0 | 256 | 29 | 0 | 132 | 3 | 16 | 0 | 61 | 28 | 142 | 0 | 100 | 0 | 49 | 10.5 | 48 | 0 | 1.5 | 22.4 | 0 | 6874.6 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40.22 | 1210 | 0 | 0 | 0 | 1189.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.15 | 20 | 0 | 0 | 24.9 | 154 | 0 | 141 | 0 | 138 | 0 | 414 | 0 | 2.39 | 180 | 39 | 0 | 10 | 34 | 0 | 0 | 0 | 2.9 | 75 | 0.04 | 0 | 307 | 65 | 220 | 0 | 835 | 920 | 0 | 6986.9 | 13861.5 | 75.69
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 17 | 34 | 48 | 15 | 15 | 0 | 0 | 0 | 0 | 306 | 395 | 0 | 0 | 308 | 0 | 0 | 12 | 123 | 15.5 | 5 | 0 | 450 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 3 | 0 | 0 | 1.13 | 65 | 0 | 3 | 860 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1164 | 0 | 12 | 0 | 230 | 280 | 220 | 51 | 0 | 214 | 40 | 0 | 20 | 0 | 0 | 19 | 0 | 142 | 0 | 7 | 15 | 310 | 0 | 256 | 29 | 0 | 129 | 9 | 16 | 0 | 61 | 28 | 142 | 0 | 102 | 0 | 49 | 10.09 | 48 | 0 | 1 | 23.07 | 0 | 6917.79 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24.31 | 1185 | 0 | 0 | 0 | 1113.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.99 | 53 | 0 | 0 | 24.3 | 152 | 0 | 137 | 0 | 134 | 0 | 397 | 0 | 2.33 | 200 | 39 | 0 | 8 | 0 | 0 | 0 | 0 | 2 | 79 | 0.02 | 0 | 271 | 65 | 220 | 0 | 834 | 810 | 0 | 6720.94 | 13638.73 | 75.73
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 17 | 34 | 48 | 15 | 15 | 17 | 17 | 0 | 0 | 304 | 396 | 0 | 0 | 300 | 0 | 0 | 0 | 123 | 15.5 | 18 | 0 | 435 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0.46 | 70 | 0 | 2 | 925 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1125 | 0 | 12 | 0 | 230 | 280 | 220 | 43 | 0 | 214 | 40 | 0 | 92 | 0 | 0 | 17 | 0 | 114 | 0 | 8 | 15 | 310 | 0 | 257 | 29 | 0 | 130 | 6 | 16 | 0 | 0 | 25 | 141 | 0 | 101 | 0 | 58 | 14 | 115 | 0 | 1.5 | 27.9 | 0 | 7039.36 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 35 | 1073 | 0 | 0 | 0 | 1054.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.33 | 30 | 0 | 0 | 43.79 | 146 | 0 | 132 | 0 | 133 | 0 | 340 | 0 | 5.13 | 200 | 39 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 125 | 0.02 | 0 | 265 | 65 | 220 | 0 | 869 | 775 | 0 | 6517.45 | 13556.81 | 75.78
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 0 | 0 | 34 | 40 | 64 | 15 | 17 | 17 | 0 | 0 | 306 | 470 | 0 | 0 | 325 | 0 | 0 | 26 | 123 | 15.5 | 21 | 0 | 510 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0.41 | 70 | 0 | 2 | 1035 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1160 | 2 | 0 | 0 | 230 | 280 | 220 | 43 | 0 | 199 | 33 | 0 | 93 | 0 | 0 | 17 | 0 | 142 | 0 | 1 | 15 | 310 | 0 | 244 | 30 | 0 | 142 | 6 | 16 | 0 | 0 | 25 | 142 | 0 | 100 | 0 | 58 | 21.13 | 115 | 0 | 2.7 | 32.12 | 0 | 7419.86 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 950 | 0 | 0 | 0 | 1057.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.93 | 59 | 0 | 0 | 23.01 | 145 | 0 | 130 | 0 | 133 | 0 | 360 | 0 | 6.99 | 200 | 41 | 0 | 17 | 0 | 0 | 0 | 0 | 5.1 | 178 | 0.08 | 0 | 231 | 65 | 220 | 0 | 869 | 780 | 0 | 6455.64 | 13875.5 | 75.83
12:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 34 | 46 | 64 | 15 | 35 | 17 | 0 | 0 | 289 | 465 | 0 | 0 | 325 | 0 | 0 | 19 | 123 | 15.5 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0.3 | 70 | 0 | 2 | 1080 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 1160 | 2 | 0 | 0 | 230 | 280 | 240 | 43 | 0 | 197 | 39 | 0 | 94 | 0 | 0 | 11 | 0 | 144 | 0 | 16 | 15 | 315 | 0 | 244 | 30 | 0 | 147 | 7 | 16 | 0 | 0 | 23 | 141 | 0 | 101 | 0 | 58 | 16.58 | 116 | 0 | 2.7 | 57.79 | 0 | 7557.87 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 900 | 0 | 0 | 0 | 1117.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.24 | 42 | 0 | 0 | 42.32 | 144 | 0 | 130 | 0 | 133 | 0 | 385 | 0 | 3.09 | 200 | 39 | 0 | 18 | 0 | 0 | 0 | 0 | 4.2 | 116 | 0.26 | 0 | 275 | 65 | 220 | 0 | 955 | 800 | 0 | 6592.32 | 14150.19 | 75.89
13:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 34 | 30 | 64 | 15 | 35 | 17 | 0 | 0 | 295 | 450 | 0 | 0 | 327 | 0 | 0 | 11 | 105 | 0 | 21 | 0 | 480 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 1.03 | 70 | 0 | 2 | 1125 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1103 | 1 | 0 | 0 | 230 | 280 | 265 | 51 | 0 | 160 | 20 | 0 | 93 | 0 | 0 | 13 | 0 | 146 | 0 | 34 | 21 | 315 | 0 | 244 | 30 | 0 | 142 | 8 | 16 | 0 | 0 | 23 | 141 | 0 | 100 | 0 | 58 | 19.23 | 116 | 0 | 1 | 49.44 | 0 | 7463.7 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 48 | 944 | 0 | 0 | 0 | 1321.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.55 | 14 | 0 | 0 | 39.1 | 142 | 0 | 131 | 0 | 132 | 0 | 380 | 0 | 3.4 | 200 | 40 | 0 | 39 | 0 | 0 | 0 | 0 | 3.3 | 131 | 0.4 | 0 | 247 | 65 | 180 | 0 | 902 | 820 | 0 | 6728.03 | 14191.73 | 75.95
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 34 | 30 | 64 | 15 | 35 | 17 | 0 | 0 | 298 | 445 | 0 | 0 | 326 | 0 | 0 | 15 | 105 | 0 | 21 | 0 | 520 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 1.84 | 70 | 0 | 2 | 1130 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1105 | 2 | 0 | 0 | 245 | 280 | 280 | 51 | 0 | 160 | 10 | 0 | 93 | 0 | 0 | 13 | 0 | 142 | 0 | 32 | 25 | 320 | 0 | 244 | 29 | 30 | 143 | 7 | 16 | 0 | 0 | 23 | 143 | 0 | 99 | 0 | 58 | 9.7 | 116 | 0 | 1.2 | 9.14 | 9 | 7528.88 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 50 | 1000 | 0 | 0 | 0 | 1273.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.4 | 8 | 0 | 0 | 21.02 | 139 | 0 | 131 | 0 | 132 | 0 | 378 | 0 | 1.52 | 200 | 40 | 0 | 25 | 0 | 0 | 0 | 0 | 2.05 | 109 | 0.27 | 0 | 238 | 65 | 220 | 0 | 874 | 815 | 0 | 6676.81 | 14205.69 | 76
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 15 | 34 | 45 | 64 | 15 | 35 | 17 | 0 | 0 | 300 | 456 | 0 | 0 | 325 | 0 | 0 | 7 | 86 | 0 | 21 | 0 | 530 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 1.3 | 70 | 0 | 0 | 1135 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1106 | 1 | 0 | 0 | 275 | 280 | 255 | 51 | 0 | 204 | 10 | 0 | 92 | 0 | 0 | 13 | 0 | 142 | 0 | 8 | 30 | 320 | 0 | 204 | 29 | 30 | 146 | 6 | 16 | 0 | 0 | 23 | 144 | 0 | 99 | 0 | 58 | 15.58 | 116 | 0 | 0.4 | 40.6 | 12 | 7565.88 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 1000 | 0 | 0 | 0 | 1290.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 21 | 0 | 0 | 15.96 | 139 | 0 | 131 | 0 | 132 | 0 | 365 | 0 | 1.48 | 201 | 38 | 0 | 26 | 0 | 0 | 0 | 0 | 2.07 | 161 | 0.1 | 0 | 253 | 65 | 220 | 0 | 868 | 835 | 0 | 6734.09 | 14299.97 | 76.07
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 9 | 28 | 34 | 45 | 64 | 24 | 35 | 17 | 0 | 0 | 291 | 450 | 0 | 17 | 325 | 0 | 0 | 6 | 86 | 0 | 21 | 0 | 440 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 1.05 | 70 | 0 | 0 | 1135 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1103 | 2 | 0 | 8 | 350 | 280 | 240 | 51 | 0 | 196 | 20 | 0 | 92 | 0 | 0 | 13 | 15 | 160 | 0 | 1 | 31 | 320 | 0 | 204 | 29 | 30 | 144 | 4 | 16 | 0 | 45 | 20 | 141 | 0 | 100 | 0 | 58 | 8.11 | 116 | 0 | 0.4 | 26.35 | 12 | 7600.91 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 901 | 0 | 0 | 0 | 1272.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.14 | 16 | 0 | 0 | 12.75 | 139 | 0 | 131 | 0 | 132 | 0 | 362 | 0 | 1.34 | 201 | 40 | 0 | 18 | 0 | 0 | 0 | 0 | 3 | 66 | 0.08 | 0 | 246 | 65 | 220 | 0 | 844 | 880 | 0 | 6501.33 | 14102.24 | 76.13
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 15 | 28 | 34 | 45 | 64 | 30 | 35 | 35 | 0 | 0 | 293 | 420 | 0 | 35 | 325 | 0 | 0 | 4 | 86 | 0 | 21 | 0 | 405 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0.37 | 70 | 0 | 3 | 1050 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1025 | 1 | 0 | 8 | 350 | 280 | 240 | 51 | 0 | 197 | 20 | 1 | 93 | 0 | 0 | 13 | 16 | 152 | 0 | 0 | 31 | 315 | 0 | 204 | 29 | 30 | 137 | 0 | 16 | 0 | 62 | 28 | 142 | 0 | 100 | 8 | 58 | 5.59 | 115 | 0 | 0.4 | 10.95 | 12 | 7433.31 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 897 | 0 | 0 | 0 | 1175.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 35 | 0 | 0 | 5.83 | 139 | 0 | 131 | 0 | 132 | 0 | 362 | 0 | 0.56 | 190 | 38 | 0 | 10 | 0 | 0 | 0 | 0 | 1.9 | 72 | 0.06 | 0 | 209 | 65 | 220 | 0 | 747 | 850 | 0 | 6229.69 | 13663 | 76.2
18:00 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 17 | 28 | 38 | 45 | 130 | 30 | 35 | 35 | 0 | 0 | 292 | 420 | 0 | 35 | 295 | 0 | 0 | 1 | 86 | 13.5 | 21 | 0 | 405 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0.08 | 68 | 0 | 7 | 1050 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1006 | 0 | 0 | 0 | 300 | 280 | 240 | 51 | 0 | 197 | 20 | 15 | 93 | 0 | 8 | 13 | 16 | 152 | 0 | 1 | 31 | 320 | 0 | 215 | 29 | 30 | 137 | 1 | 16 | 0 | 63 | 30 | 142 | 0 | 101 | 17 | 59 | 1.36 | 116 | 0 | 0.2 | 2.87 | 12 | 7453.01 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 897 | 0 | 0 | 0 | 1081.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.92 | 9 | 0 | 0 | 3.14 | 139 | 0 | 131 | 0 | 132 | 0 | 363 | 0 | 0.22 | 180 | 38 | 0 | 2 | 0 | 0 | 0 | 0 | 0.65 | 23 | 0 | 0 | 213 | 65 | 180 | 0 | 755 | 800 | 0 | 5955.9 | 13408.91 | 76.3
19:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 28 | 92 | 76 | 130 | 30 | 35 | 70 | 0 | 0 | 303 | 395 | 0 | 35 | 304 | 0 | 0 | 0 | 112 | 15 | 21 | 0 | 470 | 0 | 0 | 3 | 0 | 37 | 51 | 0 | 0 | 12 | 3 | 0 | 68 | 0 | 7 | 1135 | 0 | 0 | 6 | 2 | 0 | 216 | 0 | 0 | 0 | 1160 | 0 | 6 | 0 | 260 | 280 | 240 | 51 | 0 | 200 | 20 | 16 | 93 | 4 | 9 | 19 | 16 | 146 | 0 | 0 | 31 | 320 | 0 | 230 | 29 | 30 | 128 | 0 | 16 | 0 | 63 | 30 | 142 | 0 | 100 | 17 | 68 | 0 | 115 | 0 | 0 | 0 | 18 | 8010 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 20 | 0 | 935 | 0 | 0 | 0 | 1379.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 131 | 0 | 132 | 0 | 359 | 0 | 0 | 180 | 37 | 50 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 235 | 65 | 220 | 0 | 1050 | 880 | 0 | 6794.23 | 14804.23 | 76.34
19:30 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 35 | 28 | 98 | 100 | 130 | 0 | 35 | 108 | 0 | 0 | 298 | 437 | 0 | 35 | 300 | 0 | 0 | 0 | 135 | 15 | 21 | 0 | 460 | 0 | 0 | 22 | 0 | 65 | 51 | 0 | 0 | 12 | 12 | 0 | 70 | 7 | 9 | 1135 | 0 | 0 | 18 | 8 | 0 | 216 | 0 | 0 | 0 | 1160 | 0 | 12 | 0 | 260 | 280 | 240 | 51 | 0 | 214 | 20 | 50 | 93 | 31 | 9 | 19 | 30 | 142 | 0 | 0 | 31 | 320 | 0 | 237 | 29 | 30 | 146 | 0 | 16 | 0 | 63 | 20 | 142 | 0 | 100 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 18 | 8345 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1044 | 0 | 0 | 0 | 1489.76 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 131 | 0 | 132 | 0 | 362 | 0 | 0 | 180 | 37 | 90 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 65 | 220 | 0 | 1050 | 1020 | 0 | 7373.76 | 15718.76 | 76.36
20:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 35 | 28 | 98 | 108 | 130 | 0 | 35 | 108 | 0 | 0 | 300 | 440 | 0 | 35 | 301 | 0 | 0 | 0 | 142 | 17 | 21 | 0 | 435 | 0 | 0 | 24 | 0 | 46 | 51 | 0 | 0 | 12 | 24 | 0 | 70 | 17 | 15 | 1135 | 0 | 0 | 18 | 8 | 0 | 216 | 0 | 0 | 0 | 1160 | 0 | 10 | 0 | 260 | 280 | 240 | 51 | 0 | 214 | 20 | 39 | 93 | 26 | 9 | 19 | 30 | 148 | 0 | 0 | 31 | 320 | 0 | 237 | 29 | 30 | 140 | 0 | 16 | 0 | 63 | 20 | 142 | 0 | 102 | 19 | 68 | 0 | 152 | 0 | 0 | 0 | 18 | 8331 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1075 | 0 | 0 | 0 | 1486.02 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 131 | 0 | 132 | 0 | 374 | 0 | 0 | 180 | 38 | 94 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 1050 | 1050 | 0 | 7448.02 | 15779.02 | 76.36
21:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 28 | 28 | 98 | 108 | 130 | 45 | 35 | 108 | 0 | 0 | 287 | 430 | 0 | 35 | 301 | 0 | 0 | 0 | 143 | 15 | 21 | 0 | 470 | 0 | 0 | 0 | 0 | 41 | 34 | 0 | 0 | 12 | 24 | 0 | 70 | 0 | 25 | 1135 | 0 | 0 | 19 | 8 | 0 | 217 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 240 | 280 | 240 | 51 | 0 | 215 | 20 | 47 | 93 | 32 | 9 | 19 | 30 | 134 | 0 | 0 | 31 | 315 | 0 | 254 | 29 | 30 | 138 | 0 | 16 | 0 | 63 | 20 | 144 | 0 | 102 | 35 | 68 | 0 | 155 | 0 | 0 | 0 | 18 | 8306 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1130 | 0 | 0 | 0 | 1489.76 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 131 | 0 | 132 | 0 | 370 | 0 | 0 | 180 | 40 | 95 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 65 | 220 | 0 | 1050 | 1050 | 0 | 7515.76 | 15821.76 | 76.42
22:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 15.4 | 28 | 98 | 108 | 130 | 55 | 35 | 108 | 0 | 0 | 290 | 435 | 0 | 35 | 300 | 0 | 0 | 0 | 143 | 5 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 27 | 34 | 0 | 0 | 12 | 24 | 0 | 106 | 0 | 31 | 1125 | 0 | 0 | 19 | 8 | 0 | 180 | 0 | 0 | 0 | 1164 | 0 | 0 | 0 | 230 | 280 | 230 | 51 | 0 | 215 | 25 | 46 | 95 | 31 | 9 | 19 | 30 | 132 | 0 | 0 | 31 | 310 | 0 | 256 | 29 | 30 | 139 | 0 | 16 | 0 | 63 | 20 | 144 | 0 | 102 | 17 | 68 | 0 | 156 | 0 | 0 | 0 | 18 | 8250.4 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1151 | 0 | 0 | 0 | 1488.78 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 131 | 0 | 132 | 0 | 370 | 0 | 0 | 180 | 39 | 95 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 65 | 220 | 0 | 1050 | 1045 | 0 | 7502.78 | 15753.18 | 76.48
23:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 16.5 | 23 | 114 | 108 | 130 | 55 | 35 | 108 | 0 | 0 | 298 | 470 | 0 | 35 | 309 | 0 | 0 | 0 | 143 | 17 | 21 | 0 | 530 | 1 | 15 | 0 | 0 | 33 | 34 | 0 | 0 | 12 | 24 | 0 | 106 | 2 | 31 | 1125 | 0 | 0 | 19 | 8 | 3 | 159 | 0 | 0 | 0 | 814 | 0 | 0 | 0 | 250 | 280 | 230 | 51 | 0 | 215 | 40 | 49 | 94 | 31 | 8 | 19 | 30 | 138 | 0 | 0 | 31 | 310 | 0 | 256 | 29 | 30 | 152 | 0 | 16 | 0 | 63 | 25 | 142 | 0 | 102 | 17 | 68 | 0 | 156 | 0 | 0 | 0 | 18 | 8105.5 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1188 | 0 | 0 | 0 | 1495.33 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 130 | 0 | 132 | 0 | 370 | 0 | 0 | 180 | 39 | 95 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 65 | 220 | 0 | 1050 | 1055 | 0 | 7593.33 | 15698.83 | 76.57
Total KWH | 0 | 816000 | 236640 | 0 | 0 | 0 | 0 | 0 | 9136800 | 0 | 0 | 188280 | 552600 | 1464624 | 1496640 | 2078782 | 571030 | 539136 | 792000 | 0 | 0 | 7178676 | 10525000 | 0 | 270456 | 7399312 | 0 | 0 | 133869 | 3136800 | 274200 | 474480 | 0 | 10731818.18 | 70255 | 82800 | 77760 | 0 | 1105920 | 308419 | 38784 | 41045 | 113280 | 203520 | 8809 | 1742100 | 635633 | 372960 | 22749090.91 | 0 | 0 | 374400 | 75954.6 | 549490 | 5248657 | 0 | 0 | 0 | 26623634 | 12285 | 341236 | 16727 | 6166000 | 7081600 | 5746000 | 1219088 | 88297 | 5051000 | 724392 | 341760 | 2559166 | 582720 | 63000 | 432100 | 534660 | 3526080 | 30346 | 122736 | 524208 | 7520000 | 0 | 5975000 | 694000 | 290520 | 3328936.36 | 56836 | 248208 | 0 | 1049280 | 578688 | 3245800 | 0 | 2411500 | 195480 | 1347600 | 123566 | 2244000 | 0 | 12300 | 296970 | 151200 | 183352940.05 | 21813818 | 0 | 0 | 0 | 0 | 912000 | 0 | 0 | 233261.82 | 0 | 339408 | 278640 | 26014550 | 0 | 0 | 0 | 31854545 | 0 | 81285 | 0 | 231936 | 556704 | 0 | 0 | 76857 | 89323 | 232368 | 383310 | 23978 | 0 | 296368 | 3535727 | 0 | 3423927 | 0 | 3481264 | 0 | 9210036 | 0 | 28740 | 4618000 | 903272 | 1121015 | 172562 | 792614 | 0 | 0 | 0 | 37071.36 | 1247040 | 1402 | 135648 | 6611000 | 1554000 | 5365830 | 0 | 22160000 | 23316363.64 | 165600 | 171299463.82 | 354652403.87 | 76.62