## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-07-2026 | during | 09-07-2026 | during | 09-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 349 | 373 | 412 | 412 | 395 | 395 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 299 | 290 | 335 | 335 | 301.5 | 301.5 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 295 | 296 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 148 | 147 | 149.36 | 149.36 | 149 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 13 | 15.5 | 33 | 33 | 17 | 17 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 20 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 97 | 145 | 300 | 300 | 64 | 130 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 105 | 115 | 149 | 149 | 70 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 35 | 105 | 105 | 17 | 51 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 72 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 8 | 0 | 16 | 0 | 16 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 28 | 28 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 450 | 475 | 583 | 583 | 524.7 | 524.7 | AGC+FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143 | 136 | 143 | 143 | 143 | 143 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2165 | 2272.5 | 5566.22 | 5550.22 | 2233.2 | 2521.2
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 5 | 25.5 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 31 | 46 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 154 | 155 | 144 | 144 | 144 | 144 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 147 | 132 | 145 | 145 | 145 | 145 | Gas shortage
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 90 | 102 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 2 | 59 | 24 | 56 | 24 | 56 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 68 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 10 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 18 | 30 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0.61 | 0 | 0.72 | 0 | 0.72 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 32 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 27 | 54.36 | 54.36 | 54.36 | 0 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 105 | 106 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 38 | 92 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 300 | 301 | 1224 | 1224 | 612 | 612 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 49 | 57 | 15 | 32 | 15 | 32 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1130 | 1130 | 1150 | 1150 | 1125 | 1125 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2120.61 | 2325.86 | 3945.58 | 4074.86 | 2478.72 | 2657
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 188 | 216 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 270 | 300 | 350.01 | 350.01 | 350.01 | 350.01 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 220 | 240 | 342.01 | 342.01 | 342.01 | 342.01 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 215 | 220 | 393 | 393 | 363 | 363 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 37 | 37 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 53 | 53 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 122 | 55 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 17 | 40 | 40 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 93 | 93 | 163 | 163 | 95 | 95 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 193 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 142 | 160 | 84 | 76 | 148 | 148 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 85 | 98 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 51 | 115 | 115 | 34 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 9 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1466 | 1774.2 | 2732.44 | 2694.44 | 1978.47 | 2216.47
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-07-2026 | during | 09-07-2026 | during | 09-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 7.8 | 0 | 18 | 0 | 18 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.6 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 113 | 154 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 8.47 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 12 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 211.87 | 245 | 532.6 | 516.5 | 258.1 | 269
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 135 | 139 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 141 | 141 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 25 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 62 | 81 | 85 | 85 | 64 | 64 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 102 | 100 | 100 | 100 | 100 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 16 | 25 | 25 | 16 | 16 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 250 | 256 | 250 | 250 | 220 | 220 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1029 | 1085 | 1184 | 1184 | 1024 | 1024
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 848 | 859 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 35 | 35 | 35 | 35 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 105 | 105 | 32 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 14 | 0 | 55 | 0 | 55 | 0 | Liquid fuel shortage
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 150 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1194 | 1198 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2094 | 2368 | 3594.2 | 3539.2 | 3004.2 | 2949.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 909 | 600 | 500 | 600 | 1050 | 1050 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 1 | 48 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 64 | 64 | 130 | 130 | 65 | 65 | GT-1 & ST under maint
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1120 | 1185 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 278 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.2 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3407.64 | 2592.2 | 2424 | 2662 | 2761 | 2920 | 2919
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 17.87 | 0 | 48 | 0 | 48 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 32 | 32 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 146 | 145 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 127 | 122 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 127 | 0 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 320 | 311 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 19 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 1 | 113 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 2.85 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1372.55 | 1467.25 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 25.32 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 27 | 0 | 85 | 0 | 85 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2166.59 | 2495.45 | 3226.72 | 3027.12 | 2791.14 | 2768.54
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 39 | 41 | 40 | 40 | 39 | 39 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 200 | 181 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 6 | 49 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.9 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 5 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 50 | 0 | 132.54 | 0 | 132.54 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 302.9 | 386 | 665.54 | 502 | 531.54 | 403
System Total |  |  |  |  | 28843.2 | 29250.117 | 14148.17 | 15376.01 | 24109.3 | 23849.34 | 17219.37 | 17727.41
Forecast Scenario (09-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15250 |  | 0 |  | 15250
|  |  |  | 1:00 | 14770 |  | 0 |  | 14770
|  |  |  | 2:00 | 14590 |  | 0 |  | 14590
|  |  |  | 3:00 | 13770 |  | 0 |  | 13770
|  |  |  | 4:00 | 13440 |  | 0 |  | 13440
|  |  |  | 5:00 | 13060 |  | 0 |  | 13060
|  |  |  | 6:00 | 12630 |  | 0 |  | 12630
|  |  |  | 7:00 | 12820 |  | 0 |  | 12820
|  |  |  | 8:00 | 12790 |  | 0 |  | 12790
|  |  |  | 9:00 | 12870 |  | 0 |  | 12870
|  |  |  | 10:00 | 13340 |  | 0 |  | 13340
|  |  |  | 11:00 | 13710 |  | 0 |  | 13710
|  |  |  | 12:00 | 14090 |  | 0 |  | 14090
|  |  |  | 13:00 | 14380 |  | 0 |  | 14380
|  |  |  | 14:00 | 14060 |  | 0 |  | 14060
|  |  |  | 15:00 | 14020 |  | 0 |  | 14020
|  |  |  | 16:00 | 13830 |  | 0 |  | 13830
|  |  |  | 17:00 | 13660 |  | 0 |  | 13660
|  |  |  | 18:00 | 13480 |  | 0 |  | 13480
|  |  |  | 18:30 | 14000 |  | 0 |  | 14000
|  |  |  | 19:00 | 14760 |  | 0 |  | 14760
|  |  |  | 19:30 | 15580 |  | 0 |  | 15580
|  |  |  | 20:00 | 15610 |  | 0 |  | 15610
|  |  |  | 21:00 | 15500 |  | 0 |  | 15500
|  |  |  | 22:00 | 15300 |  | 0 |  | 15300
|  |  |  | 23:00 | 15100 |  | 0 |  | 15100
Probable Maximum Temperature: |  |  | 33.80°C
Probable Maximum Demand at Day Peak: |  |  | 14090.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15610.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 335.05 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:45 hrs on 09-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-07-2026 | [28 empty] | Date: | 08-07-2026 | [28 empty] | Date: | 08-07-2026 | [28 empty] | Date: | 08-07-2026 | [28 empty] | Date: | 08-07-2026 | [18 empty] | Date: | 08-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [18 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 35 | 28 | 132 | 148 | 245 | 55 | 35 | 162 | 0 | 0 | 288 | 480 | 0 | 35 | 301 | 0 | 0 | 0 | 143 | 16 | 21 | 0 | 0 | 15 | 16 | 0 | 0 | 45 | 34 | 45 | 37 | 12 | 12 | 0 | 146 | 108 | 9 | 725 | 0 | 0 | 50 | 8 | 66 | 141 | 0 | 0 | 0 | 612 | 0 | 12 | 0 | 215 | 270 | 220 | 51 | 0 | 200 | 0 | 70 | 94 | 31 | 27 | 19 | 65 | 130 | 8 | 0 | 39 | 315 | 0 | 254 | 0 | 0 | 144 | 0 | 16 | 0 | 62 | 28 | 143 | 0 | 101 | 0 | 69 | 0 | 156 | 0 | 0 | 0 | 24 | 7386 | 880 | 0 | 0 | 28 | 33 | 38 | 0 | 0 | 100 | 0 | 50 | 0 | 1130 | 0 | 0 | 0 | 1483.04 | 0 | 32 | 0 | 35 | 35 | 0 | 92 | 19 | 8 | 0 | 0 | 18 | 0 | 0 | 143 | 0 | 135 | 0 | 134 | 0 | 395 | 0 | 0 | 180 | 40 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 237 | 65 | 220 | 0 | 1017 | 1130 | 17 | 7854.04 | 15240.04 | 80.26
01:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 28 | 75 | 149 | 245 | 55 | 35 | 54 | 0 | 0 | 294 | 485 | 0 | 0 | 315 | 0 | 0 | 0 | 143 | 16 | 19 | 0 | 0 | 17 | 16 | 0 | 0 | 40 | 34 | 45 | 37 | 12 | 12 | 0 | 148 | 109 | 12 | 725 | 0 | 0 | 50 | 8 | 71 | 141 | 0 | 0 | 0 | 460 | 0 | 12 | 0 | 215 | 270 | 220 | 51 | 0 | 202 | 0 | 0 | 93 | 48 | 16.8 | 19 | 98 | 134 | 8 | 0 | 39 | 315 | 0 | 255 | 0 | 0 | 145 | 0 | 16 | 0 | 62 | 28 | 144 | 0 | 102 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 19 | 6840.8 | 848 | 0 | 0 | 28 | 38 | 38 | 0 | 0 | 50 | 0 | 15 | 0 | 1162 | 0 | 0 | 0 | 1479.53 | 0 | 32 | 0 | 70 | 61 | 0 | 0 | 19 | 8 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 136 | 0 | 134 | 0 | 394 | 0 | 0 | 180 | 39 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 1050 | 1147 | 17 | 7825.53 | 14666.33 | 80.36
02:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 17 | 35 | 149 | 245 | 55 | 35 | 0 | 0 | 0 | 284 | 460 | 0 | 0 | 295 | 0 | 0 | 0 | 143 | 16 | 20 | 0 | 0 | 60 | 16 | 0 | 0 | 51 | 0 | 0 | 37 | 12 | 12 | 0 | 148 | 107 | 15 | 1030 | 0 | 0 | 50 | 0 | 98 | 141 | 0 | 0 | 0 | 315 | 0 | 12 | 0 | 215 | 270 | 220 | 51 | 0 | 202 | 0 | 0 | 93 | 78 | 0 | 19 | 97 | 128 | 0 | 0 | 39 | 305 | 0 | 244 | 0 | 0 | 137 | 0 | 0 | 0 | 62 | 25 | 143 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6797 | 848 | 0 | 0 | 0 | 10 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 1472.85 | 0 | 0 | 0 | 70 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 137 | 0 | 134 | 0 | 404 | 0 | 0 | 180 | 39 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 272 | 65 | 220 | 0 | 1015 | 1155 | 17 | 7690.85 | 14487.85 | 80.46
03:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 34 | 148 | 180 | 55 | 0 | 0 | 0 | 0 | 290 | 400 | 0 | 0 | 307 | 0 | 0 | 0 | 143 | 17 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 36 | 0 | 12 | 0 | 148 | 107 | 15 | 1135 | 0 | 0 | 6 | 0 | 68 | 141 | 0 | 0 | 0 | 300 | 0 | 12 | 0 | 215 | 270 | 220 | 51 | 0 | 202 | 0 | 0 | 94 | 17 | 0 | 19 | 17 | 126 | 0 | 0 | 39 | 305 | 0 | 244 | 0 | 0 | 131 | 0 | 0 | 0 | 62 | 25 | 143 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6421 | 848 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 1392.34 | 0 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 139 | 0 | 134 | 0 | 410 | 0 | 0 | 180 | 39 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 65 | 220 | 0 | 824 | 1170 | 17 | 7300.34 | 13721.34 | 80.56
04:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 34 | 148 | 180 | 55 | 0 | 0 | 0 | 0 | 287 | 445 | 0 | 0 | 307 | 0 | 0 | 0 | 143 | 17 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 36 | 0 | 12 | 0 | 148 | 103 | 15 | 1135 | 0 | 0 | 0 | 0 | 4 | 141 | 0 | 0 | 0 | 300 | 0 | 12 | 0 | 215 | 270 | 220 | 51 | 0 | 207 | 0 | 0 | 94 | 0 | 0 | 19 | 0 | 118 | 0 | 0 | 39 | 310 | 0 | 244 | 0 | 0 | 140 | 0 | 0 | 0 | 62 | 25 | 142 | 0 | 102 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6355 | 848 | 0 | 0 | 0 | 3 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1215 | 0 | 0 | 0 | 1346.71 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 139 | 0 | 135 | 0 | 410 | 0 | 0 | 180 | 38 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 276 | 65 | 220 | 0 | 735 | 1170 | 0 | 7050.71 | 13405.71 | 80.66
05:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 34 | 148 | 80 | 30 | 0 | 0 | 0 | 0 | 291 | 470 | 0 | 0 | 300 | 0 | 0 | 0 | 105 | 17 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 12 | 0 | 146 | 66 | 15 | 1135 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 300 | 0 | 12 | 0 | 215 | 270 | 220 | 51 | 0 | 208 | 0 | 0 | 94 | 0 | 0 | 19 | 0 | 114 | 0 | 0 | 0 | 315 | 0 | 244 | 0 | 0 | 141 | 0 | 0 | 0 | 62 | 25 | 140 | 0 | 103 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6034 | 848 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1191 | 0 | 0 | 0 | 1316.11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 141 | 0 | 141 | 0 | 414 | 0 | 0 | 180 | 38 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 65 | 220 | 0 | 771 | 1170 | 0 | 7028.11 | 13062.11 | 80.76
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 34 | 148 | 0 | 30 | 0 | 0 | 0 | 0 | 296 | 480 | 0 | 0 | 312 | 0 | 0 | 0 | 68 | 17 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 12 | 0.03 | 144 | 33 | 10 | 1135 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 215 | 270 | 220 | 51 | 0 | 208 | 0 | 0 | 93 | 0 | 0 | 19 | 0 | 114 | 0 | 1 | 0 | 310 | 0 | 244 | 0 | 0 | 139 | 0 | 8 | 0 | 62 | 25 | 141 | 0 | 102 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 6 | 5879.03 | 848 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.19 | 1036 | 0 | 0 | 0 | 1315.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 141 | 0 | 142 | 0 | 414 | 0 | 0 | 180 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.01 | 0 | 277 | 64 | 220 | 0 | 759 | 1170 | 0 | 6792.26 | 12671.29 | 80.86
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 34 | 148 | 0 | 15 | 0 | 0 | 0 | 0 | 285 | 510 | 0 | 0 | 308 | 0 | 0 | 0 | 68 | 16 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0.26 | 144 | 0 | 12 | 1135 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 215 | 270 | 220 | 51 | 0 | 202 | 0 | 0 | 93 | 0 | 0 | 19 | 0 | 114 | 0 | 6 | 0 | 315 | 0 | 244 | 0 | 0 | 140 | 0 | 16 | 0 | 62 | 25 | 144 | 0 | 101 | 13 | 49 | 0.33 | 48 | 0 | 0.1 | 1.81 | 11 | 5825.5 | 848 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7.81 | 1000 | 0 | 0 | 0 | 1393.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38 | 0 | 0 | 0 | 0.13 | 148 | 0 | 141 | 0 | 141 | 0 | 414 | 0 | 0.01 | 180 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 3 | 0.03 | 0 | 226 | 64 | 220 | 0 | 1017 | 1170 | 0 | 7049.65 | 12875.15 | 80.96
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 35 | 148 | 0 | 15 | 0 | 0 | 0 | 0 | 298 | 480 | 0 | 0 | 317 | 0 | 0 | 1 | 68 | 16 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0.16 | 144 | 0 | 2 | 1130 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 301 | 2 | 0 | 0 | 215 | 270 | 220 | 51 | 0 | 200 | 0 | 0 | 93 | 0 | 0 | 19 | 0 | 120 | 0 | 2 | 0 | 305 | 0 | 244 | 0 | 0 | 134 | 2 | 0 | 0 | 62 | 25 | 143 | 0 | 103 | 17 | 49 | 3.1 | 48 | 0 | 0.4 | 7.21 | 12 | 5810.87 | 848 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10.32 | 995 | 0 | 0 | 0 | 1370.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.49 | 4 | 0 | 0 | 8.85 | 148 | 0 | 141 | 0 | 140 | 0 | 403 | 0 | 0.87 | 180 | 38 | 0 | 2 | 0 | 0 | 0 | 0 | 0.6 | 5 | 0.05 | 0 | 228 | 64 | 220 | 0 | 1018 | 1175 | 0 | 7040.63 | 12851.5 | 81.11
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 9 | 35 | 147 | 67 | 16 | 0 | 17 | 0 | 0 | 291 | 495 | 0 | 0 | 307 | 0 | 0 | 3 | 76 | 14.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0.21 | 144 | 4 | 2 | 1130 | 0 | 0 | 0 | 0 | 2 | 147 | 0 | 0 | 0 | 301 | 2 | 6 | 0 | 215 | 270 | 220 | 51 | 0 | 195 | 0 | 0 | 94 | 1 | 0 | 19 | 20 | 122 | 0 | 2 | 0 | 310 | 0 | 250 | 0 | 0 | 137 | 3 | 8 | 0 | 62 | 25 | 141 | 0 | 101 | 17 | 49 | 7.1 | 48 | 0 | 0.6 | 10.23 | 12 | 5983.64 | 848 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28.65 | 1050 | 0 | 0 | 0 | 1386.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.03 | 22 | 0 | 0 | 22.14 | 148 | 0 | 141 | 0 | 138 | 0 | 300 | 0 | 1.58 | 200 | 38 | 0 | 3 | 0 | 0 | 0 | 0 | 0.5 | 15 | 0.11 | 0 | 179 | 64 | 180 | 0 | 1000 | 1170 | 0 | 6980.75 | 12964.39 | 81.31
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 37 | 148 | 97 | 55 | 17 | 50 | 0 | 0 | 298 | 455 | 0 | 0 | 308 | 0 | 0 | 7 | 143 | 14 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 8 | 12 | 0.11 | 144 | 57 | 2 | 1130 | 0 | 0 | 17 | 0 | 35 | 147 | 0 | 0 | 0 | 301 | 2 | 50 | 0 | 215 | 270 | 220 | 43 | 0 | 205 | 0 | 0 | 94 | 15 | 0 | 19 | 50 | 122 | 8 | 1 | 0 | 310 | 0 | 243 | 0 | 0 | 132 | 3 | 8 | 0 | 62 | 25 | 143 | 0 | 101 | 17 | 49 | 9.95 | 48 | 0 | 1.3 | 11.23 | 7 | 6375.59 | 848 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 1105 | 0 | 0 | 0 | 1365.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.23 | 52 | 0 | 0 | 20.12 | 148 | 0 | 135 | 0 | 136 | 0 | 340 | 0 | 1.73 | 200 | 38 | 0 | 8 | 0 | 0 | 0 | 0 | 0.9 | 21 | 0.11 | 0 | 182 | 64 | 220 | 0 | 978 | 1130 | 0 | 7068.35 | 13443.94 | 81.5
11:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 17 | 68 | 148 | 97 | 55 | 35 | 72 | 0 | 0 | 303 | 465 | 0 | 0 | 297 | 0 | 0 | 8 | 143 | 14 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 12 | 12 | 0.15 | 154 | 101 | 2 | 1130 | 0 | 0 | 19 | 0 | 66 | 147 | 0 | 0 | 0 | 303 | 0 | 58 | 0 | 215 | 270 | 220 | 43 | 0 | 198 | 0 | 0 | 94 | 17 | 0 | 19 | 70 | 132 | 8 | 3 | 0 | 310 | 0 | 250 | 0 | 0 | 132 | 3 | 8 | 0 | 62 | 25 | 140 | 0 | 101 | 17 | 58 | 9.2 | 113 | 0 | 0.9 | 9.72 | 6 | 6691.97 | 848 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44 | 1123 | 0 | 0 | 0 | 1343.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.07 | 63 | 0 | 0 | 21.32 | 144 | 0 | 132 | 0 | 132 | 0 | 334 | 0 | 2.04 | 200 | 39 | 0 | 6 | 0 | 0 | 0 | 0 | 1.9 | 43 | 0.64 | 0 | 278 | 64 | 220 | 0 | 930 | 1095 | 0 | 7119.92 | 13811.89 | 81.81
12:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 17 | 105 | 148 | 97 | 55 | 35 | 72 | 0 | 0 | 299 | 450 | 0 | 0 | 295 | 0 | 0 | 8 | 143 | 13 | 20 | 0 | 0 | 38 | 16 | 0 | 0 | 49 | 0 | 2 | 27 | 12 | 12 | 0.61 | 154 | 105 | 2 | 1130 | 0 | 0 | 31 | 5 | 90 | 147 | 0 | 0 | 0 | 300 | 0 | 122 | 0 | 215 | 270 | 220 | 43 | 0 | 188 | 0 | 0 | 93 | 17 | 0 | 19 | 85 | 142 | 43 | 9 | 0 | 305 | 0 | 250 | 0 | 0 | 135 | 2 | 8 | 0 | 62 | 25 | 141 | 0 | 101 | 17 | 58 | 7.8 | 113 | 0 | 1.6 | 8.47 | 6 | 6992.48 | 848 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 1194 | 0 | 0 | 0 | 1372.55 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 17.87 | 27 | 0 | 0 | 25.32 | 146 | 0 | 127 | 0 | 127 | 0 | 320 | 0 | 2.85 | 200 | 39 | 0 | 5 | 6 | 0 | 0 | 0 | 2.9 | 50 | 0.2 | 1 | 278 | 64 | 220 | 0 | 909 | 1120 | 0 | 7155.69 | 14148.17 | 82.4
13:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 17 | 118 | 147 | 97 | 55 | 35 | 72 | 0 | 0 | 289 | 440 | 0 | 0 | 283 | 0 | 0 | 7 | 143 | 13 | 19 | 0 | 0 | 89 | 16 | 0 | 0 | 22 | 0 | 34 | 36 | 12 | 12 | 0.34 | 154 | 105 | 7 | 1130 | 0 | 0 | 49 | 14 | 96 | 145 | 0 | 0 | 0 | 300 | 0 | 150 | 0 | 215 | 270 | 200 | 51 | 0 | 195 | 0 | 0 | 93 | 17 | 0 | 19 | 97 | 136 | 52.2 | 19 | 16 | 305 | 0 | 250 | 0 | 0 | 133 | 0 | 0 | 0 | 62 | 30 | 142 | 0 | 102 | 17 | 59 | 4.01 | 113 | 0 | 0.8 | 7.08 | 6 | 7125.43 | 849 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13 | 1205 | 0 | 0 | 0 | 1354.19 | 0 | 0 | 0 | 20 | 35 | 0 | 0 | 0 | 30 | 25.86 | 66 | 0 | 0 | 27.39 | 144 | 0 | 125 | 0 | 0 | 0 | 317 | 0 | 2.42 | 200 | 39 | 70 | 5 | 76 | 0 | 0 | 0 | 2.1 | 27 | 0.23 | 32 | 275 | 64 | 220 | 0 | 850 | 1160 | 17 | 7289.19 | 14414.62 | 84.6
14:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 17 | 17 | 111 | 130 | 97 | 55 | 35 | 17 | 0 | 0 | 284 | 420 | 0 | 0 | 291 | 0 | 0 | 5 | 143 | 15 | 19 | 0 | 0 | 90 | 16 | 0 | 0 | 32 | 0 | 40 | 50 | 12 | 12 | 0.59 | 156 | 104 | 2 | 1130 | 0 | 0 | 50 | 22 | 100 | 145 | 0 | 0 | 0 | 303 | 4 | 78 | 0 | 215 | 270 | 200 | 51 | 0 | 204 | 0 | 0 | 93 | 17 | 0 | 19 | 97 | 142 | 52.2 | 16 | 17 | 300 | 0 | 239 | 0 | 0 | 129 | 0 | 0 | 0 | 62 | 30 | 143 | 0 | 101 | 17 | 59 | 6.07 | 106 | 0 | 0.6 | 15.08 | 6 | 6980.54 | 848 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 1190 | 0 | 0 | 0 | 1323.37 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 52.2 | 17.49 | 39 | 0 | 0 | 23.11 | 144 | 0 | 125 | 0 | 0 | 0 | 300 | 0 | 1.54 | 195 | 42 | 95 | 27 | 104 | 0 | 0 | 0 | 0.9 | 72 | 0.09 | 32 | 275 | 64 | 220 | 0 | 600 | 1145 | 17 | 7084.7 | 14065.24 | 84.4
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 17 | 17 | 71 | 129 | 97 | 28 | 35 | 17 | 0 | 0 | 301 | 435 | 0 | 0 | 300 | 0 | 0 | 3 | 129 | 15 | 19 | 0 | 0 | 91 | 16 | 0 | 0 | 50 | 0 | 40 | 54.36 | 12 | 12 | 0.72 | 160 | 105 | 0 | 1130 | 0 | 0 | 50 | 17 | 99 | 131 | 0 | 0 | 0 | 302 | 0 | 55 | 0 | 220 | 270 | 200 | 35 | 0 | 202 | 0 | 0 | 93 | 29 | 0 | 19 | 97 | 126 | 52.2 | 0 | 17 | 305 | 0 | 284 | 0 | 0 | 126 | 1 | 16 | 0 | 62 | 30 | 142 | 0 | 101 | 17 | 59 | 5 | 105 | 0 | 0.3 | 3.86 | 6 | 6901.44 | 848 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9 | 1188 | 0 | 0 | 0 | 1490.33 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 52.2 | 8.05 | 34 | 0 | 0 | 13.33 | 145 | 0 | 125 | 0 | 0 | 0 | 300 | 0 | 1.18 | 200 | 41 | 95 | 15 | 34 | 0 | 0 | 0 | 7.1 | 65 | 0.04 | 32 | 248 | 64 | 220 | 0 | 614 | 1120 | 17 | 7109.23 | 14010.67 | 84.45
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 17 | 17 | 55 | 129 | 97 | 15 | 17 | 17 | 0 | 0 | 322 | 420 | 0 | 17 | 280 | 0 | 0 | 2 | 113 | 15 | 19 | 0 | 0 | 89 | 32 | 0 | 0 | 42 | 0 | 62 | 54.36 | 12 | 12 | 0.26 | 162 | 103 | 0 | 1130 | 0 | 0 | 50 | 17 | 97 | 131 | 0 | 0 | 0 | 302 | 1 | 30 | 0 | 220 | 270 | 200 | 37 | 0 | 202 | 0 | 0 | 93 | 51 | 0 | 14 | 98 | 120 | 52.2 | 4 | 17 | 305 | 0 | 266 | 0 | 0 | 129 | 0 | 16 | 0 | 60 | 30 | 143 | 0 | 101 | 17 | 59 | 2.09 | 105 | 0 | 0.2 | 3.84 | 6 | 6824.95 | 848 | 0 | 0 | 0 | 3 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 1114 | 0 | 0 | 0 | 1473.22 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 52.2 | 4.09 | 18 | 0 | 0 | 6.11 | 145 | 0 | 125 | 0 | 0 | 0 | 310 | 0 | 0.64 | 170 | 41 | 115 | 12 | 34 | 0 | 0 | 0 | 7 | 39 | 0.03 | 32 | 247 | 64 | 220 | 0 | 613 | 1130 | 17 | 6966.29 | 13791.24 | 84.52
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 17 | 17 | 35 | 145 | 95 | 15 | 35 | 17 | 0 | 0 | 290 | 405 | 0 | 35 | 290 | 0 | 0 | 2 | 73 | 15 | 19 | 0 | 0 | 45 | 32 | 0 | 0 | 36 | 0 | 59 | 54.36 | 12 | 12 | 0.24 | 160 | 104 | 3 | 1135 | 0 | 0 | 50 | 25.5 | 96 | 132 | 0 | 0 | 0 | 301 | 1 | 20 | 0 | 220 | 270 | 200 | 41 | 0 | 200 | 0 | 0 | 93 | 51 | 0 | 14 | 97 | 134 | 16 | 5 | 17 | 300 | 0 | 268 | 0 | 0 | 129 | 1 | 0 | 0 | 75 | 30 | 141 | 0 | 101 | 17 | 59 | 0.28 | 115 | 0 | 0.1 | 0.87 | 6 | 6692.35 | 848 | 0 | 0 | 33 | 28 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 1102 | 0 | 0 | 0 | 1490.37 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 16 | 4.59 | 12 | 0 | 0 | 2.35 | 145 | 0 | 125 | 0 | 0 | 0 | 312 | 0 | 0.29 | 183 | 42 | 115 | 7 | 34 | 0 | 0 | 0 | 0.7 | 34 | 0.06 | 32 | 246 | 64 | 220 | 0 | 600 | 1085 | 17 | 6924.36 | 13616.71 | 84.59
18:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 17 | 17 | 35 | 146 | 95 | 15 | 35 | 17 | 0 | 0 | 292 | 385 | 0 | 35 | 295 | 0 | 0 | 1 | 72 | 15 | 18 | 0 | 0 | 45 | 32 | 0 | 0 | 53 | 0 | 59 | 54.36 | 12 | 12 | 0.02 | 161 | 105 | 10 | 1135 | 0 | 0 | 46 | 17 | 99 | 132 | 0 | 0 | 0 | 301 | 0 | 20 | 0 | 220 | 270 | 200 | 46 | 0 | 200 | 0 | 12 | 93 | 51 | 8 | 14 | 97 | 128 | 16 | 1 | 17 | 305 | 0 | 268 | 0 | 0 | 128 | 0 | 0 | 0 | 80 | 30 | 139 | 0 | 101 | 17 | 59 | 0 | 115 | 0 | 0 | 0.56 | 6 | 6796.94 | 848 | 0 | 0 | 33 | 32 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 1032 | 0 | 0 | 0 | 1374.12 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 16 | 2.08 | 5 | 0 | 0 | 0.48 | 145 | 0 | 125 | 0 | 0 | 0 | 307 | 0 | 0.04 | 181 | 41 | 115 | 2 | 34 | 0 | 0 | 0 | 0.7 | 19 | 0.01 | 38 | 218 | 64 | 180 | 0 | 600 | 1015 | 17 | 6568.43 | 13365.37 | 84.66
19:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 17 | 17 | 34 | 146 | 105 | 15 | 35 | 54 | 0 | 0 | 303 | 440 | 0 | 35 | 296 | 0 | 0 | 0 | 88 | 15.5 | 19 | 0 | 0 | 53 | 32 | 0 | 0 | 56 | 0 | 59 | 54.36 | 12 | 12 | 0 | 158 | 106 | 15 | 1135 | 0 | 0 | 46 | 17 | 100 | 132 | 0 | 0 | 0 | 302 | 0 | 21 | 0 | 220 | 270 | 200 | 51 | 0 | 209 | 0 | 28 | 93 | 73 | 9 | 14 | 98 | 160 | 20 | 0 | 17 | 305 | 0 | 254 | 0 | 0 | 134 | 0 | 8 | 0 | 81 | 30 | 140 | 0 | 102 | 17 | 59 | 0 | 119 | 0 | 0 | 0 | 6 | 7078.86 | 847 | 0 | 0 | 37 | 52 | 38 | 0 | 0 | 0 | 0 | 34 | 0 | 1050 | 0 | 0 | 0 | 1482.78 | 0 | 0 | 0 | 110 | 77 | 0 | 80 | 16 | 52.2 | 0 | 0 | 18 | 0 | 0 | 144 | 0 | 125 | 0 | 0 | 0 | 305 | 0 | 0 | 170 | 41 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 278 | 64 | 220 | 0 | 600 | 1000 | 0 | 7037.98 | 14116.84 | 84.73
19:30 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 35 | 17 | 88 | 146 | 145 | 15 | 35 | 72 | 0 | 0 | 296 | 450 | 0 | 35 | 295 | 0 | 0 | 0 | 123 | 15.5 | 19 | 0 | 0 | 90 | 32 | 0 | 0 | 53 | 0 | 59 | 54.36 | 12 | 12 | 0 | 156 | 105 | 10 | 1135 | 0 | 0 | 46 | 17 | 96 | 132 | 0 | 0 | 0 | 302 | 0 | 50 | 0 | 220 | 270 | 200 | 51 | 0 | 198 | 0 | 51 | 93 | 193 | 9 | 14 | 99 | 164 | 52.2 | 0 | 17 | 310 | 0 | 253 | 0 | 0 | 137 | 0 | 16 | 0 | 81 | 30 | 143 | 0 | 102 | 17 | 68 | 0 | 152 | 0 | 0 | 0 | 6 | 7542.06 | 859 | 0 | 0 | 33 | 46 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1120 | 0 | 0 | 0 | 1475.55 | 0 | 0 | 0 | 113 | 113 | 0 | 93 | 21 | 52.2 | 0 | 0 | 19 | 0 | 0 | 145 | 0 | 122 | 0 | 0 | 0 | 311 | 0 | 0 | 180 | 41 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 64 | 220 | 0 | 600 | 1130 | 0 | 7349.75 | 14891.81
20:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 35 | 17 | 98 | 146 | 145 | 15 | 35 | 72 | 0 | 0 | 292 | 460 | 0 | 35 | 296 | 0 | 0 | 0 | 123 | 15.5 | 19 | 0 | 0 | 89 | 32 | 0 | 0 | 64 | 0 | 59 | 54.36 | 12 | 12 | 0 | 155 | 107 | 10 | 1135 | 0 | 0 | 46 | 17 | 99 | 132 | 0 | 0 | 0 | 302 | 0 | 50 | 0 | 220 | 270 | 200 | 51 | 0 | 198 | 0 | 51 | 93 | 190 | 9 | 19 | 98 | 164 | 52.2 | 0 | 17 | 310 | 0 | 256 | 0 | 0 | 137 | 0 | 16 | 0 | 81 | 30 | 141 | 0 | 102 | 17 | 68 | 0 | 152 | 0 | 0 | 0 | 6 | 7577.06 | 859 | 0 | 0 | 33 | 41 | 38 | 0 | 0 | 30 | 0 | 50 | 0 | 1173 | 0 | 0 | 0 | 1474.25 | 0 | 14 | 0 | 113 | 113 | 0 | 94 | 27 | 52.2 | 0 | 0 | 19 | 0 | 0 | 145 | 0 | 122 | 0 | 0 | 0 | 311 | 0 | 0 | 180 | 41 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 64 | 220 | 0 | 600 | 1140 | 0 | 7472.45 | 15049.51 | 84.8
21:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 35 | 17 | 115 | 147 | 145 | 15 | 35 | 72 | 0 | 0 | 290 | 475 | 0 | 35 | 296 | 0 | 0 | 0 | 136 | 15.5 | 20 | 0 | 0 | 92 | 32 | 0 | 0 | 57 | 0 | 59 | 54.36 | 12 | 12 | 0 | 155 | 106 | 10 | 1130 | 0 | 0 | 46 | 25.5 | 102 | 132 | 0 | 0 | 0 | 301 | 0 | 55 | 0 | 220 | 300 | 240 | 51 | 0 | 216 | 0 | 51 | 93 | 193 | 9 | 19 | 98 | 160 | 52.2 | 0 | 17 | 320 | 0 | 256 | 0 | 0 | 139 | 0 | 16 | 0 | 81 | 30 | 141 | 0 | 102 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 6 | 7702.56 | 859 | 0 | 0 | 33 | 40 | 38 | 0 | 0 | 150 | 0 | 50 | 0 | 1198 | 0 | 0 | 0 | 1467.25 | 0 | 32 | 0 | 113 | 113 | 0 | 94 | 27 | 52.2 | 0 | 0 | 19 | 0 | 0 | 145 | 0 | 122 | 0 | 0 | 0 | 311 | 0 | 0 | 181 | 41 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 64 | 220 | 0 | 600 | 1185 | 0 | 7673.45 | 15376.01 | 84.75
22:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 35 | 17 | 115 | 147 | 145 | 15 | 35 | 72 | 0 | 0 | 302 | 460 | 0 | 35 | 295 | 0 | 0 | 0 | 51 | 15.5 | 20 | 0 | 0 | 89 | 16 | 0 | 0 | 32 | 0 | 59 | 54.36 | 12 | 12 | 0 | 155 | 105 | 15 | 1130 | 0 | 0 | 49 | 25.5 | 100 | 132 | 0 | 0 | 0 | 302 | 0 | 53 | 0 | 220 | 300 | 240 | 51 | 0 | 216 | 0 | 0 | 93 | 192 | 9 | 19 | 98 | 156 | 52.2 | 0 | 17 | 310 | 0 | 256 | 0 | 0 | 137 | 0 | 16 | 0 | 81 | 30 | 141 | 0 | 102 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 0 | 7473.56 | 859 | 0 | 0 | 33 | 36 | 38 | 0 | 0 | 150 | 0 | 50 | 0 | 1197 | 0 | 0 | 0 | 1472.05 | 0 | 32 | 0 | 35 | 50 | 0 | 94 | 27 | 52.2 | 0 | 0 | 19 | 0 | 0 | 145 | 0 | 122 | 0 | 0 | 0 | 318 | 0 | 0 | 181 | 42 | 115 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 64 | 220 | 0 | 600 | 1190 | 17 | 7555.25 | 15028.81 | 84.8
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17 | 17 | 74 | 15 | 146 | 15 | 35 | 54 | 0 | 0 | 299 | 455 | 0 | 35 | 300 | 0 | 0 | 0 | 51 | 15.5 | 20 | 0 | 0 | 91 | 16 | 0 | 0 | 46 | 0 | 59 | 54.36 | 12 | 12 | 0 | 142 | 106 | 17 | 1130 | 0 | 0 | 50 | 0 | 99 | 133 | 0 | 0 | 0 | 300 | 0 | 36 | 0 | 220 | 300 | 240 | 51 | 0 | 216 | 10 | 2 | 93 | 195 | 9 | 19 | 97 | 164 | 52.2 | 0 | 17 | 310 | 0 | 256 | 0 | 0 | 135 | 0 | 16 | 0 | 81 | 30 | 141 | 0 | 102 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 0 | 7198.06 | 859 | 0 | 0 | 33 | 41 | 38 | 0 | 0 | 150 | 0 | 50 | 0 | 1195 | 0 | 0 | 0 | 1494.14 | 0 | 32 | 0 | 35 | 50 | 0 | 94 | 27 | 52.2 | 0 | 0 | 19 | 0 | 0 | 145 | 0 | 122 | 0 | 0 | 0 | 312 | 0 | 0 | 181 | 43 | 115 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 64 | 220 | 0 | 600 | 1190 | 17 | 7575.34 | 14773.4 | 84.65
Total KWH | 0 | 827520 | 268800 | 0 | 0 | 0 | 0 | 0 | 7934400 | 0 | 0 | 260280 | 339120 | 1485072 | 3281280 | 2791615 | 802814 | 538342 | 812160 | 0 | 0 | 7139869 | 10931248 | 0 | 270208 | 7274276 | 0 | 0 | 46220 | 2680800 | 363000 | 468000 | 0 | 0 | 1125327 | 341236 | 0 | 0 | 983040 | 50645 | 678672 | 839738 | 192960 | 254400 | 4203 | 3603585 | 2169500 | 213600 | 26181818.18 | 0 | 0 | 788640 | 213316.2 | 1709527 | 3315996 | 0 | 0 | 0 | 7538181 | 12015 | 914981 | 0 | 5252000 | 6964900 | 5372000 | 1102792 | 0 | 4991000 | 17136 | 218880 | 2223611 | 1401120 | 81480 | 450070 | 1626780 | 3182400 | 593664 | 84682 | 366688 | 7470000 | 0 | 6140000 | 0 | 0 | 3242372.73 | 18266 | 194688 | 0 | 1617600 | 660960 | 3257000 | 0 | 2433320 | 317880 | 1335600 | 50580 | 2172000 | 0 | 6200 | 79840 | 191520 | 162763434.11 | 20541818 | 0 | 0 | 260160 | 321152 | 912000 | 0 | 0 | 641407 | 0 | 287856 | 174240 | 27360000 | 0 | 0 | 0 | 33942180 | 0 | 175762 | 0 | 809184 | 1209504 | 0 | 532304 | 137791 | 483691 | 109288 | 334220 | 110130 | 0 | 169648 | 3544091 | 0 | 3337382 | 0 | 1825736 | 0 | 8350254.5 | 0 | 15720 | 4586000 | 943418 | 1552875 | 93653 | 836640 | 0 | 0 | 0 | 20371.56 | 426240 | 945 | 574272 | 6370000 | 1534000 | 5361860 | 0 | 18661818 | 27735272.73 | 242400 | 174525283.79 | 337288717.9

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14148.17 | MW | 12:00 Hr. | Energy Generated |  |  | 337.2887 |  | MKWHr.
| Day Peak Demand |  |  | 14199.17 | MW | 12:00 Hr. | Energy Unserverd |  |  | 4.828 |  | MKWHr.
| Evening Peak Generation |  |  | 15376.01 | MW | 21:00 Hr. | Energy Demand |  |  | 342.1167 |  | MKWHr.
| Evening Peak Demand |  |  | 15737.01 | MW | 21:00 Hr. | Maximum Temperature |  |  | 29.9 |  | °C
| Minimum Generation of the Day |  |  | 12671.29 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 825.44 |  | MMCFD
| Maximum Generation of the Day |  |  | 15376.01 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.7788 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.1108 | 0 | 14.358 | 0 | 0 | 0.04622 | 0 | 0 | 48.515 | Gas | 112.9832 | Gas | 378200848.2066
| Chattogram Zone |  |  | 3.5296 | 33.72 | 8.364 | 0 | 3.6036 | 0.016218 | 0 | 0.98304 | 50.2164 | Coal | 119.3765 | Coal | 796518268.7063
| Cumilla Zone |  |  | 26.3735 | 0 | 5.2036 | 0 | 0 | 0.084682 | 3.1824 | 0 | 34.8442 | HFO | 39.4763 | HFO | 690434694.202
| Mymensingh Zone |  |  | 0 | 0 | 4.017 | 0 | 0 | 0.13662 | 0 | 0 | 4.1536 | HSD | 0.64141 | HSD | 12956421.4
| Sylhet Zone |  |  | 25.0159 | 0 | 0 | 0 | 0 | 0.018266 | 0 | 0 | 25.0342 | Hydro | 3.6036 | Hydro | 13729658.85
| Khulna Zone |  |  | 0 | 27.36 | 0.86917 | 0.64141 | 0 | 0.17424 | 21.4538 | 0 | 50.4986 | Solar | 1.6463 | Solar | 26423152.0612
| Barishal Zone |  |  | 6.8959 | 52.7671 | 0.81667 | 0 | 0 | 0.000945 | 0 | 0 | 60.4806 | Import | 58.5784 | Import | 353703287.48
| Rajshahi Zone |  |  | 17.0575 | 0 | 3.4584 | 0 | 0 | 0.62888 | 33.9422 | 0 | 55.0869 | Wind | 0.98304 | Wind | 14460518.4
| Rangpur Zone |  |  | 0 | 5.5294 | 2.3895 | 0 | 0 | 0.54026 | 0 | 0 | 8.4592
| Total |  |  | 112.9832 | 119.3765 | 39.4763 | 0.64141 | 3.6036 | 1.6463 | 58.5784 | 0.98304 | 337.2887
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 378200848.2066 |  | Hydro | 13729658.85
|  |  |  | Coal | 796518268.7063 |  | Solar | 26423152.0612
|  |  |  | HFO | 690434694.202 |  | Import | 353703287.48
|  |  |  | HSD | 12956421.4 |  | Wind | 14460518.4
[5 empty] | Total: | 228,64,26,849 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.5418 | Peak Hr Flow | 859.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 61096309.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.9422 | Peak Hr Flow | 1467.25 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2539 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.1824 | Peak Hr Flow | 160.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 3166 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 57.6664 | Peak Hr Flow | 2486.25 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 40 |  | 5738
|  |  |  | Chattogram |  | 0 |  | 1061
|  |  |  | Cumilla |  | 93 |  | 1474
|  |  |  | Mymensingh |  | 174 |  | 1315
|  |  |  | Sylhet |  | 38 |  | 635
|  |  |  | Khulna |  | 0 |  | 1898
|  |  |  | Barishal |  | 0 |  | 438
|  |  |  | Rajshahi |  | 0 |  | 1564
|  |  |  | Rangpur |  | 0 |  | 1031
|  |  |  | Total |  | 345 |  | 15154
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Fenchugonj CCPP Phase-2 GT-4 |  |  | 35
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Karnaphuli Hydro PP Unit-5 |  |  | 50
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 350 |  |  |  | Total | 35
|  |  |  | Total Unavailable Capacity |  |  |  | 385
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:11 | 18:22 | Madunaghat-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Requested by korerhat
| 09:13 | 18:21 | Korerhat 400/230/132kV S/S Meghnaghat-2 Project Work S/D Due to Project Work
| 09:21 | 18:01 | Korerhat 400/230/132kV S/S ATR-3(7103T) LT Project Work S/D Due to Project Work
| 09:22 | 14:37 | Korerhat 400/230/132kV S/S ATR-3(7103T) HT Project Work S/D Due to Project Work
| 09:53 | 09:55 | Bhulta-Haripur 230 kV Ckt-1 Tripped from Haripur 230/132kV end showing
Micromho:DIRL Optimho: DEF Delay relays.
| 09:53 | 10:57 | Bhulta-Haripur 230 kV Ckt-2 Tripped from Haripur 230/132kV end showing Relay did not
picked up. relays.
| 09:56 | 12:41 | BIPTC S/S 20DF44 Scheduled S/D Due to Tripped by PRD Operated, hence corrective
maintenance is required.
| 10:12 | 15:40 | Kachua 230/132/33kV S/S Laksam CKT-1 Scheduled S/D Due to SAS signal checking by spmd
| 10:15 | 18:59 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 LT Scheduled S/D Due to SAS, DFDR | [7 empty] | 50.0MW load
interrup.
| 10:24 | 18:58 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 HT Scheduled S/D Due to SAS ,DFDR | [7 empty] | 50.0MW load
interrup.
| 12:00 |  | Day Peak Generation: 14148 MW.
| 13:16 | 15:10 | Chapai 132/33kV S/S T-2 (415T) HT Forced S/D Due to Section bus DS maintenance. | [7 empty] | 38.0MW load
interrup.
| 13:16 | 15:57 | Chapai 132/33kV S/S T-3 (425T) HT Forced S/D Due to Section bus DS maintenance
| 13:16 | 13:34 | Maijdee 132/33kV S/S Tr-02 HT Scheduled S/D Due to For the replacement of the Auxiliary
Transformer-02 fuse.
| 13:23 | 13:33 | Rajbari 132/33kV S/S Transformer-2 HT Tripped showing 86.1&86.2 relays Due to 33kV | [7 empty] | 19.0MW load
|  |  | Binodpur wz feeder fault. | [7 empty] | interrup.
| 13:23 | 13:33 | Rajbari 132/33kV S/S Transformer-2 LT Tripped showing 86.1 &86.2 relays Due to 33kV | [7 empty] | 19.0MW load
|  |  | Binodpur wz feeder fault. | [7 empty] | interrup.
| 13:23 | 13:34 | Rajbari 132/33kV S/S Transformer-1 LT Tripped showing 86.1 & 86.2 relays Due to 33kV | [7 empty] | 19.0MW load
|  |  | Binodpur wz feeder fault. | [7 empty] | interrup.
|  | 13:23 | Natore 132/33kV S/S TR-1 (405 T) HT is restored.
| 13:54 | 00:20 | Natore 132/33kV S/S TR-2 (415 T) LT Scheduled S/D Due to Maintenance work at 33KV C.B
| 14:34 | 00:02 | Natore 132/33kV S/S TR-2 (415 T) HT Scheduled S/D Due to Maintenance work at 33KV C.B
| 15:24 | 15:57 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Forced S/D Due to Pdb incomer -3 ct joint red
hot.
| 15:41 | 18:50 | Kachua 230/132/33kV S/S Laksam CKT-2 Scheduled S/D Due to SAS signal checking by SPMD
| 15:56 | 18:26 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Project Work S/D Due to Measurement of
Jumparing in Moheshpur Grid
| 17:08 | 18:45 | Kabirpur 132/33kV S/S XFR, T-2 LT Forced S/D Due to 33 kV Feeder red hot maintenance | [7 empty] | 80.0MW load
interrup.
| 17:09 | 18:44 | Kabirpur 132/33kV S/S XFR, T-2 HT Forced S/D Due to 33 kV feeder Red hot maintenance | [7 empty] | 80.0MW load
interrup.
| 19:21 | 19:27 | Ramganj 132/33kV S/S Transformer -02 LT Tripped showing k31,K32 R phase Trip relays Due | [7 empty] | 30.0MW load
|  |  | to Oil temp. high trip | [7 empty] | interrup.
| 19:21 | 19:27 | Ramganj 132/33kV S/S Transformer -02 HT Tripped showing k31,K32 R phase Trip relays Due | [7 empty] | 30.0MW load
|  |  | to Oil temp. high trip | [7 empty] | interrup.
| 21:15 | 21:47 | Chapainawabganj-Rahanpur 132kV Ckt-1 Tripped from Chapai 132/33kV end showing SIEMENS,
Siprotec 7SA87 relays Due to Heavy Thundering
| 21:53 | 00:14 | Kushtia 132/33kV S/S T2 HT Forced S/D Due to Mazompur 33 kv fedeer's bus D/S red hot | [7 empty] | 26.5MW load
|  |  | maintenance | [7 empty] | interrup.
| 21:54 | 00:14 | Kushtia 132/33kV S/S T2 LT Forced S/D Due to Mazompur 33 kv fedeer's bus D/S red hot | [7 empty] | 26.5MW load
|  |  | maintenance | [7 empty] | interrup.
| 00:29 | 00:52 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Forced S/D Due to PDB red hot maintenance in
their CT section.
| 01:59 | 02:37 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Tripped showing Over current, Earth fault.
relays Due to Nawabganj -2 33kv feeder fault
| 01:59 | 02:37 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Tripped showing Over current, Earth fault.
relays Due to Over current, Earth fault.
| 01:59 | 02:37 | Hasnabad 132/33kV S/S 33kv Main Bus Tripped showing Over current, Earth Fault relays Due | [7 empty] | 46.0MW load
|  |  | to Nawabganj-2 33Kv feeder fault. | [7 empty] | interrup.
| 04:41 |  | Kalurghat 132/33kV S/S TRFO-01(506T) HT Tripped showing 33 kv REF 615 Relay relays Due to
B-phase cable blust at LT side.
| 05:46 |  | Coxsbazar 132/33kV S/S 415T-T2 HT Project Work S/D Due to Project work | [7 empty] | 5.0MW load
interrup.
| 05:46 |  | Coxsbazar 132/33kV S/S 415T-T2 LT Project Work S/D Due to Project work | [7 empty] | 5.0MW load
interrup.
| 05:46 |  | Coxsbazar 132/33kV S/S 415T-T2 LT Project Work S/D Due to Project work | [7 empty] | 5.0MW load
interrup.
| 05:55 |  | Sirajganj 132/33kV S/S Solar Park 1 Tripped showing Main-1, Main-2, GR-A (86A) TRIP RELAY
OPTD, GR-A (86B) TRIP RELAY OPTD. relays Due to Thunderstorm
| 06:44 |  | Natore 132/33kV S/S TR-1 (405 T) LT Scheduled S/D
| 06:44 |  | Natore 132/33kV S/S TR-2 (415 T) LT Scheduled S/D
| 06:45 |  | Natore 132/33kV S/S TR-1 (405 T) HT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
| 06:45 |  | Natore 132/33kV S/S TR-2 (415 T) HT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
| 07:05 |  | Bhaluka-Mymensingh 132 kV Ckt-1 Project Work S/D from Mymensingh 132/33kV end. and from | [7 empty] | 80.0MW load
|  |  | Bhaluka 132/33kV end Due to Bhaluka-Mymensingh 400KV line stringing work. | [7 empty] | interrup.
Mymensingh 132/33kV
end
| 07:06 |  | Bhaluka-Mymensingh 132 kV Ckt-2 Project Work S/D from Mymensingh 132/33kV end. and from | [7 empty] | 80.0MW load
|  |  | Bhaluka 132/33kV end Due to Bhaluka-Mymensingh 400KV line Stringing work. | [7 empty] | interrup.
Mymensingh 132/33kV end
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 373 | 7934400 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 290 | 7139869 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 802814 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 296 | 7274276 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 260280 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 147 | 3281280 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 538342 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 270208 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15.5 | 363000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 468000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 268800 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 2791615 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 1485072 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 35 | 827520 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 812160 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 46220 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 339120 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 475 | 10931248 | AGC+FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 136 | 2680800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2272.5 | 48515024
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 213316.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 12015 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 788640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 155 | 3603585 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 132 | 3315996 | plant availability zero
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 102 | 1709527 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 59 | 678672 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 50645 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 192960 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 213600 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 4203 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 341236 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 839738 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 106 | 2169500 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 254400 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 92 | 1125327 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 301 | 7538181 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 57 | 983040 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1130 | 26181818.18 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 2325.86 | 50216399.38
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 216 | 4991000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 300 | 6964900 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 240 | 5372000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 220 | 5252000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 17136 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1102792 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 55 | 914981 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 17 | 366688 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 93 | 2223611 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 193 | 1401120 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 160 | 3182400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 593664 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 450070 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1626780 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 81480 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 51 | 218880 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 84682 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1774.2 | 34844184
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 50580 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 154 | 2172000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1335600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 79840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 191520 | From 00:00-17:00 hrs 12MW&18:00-24:00 hrs 24MW dis
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 317880 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 245 | 4153620
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 18266 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 0 | 0 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 139 | 3242372.73 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 141 | 3257000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 660960 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1617600 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 2433320 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 194688 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7470000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 256 | 6140000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1085 | 25034206.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 859 | 20541818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 260160 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 40 | 321152 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 287856 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 174240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 150 | 641407 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1198 | 27360000 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2368 | 50498633
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 600 | 18661818 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 574272 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 64 | 1534000 | GT-1 & ST under maint
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1185 | 27735272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5361860 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 242400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6370000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 945 | -
Barishal Area Total |  |  |  |  | 3407.64 | 2424 | 60480567.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 109288 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 175762 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 137791 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 145 | 3544091 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 122 | 3337382 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 1825736 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 311 | 8350254.5 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 19 | 110130 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 483691 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 532304 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1209504 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 113 | 809184 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 15720 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1467.25 | 33942180 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 169648 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 334220 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2495.45 | 55086885.5
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 41 | 943418 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 181 | 4586000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 836640 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 20371.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1552875 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 93653 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 426240 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 386 | 8459197.56
Eastern Grid Total |  |  |  |  | 17438.042 | 7702.56 | 162763434.11
Western Grid Total |  |  |  |  | 11812.075 | 7673.45 | 174525283.79
National Grid Total |  |  |  |  | 29250.117 | 15376.01 | 337288717.9
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9904.07 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4930.2 | MW
i) Dhaka area |  |  | 5698.07 |  | MW | i) Khulna area |  |  |  | 1898 | MW
ii) Chattogram area |  |  | 1087 |  | MW | ii) Barishal area |  |  |  | 437.6 | MW
iii) Cumilla area |  |  | 1381 |  | MW | iii) Rajshahi area |  |  |  | 1563.6 | MW
iv) Mymensingh area |  |  | 1141 |  | MW | iv) Rangpur area |  |  |  | 1031 | MW
v) Sylhet area |  |  | 597 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14834.27 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 141 | 10:00 | 133 | Narshingdi | 193 | 22:00 | 199 | Uttara | 94 | 13:00
2 | AKSML | 150.1 | 08:00 | 68 | Hasnabad | 91 | 12:00 | 134 | Natore | 129 | 21:00 | 200 | UttaraNew | 57 | 13:00
3 | Aftabnagar | 44 | 13:00 | 69 | Hathazari | 72 | 19:00 | 135 | Nawabganj | 62.8 | 22:00 | 201 | Zigatola | 92 | 13:00
4 | Agargaon | 119 | 13:00 | 70 | Hatirjheel | 47 | 12:00 | 136 | Netrakona | 127 | 21:00
5 | Agrabad | 76 | 13:00 | 71 | Ishurdi | 83 | 21:00 | 137 | New | 87.2 | 12:00
6 | Amnura | 39 | 13:00 | 72 | Jaldhaka | 84 | 21:00 | 138 | Niamatpur | 82 | 00:00
7 | Ashuganj | 57 | 23:00 | 73 | Jamalpur | 124 | 00:00 | 139 | Noapara | 41 | 20:00
8 | BSRM | 186 | 02:00 | 74 | Jashore | 166 | 19:30 | 140 | PHP | 9 | 11:00
9 | Bagerhat | 92 | 19:30 | 75 | Jhenaidah | 93 | 00:00 | 141 | Pabna | 103 | 21:00
10 | Bajitpur | 92 | 19:00 | 76 | Joydebpur | 176 | 12:00 | 142 | Palashbari | 120 | 00:00
11 | Bakerganj | 15.8 | 19:00 | 77 | Joypurhat | 65 | 00:00 | 143 | Panchagarh | 65 | 20:00
12 | Bakulia | 79 | 13:00 | 78 | Juldah | 15 | 00:00 | 144 | Patiya | 7.8 | 00:00
13 | Banani | 69 | 13:00 | 79 | KSRM | 51 | 12:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 17 | 11:00 | 80 | Kabirpur | 258 | 11:00 | 146 | Patuakhali | 63 | 19:30
15 | Barapukuria | 63 | 02:00 | 81 | Kachua | 88 | 00:00 | 147 | Payra | 32 | 00:00
16 | Barguna | 22 | 22:00 | 82 | Kaliganj | 37 | 00:00 | 148 | Postogola | 62 | 12:00
17 | Barishal | 106 | 12:00 | 83 | Kallyanpur | 123 | 19:00 | 149 | Pubail | 43 | 19:00
18 | Barishal-230 | 102 | 22:00 | 84 | Kalurghat | 36 | 11:00 | 150 | Purbachal | 30 | 12:00
19 | Baroaulia | 38 | 11:00 | 85 | Kamrangirchar | 79 | 12:00 | 151 | Purbasadipur | 134 | 20:00
20 | Baroirhat | 59 | 21:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 40 | 00:00
21 | Bashundhara | 200 | 13:00 | 87 | Kasba | 37 | 21:00 | 153 | Rahim | 50 | 16:00
22 | BashundharaCement | 6 | 00:00 | 88 | Kazla | 126 | 13:00 | 154 | Rajbari | 89 | 22:00
23 | Beanibazar | 76 | 01:00 | 89 | Keranigonj | 90 | 19:30 | 155 | Rajendrapur | 118 | 13:00
24 | Benapole | 66 | 21:00 | 90 | Khagrachori | 30 | 18:30 | 156 | Rajshahi | 145 | 23:00
25 | Bhaluka | 181 | 19:30 | 91 | Khulna | 70 | 13:00 | 157 | Rajshahi-230 | 112 | 13:00
26 | Bhandaria | 60 | 21:00 | 92 | Khulshi | 177 | 22:00 | 158 | Ramganj | 108 | 23:00
27 | Bhangura | 40 | 19:30 | 93 | Kishoreganj | 133 | 20:00 | 159 | Rampur | 34 | 00:00
28 | Bheramara(GK) | 70 | 19:30 | 94 | Kodda | 309 | 11:00 | 160 | Rangamati | 12 | 14:00
29 | Bhulta | 225 | 15:00 | 95 | Kulaura | 50 | 00:00 | 161 | Rangpur | 140 | 21:00
30 | Bog-Sherpur | 80 | 00:00 | 96 | Kurigram | 68 | 21:00 | 162 | Ruppur | 4.2 | 10:00
31 | Bogura | 168 | 00:00 | 97 | Kushtia | 154 | 20:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 72 | 19:30 | 98 | Laksam | 36 | 21:00 | 164 | Saidpur | 103 | 21:00
33 | Brahmanbaria | 124 | 20:00 | 99 | Lakshmipur | 41 | 20:00 | 165 | Santhia | 40 | 19:30
34 | Cantonment | 134 | 13:00 | 100 | Lalbag | 80 | 13:00 | 166 | Satkhira | 140 | 22:00
35 | Chandina | 19 | 19:00 | 101 | Lalmonirhat | 66 | 21:00 | 167 | Satmasjid | 106 | 13:00
36 | Chandpur | 84 | 00:00 | 102 | MI_Cement | 15.7 | 20:00 | 168 | Savar | 216 | 10:00
37 | Chandraghona | 27 | 19:00 | 103 | Madanganj | 34 | 11:00 | 169 | SevenRings | 12.21 | 18:00
38 | Chapai | 79 | 23:00 | 104 | Madaripur | 108 | 21:00 | 170 | ShahCement | 32 | 20:00
39 | Charfasson | 28 | 01:00 | 105 | Madartek | 80 | 21:00 | 171 | Shahjadpur | 83 | 21:00
40 | Charsaidpur | 41 | 19:30 | 106 | Madunaghat | 54 | 13:00 | 172 | Shahjibazar | 137 | 00:00
41 | Chauddagram | 75 | 21:00 | 107 | Magura | 70 | 19:30 | 173 | Shahmirpur | 29 | 12:00
42 | Chhatak | 41 | 00:00 | 108 | Mahasthangarh | 81 | 00:00 | 174 | Shariatpur | 94 | 22:00
43 | Chowmuhani | 156 | 21:00 | 109 | Maijdee | 36 | 19:30 | 175 | Sherpur | 150 | 00:00
44 | Chuadanga | 129 | 21:00 | 110 | Manikganj | 158 | 21:00 | 176 | Shikalbaha | 20 | 23:00
45 | Coxsbazar | 135 | 01:00 | 111 | Maniknagar | 76 | 13:00 | 177 | Shitalakhya | 81.2 | 13:00
46 | Cumilla(N) | 157 | 02:00 | 112 | Matarbari | 54 | 00:00 | 178 | Sholosohor | 43 | 13:00
47 | Cumilla(S) | 165 | 23:00 | 113 | Matuail | 82 | 13:00 | 179 | Shomvuganj | 37 | 19:00
48 | Daganbhuiyan | 29 | 21:00 | 114 | Metrorail_Motijheel | 21 | 17:00 | 180 | Shyampur | 188 | 12:00
49 | Daudkandi | 147 | 22:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 134 | 12:00
50 | DhakaUniversity | 96 | 13:00 | 116 | Millgate | 107 | 12:00 | 182 | Sirajganj | 124 | 20:00
51 | Dhamrai | 106 | 00:00 | 117 | Mirpur | 155 | 13:00 | 183 | Sitakunda | 31 | 19:00
52 | Dhanmondi | 121 | 13:00 | 118 | Mirsorai | 48 | 09:00 | 184 | Sonargaon | 150 | 01:00
53 | Dohazari | 75 | 03:00 | 119 | Mirzapur | 45 | 00:00 | 185 | Sreemongol | 71 | 18:30
54 | Faridpur | 179 | 21:00 | 120 | Mithapukur | 76 | 01:00 | 186 | Sreepur | 134 | 19:30
55 | Fatullah | 109 | 12:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 50 | 22:00
56 | Fenchuganj | 42 | 01:00 | 122 | Mogbazar | 95.1 | 13:00 | 188 | Sunamganj | 62 | 00:00
57 | Feni | 109 | 21:00 | 123 | Mongla | 47 | 10:00 | 189 | Sylhet | 112 | 14:00
58 | GPH | 1 | 00:00 | 124 | Motijheel | 51 | 13:00 | 190 | Sylhet_(South) | 69 | 21:00
59 | Ghatail | 76 | 21:00 | 125 | Muktagacha | 36 | 00:00 | 191 | TK | 20.5 | 19:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 111 | 00:00 | 192 | Tangail | 174 | 00:00
61 | Ghorashal-230 | 104 | 01:00 | 127 | Muradnagar | 50 | 21:00 | 193 | Taraganj | 27 | 19:30
62 | Goalpara | 39 | 19:30 | 128 | Mymensingh | 142 | 20:00 | 194 | Tasnim | 48 | 12:00
63 | Gollamari | 106 | 20:00 | 129 | Nabinagar | 110 | 12:00 | 195 | Thakurgaon | 119 | 20:00
64 | Gopalganj | 111 | 21:00 | 130 | Naogaon | 140 | 01:00 | 196 | Tongi | 154 | 11:00
65 | Gulshan | 116 | 12:00 | 131 | Narail | 55 | 00:00 | 197 | Ullahpara | 43 | 20:00
66 | Halishahar | 86.5 | 09:00 | 132 | Narinda | 76 | 13:00 | 198 | Ullon | 55 | 18:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15240.04 | 108 |  | 15353.04
1:00 | 14666.33 | 197 |  | 14872.33
2:00 | 14487.85 | 197 |  | 14693.85
3:00 | 13721.34 | 145 |  | 13872.87
4:00 | 13405.71 | 130 |  | 13541.56
5:00 | 13062.11 | 95 |  | 13161.11
6:00 | 12671.29 | 65 |  | 12739.22
7:00 | 12875.15 | 43 |  | 12920.09
8:00 | 12851.5 | 43 |  | 12896.44
9:00 | 12964.39 | 10 |  | 12974.84
10:00 | 13443.94 | 0 |  | 13443.94
11:00 | 13811.89 | 0 |  | 13811.89
12:00 | 14148.17 | 49 |  | 14199.17
13:00 | 14414.62 | 70 |  | 14487.62
14:00 | 14065.24 | 100 |  | 14169.24
15:00 | 14010.67 | 107 |  | 14122.67
16:00 | 13791.24 | 135 |  | 13932.24
17:00 | 13616.71 | 145 |  | 13768.24
18:00 | 13365.37 | 210 |  | 13584.37
19:00 | 14116.84 | 711 |  | 14859.84
19:30 | 14891.81 | 760 |  | 15685.81
20:00 | 15049.51 | 637 |  | 15715.51
21:00 | 15376.01 | 345 |  | 15737.01
22:00 | 15028.81 | 467 |  | 15516.81
23:00 | 14773.4 | 819 |  | 15629.4
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7386 | 7854.04 | 15240.04 | DAILY GENERATION CURVE
00:30 | 7113.4 | 7839.785 | 14953.185
01:00 | 6840.8 | 7825.53 | 14666.33 | 08-07-2026
01:30 | 6818.9 | 7758.19 | 14577.09
02:00 | 6797 | 7690.85 | 14487.85
02:30 | 6609 | 7495.595 | 14104.595
03:00 | 6421 | 7300.34 | 13721.34
03:30 | 6388 | 7175.525 | 13563.525
04:00 | 6355 | 7050.71 | 13405.71
04:30 | 6194.5 | 7039.41 | 13233.91
05:00 | 6034 | 7028.11 | 13062.11
05:30 | 5956.515 | 6910.185 | 12866.7
06:00 | 5879.03 | 6792.26 | 12671.29
06:30 | 5852.265 | 6920.955 | 12773.22
07:00 | 5825.5 | 7049.65 | 12875.15
07:30 | 5818.185 | 7045.14 | 12863.325
08:00 | 5810.87 | 7040.63 | 12851.5
08:30 | 5897.255 | 7010.69 | 12907.945
09:00 | 5983.64 | 6980.75 | 12964.39
09:30 | 6179.615 | 7024.55 | 13204.165
10:00 | 6375.59 | 7068.35 | 13443.94
10:30 | 6533.78 | 7094.135 | 13627.915
11:00 | 6691.97 | 7119.92 | 13811.89
11:30 | 6842.225 | 7137.805 | 13980.03
12:00 | 6992.48 | 7155.69 | 14148.17
12:30 | 7058.955 | 7222.44 | 14281.395
13:00 | 7125.43 | 7289.19 | 14414.62
13:30 | 7052.985 | 7186.945 | 14239.93
14:00 | 6980.54 | 7084.7 | 14065.24
14:30 | 6940.99 | 7096.965 | 14037.955
15:00 | 6901.44 | 7109.23 | 14010.67
15:30 | 6863.195 | 7037.76 | 13900.955
16:00 | 6824.95 | 6966.29 | 13791.24
16:30 | 6758.65 | 6945.325 | 13703.975
17:00 | 6692.35 | 6924.36 | 13616.71
17:30 | 6744.645 | 6746.395 | 13491.04
18:00 | 6796.94 | 6568.43 | 13365.37
18:30 | 6937.9 | 6803.205 | 13741.105
19:00 | 7078.86 | 7037.98 | 14116.84
19:30 | 7542.06 | 7349.75 | 14891.81
20:00 | 7577.06 | 7472.45 | 15049.51
20:30 | 7639.81 | 7572.95 | 15212.76 |  | Executive Engineer
21:00 | 7702.56 | 7673.45 | 15376.01 |  | Network Operation Division
21:30 | 7588.06 | 7614.35 | 15202.41
22:00 | 7473.56 | 7555.25 | 15028.81
22:30 | 7335.81 | 7565.295 | 14901.105
23:00 | 7198.06 | 7575.34 | 14773.4

## En-Curve
QF-LDC-12
Date | 08-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3144 | 1641 | 880 | 38 | 130 | 1483.04 | 146 | 5071 | 0 | 794 | 1768 | 100 | 0 | 45 | 108 | DAILY ENERGY CURVE
00:30 | 3153 | 1647.5 | 864 | 38 | 132 | 1481.285 | 147 | 5070.5 | 0 | 706.5 | 1595.9 | 75 | 0 | 42.5 | 152.5 | 08-07-2026
01:00 | 3162 | 1654 | 848 | 38 | 134 | 1479.53 | 148 | 5070 | 0 | 619 | 1423.8 | 50 | 0 | 40 | 197
01:30 | 3160.5 | 1621.5 | 848 | 38 | 131 | 1476.19 | 148 | 5143 | 0 | 518.5 | 1421.9 | 25 | 0 | 45.5 | 197 | Energy Generated | 337.2887 |  | MKWHr
02:00 | 3159 | 1589 | 848 | 38 | 128 | 1472.85 | 148 | 5216 | 0 | 418 | 1420 | 0 | 0 | 51 | 197 | Energy not Served | 4.828 |  | MKWHr
02:30 | 3176 | 1559.5 | 848 | 38 | 127 | 1432.595 | 148 | 5175.5 | 0 | 412.5 | 1140 | 0 | 0 | 47.5 | 171 | Total Energy Requirement | 342.1167 |  | MKWHr
03:00 | 3193 | 1530 | 848 | 38 | 126 | 1392.34 | 148 | 5135 | 0 | 407 | 860 | 0 | 0 | 44 | 145
03:30 | 3192 | 1558 | 848 | 38 | 122 | 1369.525 | 148 | 5092 | 0 | 408.5 | 745 | 0 | 0 | 42.5 | 137.5
04:00 | 3191 | 1586 | 848 | 38 | 118 | 1346.71 | 148 | 5049 | 0 | 410 | 630 | 0 | 0 | 41 | 130
04:30 | 3185 | 1603.5 | 848 | 38 | 116 | 1331.41 | 147 | 5056 | 0 | 352.5 | 521 | 0 | 0 | 35.5 | 112.5
05:00 | 3179 | 1621 | 848 | 38 | 114 | 1316.11 | 146 | 5063 | 0 | 295 | 412 | 0 | 0 | 30 | 95
05:30 | 3182.5 | 1626.5 | 848 | 38 | 114 | 1315.585 | 145 | 4979 | 1.615 | 264 | 312 | 0 | 0 | 40.5 | 80
06:00 | 3186 | 1632 | 848 | 38 | 114 | 1315.06 | 144 | 4895 | 3.23 | 233 | 212 | 0 | 0 | 51 | 65
06:30 | 3181.5 | 1649 | 848 | 38 | 114 | 1354.125 | 144 | 4981.5 | 11.595 | 233 | 191 | 0 | 0 | 27.5 | 54
07:00 | 3177 | 1666 | 848 | 38 | 114 | 1393.19 | 144 | 5068 | 19.96 | 233 | 170 | 0 | 0 | 4 | 43
07:30 | 3180.5 | 1636.5 | 848 | 38 | 117 | 1381.82 | 144 | 5066.5 | 36.005 | 233 | 173 | 0 | 0 | 9 | 43
08:00 | 3184 | 1607 | 848 | 38 | 120 | 1370.45 | 144 | 5065 | 52.05 | 233 | 176 | 0 | 0 | 14 | 43
08:30 | 3131.5 | 1598.25 | 848 | 38 | 121 | 1378.595 | 144 | 5066.5 | 90.1 | 236.5 | 239.5 | 0 | 0 | 16 | 26.5
09:00 | 3079 | 1589.5 | 848 | 38 | 122 | 1386.74 | 144 | 5068 | 128.15 | 240 | 303 | 0 | 0 | 18 | 10
09:30 | 3104 | 1586.25 | 848 | 38 | 122 | 1376 | 144 | 5066 | 152.415 | 278 | 474.5 | 0 | 0 | 15 | 5
10:00 | 3129 | 1583 | 848 | 38 | 122 | 1365.26 | 144 | 5064 | 176.68 | 316 | 646 | 0 | 0 | 12 | 0
10:30 | 3114 | 1590.5 | 848 | 38 | 127 | 1354.605 | 149 | 5081 | 204.81 | 324.5 | 773.5 | 0 | 0 | 23 | 0
11:00 | 3099 | 1598 | 848 | 38 | 132 | 1343.95 | 154 | 5098 | 232.94 | 333 | 901 | 0 | 0 | 34 | 0
11:30 | 3088.5 | 1587 | 848 | 38 | 137 | 1358.25 | 154 | 5134 | 207.78 | 342.5 | 1043.5 | 0 | 0 | 41.5 | 24.5
12:00 | 3078 | 1576 | 848 | 38 | 142 | 1372.55 | 154 | 5170 | 182.62 | 352 | 1186 | 0 | 0 | 49 | 49
12:30 | 3001 | 1567 | 848.5 | 38 | 139 | 1363.37 | 154 | 5164.5 | 194.925 | 375.5 | 1400.1 | 0 | 0 | 35.5 | 59.5
13:00 | 2924 | 1558 | 849 | 38 | 136 | 1354.19 | 154 | 5159 | 207.23 | 399 | 1614.2 | 0 | 0 | 22 | 70
13:30 | 2912.5 | 1539.5 | 848.5 | 38 | 139 | 1338.78 | 155 | 5019.5 | 222.35 | 381.5 | 1618.3 | 0 | 0 | 27 | 85
14:00 | 2901 | 1521 | 848 | 38 | 142 | 1323.37 | 156 | 4880 | 237.47 | 364 | 1622.4 | 0 | 0 | 32 | 100
14:30 | 2915.5 | 1537 | 848 | 38 | 134 | 1406.85 | 158 | 4861.5 | 202.025 | 348 | 1548.08 | 0 | 0 | 41 | 103.5
15:00 | 2930 | 1553 | 848 | 38 | 126 | 1490.33 | 160 | 4843 | 166.58 | 332 | 1473.76 | 0 | 0 | 50 | 107
15:30 | 2909 | 1555 | 848 | 38 | 123 | 1481.775 | 161 | 4795 | 134.92 | 336.5 | 1472.76 | 0 | 0 | 46 | 121
16:00 | 2888 | 1557 | 848 | 38 | 120 | 1473.22 | 162 | 4747 | 103.26 | 341 | 1471.76 | 0 | 0 | 42 | 135
16:30 | 2885 | 1534 | 848 | 38 | 127 | 1481.795 | 161 | 4720.5 | 88.87 | 356.5 | 1424.31 | 0 | 0 | 39 | 140
17:00 | 2882 | 1511 | 848 | 38 | 134 | 1490.37 | 160 | 4694 | 74.48 | 372 | 1376.86 | 0 | 0 | 36 | 145
17:30 | 2888.5 | 1492 | 848 | 38 | 131 | 1432.245 | 160.5 | 4608.5 | 53.685 | 408.5 | 1385.61 | 0 | 0 | 44.5 | 177.5
18:00 | 2895 | 1473 | 848 | 38 | 128 | 1374.12 | 161 | 4523 | 32.89 | 445 | 1394.36 | 0 | 0 | 53 | 210
18:30 | 2912.5 | 1539.25 | 847.5 | 38 | 144 | 1428.45 | 159.5 | 4549.5 | 16.445 | 539 | 1512.46 | 0 | 0 | 54.5 | 460.5
19:00 | 2930 | 1605.5 | 847 | 38 | 160 | 1482.78 | 158 | 4576 | 0 | 633 | 1630.56 | 0 | 0 | 56 | 711
19:30 | 2940 | 1619.5 | 859 | 38 | 164 | 1475.55 | 156 | 4815 | 0 | 693 | 2078.76 | 0 | 0 | 53 | 760
20:00 | 2944 | 1630.5 | 859 | 38 | 164 | 1474.25 | 155 | 4878 | 0 | 709 | 2103.76 | 30 | 0 | 64 | 637
20:30 | 2992.5 | 1643.5 | 859 | 38 | 162 | 1470.75 | 155 | 4910.5 | 0 | 707 | 2124.01 | 90 | 0 | 60.5 | 491
21:00 | 3041 | 1656.5 | 859 | 38 | 160 | 1467.25 | 155 | 4943 | 0 | 705 | 2144.26 | 150 | 0 | 57 | 345
21:30 | 3039 | 1651.5 | 859 | 38 | 158 | 1469.65 | 155 | 4946 | 0 | 652.5 | 2039.26 | 150 | 0 | 44.5 | 406
22:00 | 3037 | 1646.5 | 859 | 38 | 156 | 1472.05 | 155 | 4949 | 0 | 600 | 1934.26 | 150 | 0 | 32 | 467
22:30 | 3027.5 | 1642.5 | 859 | 38 | 160 | 1483.095 | 148.5 | 4947.5 | 0 | 527.5 | 1878.51 | 150 | 0 | 39 | 643
23:00 | 3018 | 1638.5 | 859 | 38 | 164 | 1494.14 | 142 | 4946 | 0 | 455 | 1822.76 | 150 | 0 | 46 | 819
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 08-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 139 | 2 | 560 | 120 | 2234 | 870 | Ishurdi-Ghorashal Ckt-1 | Export | 4041309.09
1:00 | 137 | 7 | 560 | 128 | 2190 | 488
2:00 | 140 | 5 | 570 | 108 | 2182 | 454 |  | Import | 0
3:00 | 138 | 14 | 520 | 96 | 2016 | 484
4:00 | 140 | 16 | 510 | 82 | 1988 | 474 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 157 | 29 | 540 | 98 | 1120 | 520
6:00 | 167 | 40 | 560 | 124 | 2002 | 572 |  | Import | 0
7:00 | 171 | 43 | 600 | 146 | 2150 | 564
8:00 | 189 | 51 | 640 | 166 | 2308 | 638 | Sirajganj-Sreepur Ckt-1 | Export | 3390000
9:00 | 202 | 58 | 670 | 180 | 2282 | 702
10:00 | 212 | 73 | 660 | 184 | 2294 | 810 |  | Import | 0
11:00 | 205 | 73 | 620 | 182 | 2288 | 820
12:00 | 181 | 60 | 560 | 180 | 2234 | 870 | Sirajganj-Sreepur Ckt-2 | Export | 3405000
13:00 | 183 | 56 | 556 | 166 | 2222 | 836
14:00 | 184 | 54 | 580 | 168 | 2066 | 796 |  | Import | 0
15:00 | 190 | 62 | 610 | 200 | 2066 | 866
16:00 | 186 | 59 | 600 | 200 | 2008 | 864 | Gopalganj-Aminbazar Ckt-1 | Export | 25110000
17:00 | 205 | 75 | 640 | 216 | 2060 | 874
18:00 | 177 | 47 | 580 | 184 | 1834 | 756 |  | Import | 0
18:30 | 172 | 37 | 584 | 168 | 1816 | 654
19:00 | 181 | 41 | 600 | 166 | 1910 | 624 | Gopalganj-Aminbazar Ckt-2 | Export | 25150000
19:30 | 143 | 17 | 520 | 164 | 1842 | 550
20:00 | 142 | 17 | 500 | 150 | 1844 | 534 |  | Import | 0
21:00 | 139 | 14 | 510 | 150 | 1890 | 548
22:00 | 147 | 15 | 500 | 122 | 1894 | 528 |  | Total Export | 61096309.09
23:00 | 150 | 20 | 500 | 118 | 1972 | 582 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 372 | 04:00 | 349 | 11:00 | Madunaghat | 394 | 19:00 | 385 | 09:00
Amtali | 412 | 18:30 | 403 | 12:00 | Meghnaghat | 377 | 04:00 | 352 | 12:00
Ashuganj | 407 | 4:00 | 383 | 12:00 | Payra | 413 | 18:30 | 405 | 10:00
Bhulta | 398 | 04:00 | 373 | 12:00 | Rahanpur | 403 | 18:30 | 392 | 00:00
Bibiana | 379 | 04:00 | 368 | 12:00 | Rampal | 393 | 06:00 | 378 | 12:00
BIPTC | 403 | 18:30 | 394 | 00:00
Bogura | 385 | 18:00 | 375 | 00:00
Gopalganj | 388 | 18:30 | 370 | 00:00
Kaliakoir | 362 | 00:00 | 343 | 11:00
Korerhat | 394 | 18:30 | 384 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 00:00 | 211 | 12:00 | Ishurdi | 235 | 06:00 | 219 | 21:00
AKSML | 238 | 20:00 | 230 | 08:00 | Jhenaidah | 228 | 18:00 | 209 | 21:00
Aminbazar | 228 | 04:00 | 212 | 11:00 | Kachua | 229 | 19:30 | 220 | 08:00
Ashuganj | 229 | 03:00 | 220 | 12:00 | Kaliakoir | 228 | 01:00 | 209 | 12:00
Ashuganj-400 | 229 | 3:00 | 220 | 12:00 | Keranigonj | 228 | 04:00 | 209 | 12:00
Baghabari | 233 | 04:00 | 223 | 21:00 | Khulna(S) | 224 | 18:30 | 220 | 19:00
Barapukuria | 226 | 14:00 | 218 | 21:00 | Korerhat | 227 | 19:30 | 221 | 03:00
Barapukuria-230 | 226 | 14:00 | 216 | 21:00 | Madunaghat | 241 | 18:00 | 236 | 04:00
Barishal | 227 | 18:30 | 218 | 12:00 | Madunaghat-400 | 242 | 19:00 | 236 | 09:00
Bheramara | 233 | 06:00 | 217 | 21:00 | Maniknagar | 228 | 04:00 | 208 | 12:00
Bhulta | 229 | 04:00 | 211 | 12:00 | Meghnaghat | 236 | 03:00 | 219 | 12:00
Bibiana | 220 | 04:00 | 215 | 13:00 | Meghnaghat-400 | 231 | 04:00 | 214 | 12:00
BIPTC | 235 | 06:00 | 217 | 21:00 | Mirsorai | 229 | 19:30 | 222 | 13:00
Bogura | 242 | 18:00 | 235 | 00:00 | Naogaon | 230 | 18:30 | 206 | 00:00
Bogura-400 | 242 | 18:00 | 235 | 21:00 | Purbasadipur | 224 | 14:00 | 215 | 21:00
Borhanuddin | 229 | 18:00 | 225 | 02:00 | Rajshahi | 231 | 18:00 | 215 | 21:00
BSRM | 229 | 19:30 | 222 | 08:00 | Rampal | 223 | 06:00 | 213 | 12:00
Charfasson | 230 | 17:00 | 224 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 225 | 17:00 | 220 | 08:00 | Rampura | 228 | 04:00 | 209 | 12:00
Cumilla(N) | 224 | 03:00 | 215 | 12:00 | Shikalbaha | 241 | 17:00 | 233 | 07:00
Faridpur | 221 | 18:30 | 211 | 12:00 | Shyampur | 229 | 04:00 | 210 | 12:00
Fenchuganj | 222 | 05:00 | 218 | 01:00 | Siddhirganj | 227 | 01:00 | 212 | 12:00
Feni | 225 | 18:30 | 218 | 12:00 | Sirajgonj | 240 | 05:00 | 235 | 15:00
Ghorashal | 230 | 00:00 | 220 | 11:00 | Sreepur | 226 | 04:00 | 217 | 15:00
Ghorashal-230 | 217 | 04:00 | 196 | 12:00 | Tongi | 220 | 04:00 | 200 | 11:00
Gopalganj | 222 | 18:30 | 212 | 00:00
GPH | 236 | 18:00 | 228 | 02:00
Haripur | 229 | 04:00 | 211 | 12:00
Hasnabad | 227 | 01:00 | 210 | 12:00
Hathazari | 238 | 09:00 | 233 | 05:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 123 | 12:00 | Madunaghat | 141 | 18:00 | 136 | 04:00
Agargaon | 135 | 04:00 | 122 | 12:00 | Magura | 130 | 06:00 | 116 | 21:00
Agrabad | 138 | 18:00 | 134 | 09:00 | Mahasthangarh | 137 | 18:00 | 131 | 00:00
AKS | 136 | 03:00 | 132 | 08:00 | Maijdee | 127 | 18:30 | 123 | 03:00
Aminbazar | 131 | 00:00 | 120 | 12:00 | Manikganj | 130 | 19:00 | 120 | 15:00
Amnura | 135 | 18:30 | 126 | 12:00 | Maniknagar | 134 | 03:00 | 120 | 12:00
Ashuganj | 133 | 04:00 | 126 | 12:00 | Matarbari | 130 | 11:00 | 120 | 00:00
Ashuganj-230 | 135 | 03:00 | 130 | 12:00 | Matuail | 133 | 04:00 | 122 | 13:00
Bagerhat | 125 | 05:00 | 116 | 21:00 | Metrorail_Motijheel | 134 | 03:00 | 120 | 12:00
Bajitpur | 128 | 06:00 | 121 | 11:00 | Metrorail_Uttara | 132 | 00:00 | 116 | 13:00
Bakerganj | 132 | 17:00 | 127 | 01:00 | Millgate | 133 | 00:00 | 117 | 12:00
Bakulia | 140 | 20:00 | 135 | 03:00 | Mirpur | 132 | 00:00 | 118 | 12:00
Banani | 137 | 04:00 | 122 | 13:00 | Mirzapur | 129 | 04:00 | 121 | 12:00
Bangabhaban | 134 | 03:00 | 120 | 12:00 | Mithapukur | 136 | 08:00 | 126 | 21:00
Barapukuria | 138 | 14:00 | 129 | 19:30 | MI_Cement | 134.9 | 05:00 | 120 | 12:00
Barguna | 133 | 18:30 | 126 | 01:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 18:30 | 126 | 11:00 | Mogbazar | 138 | 06:00 | 125 | 12:00
Barishal-230 | 132 | 18:30 | 126 | 01:00 | Mongla | 125 | 07:00 | 118 | 19:30
Baroaulia | 139 | 14:00 | 135 | 03:00 | Motijheel | 134 | 04:00 | 120 | 12:00
Baroirhat | 132 | 19:00 | 128 | 08:00 | Muktagacha | 130 | 20:00 | 118 | 15:00
Bashundhara | 137 | 03:00 | 117 | 12:00 | Munshiganj | 132 | 03:00 | 121 | 12:00
BashundharaCement | 133 | 00:00 | 120 | 17:00 | Muradnagar | 127 | 19:00 | 118 | 12:00
Beanibazar | 124 | 07:00 | 118 | 02:00 | Mymensingh | 130 | 20:00 | 110 | 21:00
Benapole | 140 | 18:00 | 114 | 21:00 | Nabinagar | 129 | 05:00 | 114 | 12:00
Bhaluka | 128 | 04:00 | 117 | 21:00 | Naogaon | 139 | 18:30 | 124 | 00:00
Bhandaria | 129 | 18:00 | 123 | 21:00 | Narail | 131 | 17:00 | 115 | 21:00
Bhangura | 134 | 06:00 | 128 | 21:00 | Narinda | 134 | 3:00 | 120 | 12:00
Bheramara | 136 | 05:00 | 126 | 21:00 | Narshingdi | 128 | 04:00 | 115 | 12:00
Bheramara(GK) | 136 | 06:00 | 127 | 21:00 | Natore | 135 | 18:30 | 127 | 21:00
Bhulta | 126 | 00:00 | 118 | 12:00 | Nawabganj | 138 | 18:30 | 127 | 11:00
Bog-Sherpur | 138 | 18:30 | 131 | 21:00 | Netrakona | 121 | 06:00 | 104 | 21:00
Bogura | 140 | 18:00 | 133 | 22:00 | New | 134 | 00:00 | 120 | 11:00
Bogura-230 | 141 | 18:30 | 135 | 00:00 | Niamatpur | 134 | 18:00 | 126 | 02:00
Brahmanbaria | 129 | 04:00 | 124 | 12:00 | Noapara | 129 | 05:00 | 122 | 21:00
Cantonment | 135 | 04:00 | 121 | 12:00 | Pabna | 134 | 05:00 | 126 | 21:00
Chandina | 130 | 19:00 | 124 | 12:00 | Palashbari | 133 | 07:00 | 125 | 21:00
Chandpur | 134 | 19:30 | 123 | 08:00 | Panchagarh | 140 | 02:00 | 129 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 140 | 16:00 | 137 | 07:00 | Patiya | 138 | 19:30 | 133 | 18:00
Chapai | 134 | 14:00 | 127 | 00:00 | Patnitala | 136 | 18:00 | 128 | 00:00
Charsaidpur | 133 | 00:00 | 122 | 12:00 | Patuakhali | 132 | 18:00 | 126 | 07:00
Chauddagram | 130 | 18:30 | 125 | 12:00 | Payra | 135 | 18:00 | 132 | 01:00
Chhatak | 126 | 08:00 | 114 | 01:00 | PHP | 132 | 19:30 | 128 | 03:00
Chowmuhani | 127 | 17:00 | 123 | 12:00 | Postogola | 136 | 05:00 | 122 | 12:00
Chuadanga | 134 | 09:00 | 117 | 21:00 | Pubail | 130 | 00:00 | 117 | 11:00
Coxsbazar | 129 | 11:00 | 120 | 00:00 | Purbachal | 136 | 03:00 | 122 | 12:00
Cumilla(N) | 130 | 19:00 | 120 | 05:00 | Purbasadipur | 136 | 14:00 | 129 | 21:00
Cumilla(S) | 130 | 04:00 | 124 | 19:00 | Rahanpur | 135 | 18:30 | 130 | 00:00
Daganbhuiyan | 130 | 19:30 | 125 | 12:00 | Rahanpur-400 | 135 | 18:00 | 130 | 00:00
Daudkandi | 125 | 18:30 | 117 | 12:00 | Rahim | 133 | 00:00 | 122 | 12:00
DhakaUniversity | 137 | 04:00 | 123 | 12:00 | Rajbari | 125 | 18:00 | 120 | 00:00
Dhamrai | 130 | 02:00 | 116 | 12:00 | Rajendrapur | 126 | 04:00 | 118 | 16:00
Dhanmondi | 137.5 | 04:00 | 122 | 12:00 | Rajshahi | 132 | 18:00 | 124 | 21:00
Dohazari | 137 | 21:00 | 132 | 00:00 | Rajshahi-230 | 133 | 18:00 | 124 | 21:00
Faridpur | 127 | 18:00 | 122 | 12:00 | Ramganj | 127 | 19:00 | 121 | 07:00
Fatullah | 135 | 00:00 | 122 | 12:00 | Rampur | 138 | 14:00 | 134 | 08:00
Fenchuganj | 131 | 06:00 | 127 | 01:00 | Rampura | 137 | 04:00 | 123 | 12:00
Feni | 130 | 01:00 | 127 | 10:00 | Rangamati | 139 | 19:30 | 129 | 17:00
Feni-230 | 131 | 19:00 | 127 | 08:00 | Rangpur | 135 | 08:00 | 124 | 21:00
Ghatail | 127 | 20:00 | 116 | 00:00 | Ruppur | 137 | 05:00 | 128 | 21:00
Ghorashal | 130 | 01:00 | 120 | 11:00 | Saidpur | 136 | 14:00 | 129 | 21:00
Goalpara | 132 | 05:00 | 125 | 13:00 | Santhia | 135 | 06:00 | 127 | 21:00
Gollamari | 132 | 06:00 | 126 | 12:00 | Satkhira | 128 | 09:00 | 119 | 21:00
Gopalganj | 131 | 18:30 | 123 | 12:00 | Satmasjid | 134 | 00:00 | 121 | 12:00
Gopalganj-400 | 131 | 18:30 | 125 | 00:00 | Savar | 133 | 00:00 | 118 | 12:00
Gulshan | 136 | 05:00 | 123 | 12:00 | SevenRings | 130 | 00:00 | 119 | 13:00
Halishahar | 139 | 17:00 | 125 | 08:00 | ShahCement | 133 | 00:00 | 122 | 12:00
Haripur | 134 | 04:00 | 123 | 12:00 | Shahjadpur | 138 | 04:00 | 132 | 00:00
HaripurSBU | 134 | 04:00 | 124 | 13:00 | Shahjibazar | 129 | 05:00 | 125 | 00:00
Hasnabad | 136 | 05:00 | 123 | 12:00 | Shahmirpur | 139 | 19:00 | 134 | 05:00
Hathazari | 140 | 22:00 | 136 | 09:00 | Shariatpur | 129 | 18:00 | 123 | 12:00
Hatirjheel | 137 | 04:00 | 123 | 12:00 | Sherpur | 131 | 20:00 | 112 | 02:00
Ishurdi | 138 | 06:00 | 128 | 21:00 | Shikalbaha | 128 | 17:00 | 124 | 09:00
Jaldhaka | 135 | 04:00 | 124 | 21:00 | Shikalbaha-230 | 140 | 17:00 | 136 | 04:00
Jamalpur | 132 | 19:30 | 114 | 02:00 | Shitalakhya | 134.8 | 05:00 | 120 | 12:00
Jashore | 141 | 18:00 | 117 | 21:00 | Sholosohor | 139 | 21:00 | 136 | 03:00
Jhenaidah | 140 | 17:00 | 121 | 23:00 | Shomvuganj | 122 | 08:00 | 115 | 19:30
Jhenaidah-230 | 141 | 18:00 | 125 | 21:00 | Shyampur | 135 | 05:00 | 122 | 12:00
Joydebpur | 126 | 00:00 | 114 | 11:00 | Shyampur-230 | 137 | 04:00 | 124 | 12:00
Joypurhat | 138 | 18:30 | 128 | 00:00 | Siddhirganj | 134 | 04:00 | 122 | 12:00
Juldah | 139 | 19:30 | 135 | 07:00 | Sirajganj | 132 | 05:00 | 126 | 21:00
Kabirpur | 133 | 19:00 | 113 | 12:00 | Sitakunda | 139 | 19:30 | 135 | 04:00
Kachua | 131 | 19:30 | 124 | 08:00 | Sonargaon | 131 | 03:00 | 120 | 12:00
Kaliakoir | 135 | 00:00 | 121 | 12:00 | Sreemongol | 128 | 06:00 | 124 | 00:00
Kaliganj | 141 | 18:00 | 123 | 21:00 | Sreepur | 128 | 04:00 | 121 | 15:00
Kallyanpur | 132 | 00:00 | 120 | 12:00 | Srinagar | 138 | 18:30 | 125 | 12:00
Kalurghat | 140 | 18:00 | 136 | 06:00 | SSM | 142 | 14:00 | 139 | 15:00
Kamrangirchar | 138 | 18:30 | 117 | 12:00 | Sunamganj | 122 | 08:00 | 113 | 00:00
Kaptai | 141 | 18:00 | 135 | 1:00 | Sylhet | 125 | 06:00 | 122 | 00:00
Kasba | 126 | 04:00 | 118 | 12:00 | Sylhet_(South) | 125 | 06:00 | 121 | 00:00
Kazla | 134 | 05:00 | 121 | 13:00 | Tangail | 127 | 19:00 | 118 | 12:00
Keranigonj | 139 | 18:30 | 126 | 12:00 | Taraganj | 135 | 08:00 | 127 | 21:00
Khagrachori | 138 | 16:00 | 136 | 01:00 | Tasnim | 131 | 04:00 | 120 | 12:00
Khulna | 131 | 04:00 | 126 | 10:00 | Thakurgaon | 140 | 02:00 | 130 | 19:30
Khulna(S) | 132 | 05:00 | 126 | 21:00 | TK | 140 | 21:00 | 137 | 11:00
Khulshi | 137 | 00:00 | 133 | 07:00 | Tongi | 135 | 04:00 | 120 | 11:00
Kishoreganj | 124 | 04:00 | 117 | 19:30 | Ullahpara | 134 | 05:00 | 127 | 21:00
Kodda | 137 | 01:00 | 121 | 08:00 | Ullon | 136 | 04:00 | 123 | 12:00
Korerhat | 134 | 19:30 | 130 | 07:00 | Uttara | 132 | 00:00 | 115 | 12:00
KSRM | 140 | 18:00 | 135 | 03:00 | UttaraNew | 132 | 00:00 | 117 | 11:00
Kulaura | 129 | 05:00 | 126 | 00:00 | Zigatola | 139 | 18:30 | 126 | 12:00
Kurigram | 133 | 08:00 | 119 | 21:00
Kushtia | 134 | 18:00 | 125 | 01:00
Laksam | 130 | 19:30 | 122 | 12:00
Lakshmipur | 127 | 19:30 | 122 | 12:00
Lalbag | 138 | 18:00 | 125 | 12:00
Lalmonirhat | 132 | 08:00 | 121 | 21:00
Madanganj | 133 | 00:00 | 123 | 13:00
Madaripur | 130 | 18:00 | 126 | 01:00
Madartek | 137 | 04:00 | 123 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division