## Forecast
6086.1 |  |  |  |  | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-12-25 | Tuesday
|  | Date (day): | 2018-12-25 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10180 | MW |  |  | (b) At Evening Peak Hour : |  | 11729 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-12-24 | 2018-12-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 38 | 38 | 38 | 38 |  | 47 | Unit #2 Under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 260 | 111 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 380 | 300 | 380 | 380
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 40 | 40
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 90 | 101
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 345 | 342 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 360 | 306 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 40 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  |  | Reserve
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 40 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 130 | 150 | 155 | 150 |  |  | FGMO
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 155 | 200 | 180 | 230
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 24 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 48 | 47 | 47 |  |  | Engine problem
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 54 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 118 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 55 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 36 | 36 |  | 19 | Engine problem
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 24 | 46 | 45 | 47 |  | 61 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 57 | 58 | 58 |  | 22 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 70 | 300 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 14 | 69 | 100 | 130 |  | 19 | Engine problem
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 2358 | 2537 | 4108 | 4427 | 260 | 535
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 120 | 120 | 120 |  |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20.3 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 50 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 32 | 31 | 33 | 63 |  | 167 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 60 | 110 | 150 | 130 |  |  | FGMO
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 40 | 40 | 40 | 50
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 81 | 81
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 78 | 90 | 90 |  |  | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 23 | 40 | 40
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 46 | 90 | 100 |  | 8 | Engine problem
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 381.3 | 713 | 929 | 939 | 180 | 440
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 120 | 80 | 80 | 49 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 120 | 80 | 80 |  |  | Gas shortage
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 184 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 255 | 265 | 265 |  | 95 | ST Under maint.
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 305 | 360 | 360 |  |  | FGMO
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 40 | 39 | 40 |  | 8 | Engine problem
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 10 | 7 | 7 | 48 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 154 | 100 | 150 |  |  | On test
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 30 | 85 | 85 | 85
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 40
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 95 | 100 | 100 |  | 63 | FGMO & STG under maint.
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 70 | 148 | 180 | 180
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 94 | 122 | 91 | 112
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 25 | 0 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 19 | 22 | 22 | 22
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1337 | 1782 | 1727 | 2124 | 467 | 166
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 162 | 146 | 160 | 160 | 56 |  | Gas shortage
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 20 | 20
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 7 | 80 | 80 | 81 |  | 14 | Engine problem.
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 0 | 50 | 150 | 200
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 188 | 293 | 412 | 461 | 56 | 14
78 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 57 | 57 | 57 | 57
79 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 63 | 63 | 63 | 63
80 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 100 | 163 | 163
81 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 241 | 225 | 225 | 230 |  |  | FGMO
82 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 50 | 51 | 51
83 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 21 | 21 | 40 | 40
84 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
85 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 34 | 66 | 66 | 66 |  |  | FGMO
86 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 30 | 86 | 86 | 86
87 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 48 | 49 | 50 | 50
88 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  |  | Under maint.
89 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
90 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 42 | 46 | 50 | 50
91 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 0 | 25
92 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 18 | 40 |  | 341 | ST Under maint.
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
93 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 0 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 725 | 799 | 880 | 942 | 0 | 361
94 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 533 | 676 | 395 | 690
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
95 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 49 | 115 | 115
96 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 43 | 0 | 40
97 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
98 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 3 | 50 | 0 | 80
99 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 304 | 270 | 300 | 300 |  |  | STG under maint.
100 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
102 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 933 | 1233 | 1055 | 1516 | 0 | 0
103 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
104 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
105 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 26 | 20 | 26 |  | 7 | Engine problem
106 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 83 | 139 | 194 | 194
107 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 53 | 96 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 152 | 325 | 419 | 455 | 0 | 7
108 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage.
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
109 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 50
110 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 42
111 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 24 | 50 | 50 | 50
112 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
113 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 0 | 35
114 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  |  | Gas shortage
115 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 168 | 183 | 220 | 220 |  |  | FGMO
116 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 141 | 141 | 0 | 0 | 0 | 0 |  |  | Gas shortage.
117 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 |  |  | Gas shortage.
118 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 0 | 40
119 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
120 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 5 | 5 | 5 | 5 |  | 5 | Engine problem
121 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
122 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 43 | 52 | 52
123 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 90 | 102
| Rajshahi Area Total |  |  |  |  | 1556 | 1546 | 245 | 487 | 500 | 679 | 71 | 105
124 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
125 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 150 | 150 | 124
126 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 18
127 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 149 | 167 | 150 | 186 | 209 | 85
| Total |  |  |  |  | 17685 | 17142 | 6468.3 | 8336 | 10180 | 11729 | 1243 | 1713
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6080.3262 | 7836 | 9569.3954 | 11025.4851
A. |  | 2018-12-24 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 8336 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 4857 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8336 | MW
3 | Day peak Generation : |  |  | 6468.3 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7836 | MW
4 | Evening peak Generation : |  |  | 8336 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 152.9762 | MKWHr | By Solar | 0.13944 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 119.2088 | MKWHr |  | By Oil: | 14.8625 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6795 | MKWHr |  | By Hydro: | 0.668 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1243 | MW | Dhaka | 2855 | 2855 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1713 | MW | Chittagong | 867 | 867 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2956 | MW | Khulna | 983 | 983 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1053.55 | MMCFD |  |  | Rajshahi | 827 | 827 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 88105211.088 | ii) Oil : | Taka | 102503022.35 | Comilla | 681 | 681 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14202870 | Total | Taka | 204811103.438 | Mymensingh | 565 | 565 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 6.0275 | MKWHr. | Sylhet | 308 | 308 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -600 | MW at | 19:00 | hrs | Barisal | 207 | 207 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -640 | MW at | 20:00 | hrs | Rangpur | 543 | 543 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 24.4° C |  |  | Total | 7836 | 7836 |  | 0
B. |  | 2018-12-25 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 24.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11729 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6500 | MW
4 | Reserve(Generation end) |  |  |  | 3729 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 146.8102 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4881 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.2138 | MKWHr. | ii) HVDC Flow at Peak Time |  | 676 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2042 | MKWHr. | iii) Maximum HVDC Flow : |  | 677 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.84 |  | (b) Today: | 98.84 |  | (c) Rule Curve: |  | 103.8
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-12-24
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 38 | 0 | 200 | 0 | 200 | 101 | 40 | 305 | 300 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 120 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 32 | 0 | 0 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 22 | 41 | 0 | 80 | 80 | 260 | 272 | 182 | 8 | 95 | 40 | 7 | 5 | 7 | 85 | 0 | 0 | 22 | 11 | 0 | 15 | 76 | 149 | 0 | 17 | 0 | 57 | 63 | 5 | 21 | 100 | 226 | 37 | 10 | 49 | 78 | 0 | 49 | 0 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 20 | 17 | 0 | 0 |  | 338 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 139 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 4415 | 1148 | 5563 | 3713 | 338 | 1178 | 76 | 150 | 32 | 0 | 76 | 0 | 0 | 98.84
2:00 | 38 | 0 | 200 | 0 | 200 | 101 | 40 | 300 | 280 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 120 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 31 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 38 | 0 | 80 | 80 | 260 | 272 | 183 | 8 | 102 | 40 | 7 | 5 | 7 | 6 | 0 | 0 | 22 | 0 | 0 | 15 | 74 | 127 | 0 | 0 | 0 | 57 | 63 | 5 | 21 | 100 | 229 | 36 | 10 | 5 | 78 | 0 | 6 | 0 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 338 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 182 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 4068 | 1121 | 5189 | 3607 | 338 | 983 | 7 | 149 | 31 | 0 | 74 | 0 | 0 | 98.84
3:00 | 38 | 0 | 200 | 0 | 200 | 12 | 0 | 298 | 270 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 120 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 30 | 0 | 0 | 120 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 38 | 0 | 80 | 80 | 260 | 272 | 183 | 8 | 100 | 5 | 2 | 5 | 7 | 6 | 0 | 0 | 22 | 0 | 0 | 15 | 72 | 169 | 0 | 0 | 0 | 57 | 63 | 5 | 2 | 100 | 226 | 35 | 3 | 2 | 78 | 0 | 3 | 0 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 338 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 176 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 3892 | 1115 | 5007 | 3604 | 338 | 807 | 7 | 149 | 30 | 0 | 72 | 0 | 0 | 98.84
4:00 | 38 | 0 | 200 | 0 | 200 | 12 | 0 | 300 | 240 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 30 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 38 | 0 | 80 | 80 | 230 | 287 | 193 | 8 | 100 | 5 | 2 | 5 | 7 | 6 | 0 | 0 | 22 | 0 | 0 | 15 | 72 | 170 | 0 | 0 | 0 | 57 | 63 | 5 | 2 | 100 | 227 | 36 | 3 | 2 | 78 | 0 | 3 | 0 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 338 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 176 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 3814 | 1115 | 4929 | 3566 | 338 | 767 | 7 | 149 | 30 | 0 | 72 | 0 | 0 | 98.84
5:00 | 38 | 0 | 200 | 0 | 200 | 12 | 0 | 300 | 240 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 120 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 29 | 0 | 0 | 120 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 41 | 0 | 80 | 80 | 230 | 272 | 192 | 8 | 100 | 5 | 2 | 5 | 7 | 6 | 0 | 0 | 22 | 0 | 0 | 15 | 70 | 171 | 0 | 0 | 0 | 57 | 63 | 5 | 2 | 100 | 233 | 37 | 3 | 2 | 78 | 0 | 3 | 0 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 338 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 151 | 0 | 12 | 0 | 0 | 0 | 0 | 0 |  | 3809 | 1048 | 4857 | 3496 | 338 | 768 | 7 | 149 | 29 | 0 | 70 | 0 | 0 | 98.84
6:00 | 38 | 0 | 200 | 0 | 230 | 12 | 0 | 312 | 270 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 150 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 30 | 0 | 0 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 0 | 80 | 80 | 200 | 272 | 183 | 8 | 100 | 40 | 2 | 5 | 7 | 6 | 0 | 0 | 22 | 0 | 0 | 15 | 70 | 171 | 0 | 0 | 0 | 57 | 63 | 11 | 8 | 100 | 229 | 36 | 50 | 48 | 98 | 0 | 45 | 0 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 3 | 0 | 0 |  | 338 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 11 | 0 | 0 | 0 | 0 | 0 |  | 4163 | 1023 | 5186 | 3603 | 338 | 985 | 10 | 150 | 30 | 0 | 70 | 0 | 0 | 98.84
7:00 | 38 | 0 | 200 | 0 | 230 | 12 | 0 | 312 | 270 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 150 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 32 | 33 | 25 | 0 | 0 | 30 | 0 | 0 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 0 | 80 | 80 | 200 | 287 | 201 | 8 | 100 | 40 | 10 | 5 | 20 | 50 | 0 | 0 | 22 | 11 | 0 | 15 | 68 | 172 | 0 | 17 | 0 | 57 | 63 | 17 | 21 | 100 | 229 | 36 | 50 | 49 | 78 | 0 | 45 | 0 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1.3 | 10 | 31 | 0 | 0 |  | 338 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 143 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 149 | 0 | 11 | 0 | 0 | 0 | 0 | 7 |  | 4346.3 | 1044 | 5390.3 | 3654 | 338 | 1073 | 76 | 150 | 30 | 0 | 68 | 1.3 | 0 | 98.83
8:00 | 38 | 0 | 197 | 0 | 266 | 12 | 0 | 312 | 270 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 120 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 2 | 0 | 0 | 0 | 0 | 25 | 30 | 33 | 25 | 6 | 0 | 30 | 0 | 0 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 80 | 80 | 200 | 279 | 186 | 8 | 100 | 40 | 10 | 5 | 30 | 50 | 0 | 0 | 22 | 11 | 0 | 18 | 82 | 172 | 7 | 17 | 0.4 | 57 | 63 | 22 | 21 | 100 | 231 | 36 | 50 | 49 | 77 | 0 | 48 | 0 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 30 | 51 | 0 | 0 |  | 539 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 145 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 155 | 0 | 11 | 0 | 0 | 0 | 0 | 70 |  | 4401.4 | 1413 | 5814.4 | 3665 | 539 | 1084 | 258 | 149 | 30 | 0 | 82 | 7.4 | 0 | 98.83
9:00 | 38 | 0 | 197 | 0 | 320 | 12 | 0 | 315 | 305 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 120 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 18 | 0 | 0 | 20 | 25 | 30 | 33 | 25 | 11 | 0 | 30 | 0 | 0 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 4 | 0 | 80 | 80 | 200 | 276 | 190 | 8 | 95 | 40 | 10 | 5 | 43 | 85 | 0 | 0 | 22 | 11 | 0 | 19 | 86 | 170 | 7 | 17 | 1.1 | 57 | 63 | 50 | 21 | 100 | 230 | 35 | 86 | 49 | 78 | 0 | 48 | 0 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 30 | 85 | 0 | 0 |  | 539 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 143 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 26 | 0 | 22 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 11 | 0 | 0 | 0 | 0 | 105 |  | 4683.1 | 1494 | 6177.1 | 3760 | 539 | 1221 | 391 | 149 | 30 | 0 | 86 | 1.1 | 0 | 98.84
10:00 | 38 | 0 | 206 | 0 | 320 | 12 | 0 | 325 | 336 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 120 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6 | 18 | 0 | 0 | 20 | 25 | 30 | 33 | 25 | 25 | 0 | 32 | 0 | 0 | 120 | 0 | 0 | 0 | 130 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 4 | 0 | 80 | 80 | 200 | 272 | 191 | 8 | 100 | 40 | 10 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 8 | 19 | 84 | 165 | 7 | 17 | 1.6 | 57 | 63 | 51 | 18 | 100 | 228 | 34 | 86 | 48 | 0 | 0 | 43 | 0 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4 | 30 | 85 | 0 | 0 |  | 540 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 86 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 26 | 0 | 21 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 147 | 0 | 11 | 0 | 0 | 0 | 0 | 53 |  | 4759 | 1383 | 6142 | 3681 | 540 | 1290 | 346 | 149 | 32 | 0 | 84 | 20 | 0 | 98.84
11:00 | 38 | 0 | 262 | 0 | 380 | 12 | 0 | 334 | 361 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 145 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 6 | 18 | 0 | 0 | 20 | 25 | 30 | 33 | 25 | 27 | 0 | 32 | 0 | 0 | 100 | 8 | 0 | 0 | 120 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 4 | 22 | 3 | 0 | 80 | 80 | 200 | 272 | 189 | 8 | 100 | 10 | 10 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 8 | 19 | 94 | 163 | 7 | 17 | 1.9 | 57 | 63 | 53 | 18 | 100 | 238 | 34 | 50 | 48 | 0 | 0 | 41 | 9 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 90 | 70 | 0 | 0 |  | 540 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 85 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 25 | 0 | 18 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 153 | 0 | 50 | 0 | 0 | 0 | 0 | 53 |  | 4894.9 | 1426 | 6320.9 | 3757 | 540 | 1294 | 431 | 149 | 32 | 2 | 94 | 21.9 | 0 | 98.84
12:00 | 38 | 0 | 260 | 0 | 380 | 12 | 0 | 345 | 360 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 155 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 6 | 18 | 18 | 0 | 22 | 25 | 30 | 33 | 25 | 43 | 0 | 32 | 0 | 0 | 100 | 8 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 6 | 22 | 3 | 0 | 80 | 80 | 240 | 290 | 203 | 8 | 100 | 10 | 10 | 5 | 51 | 30 | 0 | 0 | 22 | 11 | 8 | 19 | 94 | 162 | 7 | 17 | 2 | 57 | 63 | 53 | 21 | 100 | 241 | 34 | 30 | 48 | 0 | 0 | 42 | 9 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 20.3 | 90 | 70 | 6 | 0 |  | 533 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 83 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 25 | 0 | 18 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 168 | 0 | 53 | 0 | 0 | 0 | 0 | 53 |  | 4989.3 | 1479 | 6468.3 | 3849 | 533 | 1294 | 492 | 149 | 32 | 3 | 94 | 22.3 | 0 | 98.84
13:00 | 38 | 0 | 199 | 0 | 340 | 12 | 0 | 350 | 317 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 220 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 6 | 20 | 35 | 0 | 22 | 25 | 31 | 33 | 25 | 43 | 0 | 32 | 0 | 0 | 100 | 25 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 0 | 50 | 38 | 14 | 22 | 8 | 0 | 80 | 80 | 255 | 301 | 185 | 8 | 94 | 10 | 10 | 5 | 51 | 30 | 0 | 0 | 22 | 11 | 25 | 19 | 98 | 147 | 7 | 17 | 2 | 57 | 63 | 53 | 21 | 100 | 226 | 20 | 30 | 48 | 0 | 0 | 44 | 9 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 18.5 | 90 | 78 | 15 | 0 |  | 533 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 34 | 0 | 18 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 203 | 0 | 64 | 0 | 0 | 0 | 0 | 53 |  | 5078.5 | 1520 | 6598.5 | 3801 | 533 | 1269 | 691 | 149 | 32 | 5 | 98 | 20.5 | 0 | 98.84
14:00 | 38 | 0 | 116 | 0 | 260 | 12 | 0 | 343 | 265 | 0 | 0 | 340 | 0 | 0 | 0 | 15 | 130 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 46 | 54 | 55 | 0 | 0 | 25 | 31 | 33 | 25 | 43 | 0 | 32 | 0 | 0 | 100 | 25 | 0 | 0 | 80 | 0 | 0 | 40 | 0 | 0 | 50 | 45 | 48 | 0 | 7 | 0 | 80 | 80 | 255 | 301 | 186 | 8 | 100 | 10 | 10 | 5 | 51 | 10 | 0 | 0 | 22 | 11 | 16 | 19 | 98 | 147 | 7 | 17 | 1.5 | 57 | 63 | 53 | 21 | 100 | 228 | 25 | 10 | 48 | 0 | 0 | 12 | 9 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 14.4 | 95 | 83 | 50 | 0 |  | 534 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40 | 138 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 43 | 0 | 18 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 0 | 0 | 0 | 53 |  | 4704.9 | 1464 | 6168.9 | 3368 | 534 | 1074 | 893 | 149 | 32 | 5 | 98 | 15.9 | 0 | 98.84
15:00 | 38 | 0 | 110 | 0 | 260 | 12 | 0 | 343 | 265 | 0 | 0 | 340 | 0 | 0 | 0 | 15 | 130 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 48 | 54 | 55 | 0 | 0 | 25 | 31 | 33 | 25 | 43 | 0 | 31 | 0 | 0 | 100 | 25 | 0 | 0 | 80 | 0 | 0 | 40 | 0 | 0 | 50 | 36 | 47 | 22 | 3 | 0 | 80 | 80 | 255 | 323 | 195 | 8 | 100 | 10 | 10 | 5 | 51 | 10 | 0 | 0 | 22 | 11 | 18 | 15 | 96 | 147 | 7 | 17 | 0.9 | 57 | 63 | 53 | 21 | 100 | 234 | 51 | 10 | 47 | 0 | 0 | 12 | 9 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 13 | 100 | 85 | 50 | 0 |  | 534 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40 | 134 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 25 | 0 | 22 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 187 | 0 | 71 | 0 | 0 | 0 | 0 | 25 |  | 4767.9 | 1422 | 6189.9 | 3445 | 534 | 1070 | 846 | 149 | 31 | 5 | 96 | 13.9 | 0 | 98.84
16:00 | 38 | 0 | 110 | 0 | 260 | 12 | 0 | 343 | 306 | 0 | 0 | 360 | 0 | 0 | 0 | 15 | 130 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 6 | 36 | 35 | 0 | 0 | 25 | 31 | 33 | 25 | 43 | 0 | 30 | 0 | 0 | 100 | 25 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 0 | 50 | 19 | 47 | 22 | 3 | 0 | 80 | 80 | 255 | 334 | 225 | 8 | 100 | 10 | 10 | 5 | 51 | 10 | 0 | 0 | 22 | 11 | 18 | 15 | 100 | 150 | 7 | 17 | 0.3 | 57 | 62 | 53 | 21 | 100 | 240 | 51 | 10 | 47 | 0 | 0 | 12 | 9 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7.1 | 100 | 34 | 50 | 0 |  | 534 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 16 | 134 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 8 | 0 | 22 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 191 | 0 | 71 | 0 | 0 | 0 | 0 | 17 |  | 4732.4 | 1445 | 6177.4 | 3578 | 534 | 1131 | 635 | 149 | 30 | 13 | 100 | 7.4 | 0 | 98.84
17:00 | 38 | 0 | 110 | 0 | 260 | 12 | 0 | 343 | 306 | 0 | 0 | 400 | 0 | 0 | 0 | 15 | 145 | 0 | 31 | 0 | 0 | 7 | 0 | 0 | 46 | 0 | 6 | 36 | 55 | 0 | 0 | 25 | 31 | 33 | 25 | 43 | 0 | 30 | 0 | 0 | 100 | 25 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 0 | 60 | 19 | 50 | 22 | 8 | 0 | 80 | 80 | 255 | 279 | 184 | 8 | 100 | 10 | 10 | 5 | 51 | 10 | 0 | 0 | 22 | 11 | 25 | 15 | 106 | 151 | 12 | 17 | 0 | 57 | 62 | 53 | 21 | 100 | 224 | 55 | 10 | 47 | 0 | 0 | 46 | 9 | 0 | 16 | 8 | 0 | 5 | 0 | 0 | 7 | 0 | 15 | 0.2 | 100 | 35 | 58 | 0 |  | 549 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 35 | 25 | 16 | 117 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 25 | 9 | 22 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 193 | 0 | 71 | 0 | 0 | 0 | 0 | 35 |  | 4810.2 | 1598 | 6408.2 | 3509 | 549 | 1213 | 782 | 150 | 30 | 69 | 106 | 0.2 | 0 | 98.84
18:00 | 38 | 0 | 110 | 0 | 300 | 12 | 0 | 300 | 362 | 0 | 0 | 420 | 0 | 7 | 22 | 25 | 214 | 0 | 103 | 0 | 0 | 48 | 0 | 0 | 46 | 0 | 43 | 54 | 55 | 17 | 22 | 25 | 26 | 33 | 25 | 43 | 0 | 30 | 0 | 0 | 110 | 25 | 0 | 0 | 130 | 0 | 0 | 40 | 0 | 68 | 60 | 19 | 50 | 22 | 15 | 0 | 100 | 100 | 255 | 327 | 202 | 8 | 100 | 10 | 10 | 5 | 51 | 85 | 8 | 0 | 22 | 11 | 25 | 15 | 128 | 158 | 62 | 17 | 0 | 57 | 66 | 53 | 21 | 100 | 240 | 67 | 86 | 47 | 0 | 0 | 45 | 9 | 0 | 16 | 8 | 0 | 55 | 0 | 0 | 7 | 0 | 24 | 0 | 100 | 100 | 152 | 0 |  | 676 | 0 | 250 | 0 | 53 | 0 | 0 | 0 | 43 | 50 | 40 | 137 | 26 | 48 | 0 | 0 | 0 | 43 | 0 | 33 | 50 | 0 | 30 | 43 | 39 | 22 | 5 | 11 | 0 | 0 | 150 | 18 | 0 | 0 | 0 | 168 | 0 | 97 | 0 | 0 | 0 | 0 | 105 |  | 5871 | 2137 | 8008 | 3820 | 676 | 1479 | 1393 | 150 | 30 | 332 | 128 | 0 | 0 | 98.84
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 38 | 0 | 111 | 0 | 300 | 12 | 0 | 342 | 306 | 0 | 0 | 420 | 0 | 40 | 40 | 15 | 200 | 0 | 150 | 0 | 0 | 24 | 0 | 0 | 46 | 0 | 48 | 54 | 55 | 17 | 22 | 25 | 32 | 33 | 25 | 43 | 0 | 31 | 0 | 0 | 120 | 25 | 0 | 0 | 110 | 0 | 0 | 40 | 0 | 68 | 78 | 46 | 50 | 22 | 23 | 0 | 120 | 120 | 255 | 305 | 184 | 8 | 95 | 40 | 10 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 25 | 22 | 122 | 146 | 80 | 17 | 0 | 57 | 63 | 50 | 21 | 100 | 225 | 66 | 86 | 49 | 0 | 0 | 46 | 9 | 0 | 16 | 11 | 0 | 70 | 0 | 0 | 50 | 0 | 69 | 0 | 100 | 148 | 154 | 0 |  | 676 | 0 | 270 | 0 | 49 | 0 | 0 | 0 | 43 | 50 | 40 | 139 | 26 | 64 | 0 | 0 | 0 | 43 | 0 | 51 | 50 | 0 | 40 | 43 | 39 | 22 | 5 | 11 | 0 | 0 | 150 | 17 | 0 | 0 | 0 | 183 | 0 | 96 | 0 | 0 | 0 | 0 | 105 |  | 6124 | 2212 | 8336 | 3933 | 676 | 1430 | 1643 | 150 | 31 | 351 | 122 | 0 | 0 | 99
19:30 | 38 | 0 | 110 | 0 | 300 | 12 | 0 | 347 | 306 | 0 | 0 | 420 | 0 | 50 | 0 | 15 | 200 | 0 | 160 | 0 | 0 | 7 | 0 | 0 | 46 | 0 | 48 | 54 | 55 | 17 | 22 | 25 | 32 | 33 | 25 | 43 | 0 | 31 | 0 | 0 | 120 | 25 | 0 | 0 | 110 | 0 | 0 | 40 | 0 | 68 | 78 | 12 | 50 | 22 | 28 | 0 | 120 | 120 | 260 | 309 | 186 | 8 | 100 | 40 | 10 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 25 | 22 | 120 | 146 | 80 | 17 | 0 | 57 | 63 | 53 | 21 | 100 | 230 | 68 | 86 | 49 | 0 | 0 | 47 | 9 | 0 | 16 | 11 | 0 | 70 | 0 | 0 | 7 | 0 | 63 | 0 | 100 | 160 | 154 | 0 |  | 676 | 0 | 270 | 0 | 49 | 0 | 0 | 0 | 43 | 50 | 40 | 139 | 27 | 64 | 0 | 0 | 0 | 43 | 0 | 51 | 50 | 0 | 40 | 43 | 39 | 22 | 5 | 11 | 0 | 0 | 150 | 17 | 0 | 0 | 0 | 178 | 0 | 96 | 0 | 0 | 0 | 0 | 105 |  | 6050 | 2208 | 8258 | 3965 | 676 | 1440 | 1525 | 150 | 31 | 351 | 120 | 0 | 0 | 0
20:00 | 38 | 0 | 110 | 0 | 300 | 12 | 0 | 340 | 306 | 0 | 0 | 420 | 0 | 50 | 0 | 15 | 200 | 0 | 148 | 0 | 0 | 7 | 0 | 0 | 46 | 0 | 48 | 54 | 55 | 0 | 22 | 25 | 32 | 33 | 25 | 43 | 0 | 31 | 0 | 0 | 120 | 25 | 0 | 0 | 110 | 0 | 0 | 42 | 0 | 68 | 78 | 12 | 50 | 22 | 30 | 0 | 120 | 120 | 260 | 305 | 184 | 8 | 100 | 40 | 10 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 25 | 22 | 120 | 145 | 80 | 17 | 0 | 57 | 63 | 53 | 21 | 100 | 224 | 68 | 86 | 49 | 0 | 0 | 47 | 9 | 0 | 16 | 11 | 0 | 12 | 0 | 0 | 7 | 0 | 53 | 0 | 100 | 160 | 154 | 0 |  | 676 | 0 | 270 | 0 | 42 | 0 | 0 | 0 | 43 | 30 | 40 | 135 | 26 | 64 | 0 | 0 | 0 | 43 | 0 | 51 | 50 | 0 | 36 | 43 | 39 | 22 | 5 | 11 | 0 | 0 | 149 | 17 | 0 | 0 | 0 | 179 | 0 | 97 | 0 | 0 | 0 | 0 | 105 |  | 5937 | 2173 | 8110 | 3930 | 676 | 1442 | 1435 | 149 | 31 | 327 | 120 | 0 | 0 | 99
21:00 | 38 | 0 | 25 | 0 | 300 | 12 | 0 | 335 | 330 | 0 | 0 | 400 | 0 | 12 | 0 | 15 | 210 | 0 | 165 | 0 | 0 | 7 | 0 | 0 | 46 | 0 | 47 | 54 | 55 | 0 | 22 | 25 | 32 | 33 | 25 | 43 | 0 | 32 | 0 | 0 | 120 | 25 | 0 | 0 | 80 | 0 | 0 | 42 | 0 | 68 | 78 | 12 | 50 | 22 | 32 | 0 | 120 | 120 | 260 | 305 | 184 | 8 | 95 | 40 | 10 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 25 | 22 | 114 | 143 | 80 | 17 | 0 | 57 | 63 | 53 | 21 | 100 | 225 | 47 | 86 | 48 | 0 | 0 | 48 | 9 | 0 | 16 | 11 | 0 | 12 | 0 | 0 | 7 | 0 | 48 | 0 | 100 | 160 | 154 | 0 |  | 676 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 43 | 21 | 40 | 125 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 0 | 0 | 43 | 39 | 22 | 5 | 11 | 0 | 0 | 150 | 17 | 0 | 0 | 0 | 184 | 0 | 97 | 0 | 0 | 0 | 0 | 105 |  | 5774 | 2095 | 7869 | 3845 | 676 | 1448 | 1365 | 150 | 32 | 239 | 114 | 0 | 0 | 99
22:00 | 38 | 0 | 0 | 0 | 260 | 12 | 0 | 325 | 330 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 228 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 12 | 54 | 55 | 0 | 22 | 25 | 32 | 33 | 25 | 43 | 0 | 32 | 0 | 0 | 120 | 25 | 0 | 0 | 100 | 0 | 0 | 44 | 0 | 34 | 50 | 0 | 50 | 22 | 38 | 0 | 100 | 120 | 260 | 305 | 184 | 8 | 100 | 40 | 10 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 25 | 22 | 104 | 143 | 80 | 17 | 0 | 57 | 63 | 53 | 21 | 100 | 226 | 64 | 86 | 49 | 0 | 0 | 47 | 9 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 40 | 0 | 100 | 120 | 102 | 0 |  | 677 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 40 | 134 | 25 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 43 | 0 | 22 | 5 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 95 | 0 | 0 | 0 | 0 | 53 |  | 5478 | 1829 | 7307 | 3790 | 677 | 1431 | 1078 | 150 | 32 | 45 | 104 | 0 | 0 | 99.94
23:00 | 38 | 0 | 0 | 0 | 300 | 12 | 0 | 315 | 360 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 200 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 32 | 33 | 25 | 0 | 0 | 32 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 0 | 0 | 44 | 0 | 17 | 0 | 0 | 41 | 22 | 41 | 0 | 120 | 120 | 260 | 305 | 183 | 8 | 100 | 40 | 10 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 25 | 22 | 92 | 146 | 21 | 17 | 0 | 57 | 63 | 53 | 21 | 100 | 228 | 56 | 86 | 49 | 0 | 0 | 47 | 9 | 0 | 17 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 90 | 0 | 0 |  | 676 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 140 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 5 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 96 | 0 | 0 | 0 | 0 | 0 |  | 4995 | 1597 | 6592 | 3721 | 676 | 1482 | 422 | 150 | 32 | 17 | 92 | 0 | 0 | 0
24:00 | 38 | 0 | 0 | 0 | 380 | 12 | 0 | 295 | 367 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 33 | 25 | 0 | 0 | 32 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 22 | 41 | 0 | 120 | 120 | 260 | 305 | 184 | 8 | 95 | 40 | 10 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 25 | 22 | 82 | 146 | 0 | 17 | 0 | 57 | 63 | 53 | 21 | 100 | 225 | 51 | 5 | 49 | 0 | 0 | 47 | 9 | 0 | 17 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 40 | 0 | 0 | 0 |  | 573 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 95 | 0 | 0 | 0 | 0 | 0 |  | 4634 | 1492 | 6126 | 3772 | 573 | 1425 | 92 | 150 | 32 | 0 | 82 | 0 | 0 | 0
KWH | 890000 | 0 | 3673000 | 0 | 6706281 | 530045 | 153664 | 7887870 | 7360000 | 0 | 0 | 8791000 | 0 | 118080 | 79272 | 156852 | 3845600 | 0 | 3095000 | 0 | 0 | 100224 | 0 | 1097 | 515520 | 0 | 419088 | 59220 | 506211 | 47840 | 230360 | 575000 | 726840 | 814100 | 586600 | 544764 | 0 | 668000 | 0 | 0 | 2800000 | 269820 | 0 | 0 | 2585025 | 0 | 0 | 672000 | 0 | 331566 | 598920 | 231360 | 534720 | 518448 | 568800 | 0 | 2186795 | 2153870 | 5950000 | 7200500 | 4658000 | 200727 | 2354350 | 616824 | 234240 | 120000 | 956766 | 1157150 | 7392 | 0 | 508464 | 210420 | 302900 | 466440 | 2204160 | 3631040 | 513600 | 327204 | 12000 | 1307000 | 1514040 | 947400 | 428000 | 2511475 | 5255000 | 1044000 | 1066560 | 968400 | 763110 | 0 | 792880 | 119340 | 0 | 370750 | 228816 | 0 | 225820 | 58512 | 0 | 187200 | 0 | 390240 | 127440 | 1435200 | 1656960 | 1022036 | 0 |  | 12213818 | 0 | 6572736 | 0 | 172800 | 0 | 0 | 0 | 198240 | 203264 | 637875 | 3091000 | 456400 | 318720 | 0 | 0 | 0 | 121968 | 0 | 192116 | 490870 | 0 | 90847 | 492960 | 157224 | 382800 | 100224 | 152244 | 0 | 0 | 3679500 | 61000 | 0 | 0 | 0 | 4366364 | 0 | 1196895 | 0 | 0 | 0 | 0 | 1041120 |  | 116585208 | 36390985 | 152976193 | 90165991 | 12213818 | 29042766 | 13498901 | 3679500 | 668000 | 1363617 | 2204160 | 139440 | 0
Fuel Cost | 765400 | 0 | 3158780 | 0 | 4292019.84 | 429336.45 | 144444.16 | 4811600.7 | 4489600 | 0 | 0 | 5889970 | 0 | 741542.4 | 529536.96 | 958365.72 | 2499640 | 0 | 3435450 | 0 | 0 | 660476.16 | 0 | 6987.89 | 3087964.8 | 0 | 2795316.96 | 422238.6 | 3163818.75 | 299956.8 | 172770 | 431250 | 0 | 0 | 0 | 5153467.44 | 0 | 0 | 0 | 0 | 3080000 | 2555195.4 | 0 | 0 | 2972778.75 | 0 | 0 | 5906880 | 0 | 3226137.18 | 3707314.8 | 1494585.6 | 3497068.8 | 440680.8 | 0 | 0 | 1989983.45 | 1960021.7 | 3689000 | 4968345 | 3260600 | 138501.63 | 2260176 | 413272.08 | 201446.4 | 110400 | 784548.12 | 1099292.5 | 80129.28 | 0 | 391517.28 | 157815 | 233233 | 349830 | 15076454.4 | 2723280 | 4719984 | 251947.08 | 0 | 1359280 | 1574601.6 | 909504 | 385200 | 1958950.5 | 3678500 | 1190160 | 1141219.2 | 1065240 | 869945.4 | 0 | 737378.4 | 110986.2 | 0 | 278062.5 | 173900.16 | 0 | 1639453.2 | 1014012.96 | 0 | 1338480 | 0 | 0 | 0 | 0 | 15476006.4 | 9545816.24 | 0 |  | 62290471.8 | 0 | 4403733.12 | 0 | 1432512 | 0 | 0 | 0 | 2232182.4 | 2394449.92 | 5026455 | 2132790 | 451836 | 2358528 | 0 | 0 | 0 | 1396533.6 | 0 | 1721359.36 | 4246025.5 | 0 | 967520.55 | 4890163.2 | 1850526.48 | 421080 | 94210.56 | 115248.708 | 0 | 0 | 14202870 | 1966030 | 0 | 0 | 0 | 3056454.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 164527048.64 | 117650980.998 | 282178029.638 | 67542066.968 | 62290471.8 | 20563144.12 | 86668153.58 | 14202870 | 0 | 15834868.77 | 15076454.4 | 0 | 0
Yesterday Day Peak | 38 | 0 | 260 | 0 | 380 | 12 | 0 | 345 | 360 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 155 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 6 | 18 | 18 | 0 | 22 | 25 | 30 | 33 | 25 | 43 | 0 | 32 | 0 | 0 | 100 | 8 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 6 | 22 | 3 | 0 | 80 | 80 | 240 | 290 | 203 | 8 | 100 | 10 | 10 | 5 | 51 | 30 | 0 | 0 | 22 | 11 | 8 | 19 | 94 | 162 | 7 | 17 | 2 | 57 | 63 | 53 | 21 | 100 | 241 | 34 | 30 | 48 | 0 | 0 | 42 | 9 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 20.3 | 90 | 70 | 6 | 0 |  | 533 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 83 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 25 | 0 | 18 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 168 | 0 | 53 | 0 | 0 | 0 | 0 | 53 |  | 6468.3 | DayPeak
Yesterday Evening Peak | 38 | 0 | 111 | 0 | 300 | 12 | 0 | 342 | 306 | 0 | 0 | 420 | 0 | 40 | 40 | 15 | 200 | 0 | 150 | 0 | 0 | 24 | 0 | 0 | 46 | 0 | 48 | 54 | 55 | 17 | 22 | 25 | 32 | 33 | 25 | 43 | 0 | 31 | 0 | 0 | 120 | 25 | 0 | 0 | 110 | 0 | 0 | 40 | 0 | 68 | 78 | 46 | 50 | 22 | 23 | 0 | 120 | 120 | 255 | 305 | 184 | 8 | 95 | 40 | 10 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 25 | 22 | 122 | 146 | 80 | 17 | 0 | 57 | 63 | 50 | 21 | 100 | 225 | 66 | 86 | 49 | 0 | 0 | 46 | 9 | 0 | 16 | 11 | 0 | 70 | 0 | 0 | 50 | 0 | 69 | 0 | 100 | 148 | 154 | 0 |  | 676 | 0 | 270 | 0 | 49 | 0 | 0 | 0 | 43 | 50 | 40 | 139 | 26 | 64 | 0 | 0 | 0 | 43 | 0 | 51 | 50 | 0 | 40 | 43 | 39 | 22 | 5 | 11 | 0 | 0 | 150 | 17 | 0 | 0 | 0 | 183 | 0 | 96 | 0 | 0 | 0 | 0 | 105 |  | 8336 | EvPeak
Forecast for Evening | 38 | 0 | 0 | 0 | 380 | 101 | 40 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 230 | 0 | 150 | 100 | 100 | 102 | 149 | 100 | 47 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 33 | 33 | 25 | 43 | 0 | 33 | 30 | 0 | 120 | 25 | 0 | 0 | 130 | 0 | 0 | 50 | 81 | 68 | 90 | 100 | 50 | 22 | 40 | 0 | 80 | 80 | 265 | 360 | 221 | 8 | 100 | 40 | 7 | 5 | 51 | 85 | 40 | 52 | 22 | 11 | 33 | 22 | 112 | 160 | 81 | 20 | 0 | 57 | 63 | 51 | 40 | 163 | 230 | 66 | 86 | 50 | 0 | 0 | 50 | 10 | 40 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 130 | 0 | 100 | 180 | 150 | 0 |  | 690 | 46 | 300 | 0 | 115 | 0 | 0 | 0 | 40 | 80 | 40 | 194 | 26 | 110 | 30 | 0 | 0 | 50 | 42 | 102 | 50 | 50 | 35 | 52 | 40 | 22 | 5 | 11 | 0 | 0 | 150 | 18 | 18 | 0 | 0 | 220 | 0 | 95 | 100 | 0 | 0 | 0 | 105
Forecast for Day | 38 | 0 | 0 | 0 | 380 | 90 | 40 | 412 | 360 | 110 | 0 | 450 | 0 | 100 | 100 | 55 | 180 | 0 | 155 | 100 | 100 | 102 | 118 | 100 | 45 | 0 | 47 | 54 | 55 | 36 | 22 | 25 | 33 | 33 | 25 | 43 | 0 | 33 | 0 | 0 | 120 | 25 | 0 | 0 | 150 | 0 | 0 | 40 | 81 | 68 | 90 | 90 | 50 | 22 | 40 | 0 | 80 | 80 | 265 | 360 | 221 | 8 | 100 | 39 | 7 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 0 | 22 | 91 | 160 | 80 | 20 | 2 | 57 | 63 | 51 | 40 | 163 | 225 | 66 | 86 | 50 | 0 | 0 | 50 | 0 | 18 | 0 | 11 | 0 | 300 | 300 | 0 | 150 | 0 | 100 | 20 | 100 | 180 | 100 | 0 |  | 395 | 0 | 300 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 194 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 90 | 50 | 50 | 0 | 52 | 0 | 22 | 5 | 11 | 0 | 0 | 150 |  | 0 | 0 | 0 | 220 | 0 | 95 | 100 | 0 | 0 | 0 | 105
Generation at 08:00(Today) | 38 | 0 | 0 | 0 | 380 | 90 | 0 | 292 | 368 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 180 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 33 | 25 | 0 | 0 | 32 | 0 | 0 | 120 | 0 | 0 | 0 | 140 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 0 | 80 | 80 | 260 | 305 | 185 | 8 | 100 | 37 | 10 | 5 | 5 | 6 | 0 | 0 | 22 | 11 | 0 | 18 | 78 | 201 | 0 | 17 | 0.4 | 30 | 44 | 16 | 40 | 100 | 222 | 51 | 5 | 48 | 0 | 0 | 42 | 0 | 18 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 349 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 144 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 192 | 0 | 12 | 0 | 0 | 0 | 0 | 53 | 0
199
| Minimum Generation |  | 4857 | 5:00
| Highest Generation |  | 8336 | 19:00
| Day Peak Generation |  | 6468.3 | 12:00
| Evening Peak Generation |  | 8336 | 19:00
| HVDC Max Flow |  | 677 | 22:00
| HVDC EvPeak Flow |  | 676 | 19:00
| Load factor L.F |  | 76.46%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-12-25
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2018-12-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6468.3 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 4881 | MW
Evening Peak Generation : |  | 8336 | MW Hour : | 19:00 | Available Max Generation : |  | 11729 | MW
E.P. Demand (at gen end) : |  | 8336 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8000 | MW
Maximum Generation : |  | 8336 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3729 | MW
Total Gen. (MKWH) : |  | 152.9762 | System Load Factor : | 76.46% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -640 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-12-25
Actual : | 98.84 | Ft.(MSL) , | Rule curve : | 103.8 | Ft.( MSL )
Gas Consumed : | Total = | 1053.55 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 88105211.088
|  | Coal : | 14202870 | Oil : | 102503022.35 | Total : | 204811103.438
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2816.5637 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 949.585 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 849.3351 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 766.927 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 693.347 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 559.4858 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 323.3923 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 144.3319 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 431.4527 |  |  | 0 | 0%
Total | 0 |  | 7534.4202 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 9) Bhagabari 71 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 10) Raozan # 01
|  |  |  | 3) Ghorasal Unit-2,3,4,5 |  | 11) Sirajganj Unit-1,3,4
|  |  |  | 4) Tongi GT |  | 12) Sylhet 150 MW
5) Haripur GT-1,2
6) Baghabari 100 MW
7) Siddhirganj ST 210 MW
8) Summit Bibiyana-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Sylhet 150 MW GT tripped at 09:05 showing generator protection.
b) Jamalpur-Mymensingh 132 kV Ckt-2 was under shut down from 08:15 to 15:41 for A/M.
c) New Tongi 132/33 kV T1 transformer was under shut down from 09:26 to 13:31 for A/M.
d) Aminbazar 230/132 kV T3 transformer was under shut down from 09:28 to 16:51 for A/M
e) Kishoreganj-Ashuganj 132 kV Ckt-2 was under shut down from 09:35 to 17:06 for A/M.
f) Shahjibazar-Sreemangal 132 kV Ckt-1 was under shut down from 09:09 to 15:05 for A/M.
g) Natore-Bogra 132 kV Ckt-2 was under shut down from 08:08 to 15:45 for A/M.
h) Bogra 230/132 kV T2 transformer was under shut down from 08:57 to 15:45 for A/M.
i) Naogaon 132/33 kV T1 transformer was under shut down from 10:35 to 13:42 for C/M.
j) Ghorasal-Ashuganj 132 kV Ckt-1 was shut down at 11:12 for red hot maintenance at Ashuganj end.
k) Siddhirganj 132 kV Bus was under shut down from 13:30 to 15:51 for red hot maintenance.
l) Hasnabad-Lalbag 132 kV was switched on at 21:57.
m) Cox's bazar 132/33 kV T3 transformer was under shut down from 06:35 to 09:10 (25/12/2018) |  |  |  | About 8 MW Power interruption occurred under Cox's Bazar
for C/M. |  |  |  | S/S area from 06:35 to 09:10.
n) Rangpur-Saidpur 132 kV Ckt-2 was shut down at 07:31 (25/12/2018) for C/M at Rangpur end.
o) Barisal (Old)-Barisal (N) 132 kV Ckt-2 was shut down at 07:39 (25/12/2018) for A/M.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-12-24 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 38 | 890000 | #2 under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 111 | 3673000 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6706281
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 153664 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 12 | 530045 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 342 | 7887870 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 306 | 7360000 | Frequency Control.
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 420 | 8791000
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 40 | 118080 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 40 | 79272 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 156852 | Low demand
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 1097 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 230360
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 150 | 3095000
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 200 | 3845600
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 24 | 100224 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 48 | 419088 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 59220
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 506211
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 17 | 47840 | Engine problem
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 46 | 515520 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1301840 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 814100
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 25 | 586600 | Engine problem
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 43 | 544764 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 70 | 225820 | Low demand
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 58512 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 69 | 390240 | Low demand
| Dhaka area Total |  |  |  | 5798 | 2537 | 49088100
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 269820
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 127440
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 50 | 534720
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 31 | 668000 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 110 | 2585025 | Gas shortage
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 40 | 672000 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 68 | 331566
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 78 | 598920 | Low demand
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 1435200
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 518448
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 568800
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 46 | 231360 | Low demand
| Chattogram area Total |  |  |  | 1681 | 713 | 11341299
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 120 | 2186795 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 120 | 2153870 | Gas shortage
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 184 | 4658000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 255 | 5950000 | ST Under maint.
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7200500 | FGMO
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 40 | 616824 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 10 | 234240 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 956766
| Midland 150MW |  | IPP | 23*7.015 | 150 | 154 | 1022036
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1157150
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 7392 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 95 | 2354350
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 148 | 1656960
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 508464
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 210420
** | Tripura |  | Imported power | 0 | 160 | 122 | 2204160
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 302900 | Engine problem
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 466440
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1782 | 34167994
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 146 | 3631040 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 17 | 327204
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 80 | 513600 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12000
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 50 | 187200 | Low demand
| Mymensingh Area Total |  |  |  | 522 | 293 | 4671044
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 57 | 1307000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 63 | 1514040
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 2511475 | Machine problem.
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 225 | 5255000 | FGMO
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 947400
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 21 | 428000 | Engine problem
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 228816
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 66 | 1044000 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1066560
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 49 | 968400
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 0 | 763110 | Under maint.
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 46 | 792880
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 16 | 370750 | Engine problem
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 0 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 119340
| Sylhet Area Total |  |  |  | 1549 | 799 | 17316771
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 676 | 12213818
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 49 | 172800 | Low demand
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 43 | 198240
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 50 | 203264 | Low demand
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 270 | 6572736 | ST Under maint.
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 637875
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 1041120
| Khulna Area Total |  |  |  | 2209 | 1233 | 21039853
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 64 | 318720 | Low demand
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 26 | 456400 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 139 | 3091000 | FGMO & ST under maint.
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 96 | 1196895
| Barisal Area Total |  |  |  | 462 | 325 | 5063015
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 121968 | Low demand
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 490870
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 40 | 90847 | Low demand
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 183 | 4366364 | Engine problem
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 141 | 0 | 0 | Gas shortage
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | Gas shortage
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 39 | 157224
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 382800
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 5 | 100224 | Engine problem
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 152244
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 492960 | Engine problem
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 51 | 192116 | Low demand
| Rajshahi Area Total |  |  |  | 1546 | 487 | 6547617
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 150 | 3679500
122 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 61000
123 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
| Rangpur Area Total |  |  |  | 484 | 167 | 3740500
| Total |  |  |  | 17142 | 8336 | 152976193
| Eastern Grid Total |  |  |  | 12441 | 6124 | 116585208
| Western Grid Total |  |  |  | 4701 | 2212 | 36390985
| National Grid Total |  |  |  | 17142 | 8336 | 152976193
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-12-24 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5276 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2560 | MW
i) Dhaka area |  |  | 2855 | MW | i) Khulna area |  |  | 983 | MW
ii) Chittagong area |  |  | 867 | MW | ii) Rajshahi area |  |  | 827 | MW
iii) Comilla area |  |  | 681 | MW | iii) Barisal area |  |  | 207 | MW
iv) Mymensingh area |  |  | 565 | MW | iv) Rangpur area |  |  | 543 | MW
v) Sylhet area |  |  | 308 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 7836 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 95 | 1200 | Netrokona | 61 | 1830 | Goalpara | 27 | 1830
Munsiganj | 70 | 1930 | Jamalpur | 86 | 1830 | Central s/s | 57 | 1830
Sonargaon | 46 | 1800 | Sherpur | 62 | 1830 | Noapara | 72 | 1830
Shyampur | 144 | 900 | Srimongal | 23 | 1800 | Jessore | 104 | 1830
Bhulta | 152 | 1900 | Shahjibazar | 79 | 1830 | Jhenida | 76 | 1800
Madanganj | 33 | 1700 | Fenchuganj | 27 | 1800 | Bottail | 78 | 1830
Shitalakhya | 94 | 1200 | Kulawara | 28 | 2000 | G.K Project | 34 | 1800
Rahim steel | 10 | 1900 | Sylhet | 86 | 1900 | Faridpur | 120 | 1830
Matuail | 82 | 1000 | Chatak | 19 | 1800 | Madaripur | 88 | 2000
Ghorasal | 55 | 2100 | Sunamganj | 24 | 1830 | Gopalganj | 59 | 1800
Narsingdi | 104 | 2100 | Biani Bazar | 27 | 1800 | Bagerhat | 63 | 1830
Haripur (SBU) | 99 | 1800 | Comilla (S) | 128 | 1800 | Mongla | 34 | 1200
Ullon | 53 | 1800 | Comilla(N) | 65 | 1800 | Satkhira | 65 | 1830
Hasnabad | 145 | 1930 | Chandpur | 78 | 1930 | Gallamari | 36 | 1300
Magbazar | 87 | 1200 | Feni | 80 | 1900 | Magura | 35 | 1800
Maniknagar | 76 | 1200 | Chowmuhani | 124 | 1930 | Chuadanga | 66 | 1900
Bangabhaban | 16 | 1100 | Ashuganj | 37 | 800 | Barisal | 80 | 1830
Narinda | 58 | 1830 | Daudkandi | 80 | 1900 | Patuakhali | 69 | 1900
Dhanmondi | 79 | 1200 | B.Baria | 78 | 1930 | Bhandaria | 38 | 1930
Lalbag | 62 | 1200 | Ramganj | 24 | 1800 | Ishurdi | 42 | 1830
Madartek | 33 | 1800 | Madunaghat | 45 | 1800 | Ruppur Paromanobik | 1 | 100
Mirpur | 83 | 1800 | Hathazari | 69 | 1900 | Natore | 85 | 1830
Kalyanpur | 60 | 1800 | Khulshi | 162 | 1200 | Bogra | 172 | 1830
Gulshan | 76 | 1800 | Halishahar | 94 | 1830 | Noagaon | 85 | 1830
Uttara | 35 | 1600 | Baraulia | 127 | 1000 | Rajshahi | 97 | 1900
Uttara(New) | 6 | 1300 | Sikalbaha | 27 | 1800 | C.Nawabganj | 55 | 1830
Kamrangirchar | 54 | 1900 | Dohazari | 70 | 1930 | Amnura | 28 | 1830
Savar | 99 | 1200 | Cox'sbazar | 56 | 1800 | Pabna | 71 | 1830
Bhasantec | 79 | 1800 | Chandraghona | 20 | 1800 | Shahjadpur | 66 | 1830
Agargaon | 36 | 1830 | Kaptai | 3 | 1800 | Serajganj | 66 | 1830
Satmosjid | 60 | 1800 | A. Khaer Stl. | 15 | 1800 | Niyamatpur | 38 | 1800
Tongi | 109 | 1100 | Bakulia | 72 | 1800 | Joypurhat | 39 | 1930
Kabirpur | 121 | 1200 | Julda | 18 | 1200 | Rangpur | 95 | 1900
Basundhara | 82 | 1200 | TK chemical | 2 | 1100 | Lalmonirhat | 69 | 1900
Manikganj | 58 | 1830 | Modern Steel | 14 | 1600 | Saidpur | 100 | 1800
Joydevpur | 184 | 1930 | Shahmirpur | 22 | 1800 | Purbasadipur | 79 | 2000
New Tongi | 89 | 1800 | Khagrachhari | 14 | 1930 | Thakurgaon | 56 | 1800
Korda | 189 | 1800 | Matarbari | 19 | 1900 | Palashbari | 82 | 1830
Dhamrai | 38 | 1800 | Baroiar Hat | 18 | 1830 | Barapukuria | 39 | 1800
Tangail | 116 | 1830 | Rangamati | 6 | 700 | Panchagar | 34 | 1830
Mymensing | 177 | 1830 | Abul Khair 230 | 191 | 1500
Kishorganj | 66 | 2000 | BSRM | 64 | 100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-12-24
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 406 | 6:00 | 390 | 12:00 | Kaliakoir | 392 | 3:00 | 378 | 12:00
Bheramara | 412 | 2:00 | 400 | 18:00 | Bhulta | 407 | 1:00 | 398 | 11:00
Ashuganj(N) | 409 | 22:00 | 400 | 11:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 18:00 | 236 | 1:00 | Hathazari | 227 | 20:00 | 219 | 8:00
Ishurdi | 236 | 1:00 | 230 | 12:00 | Megnaghat | 238 | 1:00 | 230 | 12:00
Ashuganj | 244 | 14:00 | 240 | 9:00 | Fenchuganj | 245 | 6:00 | 236 | 12:00
Serajganj | 232 | 2:00 | 222 | 12:00 | Siddhirganj | 235 | 4:00 | 229 | 10:00
Baghabari | 230 | 2:00 | 225 | 18:00 | Maniknagar | 232 | 1:00 | 227 | 15:00
Barapukuria | 235 | 7:00 | 226 | 18:00 | Old Airport | 235 | 5:00 | 227 | 12:00
Bogra | 230 | 4:00 | 218 | 18:30 | Barisal | 237 | 20:00 | 231 | 1:00
Khulna South | 238 | 5:00 | 225 | 12:00 | AKSML | 225 | 19:30 | 214 | 10:00
Rampura | 231 | 6:00 | 228 | 11:00 | BSRM | 228 | 20:00 | 220 | 10:00
Haripur | 232 | 5:00 | 229 | 11:00 | Bibiyana | 241 | 4:00 | 233 | 12:00
Hasnabad | 234 | 20:00 | 230 | 8:00 | Bhulta | 234 | 2:00 | 228 | 12:00
Aminbazar | 236 | 3:00 | 229 | 11:00 | Ashuganj (S) | 242 | 21:00 | 237 | 13:00
Tongi | 233 | 5:00 | 226 | 11:00 | Kaliakoir | 240 | 1:00 | 231 | 12:00
Comilla (N) | 240 | 21:00 | 235 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 138 | 100 | 134 | 1600 | Ramganj | 136 | 1800 | 135 | 700
Munsiganj | 138 | 1800 | 134 | 1100 | Madanhat | 135 | 2000 | 127 | 1000
Megnaghat | 137 | 100 | 133 | 1100 | Hathazari | 134 | 2000 | 130 | 800
Shyampur | 134 | 400 | 129 | 1100 | Khulshi | 132 | 2000 | 124 | 1000
Bhulta | 135 | 300 | 126 | 1000 | Halishahar | 135 | 1930 | 126 | 1000
Madanganj | 139 | 2000 | 134 | 1000 | Baraulia | 133 | 2000 | 125 | 1000
Shitalakhya | 142 | 1830 | 134 | 1200 | Sikalbaha | 133 | 2000 | 125 | 1000
Rahim steal | 138 | 500 | 134 | 1100 | Dohazari | 128 | 1000 | 126 | 1100
Matuail | 137 | 300 | 133 | 1100 | Cox'sbazar | 127 | 1300 | 121 | 1000
Ghorasal | 140 | 100 | 138 | 1500 | Chandraghona | 134 | 2000 | 129 | 900
Narsinghdi | 139 | 1000 | 135 | 1400 | Kaptai | 135 | 2000 | 130 | 1000
Haripur (SBU) | 137 | 100 | 134 | 1100 | A. Khaer Stl. | 132 | 2100 | 126 | 1100
Ullon | 137 | 400 | 128 | 1200 | Bakulia | 133 | 2100 | 124 | 1000
Hasnabad | 141 | 200 | 136 | 1000 | Julda | 134 | 1900 | 125 | 1000
Magbazar | 137 | 100 | 130 | 1000 | TK Chemical | 134 | 1930 | 129 | 1000
Maniknagar | 135 | 200 | 132 | 1200 | Modern Steel | 133 | 1930 | 125 | 1000
Bangabhaban | 137 | 100 | 128 | 1200 | Shahmirpur | 133 | 1400 | 126 | 900
Narinda | 137 | 200 | 129 | 1200 | Khagrachhari | 133 | 1930 | 126 | 1000
Dhanmondi | 137 | 400 | 128 | 1200 | Matarbari | 129 | 1500 | 122 | 1000
Lalbag | 137 | 100 | 128 | 1200 | Baroiar Hat | 134 | 100 | 130 | 1100
Madartek | 137 | 200 | 129 | 1200 | Rangamati | 134 | 2100 | 126 | 1000
Mirpur | 136 | 600 | 131 | 1200 | Goalpara | 137 | 900 | 128 | 1600
Kalyanpur | 139 | 600 | 132 | 1200 | Central s/s | 137 | 900 | 126 | 1200
Gulshan | 137 | 100 | 128 | 1200 | Noapara | 136 | 900 | 124 | 1600
Uttara | 139 | 100 | 133 | 1200 | Jessore | 132 | 900 | 120 | 1800
Uttara(New) | 136 | 200 | 130 | 1200 | Jhenida | 133 | 900 | 120 | 1200
Kamrangirchar | 141 | 100 | 134 | 1200 | Bottail | 139 | 600 | 132 | 1800
Savar | 136 | 200 | 128 | 1200 | G.K.Project | 143 | 200 | 137 | 1830
Bhasantec | 137 | 200 | 131 | 1200 | Faridpur | 137 | 1700 | 132 | 1200
Agargaon | 137 | 200 | 131 | 1200 | Madaripur | 137 | 1700 | 132 | 1830
Satmosjid | 137 | 600 | 131 | 1200 | Gopalganj | 142 | 1700 | 131 | 2200
Tongi | 140 | 500 | 134 | 1100 | Bagerhat | 136 | 2100 | 126 | 1600
Kabirpur | 136 | 400 | 131 | 1800 | Mongla | 134 | 2100 | 121 | 1600
Basundhara | 133 | 500 | 124 | 1200 | Satkhira | 136 | 900 | 126 | 1600
Manikganj | 141 | 500 | 136 | 1800 | Gallamari | 138 | 900 | 127 | 1600
Joydevpur | 143 | 2000 | 136 | 1200 | Magura | 137 | 300 | 121 | 1830
New Tongi | 140 | 400 | 134 | 1200 | Chuadanga | 136 | 300 | 119 | 1830
Kodda | 141 | 1830 | 134 | 1500 | Barisal | 140 | 1700 | 135 | 100
Dhamrai | 136 | 200 | 131 | 1800 | Patuakhali | 140 | 1700 | 133 | 100
Tangail | 139 | 100 | 132 | 1200 | Bhandaria | 138 | 1700 | 124 | 1600
Mymensing | 137 | 100 | 132 | 1200 | Ishurdi | 140 | 600 | 135 | 1930
Kishorganj | 137 | 300 | 133 | 1400 | Ruppur Paromanobik | 140 | 600 | 136 | 1200
Netrokona | 138 | 400 | 133 | 1100 | Natore | 137 | 1700 | 132 | 1200
Jamalpur | 138 | 1900 | 126 | 1200 | Bogra | 138 | 600 | 139 | 1830
Sherpur | 135 | 2200 | 124 | 1200 | Noagaon | 135 | 500 | 127 | 1800
Srimongal | 140 | 100 | 136 | 1200 | Rajshahi | 135 | 600 | 129 | 1200
Shahjibazar | 140 | 100 | 137 | 1600 | C.Nawabganj | 131 | 2000 | 122 | 800
Fenchuganj | 136 | 200 | 132 | 1100 | Amnura | 135 | 1930 | 128 | 300
Khulawara | 136 | 500 | 131 | 1200 | Pabna | 136 | 500 | 130 | 1800
Sylhet | 136 | 600 | 130 | 1500 | Shahjadpur | 142 | 600 | 138 | 1800
Chatak | 136 | 100 | 129 | 1600 | Serajganj | 137 | 600 | 130 | 1930
Sunamganj | 136 | 700 | 129 | 1200 | Niyamatpur | 134 | 600 | 125 | 1800
Biani Bazar | 136 | 100 | 130 | 1200 | Joypurhat | 138 | 600 | 126 | 1800
Cumilla(s) | 131 | 700 | 129 | 1000 | Rangpur | 133 | 600 | 118 | 1830
Cumilla(n) | 144 | 2100 | 140 | 1830 | Lalmonirhat | 132 | 600 | 112 | 1830
Chandpur | 142 | 1800 | 140 | 1000 | Saidpur | 132 | 500 | 118 | 1800
Feni | 135 | 2100 | 133 | 1600 | Purbasadipur | 130 | 600 | 116 | 1800
Chowmuhani | 134 | 1500 | 130 | 1800 | Thakurgaon | 127 | 600 | 104 | 1800
Ashuganj | 142 | 700 | 140 | 1700 | Palashbari | 130 | 100 | 121 | 1800
Daudkandi | 138 | 1400 | 134 | 1200 | Barapukuria | 135 | 700 | 126 | 1800
B.Baria | 141 | 800 | 136 | 1600 | Panchagar | 126 | 500 | 102 | 1800

## L-Curve
Date | 2018-12-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 400 | 4634 | 1492 | 6126 |  |  |  | QF-LDC-12
0:30 | 435 | 4524.5 | 1320 | 5844.5 | Date: | 2018-12-24
1:00 | 470 | 4415 | 1148 | 5563
1:30 | 460 | 4241.5 | 1134.5 | 5376
2:00 | 450 | 4068 | 1121 | 5189
2:30 | 455 | 3980 | 1118 | 5098 | [5 empty] | Gen. at Eve. Peak | 8336 | 8336 MW (19:00 )
3:00 | 460 | 3892 | 1115 | 5007 | [6 empty] | 19:00
3:30 | 480 | 3853 | 1115 | 4968 | [5 empty] | Gen. at Day Peak | 6468.3 | 6468.3 MW (12:00 )
4:00 | 500 | 3814 | 1115 | 4929 | [6 empty] | 12:00
4:30 | 500 | 3811.5 | 1081.5 | 4893 | [5 empty] | Highest Generation | 8336
5:00 | 500 | 3809 | 1048 | 4857 | [6 empty] | 19:00
5:30 | 510 | 3986 | 1035.5 | 5021.5
6:00 | 520 | 4163 | 1023 | 5186
6:30 | 550 | 4254.65 | 1033.5 | 5288.15
7:00 | 580 | 4346.3 | 1044 | 5390.3
7:30 | 530 | 4373.85 | 1228.5 | 5602.35
8:00 | 480 | 4401.4 | 1413 | 5814.4
8:30 | 415 | 4542.25 | 1453.5 | 5995.75
9:00 | 350 | 4683.1 | 1494 | 6177.1
9:30 | 355 | 4721.05 | 1438.5 | 6159.55
10:00 | 360 | 4759 | 1383 | 6142
10:30 | 350 | 4826.95 | 1404.5 | 6231.45
11:00 | 340 | 4894.9 | 1426 | 6320.9
11:30 | 360 | 4942.1 | 1452.5 | 6394.6
12:00 | 380 | 4989.3 | 1479 | 6468.3
12:30 | 425 | 5033.9 | 1499.5 | 6533.4
13:00 | 470 | 5078.5 | 1520 | 6598.5
13:30 | 395 | 4891.7 | 1492 | 6383.7
14:00 | 320 | 4704.9 | 1464 | 6168.9
14:30 | 280 | 4736.4 | 1443 | 6179.4
15:00 | 240 | 4767.9 | 1422 | 6189.9
15:30 | 220 | 4750.15 | 1433.5 | 6183.65
16:00 | 200 | 4732.4 | 1445 | 6177.4
16:30 | 210 | 4771.3 | 1521.5 | 6292.8
17:00 | 220 | 4810.2 | 1598 | 6408.2
17:30 | 390 | 5340.6 | 1867.5 | 7208.1
18:00 | 560 | 5871 | 2137 | 8008
18:30 | 580 | 5997.5 | 2174.5 | 8172
19:00 | 600 | 6124 | 2212 | 8336
19:30 | 600 | 6050 | 2208 | 8258
20:00 | 640 | 5937 | 2173 | 8110 |  |  |  | Executive Engineer
20:30 | 585 | 5855.5 | 2134 | 7989.5 |  |  |  | Network Operation Division
21:00 | 530 | 5774 | 2095 | 7869
21:30 | 505 | 5626 | 1962 | 7588
22:00 | 480 | 5478 | 1829 | 7307 |  |  |  |  | Page 6 of 7
22:30 | 440 | 5236.5 | 1713 | 6949.5
23:00 | 400 | 4995 | 1597 | 6592
23:30 | 400 | 4814.5 | 1544.5 | 6359
24:00 | 400 | 4634 | 1492 | 6126
8336 MW (19:00 )
6468.3 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-12-24 |  | Energy | 152976193
[10 empty] | 2018-12-24 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3772 | 573 | 1425 | 92 | 150 | 32 | 0 | 0 | 82
0:30 | 3742.5 | 455.5 | 1301.5 | 84 | 150 | 32 | 0 | 0 | 79 | Date: | 2018-12-24
1:00 | 3713 | 338 | 1178 | 76 | 150 | 32 | 0 | 0 | 76
1:30 | 3660 | 338 | 1080.5 | 41.5 | 149.5 | 31.5 | 0 | 0 | 75 | [7 empty] | Total Energy | 152.9762 | Total Energy Gen 152.976 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 152.976 MKWHr
2:00 | 3607 | 338 | 983 | 7 | 149 | 31 | 0 | 0 | 74 | [7 empty] | Energy not Served | 0
2:30 | 3605.5 | 338 | 895 | 7 | 149 | 30.5 | 0 | 0 | 73 | [7 empty] | Energy Requirement | 152.9762
3:00 | 3604 | 338 | 807 | 7 | 149 | 30 | 0 | 0 | 72
3:30 | 3585 | 338 | 787 | 7 | 149 | 30 | 0 | 0 | 72 | [6 empty] | Shortage
4:00 | 3566 | 338 | 767 | 7 | 149 | 30 | 0 | 0 | 72
4:30 | 3531 | 338 | 767.5 | 7 | 149 | 29.5 | 0 | 0 | 71
5:00 | 3496 | 338 | 768 | 7 | 149 | 29 | 0 | 0 | 70
5:30 | 3549.5 | 338 | 876.5 | 8.5 | 149.5 | 29.5 | 0 | 0 | 70
6:00 | 3603 | 338 | 985 | 10 | 150 | 30 | 0 | 0 | 70
6:30 | 3628.5 | 338 | 1029 | 43 | 150 | 30 | 0 | 0 | 69 |  |  |  |  | Coal
7:00 | 3654 | 338 | 1073 | 76 | 150 | 30 | 0 | 0 | 68
7:30 | 3659.5 | 438.5 | 1078.5 | 167 | 149.5 | 30 | 0 | 0 | 75 |  |  |  | Oil |  |  |  | ,
8:00 | 3665 | 539 | 1084 | 258 | 149 | 30 | 0 | 0 | 82
8:30 | 3712.5 | 539 | 1152.5 | 324.5 | 149 | 30 | 0 | 0 | 84
9:00 | 3760 | 539 | 1221 | 391 | 149 | 30 | 0 | 0 | 86
9:30 | 3720.5 | 539.5 | 1255.5 | 368.5 | 149 | 31 | 0 | 0 | 85
10:00 | 3681 | 540 | 1290 | 346 | 149 | 32 | 0 | 0 | 84
10:30 | 3719 | 540 | 1292 | 388.5 | 149 | 32 | 1 | 0 | 89
11:00 | 3757 | 540 | 1294 | 431 | 149 | 32 | 2 | 0 | 94
11:30 | 3803 | 536.5 | 1294 | 461.5 | 149 | 32 | 2.5 | 0 | 94
12:00 | 3849 | 533 | 1294 | 492 | 149 | 32 | 3 | 0 | 94
12:30 | 3825 | 533 | 1281.5 | 591.5 | 149 | 32 | 4 | 0 | 96
13:00 | 3801 | 533 | 1269 | 691 | 149 | 32 | 5 | 0 | 98
13:30 | 3801 | 533 | 1269 | 691 | 149 | 32 | 5 | 0 | 98
14:00 | 3801 | 533 | 1269 | 691 | 149 | 32 | 5 | 0 | 98
14:30 | 3623 | 533.5 | 1169.5 | 768.5 | 149 | 31.5 | 5 | 0 | 97
15:00 | 3445 | 534 | 1070 | 846 | 149 | 31 | 5 | 0 | 96
15:30 | 3511.5 | 534 | 1100.5 | 740.5 | 149 | 30.5 | 9 | 0 | 98
16:00 | 3578 | 534 | 1131 | 635 | 149 | 30 | 13 | 0 | 100
16:30 | 3543.5 | 541.5 | 1172 | 708.5 | 149.5 | 30 | 41 | 0 | 103
17:00 | 3509 | 549 | 1213 | 782 | 150 | 30 | 69 | 0 | 106
17:30 | 3664.5 | 612.5 | 1346 | 1087.5 | 150 | 30 | 200.5 | 0 | 117
18:00 | 3820 | 676 | 1479 | 1393 | 150 | 30 | 332 | 0 | 128
18:30 | 3876.5 | 676 | 1454.5 | 1518 | 150 | 30.5 | 341.5 | 0 | 125
19:00 | 3933 | 676 | 1430 | 1643 | 150 | 31 | 351 | 0 | 122
19:30 | 3965 | 676 | 1440 | 1525 | 150 | 31 | 351 | 0 | 120
20:00 | 3930 | 676 | 1442 | 1435 | 149 | 31 | 327 | 0 | 120
20:30 | 3887.5 | 676 | 1445 | 1400 | 149.5 | 31.5 | 283 | 0 | 117
21:00 | 3845 | 676 | 1448 | 1365 | 150 | 32 | 239 | 0 | 114
21:30 | 3817.5 | 676.5 | 1439.5 | 1221.5 | 150 | 32 | 142 | 0 | 109
22:00 | 3790 | 677 | 1431 | 1078 | 150 | 32 | 45 | 0 | 104
22:30 | 3755.5 | 676.5 | 1456.5 | 750 | 150 | 32 | 31 | 0 | 98
23:00 | 3721 | 676 | 1482 | 422 | 150 | 32 | 17 | 0 | 92
23:30 | 3746.5 | 624.5 | 1453.5 | 257 | 150 | 32 | 8.5 | 0 | 87 | Max Temp. in Dhaka |  | 24.4° C
24:00 | 3772 | 573 | 1425 | 92 | 150 | 32 | 0 | 0 | 82
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 152.976 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 152.976 MKWHr
Note on W13: Author:

## Generation
2018-12-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 32 | 31 | 30 | 30 | 29 | 30 | 30 | 30 | 30 | 32 | 32 | 32 | 32 | 32 | 31 | 30 | 30 | 30 |  | 31 | 31 | 31 | 32 | 32 | 32 | 32 | 668000
2 | Kaptai Unit-4 & 5
3 | Chattogram ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 110 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
5 | Raozan 25 MW (RPCL) | [8 empty] | 0 | 0 | 8 | 8 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 269820
| Teknaf Solartech 20MW | [5 empty] | 0 | 1.3 | 7 | 0 | 18.4 | 20 | 20.3 | 18.5 | 14.4 | 13 | 7.1 | 0.2 | 0 |  | 0 | [6 empty] | 127440
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 120 | 100 | 102 | 100 | 102 | 130 | 130 | 130 | 130 | 130 | 120 | 60 | 70 | 80 | 80 | 100 | 130 | 130 |  | 110 | 110 | 110 | 80 | 100 | 100 | 100 | 2585025
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [16 empty] | 0 | 68 |  | 68 | 68 | 68 | 68 | 34 | 17 | 0 | 331566
12 | Hathazari peaking
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [16 empty] | 0 | 8 |  |  | 0 | [5 empty] | 7392
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 180 | 135 | 137 | 101 | 102 | 125 | 139 | 130 | 130 | 155 | 130 | 130 | 108 | 40 | 40 | 40 | 31 | 103 |  | 150 | 160 | 148 | 165 | 180 | 125 | 81 | 3095000
17 | Siddhirganj CCPP-335 MW | 120 | 120 | 120 | 120 | 120 | 150 | 150 | 120 | 120 | 120 | 145 | 155 | 220 | 130 | 130 | 130 | 145 | 214 |  | 200 | 200 | 200 | 210 | 228 | 200 | 180 | 3845600
18 | Summit Gazipur -2 | [16 empty] | 5 | 55 |  | 70 | 70 | 12 | 12 | 0 |  |  | 225820
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal ST: Unit-1,2 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 890000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 197 | 197 | 206 | 262 | 260 | 199 | 116 | 110 | 110 | 110 | 110 |  | 111 | 110 | 110 | 25 | 0 |  |  | 3673000
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 200 | 200 | 200 | 200 | 200 | 230 | 230 | 266 | 320 | 320 | 380 | 380 | 340 | 260 | 260 | 260 | 260 | 300 |  | 300 | 300 | 300 | 300 | 260 | 300 | 380 | 6706281
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 |  | 120 | 120 | 120 | 120 | 100 | 120 | 120 | 2186795
30 | Ashuganj ST: Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2153870
32 | Ashuganj Engines TSK | 40 | 40 | 5 | 5 | 5 | 40 | 40 | 40 | 40 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 616824
33 | Ashuganj CCPP 225 MW | 182 | 183 | 183 | 193 | 192 | 183 | 201 | 186 | 190 | 191 | 189 | 203 | 185 | 186 | 195 | 225 | 184 | 202 |  | 184 | 186 | 184 | 184 | 184 | 183 | 184 | 4658000
34 | Ashuganj CCPP(South) | 272 | 272 | 272 | 287 | 272 | 272 | 287 | 279 | 276 | 272 | 272 | 290 | 301 | 301 | 323 | 334 | 279 | 327 |  | 305 | 309 | 305 | 305 | 305 | 305 | 305 | 7200500
| Ashuganj CCPP(North) | 260 | 260 | 260 | 230 | 230 | 200 | 200 | 200 | 200 | 200 | 200 | 240 | 255 | 255 | 255 | 255 | 255 | 255 |  | 255 | 260 | 260 | 260 | 260 | 260 | 260 | 5950000
35 | Ashuganj (Precision) 55MW | 7 | 7 | 2 | 2 | 2 | 2 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 234240
36 | Chandpur CCPP | 95 | 102 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 100 | 100 | 100 | 94 | 100 | 100 | 100 | 100 | 100 |  | 95 | 100 | 100 | 95 | 100 | 100 | 95 | 2354350
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 305 | 300 | 298 | 300 | 300 | 312 | 312 | 312 | 315 | 325 | 334 | 345 | 350 | 343 | 343 | 343 | 343 | 300 |  | 342 | 347 | 340 | 335 | 325 | 315 | 295 | 7887870
40 | Meghnaghat CCPP 450MW | 310 | 310 | 310 | 300 | 300 | 340 | 340 | 340 | 340 | 380 | 350 | 420 | 420 | 340 | 340 | 360 | 400 | 420 |  | 420 | 420 | 420 | 400 | 380 | 400 | 420 | 8791000
41 | Haripur Power CCPP 360MW | 300 | 280 | 270 | 240 | 240 | 270 | 270 | 270 | 305 | 336 | 361 | 360 | 317 | 265 | 265 | 306 | 306 | 362 |  | 306 | 306 | 306 | 330 | 330 | 360 | 367 | 7360000
42 | Mymensingh RPCL 210MW | 149 | 127 | 169 | 170 | 171 | 171 | 172 | 172 | 170 | 165 | 163 | 162 | 147 | 147 | 147 | 150 | 151 | 158 |  | 146 | 146 | 145 | 143 | 143 | 146 | 146 | 3631040
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 |  | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 1307000
45 | Fenchugonj CCPP-2 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 62 | 62 | 66 |  | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 1514040
46 | Shajibazar 330 MW | 226 | 229 | 226 | 227 | 233 | 229 | 229 | 231 | 230 | 228 | 238 | 241 | 226 | 228 | 234 | 240 | 224 | 240 |  | 225 | 230 | 224 | 225 | 226 | 228 | 225 | 5255000
47 | Shahjibazar GT: Unit- 8, 9 | 37 | 36 | 35 | 36 | 37 | 36 | 36 | 36 | 35 | 34 | 34 | 34 | 20 | 25 | 51 | 51 | 55 | 67 |  | 66 | 68 | 68 | 47 | 64 | 56 | 51 | 1044000
48 | Shahjibazar 86MW | 10 | 10 | 3 | 3 | 3 | 50 | 50 | 50 | 86 | 86 | 50 | 30 | 30 | 10 | 10 | 10 | 10 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 5 | 1066560
49 | Shahjibazar (EPL) 50MW | 49 | 5 | 2 | 2 | 2 | 48 | 49 | 49 | 49 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 47 |  | 49 | 49 | 49 | 48 | 49 | 49 | 49 | 968400
50 | Sylhet GT 150 MW | 78 | 78 | 78 | 78 | 78 | 98 | 78 | 77 | 78 | 0 | 0 | [15 empty] | 763110
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 49 | 6 | 3 | 3 | 3 | 45 | 45 | 48 | 48 | 43 | 41 | 42 | 44 | 12 | 12 | 12 | 46 | 45 |  | 46 | 47 | 47 | 48 | 47 | 47 | 47 | 792880
53 | Sylhet (Desh) 10MW | [9 empty] | 0 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 119340
54 | Hobiganj 11MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 228816
55 | Fenchugonj (Barakatullah) 51MW | 5 | 5 | 5 | 5 | 5 | 11 | 17 | 22 | 50 | 51 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 50 | 53 | 53 | 53 | 53 | 53 | 53 | 947400
56 | Shahjahanulla 25 MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 370750
57 | Summit Bibiana- 2
58 | Southern 55MW | [16 empty] | 0 | 17 |  | 17 | 17 | 0 | 0 |  |  |  | 47840
59 | Sikalbaha (Energis) | 8 | 0 |  |  |  | 0 | 5 | 12 | 24 | 24 | 35 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 42 | 42 | 44 | 44 | 45 | 672000
60 | Barabkunda (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 518448
61 | Narshingdi (Doreen) | [7 empty] | 0 | 20 | 20 | 20 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 230360
62 | Tangail (Doreen) 22MW | 17 | 0 |  |  |  | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 327204
63 | Tripura | 76 | 74 | 72 | 72 | 70 | 70 | 68 | 82 | 86 | 84 | 94 | 94 | 98 | 98 | 96 | 100 | 106 | 128 |  | 122 | 120 | 120 | 114 | 104 | 92 | 82 | 2204160
64 | Malancha, Ctg. EPZ (United) | 41 | 38 | 38 | 38 | 41 | 40 | 40 | 14 | 4 | 4 | 3 | 3 | 8 | 7 | 3 | 3 | 8 | 15 |  | 23 | 28 | 30 | 32 | 38 | 41 | 41 | 568800
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 508464
66 | Feni, Mohipal (Doreen) | 11 | 0 |  |  |  | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 210420
67 | Jangalia (Summit) 33MW | [7 empty] | 0 | 0 | 8 | 8 | 8 | 25 | 16 | 18 | 18 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 302900
68 | Summit Cumilla 25MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 15 | 15 | 15 | 15 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 466440
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 575000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 30 | 30 | 30 | 30 | 31 | 31 | 31 | 31 | 31 | 26 |  | 32 | 32 | 32 | 32 | 32 | 32 | 33 | 726840
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 814100
72 | Summit Rupganj | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 586600
73 | Ghorashal (Regent) | 101 | 101 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 530045
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | [6 empty] | 0 | 6 | 11 | 25 | 27 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 0 |  | 544764
79 | Kodda 149MW
80 | Jamalpur 95MW | [6 empty] | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 12 | 62 |  | 80 | 80 | 80 | 80 | 80 | 21 | 0 | 513600
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW | [17 empty] | 22 |  | 40 | 0 | 0 |  |  |  |  | 79272
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | 85 | 6 | 6 | 6 | 6 | 6 | 50 | 50 | 85 | 85 | 85 | 30 | 30 | 10 | 10 | 10 | 10 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1157150
85 | Keraniganj (Powerpac) 100MW | [26 empty] | 1097
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | [16 empty] | 0 | 7 |  | 40 | 50 | 50 | 12 | 0 |  |  | 118080
88 | Ghorashal 78MW (MAX) | 40 | 40 | 0 | [23 empty] | 153664
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | [11 empty] | 0 | 50 | 50 | 50 | 50 | 60 | 60 |  | 78 | 78 | 78 | 78 | 50 | 0 | 0 | 598920
92 | Fenchuganj (EPL) 44MW | 21 | 21 | 2 | 2 | 2 | 8 | 21 | 21 | 21 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 428000
93 | Ashuganj (Midland) 51MW | 7 | 7 | 7 | 7 | 7 | 7 | 20 | 30 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 956766
94 | Gagnagar (Orion) | [16 empty] | 7 | 48 |  | 24 | 7 | 7 | 7 | 0 | 0 | 0 | 100224
95 | Patenga 50MW | [9 empty] | 0 | 4 | 6 | 14 | 48 | 47 | 47 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 41 |  | 534720
96 | Chattogram ECPV 108 MW | [11 empty] | 0 | 38 | 45 | 36 | 19 | 19 | 19 |  | 46 | 12 | 12 | 12 | 0 |  |  | 231360
97 | Katpotti 51 MW | [6 empty] | 0 | 2 | 6 | 6 | 6 | 6 | 6 | 46 | 48 | 6 | 6 | 43 |  | 48 | 48 | 48 | 47 | 12 | 0 | 0 | 419088
98 | Bosila 108MW | [6 empty] | 0 | 8 | 8 | 8 | 24 | 24 | 47 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 0 |  | 515520
99 | Madanganj-55 MW | [12 empty] | 0 | 15 | 15 | 15 | 15 | 25 |  | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 156852
100 | Northern 55 MW | [10 empty] | 0 | 18 | 35 | 55 | 55 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 0 |  | 506211
101 | Kushiara 163 MW CCPP GT | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2511475
102 | Sarishabari (Solar) | [6 empty] | 0 | 0.4 | 1.1 | 1.6 | 1.9 | 2 | 2 | 1.5 | 0.9 | 0.3 | 0 | 0 | [8 empty] | 12000
103 | Banco Energy 54MW | [7 empty] | 0 | 18 | 18 | 18 | 18 | 20 | 54 | 54 | 36 | 36 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 |  | 59220
104 | APR Energy , Keranigonj | [26 empty] | 58512
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 0 | 0 |  |  |  | 0 | 0 | 7 | 7 |  | 50 | 7 | 7 | 7 | 7 | 7 | 7 | 187200
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [10 empty] | 0 | 14 | 32 | 31 | 31 | 17 | 15 | 24 |  | 69 | 63 | 53 | 48 | 40 | 0 |  | 390240
115 | Juldah 100 MW Unit-3 | 20 | 0 |  |  |  | 0 | 10 | 30 | 30 | 30 | 90 | 90 | 90 | 95 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 40 | 1435200
116 | Chandpur Desh 200MW | 17 | 0 |  |  | 0 | 3 | 31 | 51 | 85 | 85 | 70 | 70 | 78 | 83 | 85 | 34 | 35 | 100 |  | 148 | 160 | 160 | 160 | 120 | 90 | 0 | 1656960
117 | Midland 150MW | [10 empty] | 0 | 6 | 15 | 50 | 50 | 50 | 58 | 152 |  | 154 | 154 | 154 | 154 | 102 | 0 |  | 1022036
118 | Bibiyana-3 285MW
120 | Eastern Zone Total | 4415 | 4068 | 3892 | 3814 | 3809 | 4163 | 4346.3 | 4401.4 | 4683.1 | 4759 | 4894.9 | 4989.3 | 5078.5 | 4704.9 | 4767.9 | 4732.4 | 4810.2 | 5871 |  | 6124 | 6050 | 5964 | 5774 | 5503 | 5038 | 4634 | 116585208
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [15 empty] | 0 | 16 | 53 |  | 49 | 49 | 42 | 16 |  |  |  | 172800
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [15 empty] | 0 | 35 | 43 |  | 43 | 43 | 43 | 43 | 11 |  |  | 198240
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [6 empty] | 7 | 70 | 105 | 53 | 53 | 53 | 53 | 53 | 25 | 17 | 35 | 105 |  | 105 | 105 | 105 | 105 | 53 |  |  | 1041120
130
131
132
133
| Summit Barisal 110 MW | [15 empty] | 0 | 32 | 48 |  | 64 | 64 | 64 | 64 | 64 |  |  | 318720
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 50 | 53 | 64 | 72 | 71 | 71 | 71 | 97 |  | 96 | 96 | 97 | 97 | 95 | 96 | 95 | 1196895
| Bhola CCPP 194MW | 139 | 143 | 143 | 143 | 143 | 136 | 143 | 145 | 143 | 86 | 85 | 83 | 65 | 138 | 134 | 134 | 117 | 137 |  | 139 | 139 | 135 | 125 | 134 | 140 | 126 | 3091000
140 | Bhola (Venture) 33MW | 20 | 19 | 19 | 19 | 17 | 19 | 17 | 17 | 17 | 16 | 17 | 16 | 16 | 18 | 16 | 16 | 19 | 26 |  | 26 | 27 | 26 | 26 | 25 | 22 | 20 | 456400
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | 24 | 0 |  |  |  | 0 | 16 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 16 | 16 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 |  | 637875
143 | Gopalganj Peaking | [9 empty] | 0 | 2 | 3 | 5 | 5 | 5 | 13 | 25 | 50 |  | 50 | 50 | 30 | 21 |  |  |  | 203264
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 338 | 338 | 338 | 338 | 338 | 338 | 338 | 539 | 539 | 540 | 540 | 533 | 533 | 534 | 534 | 534 | 549 | 676 |  | 676 | 676 | 676 | 676 | 677 | 676 | 573 | 12213818
147 | Bheramara 360 MW | 270 | 270 | 270 | 270 | 230 | 200 | 200 | 230 | 230 | 260 | 260 | 304 | 306 | 180 | 180 | 240 | 250 | 250 |  | 270 | 270 | 270 | 310 | 270 | 230 | 314 | 6572736
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 150 | 149 | 149 | 149 | 149 | 150 | 150 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 150 |  | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 3679500
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [17 empty] | 43 |  | 43 | 43 | 43 | 0 |  |  |  | 121968
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 182 | 182 | 176 | 176 | 151 | 161 | 149 | 155 | 178 | 147 | 153 | 168 | 203 | 180 | 187 | 191 | 193 | 168 |  | 183 | 178 | 179 | 184 | 179 | 183 | 182 | 4366364
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas)
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking
162 | Bogra (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 22 | 22 | 21 | 18 | 18 | 18 | 18 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 382800
163 | Bogra (EPL) | 5 | 0 |  |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 100224
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 5 | 152244
165 | Amnura 50MW | [7 empty] | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 50 |  | 50 | 50 | 50 | 50 | 50 | 0 |  | 490870
166 | Katakhali (Northern)
167 | Katakhali Peaking | [16 empty] | 0 | 30 |  | 40 | 40 | 36 | 0 |  |  |  | 90847
168 | Santahar Peaking | [15 empty] | 0 | 9 | 39 |  | 39 | 39 | 39 | 39 | 0 |  |  | 157224
169 | Rajlanka 52 MW | [6 empty] | 0 | 25 | 26 | 26 | 25 | 25 | 34 | 43 | 25 | 8 | 25 | 43 |  | 43 | 43 | 43 | 43 | 43 | 25 |  | 492960
170 | Chapainawabganj-100 MW | [16 empty] | 0 | 33 |  | 51 | 51 | 51 | 51 | 0 |  |  | 192116
171
172
173 | Rangpur GT | [17 empty] | 18 |  | 17 | 17 | 17 | 17 | 0 |  |  | 61000
175 | Saidpur GT | [16 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 0
176
177
178
178 | Western Zone Total | 1148 | 1121 | 1115 | 1115 | 1048 | 1023 | 1044 | 1413 | 1494 | 1383 | 1426 | 1479 | 1520 | 1464 | 1422 | 1445 | 1598 | 2137 |  | 2212 | 2208 | 2173 | 2095 | 1829 | 1597 | 1492 | 36390985