## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 10-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-07-2026 | during | 10-07-2026 | during | 10-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 357 | 350 | 412 | 412 | 380 | 380 | DP High
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 296 | 302 | 335 | 335 | 301.5 | 301.5 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 37 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 303 | 295 | 335 | 335 | 317 | 317 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16 | 0 | 33 | 33 | 17 | 17 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 130 | 195 | 300 | 300 | 64 | 130 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 53 | 132 | 149 | 149 | 70 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 17 | 51 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 8 | 0 | 20 | 0 | 20 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 405 | 475 | 583 | 583 | 524.7 | 524.7 | AGC+Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 300 | 300 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 143 | 143 | 143 | 143 | 143 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1761 | 2310 | 5795.22 | 5775.22 | 2193.2 | 2477.2
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 0 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 2 | 0 | 5 | 0 | 5 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 148 | 155 | 144 | 144 | 144 | 144 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 157 | 174 | 145 | 145 | 145 | 145 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 78 | 34 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 23 | 16 | 16 | 24 | 56 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 68 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 4 | 18 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.48 | 0 | 0.72 | 0 | 0.72 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 26 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 18 | 17 | 54.36 | 54.36 | 0 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 58 | 51 | 110 | 110 | 17 | 17 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 76 | 15 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 300 | 300 | 1224 | 1224 | 300 | 300 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 50 | 7 | 25 | 20 | 25 | 20 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1135 | 1135 | 720 | 1150 | 1150 | 1150 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2109.48 | 2032 | 3516.58 | 4022.86 | 3049.72 | 3254
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 208 | 196 | 221.25 | 221.25 | 220 | 220 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 300 | 320 | 350.01 | 350.01 | 280 | 280 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 240 | 300 | 342.01 | 342.01 | 240 | 240 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 280 | 350 | 393 | 393 | 250 | 250 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 37 | 40 | 41.65 | 41.65 | 37 | 37 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 20 | 0 | 52.82 | 52.82 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 150 | 37 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 17 | 17 | 40 | 40 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 93 | 94 | 163 | 163 | 95 | 95 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 124 | 142 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 33 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 28 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 67 | 115 | 115 | 0 | 51 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 10 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1708.2 | 1763.2 | 2732.44 | 2696.44 | 1653.2 | 1886.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-07-2026 | during | 10-07-2026 | during | 10-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 6.4 | 0 | 10 | 0 | 10 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.6 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 117 | 155 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 69 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 25.93 | 0 | 35 | 0 | 35 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 1 | 22 | 22 | 12 | 22 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 224.93 | 242 | 513.6 | 516.5 | 239.1 | 269
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 29 | 0 | 0 | 0 | 0 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 136 | 143 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 143 | 142 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 28 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 80 | 83 | 83 | 83 | 83 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 104 | 102 | 102 | 102 | 102 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 16 | 16 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 268 | 330 | 220 | 220 | 220 | 220 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1079 | 1177 | 1104 | 1104 | 1045 | 1045
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 905 | 905 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 35 | 35 | 35 | 35 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 50 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 105 | 105 | 32 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 45 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1195 | 1202 | 1234.2 | 1234.2 | 1200 | 1200 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2183 | 2245 | 3604.2 | 3539.2 | 2454.2 | 2389.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 500 | 882 | 500 | 600 | 500 | 600 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 8 | 48 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 64 | 65 | 130 | 130 | 65 | 65 | GT-1 & ST under maint
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1035 | 1180 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 237 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.18 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3407.64 | 2064.18 | 2756 | 2662 | 2761 | 2370 | 2469
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 21.74 | 0 | 18 | 0 | 18 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 26 | 40 | 40 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 11 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 154 | 161 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 141 | 153 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 150 | 150 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 350 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 25 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 101 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 1.91 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1412.2 | 1477.31 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 18.74 | 0 | 53 | 0 | 53 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 45 | 0 | 85 | 0 | 85 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2204.59 | 2505.31 | 3196.72 | 3035.12 | 2727.34 | 2742.74
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 40 | 40 | 40 | 40 | 39 | 39 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 188 | 180 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 40 | 42 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.7 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 110 | 115 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 11 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 28 | 0 | 164.02 | 0 | 164.02 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 419.7 | 377 | 683.02 | 488 | 549.02 | 389
System Total |  |  |  |  | 28843.2 | 29250.117 | 13754.08 | 15407.51 | 23807.78 | 23938.34 | 16280.78 | 16921.34
Forecast Scenario (10-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15160 |  | 350 |  | 15510
|  |  |  | 1:00 | 14900 |  | 320 |  | 15220
|  |  |  | 2:00 | 14750 |  | 150 |  | 14900
|  |  |  | 3:00 | 14470 |  | 140 |  | 14610
|  |  |  | 4:00 | 14090 |  | 120 |  | 14210
|  |  |  | 5:00 | 13840 |  | 100 |  | 13940
|  |  |  | 6:00 | 13110 |  | 60 |  | 13170
|  |  |  | 7:00 | 13040 |  | 50 |  | 13090
|  |  |  | 8:00 | 12750 |  | 0 |  | 12750
|  |  |  | 9:00 | 12440 |  | 0 |  | 12440
|  |  |  | 10:00 | 12420 |  | 0 |  | 12420
|  |  |  | 11:00 | 12780 |  | 0 |  | 12780
|  |  |  | 12:00 | 13290 |  | 0 |  | 13290
|  |  |  | 13:00 | 13900 |  | 0 |  | 13900
|  |  |  | 14:00 | 13480 |  | 0 |  | 13480
|  |  |  | 15:00 | 13550 |  | 0 |  | 13550
|  |  |  | 16:00 | 13190 |  | 0 |  | 13190
|  |  |  | 17:00 | 12650 |  | 0 |  | 12650
|  |  |  | 18:00 | 12010 |  | 0 |  | 12010
|  |  |  | 18:30 | 12450 |  | 0 |  | 12450
|  |  |  | 19:00 | 12910 |  | 0 |  | 12910
|  |  |  | 19:30 | 14600 |  | 0 |  | 14600
|  |  |  | 20:00 | 14540 |  | 0 |  | 14540
|  |  |  | 21:00 | 15000 |  | 0 |  | 15000
|  |  |  | 22:00 | 14940 |  | 0 |  | 14940
|  |  |  | 23:00 | 15040 |  | 0 |  | 15040
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 13290.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 328.25 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:28 hrs on 10-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 09-07-2026 | [28 empty] | Date: | 09-07-2026 | [28 empty] | Date: | 09-07-2026 | [28 empty] | Date: | 09-07-2026 | [28 empty] | Date: | 09-07-2026 | [18 empty] | Date: | 09-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [18 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 18 | 17 | 37 | 15 | 146 | 15 | 35 | 35 | 0 | 0 | 300 | 430 | 0 | 0 | 295 | 0 | 0 | 0 | 51 | 16 | 21 | 0 | 0 | 90 | 16 | 0 | 0 | 41 | 0 | 31 | 54.36 | 12 | 12 | 0 | 142 | 108 | 18 | 1130 | 0 | 0 | 50 | 0 | 98 | 133 | 0 | 0 | 0 | 300 | 0 | 20 | 0 | 220 | 300 | 225 | 51 | 0 | 220 | 15 | 0 | 96 | 108 | 3 | 19 | 98 | 152 | 52.2 | 0 | 17 | 305 | 0 | 256 | 0 | 0 | 132 | 0 | 16 | 0 | 81 | 30 | 141 | 0 | 102 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6798.56 | 859 | 0 | 0 | 23 | 36 | 38 | 0 | 0 | 151 | 0 | 15 | 0 | 1210 | 0 | 0 | 0 | 1477.65 | 0 | 32 | 0 | 35 | 35 | 0 | 94 | 19 | 52.2 | 0 | 0 | 19 | 0 | 0 | 145 | 0 | 122 | 0 | 0 | 0 | 250 | 0 | 0 | 181 | 42 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 64 | 180 | 0 | 500 | 1190 | 17 | 7290.85 | 14089.41 | 84.6
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 17 | 35 | 15 | 146 | 15 | 35 | 35 | 0 | 0 | 289 | 400 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 16 | 21 | 0 | 0 | 89 | 16 | 0 | 0 | 62 | 0 | 23 | 0 | 12 | 12 | 0 | 147 | 35 | 20 | 1130 | 0 | 0 | 50 | 0 | 34 | 134 | 0 | 0 | 0 | 300 | 0 | 20 | 0 | 250 | 300 | 220 | 51 | 0 | 219 | 15 | 0 | 94 | 17 | 0 | 19 | 98 | 148 | 52.2 | 0 | 17 | 310 | 0 | 256 | 0 | 0 | 131 | 0 | 16 | 0 | 81 | 28 | 143 | 0 | 102 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6463.2 | 889 | 0 | 0 | 0 | 37 | 38 | 0 | 0 | 101 | 0 | 15 | 0 | 1208 | 0 | 0 | 0 | 1476.56 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 19 | 52.2 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 122 | 0 | 0 | 0 | 339 | 0 | 0 | 181 | 43 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 275 | 64 | 220 | 0 | 500 | 1175 | 17 | 7151.76 | 13614.96 | 84.76
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 17 | 34 | 16 | 146 | 15 | 35 | 0 | 0 | 0 | 284 | 360 | 0 | 0 | 290 | 0 | 0 | 0 | 17 | 16.5 | 21 | 0 | 0 | 91 | 16 | 0 | 0 | 60 | 0 | 23 | 0 | 12 | 12 | 0 | 148 | 17 | 22 | 1130 | 0 | 0 | 50 | 0 | 34 | 134 | 0 | 0 | 0 | 300 | 0 | 20 | 0 | 250 | 300 | 220 | 51 | 0 | 220 | 15 | 0 | 94 | 17 | 0 | 19 | 97 | 140 | 52.2 | 0 | 17 | 300 | 0 | 256 | 0 | 0 | 125 | 0 | 16 | 0 | 81 | 28 | 142 | 0 | 102 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6358.7 | 889 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1206 | 0 | 0 | 0 | 1476.13 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 19 | 52.2 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 122 | 0 | 0 | 0 | 300 | 0 | 0 | 181 | 43 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 268 | 0 | 180 | 0 | 500 | 1175 | 17 | 6867.33 | 13226.03 | 84.92
03:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 17 | 34 | 16 | 45 | 15 | 0 | 0 | 0 | 0 | 287 | 420 | 0 | 0 | 290 | 0 | 0 | 0 | 17 | 16.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 12 | 12 | 0 | 150 | 17 | 22 | 1130 | 0 | 0 | 0 | 0 | 34 | 140 | 0 | 0 | 0 | 300 | 0 | 20 | 0 | 290 | 320 | 270 | 51 | 0 | 220 | 0 | 0 | 96 | 0 | 0 | 19 | 52 | 134 | 0 | 0 | 17 | 295 | 0 | 256 | 0 | 0 | 133 | 0 | 16 | 0 | 80 | 28 | 141 | 0 | 102 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6054.5 | 889 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1149 | 0 | 0 | 0 | 1476.08 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 122 | 0 | 0 | 0 | 372 | 0 | 0 | 181 | 43 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 274 | 0 | 220 | 0 | 500 | 1175 | 17 | 6802.08 | 12856.58 | 85.08
04:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 17 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 420 | 0 | 0 | 275 | 0 | 0 | 0 | 17 | 10 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 24 | 1130 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 300 | 320 | 240 | 51 | 0 | 198 | 0 | 0 | 94 | 0 | 0 | 19 | 0 | 122 | 0 | 0 | 0 | 295 | 0 | 256 | 0 | 0 | 132 | 0 | 16 | 0 | 80 | 28 | 140 | 0 | 102 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 5718 | 890 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 0 | 0 | 1442.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 122 | 0 | 0 | 0 | 376 | 0 | 0 | 181 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 30 | 220 | 0 | 500 | 1175 | 0 | 6510.41 | 12228.41 | 85.24
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 395 | 0 | 0 | 281 | 0 | 0 | 0 | 17 | 10 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 24 | 930 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 300 | 320 | 240 | 51 | 0 | 199 | 0 | 0 | 94 | 0 | 0 | 19 | 0 | 120 | 0 | 0 | 0 | 295 | 0 | 256 | 0 | 0 | 130 | 0 | 16 | 0 | 80 | 30 | 141 | 0 | 102 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 5453 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 992 | 0 | 0 | 0 | 1385.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 122 | 0 | 0 | 0 | 393 | 0 | 0 | 181 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 45 | 220 | 0 | 500 | 1105 | 0 | 6283.24 | 11736.24 | 85.4
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 385 | 0 | 0 | 283 | 0 | 0 | 1 | 17 | 10 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 10 | 10 | 0 | 150 | 0 | 24 | 907 | 0 | 0 | 1 | 0 | 0 | 141 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 300 | 320 | 240 | 51 | 0 | 221 | 0 | 0 | 96 | 0 | 0 | 19 | 0 | 122 | 0 | 1 | 0 | 300 | 0 | 256 | 0 | 0 | 129 | 0 | 16 | 0 | 80 | 30 | 143 | 0 | 104 | 0 | 49 | 0.03 | 48 | 0 | 0 | 0 | 0 | 5435.03 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0.39 | 876 | 0 | 0 | 0 | 1293.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54 | 0 | 0 | 0 | 0 | 148 | 0 | 122 | 0 | 0 | 0 | 407 | 0 | 0 | 181 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 170 | 50 | 220 | 0 | 500 | 1000 | 0 | 5945.06 | 11380.09 | 85.56
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 450 | 0 | 0 | 288 | 0 | 0 | 2 | 17 | 10 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 12 | 12 | 0 | 147 | 0 | 17 | 955 | 0 | 0 | 35 | 0 | 0 | 142 | 0 | 0 | 0 | 300 | 1 | 0 | 0 | 250 | 320 | 240 | 51 | 4 | 219 | 15 | 0 | 94 | 0 | 0 | 19 | 0 | 120 | 0 | 1 | 0 | 305 | 0 | 256 | 0 | 0 | 135 | 1 | 16 | 0 | 80 | 30 | 143 | 0 | 103 | 0 | 49 | 0.82 | 48 | 0 | 0 | 1.85 | 0 | 5578.67 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3.9 | 780 | 0 | 0 | 0 | 1319.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.75 | 2 | 0 | 0 | 0 | 150 | 0 | 124 | 0 | 0 | 0 | 408 | 0 | 0 | 181 | 42 | 0 | 4 | 0 | 0 | 0 | 0 | 0.3 | 9 | 0.07 | 0 | 166 | 50 | 220 | 0 | 500 | 982 | 0 | 5878.38 | 11457.05 | 85.72
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 460 | 0 | 0 | 288 | 0 | 0 | 2 | 17 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 12 | 12 | 0.65 | 144 | 0 | 10 | 1020 | 0 | 0 | 50 | 0 | 0 | 141 | 0 | 0 | 0 | 302 | 2 | 0 | 0 | 250 | 320 | 240 | 51 | 5 | 220 | 15 | 0 | 94 | 0 | 0 | 19 | 0 | 136 | 0 | 16 | 0 | 305 | 0 | 256 | 0 | 0 | 137 | 1 | 16 | 0 | 80 | 30 | 143 | 0 | 102 | 0 | 49 | 2.5 | 48 | 0 | 0.2 | 1.7 | 0 | 5710.05 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 770 | 0 | 0 | 0 | 1393.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.29 | 1 | 0 | 0 | 0 | 153 | 0 | 129 | 0 | 0 | 0 | 408 | 0 | 0 | 181 | 40 | 0 | 2 | 0 | 0 | 0 | 0 | 1.2 | 12 | 0.07 | 0 | 181 | 60 | 220 | 0 | 500 | 1040 | 0 | 6051.59 | 11761.64 | 85.92
09:00 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 5 | 34 | 15 | 15 | 0 | 0 | 17 | 0 | 0 | 292 | 465 | 0 | 0 | 281 | 0 | 0 | 3 | 17 | 17 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 18 | 12 | 12 | 1.04 | 144 | 0 | 0 | 975 | 0 | 0 | 50 | 0 | 1 | 141 | 0 | 0 | 0 | 300 | 1 | 6 | 0 | 220 | 280 | 220 | 51 | 5 | 195 | 29 | 0 | 93 | 0 | 0 | 19 | 20 | 140 | 0 | 17 | 0 | 310 | 0 | 268 | 0 | 0 | 139 | 1 | 16 | 0 | 78 | 30 | 142 | 0 | 102 | 0 | 49 | 1.3 | 48 | 0 | 0.6 | 3.26 | 0 | 5681.2 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 925 | 0 | 0 | 0 | 1449.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.61 | 3 | 0 | 0 | 0 | 153 | 0 | 135 | 0 | 0 | 0 | 402 | 0 | 0 | 189 | 40 | 0 | 12 | 0 | 0 | 0 | 0 | 1.2 | 26 | 0.13 | 0 | 277 | 64 | 220 | 0 | 500 | 1100 | 0 | 6468.46 | 12149.66 | 86.12
10:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 17 | 34 | 15 | 97 | 10 | 17 | 17 | 0 | 0 | 290 | 445 | 0 | 0 | 275 | 0 | 0 | 5 | 17 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 12 | 1.06 | 144 | 26 | 5 | 965 | 0 | 0 | 50 | 0 | 17 | 141 | 0 | 0 | 0 | 300 | 0 | 56 | 0 | 260 | 280 | 220 | 43 | 16 | 220 | 36 | 0 | 93 | 14 | 0 | 19 | 58 | 144 | 8 | 14 | 0 | 310 | 0 | 268 | 0 | 0 | 134 | 2 | 16 | 0 | 78 | 30 | 143 | 0 | 102 | 0 | 58 | 3.8 | 114 | 0 | 0.7 | 13.14 | 0 | 6094.7 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 1062 | 0 | 0 | 0 | 1449.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.55 | 6 | 0 | 0 | 0 | 154 | 0 | 135 | 0 | 0 | 0 | 401 | 0 | 0 | 183 | 40 | 0 | 8 | 0 | 0 | 0 | 0 | 2.3 | 21 | 0.15 | 0 | 273 | 64 | 220 | 0 | 500 | 1055 | 0 | 6548.17 | 12642.87 | 86.32
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 44 | 0 | 97 | 37 | 17 | 17 | 0 | 0 | 293 | 440 | 0 | 0 | 300 | 0 | 0 | 9 | 17 | 16 | 21 | 0 | 0 | 26 | 16 | 0 | 0 | 16 | 0 | 4 | 18 | 12 | 12 | 1.68 | 144 | 51 | 6 | 965 | 0 | 0 | 50 | 0 | 49 | 141 | 0 | 0 | 0 | 300 | 2 | 105 | 0 | 375 | 280 | 220 | 43 | 20 | 200 | 37 | 0 | 93 | 17 | 0 | 19 | 97 | 134 | 43 | 25 | 1 | 305 | 0 | 256 | 0 | 0 | 139 | 2 | 16 | 0 | 80 | 30 | 143 | 0 | 102 | 15 | 58 | 8.3 | 114 | 0 | 0.6 | 3.82 | 0 | 6523.4 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 1122 | 0 | 0 | 0 | 1433.47 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 19.81 | 24 | 0 | 0 | 19 | 154 | 0 | 142 | 0 | 0 | 0 | 395 | 0 | 2.02 | 191 | 40 | 0 | 7 | 0 | 0 | 0 | 0 | 2.4 | 25 | 0.18 | 0 | 275 | 64 | 220 | 0 | 500 | 1050 | 0 | 6664.88 | 13188.28 | 86.52
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 17 | 17 | 53 | 0 | 130 | 37 | 17 | 17 | 0 | 0 | 296 | 405 | 0 | 0 | 303 | 0 | 0 | 8 | 17 | 16 | 21 | 0 | 0 | 76 | 16 | 0 | 0 | 50 | 0 | 16 | 18 | 12 | 12 | 1.48 | 148 | 58 | 4 | 1135 | 0 | 0 | 25 | 1 | 78 | 157 | 0 | 0 | 0 | 300 | 2 | 150 | 0 | 280 | 300 | 240 | 43 | 20 | 208 | 37 | 0 | 93 | 17 | 0 | 19 | 98 | 124 | 52.2 | 10 | 17 | 305 | 0 | 268 | 0 | 0 | 136 | 2 | 16 | 0 | 77 | 30 | 143 | 0 | 102 | 17 | 58 | 6.4 | 117 | 0 | 0.6 | 25.93 | 0 | 6882.61 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 1195 | 0 | 0 | 0 | 1412.2 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 21.74 | 45 | 0 | 0 | 18.74 | 154 | 0 | 141 | 0 | 0 | 0 | 350 | 0 | 1.91 | 188 | 40 | 110 | 11 | 40 | 0 | 0 | 0 | 2.7 | 28 | 0.18 | 8 | 237 | 64 | 220 | 0 | 500 | 1035 | 0 | 6871.47 | 13754.08 | 86.72
13:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 17 | 52 | 0 | 130 | 43 | 35 | 17 | 0 | 0 | 289 | 485 | 0 | 0 | 290 | 0 | 0 | 9 | 17 | 16 | 21 | 0 | 0 | 60 | 16 | 0 | 0 | 13 | 0 | 16 | 18 | 12 | 12 | 0.75 | 126 | 73 | 2 | 1135 | 0 | 0 | 0 | 8 | 105 | 174 | 0 | 0 | 0 | 302 | 5 | 68 | 0 | 250 | 280 | 220 | 43 | 0 | 217 | 34 | 1 | 92 | 75 | 0 | 19 | 97 | 126 | 52.2 | 14 | 17 | 310 | 0 | 256 | 0 | 0 | 140 | 4 | 16 | 0 | 77 | 30 | 143 | 0 | 102 | 17 | 58 | 2.7 | 117 | 0 | 1.9 | 25.49 | 0 | 6828.04 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 70 | 1175 | 0 | 0 | 0 | 1414.21 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 52.2 | 33.05 | 76 | 0 | 0 | 17.74 | 155 | 0 | 141 | 0 | 0 | 0 | 340 | 0 | 1.11 | 188 | 40 | 115 | 12 | 100 | 0 | 0 | 0 | 3.9 | 34 | 0.29 | 32 | 270 | 64 | 180 | 0 | 500 | 1045 | 0 | 7052.5 | 13880.54 | 86.9
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 17 | 17 | 68 | 0 | 130 | 55 | 35 | 17 | 0 | 0 | 290 | 425 | 0 | 0 | 300 | 0 | 0 | 17 | 17 | 16 | 20 | 0 | 0 | 61 | 16 | 0 | 0 | 19 | 0 | 16 | 18 | 12 | 12 | 0.37 | 128 | 110 | 2 | 1135 | 0 | 0 | 0 | 17 | 105 | 174 | 0 | 0 | 0 | 302 | 1 | 53 | 0 | 250 | 280 | 220 | 43 | 0 | 198 | 39 | 16 | 91 | 193 | 0 | 19 | 97 | 116 | 52.2 | 49 | 17 | 300 | 0 | 256 | 0 | 0 | 131 | 4 | 16 | 0 | 77 | 30 | 142 | 0 | 102 | 0 | 58 | 8.6 | 117 | 0 | 1 | 6.48 | 0 | 6911.65 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 1205 | 0 | 0 | 0 | 1368.64 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 52.2 | 20.99 | 29 | 0 | 0 | 28.82 | 154 | 0 | 141 | 0 | 0 | 0 | 300 | 0 | 2.59 | 190 | 40 | 115 | 11 | 106 | 0 | 0 | 0 | 2.2 | 58 | 0.07 | 32 | 273 | 64 | 220 | 0 | 500 | 1035 | 17 | 6978.51 | 13890.16 | 87.3
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 61 | 0 | 130 | 55 | 35 | 17 | 0 | 0 | 288 | 480 | 0 | 0 | 300 | 0 | 0 | 17 | 17 | 15 | 20 | 0 | 0 | 60 | 16 | 0 | 0 | 53 | 0 | 23 | 18 | 12 | 12 | 0.09 | 132 | 110 | 4 | 1135 | 0 | 0 | 0 | 8 | 105 | 174 | 0 | 0 | 0 | 300 | 2 | 53 | 0 | 250 | 280 | 220 | 51 | 0 | 200 | 37 | 17 | 92 | 192 | 0 | 19 | 97 | 122 | 52.2 | 1 | 17 | 305 | 0 | 256 | 0 | 0 | 149 | 3 | 16 | 0 | 76 | 30 | 144 | 0 | 104 | 5 | 58 | 13.73 | 117 | 0 | 1 | 20.25 | 0 | 7000.27 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24 | 1154 | 0 | 0 | 0 | 1324.17 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 52.2 | 28.01 | 30 | 0 | 0 | 22.39 | 155 | 0 | 141 | 0 | 0 | 0 | 300 | 0 | 1.05 | 200 | 40 | 115 | 10 | 34 | 0 | 0 | 0 | 0.6 | 64 | 0.17 | 40 | 275 | 64 | 220 | 0 | 600 | 1040 | 17 | 6944.59 | 13944.86 | 87.5
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 12 | 51 | 0 | 130 | 55 | 35 | 17 | 0 | 0 | 292 | 455 | 0 | 17 | 300 | 0 | 0 | 2 | 17 | 15 | 20 | 0 | 0 | 15 | 16 | 0 | 0 | 46 | 0 | 23 | 18 | 12 | 12 | 0.08 | 132 | 110 | 5 | 1135 | 0 | 0 | 11 | 8 | 105 | 174 | 0 | 0 | 0 | 300 | 1 | 55 | 0 | 250 | 280 | 240 | 51 | 0 | 198 | 39 | 16 | 92 | 155 | 0 | 19 | 97 | 128 | 52.2 | 4 | 17 | 305 | 0 | 242 | 0 | 0 | 143 | 1 | 16 | 0 | 78 | 30 | 140 | 0 | 103 | 17 | 58 | 5.6 | 117 | 0 | 1 | 20 | 0 | 6870.88 | 904 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19 | 1066 | 0 | 0 | 0 | 1237.22 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 52.2 | 10.02 | 50 | 0 | 0 | 1.77 | 155 | 0 | 141 | 0 | 0 | 0 | 414 | 0 | 0.15 | 185 | 41 | 115 | 7 | 34 | 0 | 0 | 0 | 0.3 | 79 | 0.12 | 48 | 277 | 64 | 220 | 0 | 600 | 1030 | 17 | 6855.78 | 13726.66 | 87.65
17:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 17 | 51 | 0 | 130 | 55 | 35 | 17 | 0 | 0 | 284 | 360 | 0 | 35 | 289 | 0 | 0 | 2 | 17 | 15 | 21 | 0 | 0 | 15 | 16 | 0 | 0 | 53 | 0 | 23 | 18 | 12 | 12 | 0.03 | 161 | 34 | 11 | 1135 | 0 | 0 | 42 | 8 | 34 | 174 | 0 | 0 | 0 | 300 | 0 | 55 | 0 | 250 | 280 | 240 | 51 | 0 | 190 | 40 | 17 | 93 | 34 | 15 | 19 | 34 | 138 | 16 | 2 | 17 | 300 | 0 | 242 | 0 | 0 | 123 | 1 | 16 | 0 | 80 | 30 | 142 | 0 | 103 | 17 | 58 | 5.66 | 116 | 0 | 0.7 | 14 | 0 | 6475.39 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 24 | 3 | 1183 | 0 | 0 | 0 | 1218.8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 16 | 4.53 | 9 | 0 | 0 | 10.41 | 155 | 0 | 142 | 0 | 0 | 0 | 374 | 0 | 1.07 | 185 | 41 | 115 | 2 | 34 | 0 | 0 | 0 | 0.9 | 35 | 0.04 | 48 | 259 | 64 | 180 | 0 | 600 | 1030 | 35 | 6762.75 | 13238.14 | 87.75
18:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 35 | 17 | 53 | 0 | 195 | 40 | 35 | 72 | 0 | 0 | 292 | 400 | 0 | 35 | 296 | 0 | 0 | 2 | 17 | 15 | 21 | 0 | 0 | 15 | 16 | 0 | 0 | 21 | 0 | 23 | 18 | 12 | 12 | 0 | 161 | 34 | 11 | 1100 | 13 | 0 | 50 | 17 | 34 | 174 | 0 | 0 | 0 | 300 | 0 | 60 | 0 | 250 | 280 | 240 | 51 | 0 | 200 | 40 | 18 | 93 | 32 | 26 | 19 | 33 | 138 | 16 | 2 | 17 | 310 | 0 | 266 | 0 | 0 | 133 | 1 | 16 | 0 | 80 | 30 | 142 | 0 | 103 | 17 | 59 | 1.66 | 116 | 0 | 0.2 | 1.34 | 0 | 6710.2 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 2 | 1139 | 0 | 0 | 0 | 1217.75 | 0 | 0 | 0 | 45 | 50 | 0 | 17 | 0 | 16 | 3.07 | 3 | 0 | 0 | 4.36 | 154 | 0 | 143 | 0 | 0 | 0 | 330 | 0 | 0.33 | 180 | 40 | 115 | 1 | 34 | 0 | 0 | 0 | 0.2 | 7 | 0.01 | 48 | 199 | 64 | 180 | 0 | 600 | 1000 | 35 | 6620.72 | 13330.92 | 87.95
19:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 35 | 17 | 105 | 0 | 195 | 40 | 35 | 108 | 0 | 0 | 292 | 365 | 0 | 35 | 300 | 0 | 0 | 0 | 143 | 0 | 21 | 0 | 0 | 13 | 16 | 0 | 0 | 31 | 0 | 23 | 20 | 12 | 12 | 0 | 166 | 41 | 12 | 1135 | 16 | 0 | 50 | 17 | 52 | 174 | 0 | 0 | 0 | 300 | 0 | 61 | 0 | 250 | 280 | 240 | 51 | 0 | 201 | 40 | 32 | 93 | 30 | 28 | 19 | 29 | 144 | 16 | 0 | 17 | 300 | 0 | 320 | 29 | 0 | 121 | 0 | 16 | 0 | 80 | 30 | 143 | 0 | 102 | 17 | 59 | 0 | 116 | 0 | 0 | 0 | 0 | 7093 | 905 | 0 | 0 | 27 | 25 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1105 | 0 | 0 | 0 | 1417.48 | 0 | 0 | 0 | 50 | 50 | 10 | 101 | 17 | 16 | 0 | 0 | 21 | 0 | 0 | 155 | 0 | 148 | 0 | 0 | 0 | 300 | 0 | 0 | 180 | 39 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 212 | 64 | 180 | 0 | 700 | 1035 | 54 | 7096.48 | 14189.48 | 88
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 35 | 17 | 133 | 0 | 195 | 55 | 35 | 108 | 0 | 0 | 303 | 385 | 0 | 0 | 298 | 0 | 0 | 0 | 143 | 0 | 21 | 0 | 0 | 15 | 22 | 0 | 0 | 7 | 0 | 23 | 54.36 | 12 | 12 | 0 | 165 | 102 | 12 | 1135 | 16 | 0 | 50 | 0 | 105 | 174 | 0 | 0 | 0 | 300 | 0 | 61 | 0 | 250 | 280 | 260 | 51 | 0 | 198 | 40 | 68 | 93 | 95 | 28 | 19 | 46 | 148 | 43 | 0 | 17 | 305 | 0 | 330 | 29 | 0 | 130 | 0 | 16 | 0 | 80 | 30 | 142 | 0 | 101 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 0 | 7485.36 | 905 | 0 | 0 | 32 | 35 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1127 | 0 | 0 | 0 | 1470.56 | 0 | 0 | 0 | 50 | 50 | 11 | 101 | 19 | 16 | 0 | 0 | 21 | 0 | 0 | 156 | 0 | 153 | 0 | 0 | 0 | 414 | 0 | 0 | 180 | 41 | 115 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 301 | 64 | 220 | 0 | 700 | 1160 | 54 | 7573.56 | 15058.92 | 88.15
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 35 | 17 | 132 | 0 | 195 | 55 | 35 | 108 | 0 | 0 | 305 | 385 | 0 | 17 | 301 | 0 | 0 | 0 | 143 | 0 | 21 | 0 | 0 | 15 | 26 | 0 | 0 | 0 | 0 | 23 | 54.36 | 12 | 12 | 0 | 160 | 110 | 13 | 1135 | 16 | 0 | 50 | 0 | 105 | 174 | 0 | 0 | 0 | 300 | 0 | 60 | 0 | 250 | 280 | 260 | 51 | 0 | 200 | 41 | 69 | 94 | 70 | 27 | 19 | 98 | 140 | 52.2 | 0 | 17 | 305 | 0 | 330 | 29 | 0 | 133 | 0 | 16 | 0 | 80 | 30 | 143 | 0 | 102 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 0 | 7552.56 | 905 | 0 | 0 | 29 | 55 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1176 | 0 | 0 | 0 | 1475.6 | 0 | 0 | 0 | 50 | 50 | 11 | 101 | 25 | 16 | 0 | 0 | 21 | 0 | 0 | 157 | 0 | 153 | 0 | 0 | 0 | 414 | 0 | 0 | 180 | 40 | 115 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 65 | 220 | 0 | 700 | 1160 | 54 | 7657.6 | 15210.16 | 88.25
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 35 | 17 | 132 | 0 | 195 | 55 | 35 | 108 | 0 | 0 | 302 | 475 | 0 | 17 | 295 | 0 | 0 | 0 | 143 | 0 | 21 | 0 | 0 | 15 | 26 | 0 | 0 | 7 | 34 | 23 | 17 | 12 | 12 | 0 | 155 | 51 | 18 | 1135 | 0 | 0 | 19 | 0 | 34 | 174 | 0 | 0 | 0 | 300 | 0 | 37 | 0 | 350 | 320 | 300 | 51 | 0 | 196 | 40 | 67 | 94 | 17 | 28 | 19 | 33 | 142 | 52.2 | 0 | 17 | 305 | 0 | 330 | 29 | 0 | 143 | 0 | 16 | 0 | 80 | 28 | 142 | 0 | 104 | 17 | 69 | 0 | 155 | 0 | 0 | 0 | 1 | 7524.2 | 905 | 0 | 0 | 0 | 50 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1202 | 0 | 0 | 0 | 1477.31 | 0 | 26 | 0 | 50 | 50 | 11 | 101 | 25 | 16 | 0 | 0 | 21 | 0 | 0 | 161 | 0 | 153 | 0 | 0 | 0 | 414 | 0 | 0 | 180 | 40 | 115 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 65 | 220 | 0 | 882 | 1180 | 54 | 7883.31 | 15407.51 | 88.35
22:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 35 | 17 | 132 | 0 | 145 | 55 | 35 | 54 | 0 | 0 | 304 | 440 | 0 | 17 | 300 | 0 | 0 | 0 | 143 | 15 | 21 | 0 | 0 | 15 | 32 | 0 | 0 | 12 | 34 | 8 | 17 | 12 | 12 | 0 | 58 | 51 | 22 | 1135 | 0 | 0 | 19 | 0 | 34 | 174 | 0 | 0 | 0 | 300 | 0 | 20 | 0 | 350 | 320 | 300 | 51 | 0 | 203 | 40 | 58 | 96 | 17 | 28 | 19 | 17 | 142 | 52.2 | 0 | 0 | 310 | 0 | 330 | 29 | 0 | 135 | 0 | 16 | 0 | 80 | 25 | 143 | 0 | 103 | 17 | 69 | 0 | 155 | 0 | 0 | 0 | 6 | 7181.2 | 905 | 0 | 0 | 0 | 34 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1205 | 0 | 0 | 0 | 1475.93 | 0 | 25 | 0 | 50 | 50 | 0 | 101 | 25 | 16 | 0 | 0 | 21 | 0 | 0 | 162 | 0 | 151 | 0 | 13 | 0 | 350 | 0 | 0 | 180 | 40 | 50 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 276 | 65 | 220 | 0 | 1050 | 1190 | 17 | 7782.93 | 14964.13 | 88.55
23:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 35 | 17 | 101 | 20 | 146 | 55 | 35 | 54 | 0 | 0 | 309 | 520 | 0 | 17 | 323 | 0 | 0 | 0 | 143 | 15 | 21 | 0 | 0 | 15 | 16 | 0 | 0 | 16 | 34 | 8 | 18 | 12 | 12 | 0 | 58 | 56 | 30 | 1000 | 0 | 0 | 19 | 0 | 34 | 174 | 0 | 0 | 0 | 303 | 0 | 13 | 0 | 300 | 300 | 280 | 51 | 0 | 196 | 40 | 33 | 96 | 17 | 28 | 19 | 17 | 144 | 52.2 | 0 | 0 | 315 | 0 | 330 | 29 | 0 | 145 | 0 | 15 | 0 | 80 | 25 | 144 | 0 | 103 | 17 | 69 | 0 | 155 | 0 | 0 | 0 | 0 | 7033.2 | 905 | 0 | 0 | 0 | 34 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1209 | 0 | 0 | 0 | 1486.11 | 0 | 25 | 0 | 50 | 50 | 0 | 101 | 25 | 16 | 0 | 0 | 21 | 0 | 0 | 158 | 0 | 144 | 0 | 22 | 0 | 414 | 0 | 0 | 180 | 40 | 65 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 1050 | 1190 | 17 | 7897.11 | 14930.31 | 88.75
Total KWH | 0 | 711360 | 219360 | 0 | 0 | 0 | 0 | 0 | 8240400 | 0 | 0 | 259200 | 348480 | 1448640 | 207360 | 2582607 | 761204 | 535204 | 721440 | 0 | 0 | 7174662 | 10399843 | 0 | 192593 | 7100521 | 0 | 0 | 97049 | 1113600 | 320400 | 509040 | 0 | 0 | 731400 | 303600 | 0 | 0 | 640320 | 127779 | 359616 | 363015 | 261120 | 258240 | 7921 | 3368113 | 1196000 | 349920 | 25709090.91 | 43491 | 0 | 728160 | 91405.8 | 1203527 | 3517204 | 0 | 0 | 0 | 7281817 | 18495 | 936727 | 0 | 6674500 | 7529300 | 5964000 | 1171680 | 83520 | 5080000 | 664056 | 372480 | 2228915 | 1075200 | 217560 | 475970 | 1230060 | 3205440 | 706229 | 176473 | 222256 | 7371000 | 0 | 6727000 | 184000 | 0 | 3242372.73 | 26020 | 395088 | 0 | 1911360 | 694080 | 3249000 | 0 | 2380320 | 311040 | 1344000 | 61369 | 2263200 | 0 | 8650 | 146910 | 10080 | 157843053.44 | 21747636 | 0 | 0 | 56160 | 256400 | 912000 | 0 | 0 | 140593 | 0 | 318960 | 277920 | 26392730 | 0 | 0 | 0 | 33617432 | 0 | 95162 | 0 | 418848 | 812160 | 29123 | 613280 | 155386 | 466762 | 158968 | 247590 | 111790 | 0 | 130336 | 3721818 | 0 | 3495418 | 0 | 93673 | 0 | 8878836 | 0 | 11340 | 4552000 | 963491 | 1737205 | 92744 | 806640 | 0 | 0 | 0 | 18674.04 | 418320 | 1609 | 569664 | 6240000 | 1353000 | 5345970 | 0 | 14727272 | 26661818.18 | 376800 | 167025528.22 | 324868581.66 | 88.8

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 09-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13754.08 | MW | 12:00 Hr. | Energy Generated |  |  | 324.8686 |  | MKWHr.
| Day Peak Demand |  |  | 13950.08 | MW | 12:00 Hr. | Energy Unserverd |  |  | 8.075 |  | MKWHr.
| Evening Peak Generation |  |  | 15407.51 | MW | 21:00 Hr. | Energy Demand |  |  | 332.9436 |  | MKWHr.
| Evening Peak Demand |  |  | 15693.51 | MW | 21:00 Hr. | Maximum Temperature |  |  | 31.1 |  | °C
| Minimum Generation of the Day |  |  | 11380.09 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 873.03 |  | MMCFD
| Maximum Generation of the Day |  |  | 15407.51 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.3972 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 33.7449 | 0 | 9.101 | 0 | 0 | 0.097049 | 0 | 0 | 42.943 | Gas | 116.5269 | Gas | 391113785.7516
| Chattogram Zone |  |  | 3.8671 | 32.9909 | 5.6674 | 0 | 3.3681 | 0.026416 | 0 | 0.64032 | 46.5602 | Coal | 112.5282 | Coal | 751494035.9717
| Cumilla Zone |  |  | 29.8719 | 0 | 4.7605 | 0 | 0 | 0.17647 | 3.2054 | 0 | 38.0144 | HFO | 30.2816 | HFO | 523889229.348
| Mymensingh Zone |  |  | 0 | 0 | 3.9283 | 0 | 0 | 0.21693 | 0 | 0 | 4.1452 | HSD | 0.14059 | HSD | 2839978.6
| Sylhet Zone |  |  | 26.1542 | 0 | 0 | 0 | 0 | 0.02602 | 0 | 0 | 26.1802 | Hydro | 3.3681 | Hydro | 12832510.53
| Khulna Zone |  |  | 0 | 26.3927 | 0.63152 | 0.14059 | 0 | 0.27792 | 22.6596 | 0 | 50.1024 | Solar | 1.9004 | Solar | 30529094.7508
| Barishal Zone |  |  | 6.699 | 47.6291 | 0.94646 | 0 | 0 | 0.001609 | 0 | 0 | 55.2761 | Import | 59.4825 | Import | 356130496.08
| Rajshahi Zone |  |  | 16.1897 | 0 | 2.7025 | 0 | 0 | 0.54823 | 33.6174 | 0 | 53.0579 | Wind | 0.64032 | Wind | 9419107.2
| Rangpur Zone |  |  | 0 | 5.5155 | 2.5438 | 0 | 0 | 0.52974 | 0 | 0 | 8.5891
| Total |  |  | 116.5269 | 112.5282 | 30.2816 | 0.14059 | 3.3681 | 1.9004 | 59.4825 | 0.64032 | 324.8686
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 391113785.7516 |  | Hydro | 12832510.53
|  |  |  | Coal | 751494035.9717 |  | Solar | 30529094.7508
|  |  |  | HFO | 523889229.348 |  | Import | 356130496.08
|  |  |  | HSD | 2839978.6 |  | Wind | 9419107.2
[5 empty] | Total: | 207,82,48,238 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7476 | Peak Hr Flow | 905.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 59206527.27 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.6174 | Peak Hr Flow | 1477.31 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2750 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.2054 | Peak Hr Flow | 142.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 3006 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 58.5705 | Peak Hr Flow | 2524.31 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 51 |  | 5604
|  |  |  | Chattogram |  | 12 |  | 1210
|  |  |  | Cumilla |  | 20 |  | 1467
|  |  |  | Mymensingh |  | 191 |  | 1317
|  |  |  | Sylhet |  | 0 |  | 627
|  |  |  | Khulna |  | 0 |  | 1867
|  |  |  | Barishal |  | 0 |  | 444
|  |  |  | Rajshahi |  | 0 |  | 1526
|  |  |  | Rangpur |  | 0 |  | 1044
|  |  |  | Total |  | 274 |  | 15106
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Fenchugonj CCPP Phase-2 GT-4 |  |  | 35
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Karnaphuli Hydro PP Unit-5 |  |  | 50
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 350 |  |  |  | Total | 35
|  |  |  | Total Unavailable Capacity |  |  |  | 385
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:10 | 18:25 | Madunaghat-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end.
| 09:11 | 18:25 | Korerhat 400/230/132kV S/S Meghnaghat-2 Project Work S/D Due to Project Work
| 09:26 | 16:55 | Korerhat 400/230/132kV S/S Madunaghat-1 Project Work S/D Due to Project Work
| 09:28 |  | Madunaghat 400/230kV S/S Madunaghat-Meghnaghat 400kV Ckt.-1 Scheduled S/D Due to SD taken
by Korerhat 400kV Grid SS
| 09:36 | 18:02 | Korerhat 400/230/132kV S/S ATR-2(7203T)-Three Ph LT Project Work S/D Due to Project Work
|  | 09:36 | Natore 132/33kV S/S TR-1 (405 T) HT is restored.
|  | 09:36 | Natore 132/33kV S/S TR-1 (405 T) LT is restored.
| 09:37 | 16:59 | Korerhat 400/230/132kV S/S ATR-2(7203T)-Three Ph HT Project Work S/D Due to Project Work
|  | 09:38 | Natore 132/33kV S/S TR-2 (415 T) LT is restored.
|  | 09:38 | Natore 132/33kV S/S TR-2 (415 T) HT is restored.
|  | 10:01 | Sirajganj 132/33kV S/S Solar Park 1 is restored.
| 10:58 | 18:29 | Bhaluka 132/33kV S/S Sreepur Ckt- 01 Scheduled S/D Due to Clamp changing
| 11:08 | 18:31 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-1 Scheduled S/D Due to NLDC instruction
| 11:14 | 20:34 | Madunaghat 132/33kV S/S TR-1(507T) LT Forced S/D Due to Due to Noapara feeder maintenance
|  | 11:19 | Cox'sbazar-Dohazari 132 kV Ckt-2 is restored.
| 12:00 |  | Day Peak Generation: 13754 MW.
| 12:16 | 15:13 | Kushtia 132/33kV S/S 132 KV Bus-A Project Work S/D
| 12:30 | 19:36 | Mymensingh RPCL -Mymensingh 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end.
| 13:13 | 18:19 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT Tripped showing Auxiliary realy K13,14
and praimary protecion K 31 relays Due to P R D Trip
| 13:13 | 18:21 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT Tripped showing MVAJM15 relays Due to P
R D Trip
| 13:23 | 13:40 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Tripped showing 33 KV Relay | [7 empty] | 11.0MW load
|  |  | Signal General trip Phs-A trip,Phs-B trip,Phs-C trip. 51/50 - O/C trip 132 KV Relay | [7 empty] | interrup.
Signal General trip R Phs trip,Y Phs trip,B Phs trip. LV-O/C trip relays Due to Due to
Bandarban 33 KV feeder .
| 13:38 | 18:50 | Mymensingh 132/33kV S/S Bus B Scheduled S/D
| 14:01 | 20:06 | Mymensingh-Netrokona 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end.
| 14:06 | 17:40 | Mymensingh 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D
| 14:06 | 17:40 | Mymensingh 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D
| 14:57 | 21:52 | Kachua 230/132/33kV S/S ATR-1 LT Scheduled S/D Due to AVR Test.
| 14:58 | 21:50 | Kachua 230/132/33kV S/S ATR-1 HT Scheduled S/D Due to AVR Test.
|  | 15:13 | Kalurghat 132/33kV S/S TRFO-01(506T) HT is restored.
| 16:37 | 17:53 | Jhenaidah 230/132kV S/S Jhenaidah2-Kaliganj Ckt-2 Project Work S/D
| 17:02 | 17:59 | Khulna (S)-Satkhira 132kV Ckt-2 Forced S/D from Satkhira 132/33kV end Due to Order by
ALDC,Khulna and from Khulna(S) 230/132kVend.
| 17:04 | 17:55 | Khulna(S) 230/132kV S/S TR-2 LT Scheduled S/D
| 17:05 | 17:54 | Khulna(S) 230/132kV S/S TR-2 HT Scheduled S/D
| 17:45 | 19:50 | Mymensingh 132/33kV S/S Transformer-3 (424T) HT Scheduled S/D
| 17:45 | 19:50 | Mymensingh 132/33kV S/S Transformer-3 (424T) LT Scheduled S/D
|  | 18:19 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT is restored.
|  | 18:19 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT is restored.
|  | 19:13 | Bhaluka-Mymensingh 132 kV Ckt-2 is restored.
|  | 19:13 | Bhaluka-Mymensingh 132 kV Ckt-1 is restored.
| 19:18 | 20:34 | Madunaghat 132/33kV S/S TR-1(507T) LT Tripped showing REF 615 relays Due to Due CUET | [7 empty] | 20.0MW load
|  |  | feeder tripped. (Bad weather) | [7 empty] | interrup.
|  | 19:39 | Coxsbazar 132/33kV S/S 415T-T2 LT is restored.
| 23:11 | 00:17 | Madunaghat 132/33kV S/S TR-1(507T) HT Forced S/D
| 23:14 | 00:16 | Madunaghat 132/33kV S/S TR-1(507T) LT Forced S/D Due to Due to Noapara feeder maintenance
| 23:30 |  | Sirajganj unit-3 ST was sync.
| 00:42 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- ST
| 01:10 |  | Ashuganj North 360 MW CCPP was shutdown.
| 01:10 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 02:23 |  | JERA Meghnaghat Power Limited 718 MW CCPP GT-12 sync.
| 04:23 |  | JERA Meghnaghat Power Limited 718 MW CCPP ST was sync.
| 05:45 | 06:15 | Gopalganj 132/33kV S/S T2 LT Tripped showing Siprotec 7SJ82 relays Due to Reb-7 feeder | [7 empty] | 15.0MW load
|  |  | fault. (Loop damaged) | [7 empty] | interrup.
| 05:46 | 06:15 | Gopalganj 132/33kV S/S T1 LT Tripped showing Siprotec 7SJ82 relays Due to REB-7 feeder | [7 empty] | 15.0MW load
|  |  | fault.(loop damaged) | [7 empty] | interrup.
| 05:59 |  | Coxsbazar 132/33kV S/S T3 HT Project Work S/D Due to Commission of T-2 secondary CRP | [7 empty] | 5.0MW load
|  |  | panel | [7 empty] | interrup.
| 06:32 |  | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end. and from
Kishoreganj 132/33kV end Due to High temperature mitigation work of 132 kv Kishorganj
-Mymensingh ckt -01 R phase line DS to line connector T - clamp
| 06:32 |  | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end. and from
Kishoreganj 132/33kV end Due to High temperature mitigation work of 132 kv Kishorganj
-Mymensingh ckt -01 R phase line DS to line connector T - clamp
| 07:00 |  | Minimum Generation: 11510 MW.
| 07:11 |  | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to Emergency | [7 empty] | 13.0MW load
|  |  | maintenance | [7 empty] | interrup. Khulna
(C) end
| 07:26 |  | Khulna(C )-Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna (C) end Due to Emergency | [7 empty] | 13.0MW load
|  |  | maintenance | [7 empty] | interrup. Khulna
(C) end
|  | 07:58 | Coxsbazar 132/33kV S/S 415T-T2 HT is restored.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 09-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 350 | 8240400 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 302 | 7174662 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 761204 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 295 | 7100521 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 259200 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 207360 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 535204 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 192593 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 320400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 509040 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 219360 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 2582607 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1448640 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 711360 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 721440 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 97049 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 348480 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 475 | 10399843 | AGC+FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143 | 1113600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2310 | 42942963
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 91405.8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 18495 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 728160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 155 | 3368113 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 174 | 3517204 | plant availability zero
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 1203527 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 23 | 359616 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 127779 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 261120 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 349920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 7921 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 26 | 303600 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 363015 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 1196000 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 258240 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 731400 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 43491 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 300 | 7281817 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 7 | 640320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1135 | 25709090.91 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 2032 | 46560234.71
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 196 | 5080000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 320 | 7529300 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 300 | 5964000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 350 | 6674500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 664056 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 83520 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1171680 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 37 | 936727 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 17 | 222256 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 94 | 2228915 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 1075200 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 142 | 3205440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 706229 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 475970 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 33 | 1230060 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 217560 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 67 | 372480 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 176473 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1763.2 | 38014366
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 61369 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8650 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 155 | 2263200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 1344000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 146910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 1 | 10080 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 311040 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 242 | 4145249
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 26020 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 29 | 184000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 143 | 3242372.73 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 3249000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 694080 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1911360 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 104 | 2380320 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 395088 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7371000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 330 | 6727000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1177 | 26180240.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 905 | 21747636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 56160 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 50 | 256400 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 318960 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 277920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 140593 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1202 | 26392730 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2245 | 50102399
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 882 | 14727272 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 569664 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 65 | 1353000 | GT-1 & ST under maint
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1180 | 26661818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5345970 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 376800 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6240000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1609 | -
Barishal Area Total |  |  |  |  | 3407.64 | 2756 | 55276133.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 158968 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 26 | 95162 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 11 | 29123 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 155386 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 161 | 3721818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 153 | 3495418 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 93673 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 8878836 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 111790 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 16 | 466762 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 101 | 613280 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 812160 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 418848 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 11340 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1477.31 | 33617432 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 130336 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 247590 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2505.31 | 53057922
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 40 | 963491 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4552000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 42 | 806640 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 18674.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1737205 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 92744 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 418320 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 377 | 8589074.04
Eastern Grid Total |  |  |  |  | 17438.042 | 7524.2 | 157843053.44
Western Grid Total |  |  |  |  | 11812.075 | 7883.31 | 167025528.22
National Grid Total |  |  |  |  | 29250.117 | 15407.51 | 324868581.66
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 09-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9992.27 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4881 | MW
i) Dhaka area |  |  | 5553.47 |  | MW | i) Khulna area |  |  |  | 1867 | MW
ii) Chattogram area |  |  | 1238.8 |  | MW | ii) Barishal area |  |  |  | 443.6 | MW
iii) Cumilla area |  |  | 1447 |  | MW | iii) Rajshahi area |  |  |  | 1526.4 | MW
iv) Mymensingh area |  |  | 1126 |  | MW | iv) Rangpur area |  |  |  | 1044 | MW
v) Sylhet area |  |  | 627 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14873.27 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 135 | 00:00 | 133 | Narshingdi | 188 | 21:00 | 199 | Uttara | 97 | 14:00
2 | AKSML | 139.6 | 13:00 | 68 | Hasnabad | 98 | 14:00 | 134 | Natore | 157 | 19:30 | 200 | UttaraNew | 53 | 13:00
3 | Aftabnagar | 44 | 13:00 | 69 | Hathazari | 69 | 19:00 | 135 | Nawabganj | 61.4 | 22:00 | 201 | Zigatola | 90 | 13:00
4 | Agargaon | 118 | 14:00 | 70 | Hatirjheel | 46 | 15:00 | 136 | Netrakona | 128 | 21:00
5 | Agrabad | 60 | 14:00 | 71 | Ishurdi | 79 | 00:00 | 137 | New | 84 | 14:00
6 | Amnura | 30 | 00:00 | 72 | Jaldhaka | 85 | 21:00 | 138 | Niamatpur | 74 | 22:00
7 | Ashuganj | 75 | 23:00 | 73 | Jamalpur | 134 | 19:30 | 139 | Noapara | 42 | 19:30
8 | BSRM | 197 | 08:00 | 74 | Jashore | 166 | 00:00 | 140 | PHP | 12 | 17:00
9 | Bagerhat | 97 | 21:00 | 75 | Jhenaidah | 92 | 19:30 | 141 | Pabna | 100 | 20:00
10 | Bajitpur | 86 | 21:00 | 76 | Joydebpur | 173 | 19:00 | 142 | Palashbari | 126 | 19:30
11 | Bakerganj | 14 | 22:00 | 77 | Joypurhat | 63 | 21:00 | 143 | Panchagarh | 67 | 19:30
12 | Bakulia | 95 | 14:00 | 78 | Juldah | 14 | 11:00 | 144 | Patiya | 10 | 00:00
13 | Banani | 66 | 13:00 | 79 | KSRM | 18 | 06:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 16 | 10:00 | 80 | Kabirpur | 235 | 18:30 | 146 | Patuakhali | 63 | 23:00
15 | Barapukuria | 65 | 21:00 | 81 | Kachua | 94 | 20:00 | 147 | Payra | 32 | 00:00
16 | Barguna | 22 | 21:00 | 82 | Kaliganj | 38 | 19:30 | 148 | Postogola | 61 | 13:00
17 | Barishal | 106 | 13:00 | 83 | Kallyanpur | 120 | 00:00 | 149 | Pubail | 43 | 20:00
18 | Barishal-230 | 94 | 23:00 | 84 | Kalurghat | 28 | 16:00 | 150 | Purbachal | 29 | 13:00
19 | Baroaulia | 43 | 15:00 | 85 | Kamrangirchar | 80 | 13:00 | 151 | Purbasadipur | 136 | 23:00
20 | Baroirhat | 61 | 19:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 39 | 23:00
21 | Bashundhara | 205 | 13:00 | 87 | Kasba | 38 | 19:30 | 153 | Rahim | 30 | 02:00
22 | BashundharaCement | 7 | 10:00 | 88 | Kazla | 115 | 16:00 | 154 | Rajbari | 91 | 19:30
23 | Beanibazar | 72 | 22:00 | 89 | Keranigonj | 84 | 20:00 | 155 | Rajendrapur | 118 | 21:00
24 | Benapole | 64 | 13:00 | 90 | Khagrachori | 30 | 19:30 | 156 | Rajshahi | 127 | 00:00
25 | Bhaluka | 180 | 19:00 | 91 | Khulna | 65 | 13:00 | 157 | Rajshahi-230 | 96 | 20:00
26 | Bhandaria | 58 | 23:00 | 92 | Khulshi | 195 | 13:00 | 158 | Ramganj | 110 | 19:30
27 | Bhangura | 38 | 00:00 | 93 | Kishoreganj | 130 | 22:00 | 159 | Rampur | 31 | 14:00
28 | Bheramara(GK) | 68 | 02:00 | 94 | Kodda | 303 | 21:00 | 160 | Rangamati | 13 | 13:00
29 | Bhulta | 224 | 12:00 | 95 | Kulaura | 54 | 21:00 | 161 | Rangpur | 140 | 19:30
30 | Bog-Sherpur | 72 | 02:00 | 96 | Kurigram | 68 | 19:30 | 162 | Ruppur | 4.2 | 15:00
31 | Bogura | 177 | 23:00 | 97 | Kushtia | 155 | 20:00 | 163 | SSM | 1 | 23:00
32 | Borhanuddin | 72 | 23:00 | 98 | Laksam | 35 | 19:30 | 164 | Saidpur | 109 | 11:00
33 | Brahmanbaria | 137 | 20:00 | 99 | Lakshmipur | 40 | 20:00 | 165 | Santhia | 40 | 19:30
34 | Cantonment | 130 | 13:00 | 100 | Lalbag | 80 | 13:00 | 166 | Satkhira | 128 | 22:00
35 | Chandina | 32 | 22:00 | 101 | Lalmonirhat | 68 | 20:00 | 167 | Satmasjid | 104 | 14:00
36 | Chandpur | 90 | 20:00 | 102 | MI_Cement | 15.7 | 00:00 | 168 | Savar | 216 | 12:00
37 | Chandraghona | 31 | 22:00 | 103 | Madanganj | 34 | 20:00 | 169 | SevenRings | 13.17 | 12:00
38 | Chapai | 75 | 21:00 | 104 | Madaripur | 122 | 20:00 | 170 | ShahCement | 31 | 03:00
39 | Charfasson | 26 | 21:00 | 105 | Madartek | 79 | 00:00 | 171 | Shahjadpur | 74 | 19:30
40 | Charsaidpur | 42 | 01:00 | 106 | Madunaghat | 46 | 00:00 | 172 | Shahjibazar | 135 | 22:00
41 | Chauddagram | 76 | 19:00 | 107 | Magura | 68 | 19:30 | 173 | Shahmirpur | 38 | 16:00
42 | Chhatak | 34 | 20:00 | 108 | Mahasthangarh | 81 | 20:00 | 174 | Shariatpur | 91 | 23:00
43 | Chowmuhani | 156 | 19:00 | 109 | Maijdee | 36 | 21:00 | 175 | Sherpur | 146 | 19:30
44 | Chuadanga | 123 | 23:00 | 110 | Manikganj | 124 | 08:00 | 176 | Shikalbaha | 26 | 16:00
45 | Coxsbazar | 137 | 20:00 | 111 | Maniknagar | 76 | 13:00 | 177 | Shitalakhya | 76.7 | 12:00
46 | Cumilla(N) | 131 | 20:00 | 112 | Matarbari | 44 | 19:00 | 178 | Sholosohor | 42 | 16:00
47 | Cumilla(S) | 153 | 00:00 | 113 | Matuail | 82 | 12:00 | 179 | Shomvuganj | 42 | 19:30
48 | Daganbhuiyan | 28 | 19:30 | 114 | Metrorail_Motijheel | 26 | 16:00 | 180 | Shyampur | 150 | 16:00
49 | Daudkandi | 146 | 21:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 131 | 12:00
50 | DhakaUniversity | 94 | 13:00 | 116 | Millgate | 107 | 12:00 | 182 | Sirajganj | 112 | 00:00
51 | Dhamrai | 104 | 00:00 | 117 | Mirpur | 151 | 13:00 | 183 | Sitakunda | 31 | 19:00
52 | Dhanmondi | 117 | 13:00 | 118 | Mirsorai | 50 | 11:00 | 184 | Sonargaon | 142 | 01:00
53 | Dohazari | 62 | 21:00 | 119 | Mirzapur | 40 | 19:30 | 185 | Sreemongol | 77 | 21:00
54 | Faridpur | 181 | 23:00 | 120 | Mithapukur | 76 | 19:30 | 186 | Sreepur | 130 | 18:30
55 | Fatullah | 105 | 12:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 49.65 | 20:00
56 | Fenchuganj | 41 | 22:00 | 122 | Mogbazar | 87.6 | 16:00 | 188 | Sunamganj | 58 | 21:00
57 | Feni | 107 | 19:30 | 123 | Mongla | 41 | 11:00 | 189 | Sylhet | 106 | 21:00
58 | GPH | 1 | 00:00 | 124 | Motijheel | 51 | 13:00 | 190 | Sylhet_(South) | 64 | 19:30
59 | Ghatail | 92 | 20:00 | 125 | Muktagacha | 43 | 19:30 | 191 | TK | 19.5 | 15:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 111 | 21:00 | 192 | Tangail | 166 | 22:00
61 | Ghorashal-230 | 99 | 02:00 | 127 | Muradnagar | 50 | 19:30 | 193 | Taraganj | 28 | 19:30
62 | Goalpara | 39 | 19:30 | 128 | Mymensingh | 152 | 19:30 | 194 | Tasnim | 43 | 09:00
63 | Gollamari | 106 | 13:00 | 129 | Nabinagar | 100 | 21:00 | 195 | Thakurgaon | 111 | 20:00
64 | Gopalganj | 114 | 20:00 | 130 | Naogaon | 121 | 19:30 | 196 | Tongi | 154 | 09:00
65 | Gulshan | 116 | 14:00 | 131 | Narail | 51 | 21:00 | 197 | Ullahpara | 38 | 00:00
66 | Halishahar | 93 | 12:00 | 132 | Narinda | 77 | 13:00 | 198 | Ullon | 54 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 09-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14089.41 | 1332 |  | 15481.35
1:00 | 13614.96 | 1249 |  | 14919.96
2:00 | 13226.03 | 532 |  | 13782.03
3:00 | 12856.58 | 431 |  | 13306.58
4:00 | 12228.41 | 358 |  | 12602.41
5:00 | 11736.24 | 262 |  | 12010.24
6:00 | 11380.09 | 60 |  | 11443.09
7:00 | 11457.05 | 5 |  | 11462.05
8:00 | 11761.64 | 25 |  | 11787.64
9:00 | 12149.66 | 126 |  | 12281.33
10:00 | 12642.87 | 120 |  | 12768.27
11:00 | 13188.28 | 105 |  | 13298.01
12:00 | 13754.08 | 188 |  | 13950.08
13:00 | 13880.54 | 251 |  | 14142.54
14:00 | 13890.16 | 295 |  | 14198.16
15:00 | 13944.86 | 501 |  | 14468.86
16:00 | 13726.66 | 368 |  | 14111.66
17:00 | 13238.14 | 345 |  | 13599.14
18:00 | 13330.92 | 323 |  | 13668.92
19:00 | 14189.48 | 364 |  | 14569.48
19:30 | 15058.92 | 130 |  | 15194.92
20:00 | 15210.16 | 160 |  | 15377.16
21:00 | 15407.51 | 274 |  | 15693.51
22:00 | 14964.13 | 150 |  | 15120.88
23:00 | 14930.31 | 251 |  | 15192.61
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 09-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6798.56 | 7290.85 | 14089.41 | DAILY GENERATION CURVE
00:30 | 6630.88 | 7221.305 | 13852.185
01:00 | 6463.2 | 7151.76 | 13614.96 | 09-07-2026
01:30 | 6410.95 | 7009.545 | 13420.495
02:00 | 6358.7 | 6867.33 | 13226.03
02:30 | 6206.6 | 6834.705 | 13041.305
03:00 | 6054.5 | 6802.08 | 12856.58
03:30 | 5886.25 | 6656.245 | 12542.495
04:00 | 5718 | 6510.41 | 12228.41
04:30 | 5585.5 | 6396.825 | 11982.325
05:00 | 5453 | 6283.24 | 11736.24
05:30 | 5444.015 | 6114.15 | 11558.165
06:00 | 5435.03 | 5945.06 | 11380.09
06:30 | 5506.85 | 5911.72 | 11418.57
07:00 | 5578.67 | 5878.38 | 11457.05
07:30 | 5644.36 | 5964.985 | 11609.345
08:00 | 5710.05 | 6051.59 | 11761.64
08:30 | 5695.625 | 6260.025 | 11955.65
09:00 | 5681.2 | 6468.46 | 12149.66
09:30 | 5887.95 | 6508.315 | 12396.265
10:00 | 6094.7 | 6548.17 | 12642.87
10:30 | 6309.05 | 6606.525 | 12915.575
11:00 | 6523.4 | 6664.88 | 13188.28
11:30 | 6703.005 | 6768.175 | 13471.18
12:00 | 6882.61 | 6871.47 | 13754.08
12:30 | 6855.325 | 6961.985 | 13817.31
13:00 | 6828.04 | 7052.5 | 13880.54
13:30 | 6869.845 | 7015.505 | 13885.35
14:00 | 6911.65 | 6978.51 | 13890.16
14:30 | 6955.96 | 6961.55 | 13917.51
15:00 | 7000.27 | 6944.59 | 13944.86
15:30 | 6935.575 | 6900.185 | 13835.76
16:00 | 6870.88 | 6855.78 | 13726.66
16:30 | 6673.135 | 6809.265 | 13482.4
17:00 | 6475.39 | 6762.75 | 13238.14
17:30 | 6592.795 | 6691.735 | 13284.53
18:00 | 6710.2 | 6620.72 | 13330.92
18:30 | 6901.6 | 6858.6 | 13760.2
19:00 | 7093 | 7096.48 | 14189.48
19:30 | 7485.36 | 7573.56 | 15058.92
20:00 | 7552.56 | 7657.6 | 15210.16
20:30 | 7538.38 | 7770.455 | 15308.835 |  | Executive Engineer
21:00 | 7524.2 | 7883.31 | 15407.51 |  | Network Operation Division
21:30 | 7352.7 | 7833.12 | 15185.82
22:00 | 7181.2 | 7782.93 | 14964.13
22:30 | 7107.2 | 7840.02 | 14947.22
23:00 | 7033.2 | 7897.11 | 14930.31

## En-Curve
QF-LDC-12
Date | 09-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2956 | 1569 | 859 | 38 | 152 | 1477.65 | 142 | 4860 | 0 | 369 | 1474.76 | 151 | 0 | 41 | 1332 | DAILY ENERGY CURVE
00:30 | 3013.5 | 1571.5 | 874 | 38 | 150 | 1477.105 | 144.5 | 4836 | 0 | 264.5 | 1305.58 | 126 | 0 | 51.5 | 1290.5 | 09-07-2026
01:00 | 3071 | 1574 | 889 | 38 | 148 | 1476.56 | 147 | 4812 | 0 | 160 | 1136.4 | 101 | 0 | 62 | 1249
01:30 | 3027.5 | 1524.75 | 889 | 38 | 144 | 1476.345 | 147.5 | 4807.5 | 0 | 144.5 | 1109.9 | 50.5 | 0 | 61 | 890.5 | Energy Generated | 324.8686 |  | MKWHr
02:00 | 2984 | 1475.5 | 889 | 38 | 140 | 1476.13 | 148 | 4803 | 0 | 129 | 1083.4 | 0 | 0 | 60 | 532 | Energy not Served | 8.075 |  | MKWHr
02:30 | 3060.5 | 1528 | 889 | 38 | 137 | 1476.105 | 149 | 4777.5 | 0 | 98 | 836.2 | 0 | 0 | 52 | 481.5 | Total Energy Requirement | 332.9436 |  | MKWHr
03:00 | 3137 | 1580.5 | 889 | 38 | 134 | 1476.08 | 150 | 4752 | 0 | 67 | 589 | 0 | 0 | 44 | 431
03:30 | 3104.5 | 1579.25 | 889.5 | 38 | 128 | 1459.245 | 151 | 4714.5 | 0 | 58.5 | 377 | 0 | 0 | 43 | 394.5
04:00 | 3072 | 1578 | 890 | 38 | 122 | 1442.41 | 152 | 4677 | 0 | 50 | 165 | 0 | 0 | 42 | 358
04:30 | 3090.5 | 1567.5 | 892.5 | 38 | 121 | 1413.825 | 152.5 | 4473.5 | 0 | 41.5 | 148 | 0 | 0 | 43.5 | 310
05:00 | 3109 | 1557 | 895 | 38 | 120 | 1385.24 | 153 | 4270 | 0 | 33 | 131 | 0 | 0 | 45 | 262
05:30 | 3135 | 1553 | 896 | 38 | 121 | 1339.18 | 151.5 | 4123 | 1.485 | 33 | 141.5 | 0 | 0 | 25.5 | 161
06:00 | 3161 | 1549 | 897 | 38 | 122 | 1293.12 | 150 | 3976 | 2.97 | 33 | 152 | 0 | 0 | 6 | 60
06:30 | 3144 | 1585.5 | 897 | 38 | 121 | 1306.24 | 148.5 | 3941 | 15.83 | 33 | 171 | 0 | 0 | 17.5 | 32.5
07:00 | 3127 | 1622 | 897 | 38 | 120 | 1319.36 | 147 | 3906 | 28.69 | 33 | 190 | 0 | 0 | 29 | 5
07:30 | 3137 | 1630.5 | 898.5 | 38 | 128 | 1356.195 | 145.5 | 3970 | 46.65 | 33 | 197.5 | 0 | 0 | 28.5 | 15
08:00 | 3147 | 1639 | 900 | 38 | 136 | 1393.03 | 144 | 4034 | 64.61 | 33 | 205 | 0 | 0 | 28 | 25
08:30 | 3127.5 | 1636 | 900 | 38 | 138 | 1421.275 | 144 | 4170 | 84.375 | 33.5 | 246 | 0 | 0 | 17 | 75.5
09:00 | 3108 | 1633 | 900 | 38 | 140 | 1449.52 | 144 | 4306 | 104.14 | 34 | 287 | 0 | 0 | 6 | 126
09:30 | 3144 | 1623 | 900 | 38 | 142 | 1449.345 | 144 | 4342 | 108.92 | 41 | 461 | 0 | 0 | 3 | 123
10:00 | 3180 | 1613 | 900 | 38 | 144 | 1449.17 | 144 | 4378 | 113.7 | 48 | 635 | 0 | 0 | 0 | 120
10:30 | 3241 | 1615.5 | 900 | 38 | 139 | 1441.32 | 144 | 4410.5 | 152.755 | 51.5 | 774 | 0 | 0 | 8 | 112.5
11:00 | 3302 | 1618 | 900 | 38 | 134 | 1433.47 | 144 | 4443 | 191.81 | 55 | 913 | 0 | 0 | 16 | 105
11:30 | 3264.5 | 1598 | 902.5 | 38 | 129 | 1422.835 | 146 | 4536.5 | 211.245 | 77.5 | 1112.1 | 0 | 0 | 33 | 146.5
12:00 | 3227 | 1578 | 905 | 38 | 124 | 1412.2 | 148 | 4630 | 230.68 | 100 | 1311.2 | 0 | 0 | 50 | 188
12:30 | 3190 | 1588 | 905 | 38 | 125 | 1413.205 | 137 | 4642.5 | 270.805 | 96 | 1380.3 | 0 | 0 | 31.5 | 219.5
13:00 | 3153 | 1598 | 905 | 38 | 126 | 1414.21 | 126 | 4655 | 310.93 | 92 | 1449.4 | 0 | 0 | 13 | 251
13:30 | 3123 | 1578.5 | 905 | 38 | 121 | 1391.425 | 127 | 4667.5 | 285.525 | 83.5 | 1548.9 | 0 | 0 | 16 | 273
14:00 | 3093 | 1559 | 905 | 38 | 116 | 1368.64 | 128 | 4680 | 260.12 | 75 | 1648.4 | 0 | 0 | 19 | 295
14:30 | 3100.5 | 1601 | 905 | 38 | 119 | 1346.405 | 130 | 4712 | 249.205 | 78.5 | 1601.9 | 0 | 0 | 36 | 398
15:00 | 3108 | 1643 | 905 | 38 | 122 | 1324.17 | 132 | 4744 | 238.29 | 82 | 1555.4 | 0 | 0 | 53 | 501
15:30 | 3152.5 | 1631 | 904.5 | 38 | 125 | 1280.695 | 132 | 4689 | 220.165 | 82 | 1531.4 | 0 | 0 | 49.5 | 434.5
16:00 | 3197 | 1619 | 904 | 38 | 128 | 1237.22 | 132 | 4634 | 202.04 | 82 | 1507.4 | 0 | 0 | 46 | 368
16:30 | 3161.5 | 1539.5 | 904.5 | 38 | 133 | 1228.01 | 146.5 | 4683.5 | 146.69 | 102.5 | 1349.2 | 0 | 0 | 49.5 | 356.5
17:00 | 3126 | 1460 | 905 | 38 | 138 | 1218.8 | 161 | 4733 | 91.34 | 123 | 1191 | 0 | 0 | 53 | 345
17:30 | 3136 | 1494 | 905 | 38 | 138 | 1218.275 | 161 | 4645.5 | 60.255 | 144.5 | 1307 | 0 | 0 | 37 | 334
18:00 | 3146 | 1528 | 905 | 38 | 138 | 1217.75 | 161 | 4558 | 29.17 | 166 | 1423 | 0 | 0 | 21 | 323
18:30 | 3166.5 | 1492.5 | 905 | 38 | 141 | 1317.615 | 163.5 | 4632 | 14.585 | 365 | 1498.5 | 0 | 0 | 26 | 343.5
19:00 | 3187 | 1457 | 905 | 38 | 144 | 1417.48 | 166 | 4706 | 0 | 564 | 1574 | 0 | 0 | 31 | 364
19:30 | 3336 | 1542 | 905 | 38 | 148 | 1470.56 | 165 | 4944 | 0 | 582 | 1921.36 | 0 | 0 | 7 | 130
20:00 | 3357 | 1548 | 905 | 38 | 140 | 1475.6 | 160 | 4998 | 0 | 605 | 1983.56 | 0 | 0 | 0 | 160
20:30 | 3451 | 1599 | 905 | 38 | 141 | 1476.455 | 157.5 | 5112 | 0 | 618 | 1807.38 | 0 | 0 | 3.5 | 217
21:00 | 3545 | 1650 | 905 | 38 | 142 | 1477.31 | 155 | 5226 | 0 | 631 | 1631.2 | 0 | 0 | 7 | 274
21:30 | 3520.5 | 1641.5 | 905 | 38 | 142 | 1476.62 | 106.5 | 5301 | 0 | 548.5 | 1496.7 | 0 | 0 | 9.5 | 212
22:00 | 3496 | 1633 | 905 | 38 | 142 | 1475.93 | 58 | 5376 | 0 | 466 | 1362.2 | 0 | 0 | 12 | 150
22:30 | 3495.5 | 1686.5 | 905 | 38 | 143 | 1481.02 | 58 | 5327.5 | 0 | 472 | 1326.7 | 0 | 0 | 14 | 200.5
23:00 | 3495 | 1740 | 905 | 38 | 144 | 1486.11 | 58 | 5279 | 0 | 478 | 1291.2 | 0 | 0 | 16 | 251
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 09-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 169 | 33 | 540 | 144 | 2058 | 626 | Ishurdi-Ghorashal Ckt-1 | Export | 4285527.27
1:00 | 173 | 35 | 570 | 152 | 2112 | 630
2:00 | 152 | 24 | 540 | 144 | 1914 | 556 |  | Import | 0
3:00 | 164 | 25 | 560 | 132 | 2032 | 582
4:00 | 157 | 22 | 542 | 106 | 1920 | 548 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 157 | 26 | 526 | 90 | 1784 | 558
6:00 | 156 | 18 | 496 | 70 | 1678 | 526 |  | Import | 0
7:00 | 157 | 22 | 488 | 70 | 1634 | 548
8:00 | 176 | 28 | 498 | 70 | 1802 | 590 | Sirajganj-Sreepur Ckt-1 | Export | 3383000
9:00 | 222 | 52 | 600 | 110 | 2134 | 704
10:00 | 211 | 44 | 622 | 110 | 2116 | 742 |  | Import | 0
11:00 | 210 | 43 | 576 | 108 | 2130 | 806
12:00 | 215 | 60 | 594 | 162 | 2044 | 904 | Sirajganj-Sreepur Ckt-2 | Export | 3388000
13:00 | 214 | 55 | 606 | 166 | 2028 | 834
14:00 | 204 | 52 | 594 | 172 | 2064 | 876 |  | Import | 0
15:00 | 206 | 58 | 578 | 170 | 2046 | 872
16:00 | 213 | 58 | 616 | 184 | 2154 | 902 | Gopalganj-Aminbazar Ckt-1 | Export | 24050000
17:00 | 202 | 64 | 580 | 180 | 2224 | 874
18:00 | 192 | 48 | 542 | 140 | 1950 | 728 |  | Import | 0
18:30 | 187 | 39 | 522 | 106 | 1976 | 662
19:00 | 172 | 23 | 474 | 74 | 1958 | 600 | Gopalganj-Aminbazar Ckt-2 | Export | 24100000
19:30 | 132 | 5 | 490 | 110 | 1944 | 536
20:00 | 136 | 3 | 502 | 120 | 1956 | 516 |  | Import | 0
21:00 | 142 | 3 | 532 | 136 | 2076 | 494
22:00 | 145 | 8 | 510 | 134 | 2108 | 468 |  | Total Export | 59206527.27
23:00 | 150 | 4 | 564 | 144 | 2168 | 478 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 09-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 381 | 06:00 | 352 | 12:00 | Madunaghat | 396 | 07:00 | 386 | 13:00
Amtali | 413 | 04:00 | 404 | 22:00 | Meghnaghat | 387 | 06:00 | 356 | 12:00
Ashuganj | 407 | 6:00 | 388 | 13:00 | Payra | 415 | 06:00 | 406 | 22:00
Bhulta | 408 | 06:00 | 377 | 13:00 | Rahanpur | 404 | 18:00 | 388 | 23:00
Bibiana | 383 | 05:00 | 369 | 12:00 | Rampal | 400 | 06:00 | 380 | 22:00
BIPTC | 401 | 05:00 | 395 | 12:00
Bogura | 387 | 06:00 | 370 | 23:00
Gopalganj | 396 | 06:00 | 375 | 12:00
Kaliakoir | 370 | 06:00 | 343 | 16:00
Korerhat | 398 | 06:00 | 385 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 06:00 | 212 | 12:00 | Ishurdi | 236 | 05:00 | 218 | 23:00
AKSML | 237.8 | 23:00 | 231.1 | 16:00 | Jhenaidah | 227 | 05:00 | 207 | 23:00
Aminbazar | 235 | 05:00 | 214 | 13:00 | Kachua | 229 | 06:00 | 220 | 12:00
Ashuganj | 234 | 05:00 | 220 | 14:00 | Kaliakoir | 232 | 05:00 | 210 | 12:00
Ashuganj-400 | 234 | 05:00 | 220 | 14:00 | Keranigonj | 234 | 06:00 | 211 | 12:00
Baghabari | 234 | 05:00 | 224 | 21:00 | Khulna(S) | 230 | 06:00 | 211 | 22:00
Barapukuria | 226 | 17:00 | 216 | 22:00 | Korerhat | 229 | 06:00 | 221 | 12:00
Barapukuria-230 | 226 | 17:00 | 216 | 22:00 | Madunaghat | 240 | 00:00 | 236 | 07:00
Barishal | 230 | 06:00 | 217 | 23:00 | Madunaghat-400 | 241 | 00:00 | 237 | 13:00
Bheramara | 233 | 05:00 | 217 | 22:00 | Maniknagar | 232 | 05:00 | 212 | 16:00
Bhulta | 234 | 05:00 | 213 | 12:00 | Meghnaghat | 237 | 04:00 | 222 | 13:00
Bibiana | 224 | 07:00 | 216 | 12:00 | Meghnaghat-400 | 237 | 06:00 | 217 | 12:00
BIPTC | 236 | 05:00 | 216 | 23:00 | Mirsorai | 231 | 06:00 | 222 | 13:00
Bogura | 243 | 18:00 | 231 | 23:00 | Naogaon | 229 | 06:00 | 205 | 20:00
Bogura-400 | 243 | 18:30 | 232 | 23:00 | Purbasadipur | 225 | 17:00 | 213 | 22:00
Borhanuddin | 232 | 06:00 | 223 | 22:00 | Rajshahi | 233 | 18:30 | 214 | 23:00
BSRM | 230 | 06:00 | 222 | 13:00 | Rampal | 228 | 06:00 | 212 | 22:00
Charfasson | 233 | 05:00 | 223 | 23:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 05:00 | 220 | 12:00 | Rampura | 234 | 06:00 | 211 | 13:00
Cumilla(N) | 230 | 05:00 | 216 | 12:00 | Shikalbaha | 240 | 19:00 | 234 | 04:00
Faridpur | 224 | 06:00 | 210 | 23:00 | Shyampur | 234 | 07:00 | 213 | 12:00
Fenchuganj | 227 | 06:00 | 215 | 11:00 | Siddhirganj | 234 | 05:00 | 214 | 12:00
Feni | 227 | 06:00 | 219 | 12:00 | Sirajgonj | 241 | 18:30 | 233 | 23:00
Ghorashal | 235 | 01:00 | 220 | 11:00 | Sreepur | 228 | 06:00 | 217 | 23:00
Ghorashal-230 | 219 | 06:00 | 196 | 12:00 | Tongi | 216 | 18:30 | 200 | 13:00
Gopalganj | 225 | 06:00 | 212 | 23:00
GPH | 236 | 18:00 | 230 | 13:00
Haripur | 235 | 06:00 | 214 | 13:00
Hasnabad | 231 | 04:00 | 212 | 12:00
Hathazari | 237 | 18:00 | 231 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 141 | 06:00 | 125 | 14:00 | Madunaghat | 139 | 00:00 | 136 | 07:00
Agargaon | 139 | 06:00 | 123 | 12:00 | Magura | 131 | 05:00 | 116 | 23:00
Agrabad | 138 | 18:00 | 134 | 08:00 | Mahasthangarh | 137 | 06:00 | 129 | 21:00
AKS | 136 | 18:00 | 133 | 00:00 | Maijdee | 128 | 06:00 | 123 | 12:00
Aminbazar | 134 | 05:00 | 120 | 13:00 | Manikganj | 129 | 05:00 | 118 | 15:00
Amnura | 138 | 18:30 | 124 | 21:00 | Maniknagar | 138 | 05:00 | 121 | 13:00
Ashuganj | 134 | 06:00 | 125 | 16:00 | Matarbari | 130 | 00:00 | 115 | 01:00
Ashuganj-230 | 135 | 04:00 | 130 | 12:00 | Matuail | 136 | 06:00 | 123.5 | 16:00
Bagerhat | 135 | 05:00 | 118 | 22:00 | Metrorail_Motijheel | 133 | 01:00 | 121 | 13:00
Bajitpur | 130 | 07:00 | 120 | 21:00 | Metrorail_Uttara | 133 | 04:00 | 118 | 13:00
Bakerganj | 133 | 05:00 | 125 | 23:00 | Millgate | 135 | 05:00 | 119 | 14:00
Bakulia | 139 | 00:00 | 133 | 10:00 | Mirpur | 133 | 05:00 | 117 | 12:00
Banani | 139 | 04:00 | 125 | 12:00 | Mirzapur | 131 | 06:00 | 120 | 13:00
Bangabhaban | 138 | 06:00 | 121 | 13:00 | Mithapukur | 135 | 14:00 | 125 | 22:00
Barapukuria | 138 | 18:30 | 127 | 23:00 | MI_Cement | 138 | 05:00 | 121 | 12:00
Barguna | 134 | 06:00 | 124 | 21:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 05:00 | 124 | 22:00 | Mogbazar | 143 | 05:00 | 125 | 13:00
Barishal-230 | 134 | 06:00 | 124 | 23:00 | Mongla | 131 | 06:00 | 117 | 23:00
Baroaulia | 139 | 00:00 | 135 | 10:00 | Motijheel | 138 | 06:00 | 121 | 13:00
Baroirhat | 133 | 05:00 | 128 | 12:00 | Muktagacha | 128 | 07:00 | 113 | 19:30
Bashundhara | 140 | 04:00 | 118 | 13:00 | Munshiganj | 134 | 06:00 | 123 | 15:00
BashundharaCement | 134 | 07:00 | 125 | 12:00 | Muradnagar | 131 | 06:00 | 122 | 12:00
Beanibazar | 127 | 06:00 | 120 | 21:00 | Mymensingh | 129 | 20:00 | 106 | 09:00
Benapole | 133 | 18:00 | 114 | 23:00 | Nabinagar | 137 | 04:00 | 117 | 12:00
Bhaluka | 130 | 19:00 | 119 | 19:30 | Naogaon | 138 | 06:00 | 123 | 22:00
Bhandaria | 133 | 05:00 | 118 | 23:00 | Narail | 132 | 05:00 | 116 | 23:00
Bhangura | 134 | 05:00 | 127 | 23:00 | Narinda | 138 | 05:00 | 121 | 13:00
Bheramara | 137 | 05:00 | 127 | 22:00 | Narshingdi | 132 | 06:00 | 116 | 12:00
Bheramara(GK) | 137 | 18:30 | 125 | 23:00 | Natore | 135 | 18:30 | 125 | 23:00
Bhulta | 130 | 07:00 | 120 | 12:00 | Nawabganj | 141 | 06:00 | 124 | 12:00
Bog-Sherpur | 138 | 06:00 | 130 | 22:00 | Netrakona | 122 | 05:00 | 100 | 19:30
Bogura | 140 | 18:00 | 133 | 21:00 | New | 136 | 06:00 | 119 | 18:30
Bogura-230 | 141 | 18:30 | 132 | 23:00 | Niamatpur | 133 | 05:00 | 126 | 20:00
Brahmanbaria | 131 | 06:00 | 123 | 13:00 | Noapara | 135 | 05:00 | 120 | 23:00
Cantonment | 138 | 06:00 | 122 | 12:00 | Pabna | 135 | 05:00 | 127 | 22:00
Chandina | 134 | 06:00 | 125 | 13:00 | Palashbari | 132 | 04:00 | 122 | 23:00
Chandpur | 131 | 00:00 | 124 | 12:00 | Panchagarh | 138 | 12:00 | 127 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 140 | 00:00 | 137 | 10:00 | Patiya | 138 | 00:00 | 133 | 09:00
Chapai | 133 | 05:00 | 129 | 23:00 | Patnitala | 135 | 06:00 | 125 | 23:00
Charsaidpur | 134 | 07:00 | 124 | 12:00 | Patuakhali | 132 | 18:00 | 126 | 22:00
Chauddagram | 131 | 06:00 | 126 | 12:00 | Payra | 136 | 05:00 | 131 | 22:00
Chhatak | 125 | 06:00 | 116 | 21:00 | PHP | 132 | 06:00 | 128 | 12:00
Chowmuhani | 129 | 05:00 | 123 | 22:00 | Postogola | 139 | 06:00 | 125 | 14:00
Chuadanga | 135 | 18:30 | 116 | 23:00 | Pubail | 128 | 19:00 | 117 | 16:00
Coxsbazar | 128 | 15:00 | 115 | 10:00 | Purbachal | 141 | 06:00 | 124 | 13:00
Cumilla(N) | 133 | 05:00 | 126 | 12:00 | Purbasadipur | 137 | 17:00 | 127 | 23:00
Cumilla(S) | 132 | 05:00 | 123 | 10:00 | Rahanpur | 135 | 03:00 | 129 | 21:00
Daganbhuiyan | 131 | 07:00 | 126 | 13:00 | Rahanpur-400 | 135 | 06:00 | 129 | 23:00
Daudkandi | 129 | 06:00 | 119 | 12:00 | Rahim | 136 | 06:00 | 124 | 12:00
DhakaUniversity | 141 | 06:00 | 125 | 12:00 | Rajbari | 127 | 06:00 | 118 | 22:00
Dhamrai | 136 | 06:00 | 116 | 12:00 | Rajendrapur | 128 | 06:00 | 119 | 21:00
Dhanmondi | 141 | 06:00 | 125 | 12:00 | Rajshahi | 133 | 18:00 | 124 | 22:00
Dohazari | 136 | 04:00 | 130 | 20:00 | Rajshahi-230 | 133 | 05:00 | 124 | 18:30
Faridpur | 130 | 07:00 | 121 | 23:00 | Ramganj | 126 | 06:00 | 120 | 13:00
Fatullah | 141 | 06:00 | 122 | 12:00 | Rampur | 138 | 00:00 | 134 | 08:00
Fenchuganj | 134 | 06:00 | 128 | 13:00 | Rampura | 141 | 06:00 | 125 | 12:00
Feni | 131 | 03:00 | 126 | 12:00 | Rangamati | 139 | 05:00 | 136 | 09:00
Feni-230 | 132 | 06:00 | 127 | 17:00 | Rangpur | 134 | 14:00 | 123 | 23:00
Ghatail | 130 | 06:00 | 113 | 16:00 | Ruppur | 138 | 18:30 | 127 | 23:00
Ghorashal | 130 | 04:00 | 120 | 11:00 | Saidpur | 134 | 12:00 | 127 | 19:30
Goalpara | 139 | 06:00 | 124 | 23:00 | Santhia | 135 | 18:00 | 127 | 22:00
Gollamari | 138 | 06:00 | 125 | 22:00 | Satkhira | 137 | 06:00 | 117 | 23:00
Gopalganj | 135 | 05:00 | 123 | 23:00 | Satmasjid | 138 | 06:00 | 122 | 13:00
Gopalganj-400 | 134 | 06:00 | 118 | 17:00 | Savar | 131 | 05:00 | 116 | 12:00
Gulshan | 140 | 06:00 | 125 | 12:00 | SevenRings | 130 | 05:00 | 120 | 12:00
Halishahar | 139 | 00:00 | 134 | 10:00 | ShahCement | 134 | 07:00 | 124 | 12:00
Haripur | 137 | 06:00 | 124 | 13:00 | Shahjadpur | 136 | 03:00 | 131 | 22:00
HaripurSBU | 136 | 05:00 | 125 | 12:00 | Shahjibazar | 131 | 06:00 | 124 | 22:00
Hasnabad | 138 | 04:00 | 124 | 12:00 | Shahmirpur | 138 | 00:00 | 135 | 09:00
Hathazari | 140 | 18:00 | 136 | 09:00 | Shariatpur | 133 | 06:00 | 121 | 23:00
Hatirjheel | 141 | 06:00 | 125 | 13:00 | Sherpur | 127 | 10:00 | 112 | 01:00
Ishurdi | 138 | 05:00 | 128 | 23:00 | Shikalbaha | 128 | 01:00 | 123 | 10:00
Jaldhaka | 132 | 12:00 | 124 | 22:00 | Shikalbaha-230 | 139 | 00:00 | 135 | 10:00
Jamalpur | 130 | 20:00 | 114 | 02:00 | Shitalakhya | 138 | 05:00 | 121 | 12:00
Jashore | 135 | 18:00 | 116 | 23:00 | Sholosohor | 139 | 07:00 | 135 | 18:00
Jhenaidah | 138 | 06:00 | 120 | 21:00 | Shomvuganj | 125 | 06:00 | 115 | 09:00
Jhenaidah-230 | 138 | 05:00 | 124 | 23:00 | Shyampur | 139 | 06:00 | 127 | 12:00
Joydebpur | 127 | 18:30 | 116 | 12:00 | Shyampur-230 | 142 | 07:00 | 127 | 12:00
Joypurhat | 136 | 18:30 | 126 | 22:00 | Siddhirganj | 136 | 04:00 | 125 | 12:00
Juldah | 138 | 00:00 | 135 | 08:00 | Sirajganj | 134 | 05:00 | 126 | 23:00
Kabirpur | 133 | 03:00 | 116 | 15:00 | Sitakunda | 138 | 00:00 | 135 | 15:00
Kachua | 130 | 06:00 | 125 | 12:00 | Sonargaon | 133 | 05:00 | 121 | 16:00
Kaliakoir | 135 | 04:00 | 122 | 12:00 | Sreemongol | 130 | 06:00 | 124 | 15:00
Kaliganj | 138 | 05:00 | 122 | 23:00 | Sreepur | 130 | 08:00 | 121 | 23:00
Kallyanpur | 133 | 04:00 | 119 | 12:00 | Srinagar | 141 | 06:00 | 125 | 12:00
Kalurghat | 139 | 00:00 | 137 | 09:00 | SSM | 142 | 00:00 | 140 | 06:00
Kamrangirchar | 141 | 05:00 | 116 | 12:00 | Sunamganj | 125 | 07:00 | 114 | 21:00
Kaptai | 140 | 1:00 | 139 | 10:00 | Sylhet | 127 | 06:00 | 122 | 22:00
Kasba | 131 | 06:00 | 121 | 13:00 | Sylhet_(South) | 128 | 06:00 | 122 | 21:00
Kazla | 138 | 06:00 | 121 | 13:00 | Tangail | 129 | 05:00 | 115 | 13:00
Keranigonj | 142 | 06:00 | 125 | 12:00 | Taraganj | 134 | 14:00 | 124 | 19:30
Khagrachori | 138 | 00:00 | 135 | 13:00 | Tasnim | 134 | 06:00 | 122 | 12:00
Khulna | 137 | 06:00 | 123 | 23:00 | Thakurgaon | 140 | 12:00 | 127 | 22:00
Khulna(S) | 138 | 06:00 | 124 | 22:00 | TK | 139 | 18:30 | 136 | 12:00
Khulshi | 137 | 18:30 | 133 | 08:00 | Tongi | 136 | 04:00 | 123 | 13:00
Kishoreganj | 129 | 07:00 | 117 | 09:00 | Ullahpara | 136 | 05:00 | 127 | 23:00
Kodda | 130 | 04:00 | 116 | 12:00 | Ullon | 139 | 07:00 | 124 | 13:00
Korerhat | 133 | 00:00 | 129 | 13:00 | Uttara | 135 | 05:00 | 117 | 12:00
KSRM | 140 | 19:30 | 133 | 08:00 | UttaraNew | 133 | 04:00 | 117 | 12:00
Kulaura | 133 | 06:00 | 126 | 21:00 | Zigatola | 142 | 06:00 | 125 | 12:00
Kurigram | 130 | 13:00 | 120 | 22:00
Kushtia | 135 | 06:00 | 122 | 23:00
Laksam | 129 | 05:00 | 124 | 12:00
Lakshmipur | 129 | 06:00 | 122 | 22:00
Lalbag | 141 | 05:00 | 124 | 12:00
Lalmonirhat | 130 | 02:00 | 120 | 22:00
Madanganj | 134 | 07:00 | 124 | 16:00
Madaripur | 131 | 07:00 | 125 | 22:00
Madartek | 140 | 06:00 | 123 | 17:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division