## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 11-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-07-2026 | during | 11-07-2026 | during | 11-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 295 | 407 | 412 | 412 | 380 | 380 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 303 | 304 | 335 | 335 | 301.5 | 301.5 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 303 | 316 | 335 | 335 | 317 | 317 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 16 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 62 | 60 | 149.36 | 149.36 | 149 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12.5 | 21 | 33 | 33 | 17 | 17 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 80 | 300 | 300 | 64 | 130 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 48 | 115 | 149 | 149 | 70 | 132 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 51 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 72 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 2 | 0 | 15 | 0 | 15 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 500 | 460 | 583 | 583 | 524.7 | 524.7 | AGC+Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 212 | 293 | 718 | 718 | 300 | 300 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 143 | 143 | 143 | 143 | 143 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 1768.5 | 2432 | 5565.22 | 5775.22 | 2488.2 | 2777.2
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 4 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 10 | 0 | 2 | 0 | 2 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 173 | 150 | 144 | 144 | 144 | 144 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 213 | 145 | 145 | 145 | 145 | plant availability zero
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 24 | 56 | 24 | 56 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 34 | 0 | 68 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 9 | 30 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.27 | 0 | 1.48 | 0 | 1.48 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 17 | 54.36 | 54.36 | 0 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 50 | 110 | 110 | 17 | 17 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 300 | 300 | 1224 | 1224 | 300 | 300 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 61 | 8 | 15 | 15 | 15 | 15 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 720 | 715 | 730 | 1150 | 670 | 1000 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 1490.27 | 1544 | 3522.34 | 4023.86 | 1633.48 | 2175
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 202 | 190 | 221.25 | 221.25 | 220 | 220 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 0 | 40 | 350.01 | 350.01 | 280 | 280 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 310 | 290 | 342.01 | 342.01 | 240 | 240 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 350 | 350 | 393 | 393 | 250 | 250 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 40 | 41 | 41.65 | 41.65 | 37 | 37 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 45 | 36 | 52.82 | 52.82 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 45 | 8 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 88 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 93 | 93 | 163 | 163 | 95 | 95 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 16 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 124 | 130 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 33 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 26 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 69 | 115 | 115 | 0 | 51 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 9 | 0 | 30 | 0 | 30 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1283 | 1480 | 2732.44 | 2696.44 | 1653.2 | 1886.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-07-2026 | during | 11-07-2026 | during | 11-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 11.48 | 0 | 12 | 0 | 12 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.4 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 117 | 156 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 14.6 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 203.48 | 253 | 526.6 | 516.5 | 252.1 | 269
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 29 | 29 | 0 | 0 | 0 | 0 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 139 | 144 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 142 | 141 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 63 | 80 | 81 | 81 | 83 | 83 | Machine Problem
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 104 | 102 | 102 | 102 | 102 | 102 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 16 | 25 | 25 | 16 | 16 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 331 | 320 | 220 | 220 | 220 | 220 | machine problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1147 | 1177 | 1122 | 1122 | 1045 | 1045
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 905 | 905 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 35 | 35 | 35 | 35 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 32 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 70 | 0 | 12 | 0 | 12 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 908 | 1210 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1921 | 2153 | 3551.2 | 3539.2 | 2731.2 | 2719.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 500 | 700 | 500 | 600 | 500 | 600 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 65 | 65 | 130 | 130 | 65 | 65 | GT-1 & ST under maint
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 996 | 1170 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 30 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 277 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.06 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3407.64 | 1868.06 | 2495 | 2662 | 2761 | 2370 | 2469
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 11.22 | 0 | 20 | 0 | 20 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 160 | 159 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 150 | 165 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 160 | 220 | 220 | 150 | 150 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 100 | 100 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 66 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 0 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1150.21 | 1473.07 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 18 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 9 | 0 | 85 | 0 | 85 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2062.43 | 2437.07 | 3206.72 | 3035.12 | 2737.34 | 2742.74
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 41 | 38 | 40 | 40 | 39 | 39 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 190 | 180 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 99 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.8 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 17 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 182 | 0 | 185.19 | 0 | 185.19 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 431.8 | 387 | 704.19 | 488 | 570.19 | 389
System Total |  |  |  |  | 28843.2 | 29250.117 | 12175.54 | 14358.07 | 23592.71 | 23957.34 | 15480.71 | 16472.34
Forecast Scenario (11-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14400 |  | 38.2 |  | 14440
|  |  |  | 1:00 | 13900 |  | 19.1 |  | 13920
|  |  |  | 2:00 | 13500 |  | 28.65 |  | 13530
|  |  |  | 3:00 | 13100 |  | 19.1 |  | 13120
|  |  |  | 4:00 | 12800 |  | 76.4 |  | 12880
|  |  |  | 5:00 | 12600 |  | 85.95 |  | 12690
|  |  |  | 6:00 | 11900 |  | 76.4 |  | 11980
|  |  |  | 7:00 | 12000 |  | 38.2 |  | 12040
|  |  |  | 8:00 | 11900 |  | 38.2 |  | 11940
|  |  |  | 9:00 | 12100 |  | 47.75 |  | 12150
|  |  |  | 10:00 | 12350 |  | 47.75 |  | 12400
|  |  |  | 11:00 | 12800 |  | 85.95 |  | 12890
|  |  |  | 12:00 | 13400 |  | 66.85 |  | 13470
|  |  |  | 13:00 | 13500 |  | 76.4 |  | 13580
|  |  |  | 14:00 | 13600 |  | 85.95 |  | 13690
|  |  |  | 15:00 | 14400 |  | 0 |  | 14220
|  |  |  | 16:00 | 14000 |  | 19.1 |  | 14020
|  |  |  | 17:00 | 13700 |  | 66.85 |  | 13770
|  |  |  | 18:00 | 12800 |  | 85.95 |  | 12890
|  |  |  | 18:30 | 12900 |  | 95.5 |  | 13000
|  |  |  | 19:00 | 13300 |  | 19.1 |  | 13320
|  |  |  | 19:30 | 14300 |  | 19.1 |  | 14320
|  |  |  | 20:00 | 14510 |  | 85.95 |  | 14600
|  |  |  | 21:00 | 14600 |  | 100 |  | 14755
|  |  |  | 22:00 | 14320 |  | 76.4 |  | 14400
|  |  |  | 23:00 | 14110 |  | 85.95 |  | 14200
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 13470.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 100
Probable Maximum Demand at Evening Peak: |  |  | 14755.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14600.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 319.59 MKWHr. |  | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 100
*** This report is generated digitally from Operation Information System (OIS) at 08:56 hrs on 11-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 10-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12175.54 | MW | 12:00 Hr. | Energy Generated |  |  | 310.2926 |  | MKWHr.
| Day Peak Demand |  |  | 12175.54 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.68 |  | MKWHr.
| Evening Peak Generation |  |  | 14358.07 | MW | 21:00 Hr. | Energy Demand |  |  | 311.9726 |  | MKWHr.
| Evening Peak Demand |  |  | 14389.07 | MW | 21:00 Hr. | Maximum Temperature |  |  | 29.2 |  | °C
| Minimum Generation of the Day |  |  | 11329.86 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 929.8 |  | MMCFD
| Maximum Generation of the Day |  |  | 14744.53 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 6.0416 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.178 | 0 | 9.3365 | 0 | 0 | 0.056671 | 0 | 0 | 49.5711 | Gas | 126.2001 | Gas | 437500964.173
| Chattogram Zone |  |  | 4.8298 | 24.1218 | 2.668 | 0 | 3.7143 | 0.05388 | 0 | 1.0469 | 36.4348 | Coal | 100.1066 | Coal | 669046298.5819
| Cumilla Zone |  |  | 28.0038 | 0 | 2.5422 | 0 | 0 | 0.1725 | 2.8051 | 0 | 33.5236 | HFO | 22.3968 | HFO | 376720175.212
| Mymensingh Zone |  |  | 0 | 0 | 3.9119 | 0 | 0 | 0.22758 | 0 | 0 | 4.1395 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.7807 | 0 | 0 | 0 | 0 | 0.031466 | 0 | 0 | 27.8122 | Hydro | 3.7143 | Hydro | 14151559.2
| Khulna Zone |  |  | 0 | 24.3854 | 0.13501 | 0 | 0 | 0.14904 | 22.768 | 0 | 47.4375 | Solar | 2.6629 | Solar | 44549837.9828
| Barishal Zone |  |  | 5.1826 | 46.1739 | 1.09 | 0 | 0 | 0.00163 | 0 | 0 | 52.4481 | Import | 54.1651 | Import | 317292313.6
| Rajshahi Zone |  |  | 20.2252 | 0 | 1.0243 | 0 | 0 | 0.57995 | 28.592 | 0 | 50.4214 | Wind | 1.0469 | Wind | 15399604.8
| Rangpur Zone |  |  | 0 | 5.4254 | 1.6888 | 0 | 0 | 1.3902 | 0 | 0 | 8.5044
| Total |  |  | 126.2001 | 100.1066 | 22.3968 | 0 | 3.7143 | 2.6629 | 54.1651 | 1.0469 | 310.2926
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 437500964.173 |  | Hydro | 14151559.2
|  |  |  | Coal | 669046298.5819 |  | Solar | 44549837.9828
|  |  |  | HFO | 376720175.212 |  | Import | 317292313.6
|  |  |  | HSD | 0 |  | Wind | 15399604.8
[5 empty] | Total: | 187,46,60,753 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.856 | Peak Hr Flow | 905.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 54581036.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.592 | Peak Hr Flow | 1473.07 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2710 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.8051 | Peak Hr Flow | 130.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 3140 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.2531 | Peak Hr Flow | 2508.07 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 14 |  | 4943
|  |  |  | Chattogram |  | 0 |  | 1292
|  |  |  | Cumilla |  | 0 |  | 1390
|  |  |  | Mymensingh |  | 16 |  | 1232
|  |  |  | Sylhet |  | 0 |  | 604
|  |  |  | Khulna |  | 0 |  | 1662
|  |  |  | Barishal |  | 0 |  | 478
|  |  |  | Rajshahi |  | 0 |  | 1521
|  |  |  | Rangpur |  | 0 |  | 954
|  |  |  | Total |  | 30 |  | 14076
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Fenchugonj CCPP Phase-2 GT-4 |  |  | 35
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 85
|  |  |  | Total Unavailable Capacity |  |  |  | 385
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:10 |  | Bhola Nutan Biddut BD LTD ST Tripped with remarks:- STG tripped on turbine protection
logic activation at 08:10hrs. on 10/07/2026
| 08:12 | 17:06 | Baroirhat-PHP 132 kV Ckt-1 Scheduled S/D from Baroirhat 132/33kV end Due to PHP
Substation Work
| 08:16 | 10:37 | Naogaon 132/33kV S/S T-2 33kV BUS Forced S/D Due to Red hot maintenance. | [7 empty] | 10.0MW load
interrup.
| 08:18 | 17:00 | Feni-PHP 132kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to PHP end maintenance
work
| 08:29 |  | Chowmuhani 230/132/33kV S/S TR2-425T HT Scheduled S/D Due to Panel replacement.
| 08:29 |  | Chowmuhani 230/132/33kV S/S TR2-425T LT Scheduled S/D Due to Panel replacement.
|  | 08:29 | Kishoreganj-Mymensingh 132kV Ckt-1 is restored.
|  | 08:29 | Kishoreganj-Mymensingh 132kV Ckt-1 is restored.
|  | 08:40 | Juldah 132/33kV S/S 133/33 KV T-2 416T LT is restored.
|  | 09:07 | GPH 230/33kV S/S Transformer-01(D05) HT is restored.
| 09:12 |  | Sonargaon 132/33kV S/S Tr-1 HT Scheduled S/D Due to Transformer Oil centrifuge purpose. | [7 empty] | 20.0MW load
interrup.
| 09:12 |  | Sonargaon 132/33kV S/S Tr-1 LT Scheduled S/D Due to Transformer Oil centrifuge purpose. | [7 empty] | 20.0MW load
interrup.
| 09:25 | 18:20 | Coxsbazar 132/33kV S/S 405T-T1 HT Project Work S/D Due to project work | [7 empty] | 5.0MW load
interrup.
| 09:34 | 17:26 | Bhaluka-Mymensingh 132 kV Ckt-1 Project Work S/D from Bhaluka 132/33kV end Due to
Mymensingh Bhaluka 400 KV line stringing work and from Mymensingh 132/33kVend.
| 09:34 | 17:30 | Bhaluka-Mymensingh 132 kV Ckt-2 Project Work S/D from Bhaluka 132/33kV end Due to
Mymensingh Bhaluka 400 KV line stringing work and from Mymensingh 132/33kVend.
| 10:14 | 17:20 | Bhaluka 132/33kV S/S Sreepur Ckt- 02 Scheduled S/D Due to Clamp changing
| 10:20 | 17:17 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-2 Scheduled S/D Due to taken by NLDC for
bhaluka end works
| 10:22 | 11:52 | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to Red hot maintenance of 33 kV Goari | [7 empty] | 70.0MW load
|  |  | feeder Source side | [7 empty] | interrup.
| 10:23 | 11:50 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to Red hot maintenance of 33 kV Goari | [7 empty] | 70.0MW load
|  |  | feeder Source Side | [7 empty] | interrup.
| 10:54 | 15:49 | Bogura 230/132kV S/S T-01 HT Scheduled S/D Due to Auxiliary Transformer Work
| 10:54 | 15:50 | Bogura 230/132kV S/S T-01 LT Scheduled S/D Due to Auxiliary Transformer work
|  | 11:30 | Khulna(S) 230/132kV S/S TR-1 HT is restored.
|  | 11:31 | Khulna(S) 230/132kV S/S TR-1 LT is restored.
|  | 11:31 | Khulna(S) 230/132kV S/S TR-3 HT is restored.
|  | 11:32 | Khulna(S) 230/132kV S/S TR-3 LT is restored.
|  | 11:34 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
|  | 11:34 | Khulna(C )-Khulna (S) 132kV Ckt-2 is restored.
|  | 11:39 | Khulna (S)-Satkhira 132kV Ckt-1 is restored.
|  | 11:40 | Gallamari- Khulna (S) 132kV Ckt-1 is restored.
|  | 11:41 | Gallamari- Khulna (S) 132kV Ckt-2 is restored.
| 11:48 | 12:00 | Khulna (S)-Satkhira 132kV Ckt-2 Forced S/D from Satkhira 132/33kV end.
|  | 11:56 | Khulna(S) 230/132kV S/S TR-2 LT is restored.
| 11:58 | 12:10 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Tripped showing O/C relays Due to Nowabganj-2 | [7 empty] | 28.0MW load
|  |  | 33 kv load side R phase conductor broke down | [7 empty] | interrup.
| 11:58 | 12:10 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Tripped showing O/C relays Due to Nowabganj-2 | [7 empty] | 28.0MW load
|  |  | 33kv feeder load side R Phase conductor broke down | [7 empty] | interrup.
| 12:00 |  | Day Peak Generation: 12175 MW.
| 12:34 | 16:39 | Lakshmipur 132/33kV S/S Transformer-2 LT Forced S/D Due to Redhot Maintenance Work.
| 12:36 | 16:38 | Lakshmipur 132/33kV S/S Transformer-2 HT Forced S/D Due to Redhot Maintenance Work.
| 14:45 | 15:45 | Ramganj 132/33kV S/S Transformer -02 LT Scheduled S/D Due to OTI Alarm Checking | [7 empty] | 15.0MW load
interrup.
| 14:54 | 17:15 | Bhaluka 132/33kV S/S Bus A Scheduled S/D
| 15:04 |  | Kachua 230/132/33kV S/S Laksam CKT-2 Project Work S/D Due to to resolve the Pole
Discrepancy fault.
| 16:07 |  | Bhola Nutan Biddut BD LTD ST Synchronized with remarks:- ST Synchronized to grid at 16:01
hrs. on 10 July 2026
| 16:24 |  | BIPTC S/S 20DF24 Tripped showing PSD relays.
| 17:02 |  | Bhola Nutan Biddut BD LTD GT-1 Synchronized with remarks:- GT-11 Synchronized to grid at
17:02hrs. on 10 July 2026.
| 17:09 | 18:23 | Lakshmipur 132/33kV S/S Transformer-1 LT Forced S/D Due to Redhot work Maintenance.
| 17:11 | 18:21 | Lakshmipur 132/33kV S/S Transformer-1 HT Forced S/D Due to Redhot work maintenance
| 17:45 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- GT
| 21:00 |  | Evening peak generation is 14358 MW.
| 21:18 | 22:44 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Forced S/D Due to Hot Spot maintenance.
| 21:19 | 22:44 | Niamatpur 132/33kV S/S Transformer-1(407T) HT Forced S/D Due to Hot Spot maintenance.
| 02:35 |  | BIPTC S/S 10CF16 Tripped showing Differential Relay relays Due to Tripped by C1 Unbalance
CPR04.
| 02:50 | 03:28 | Bakulia-MSML 132 kV Ckt-2 Tripped from Bakulia 132/33kV end showing Siemens Relay relays
Due to Bakali khulshi cKt-02 Trip Due to Heavy thunder & rain
| 03:01 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- ST
| 06:00 |  | Minimum Generation: 12277 MW.
| 06:36 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Hot spot maintenance | [7 empty] | 20.0MW load
interrup.
| 06:36 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Hot spot maintenance | [7 empty] | 20.0MW load
interrup.
| 07:30 |  | Jhenaidah 132/33kV S/S Transformer T-3 LT Forced S/D Due to For, Maintainance of 33kv
'R' phase Redhot at CB input side.
| 07:30 |  | Jhenaidah 132/33kV S/S Transformer T-3 HT Forced S/D Due to For, Maintainance of 33kv
'R' phase Redhot at CB input side.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 10-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 407 | 7984800 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 304 | 7283055 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 486309 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 316 | 7480021 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 16 | 100440 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 60 | 2149920 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 220181 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 70050 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 441600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 404640 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 217920 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 80 | 1357920 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 1478592 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 413760 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 354240 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 56671 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 148320 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 460 | 11347655 | AGC+Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 293 | 5236254 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143 | 2338800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2432 | 49571148
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 4 | 46321.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 43200 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 347520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 150 | 3714320 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 213 | 4300403 | plant availability zero
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 505163 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 45178 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 98880 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 30 | 529440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 10680 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 42655 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 330848 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 50 | 951800 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 128640 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 164345 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 6691 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 300 | 7249090 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 1046880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 715 | 16872727.27 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 1544 | 36434781.47
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 190 | 4942000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 40 | 605100 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 290 | 7356000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 350 | 8671500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 41 | 967752 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 36 | 753600 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 903272.73 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1180888 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 88 | 526909 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 93 | 2217644 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 16 | 668160 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 130 | 2805120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 88282 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 406020 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 33 | 648660 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 244440 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 365760 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 172500 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1480 | 33523607.73
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 73764 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 156 | 2220000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1320000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 144720 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 95760 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 276120 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 253 | 4139464
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 31466 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 29 | 693000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under Maintenance
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 144 | 3325172.73 | AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 141 | 3283000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 681312 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1704960 | Machine Problem
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 2396160 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 329088 | Machine Problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7407000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 320 | 7961000 | machine problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1177 | 27812158.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 905 | 21856000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 62575 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 72432 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 149040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1210 | 24385450 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2153 | 47437497
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 700 | 13367273 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 808032 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 65 | 1558000 | GT-1 & ST under maint
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1170 | 27067636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 3624560 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 282000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5739000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1630 | -
Barishal Area Total |  |  |  |  | 3407.64 | 2495 | 52448131.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 111528 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 25000 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 51562 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 159 | 3857727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 165 | 3846245 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 160 | 3821327 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 8699855 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 33008 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 51278 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 108544 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 66 | 592128 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 162816 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 16140 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1473.07 | 28592000 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 218400 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 233880 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2437.07 | 50421438
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 38 | 933382 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4492000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 707078 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 23081.64 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 981754 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 112881 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1254240 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 387 | 8504416.64
Eastern Grid Total |  |  |  |  | 17438.042 | 6886 | 151481159.93
Western Grid Total |  |  |  |  | 11812.075 | 7472.07 | 158811483
National Grid Total |  |  |  |  | 29250.117 | 14358.07 | 310292642.93
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 10-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9476.6 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4615.8 | MW
i) Dhaka area |  |  | 4928.6 |  | MW | i) Khulna area |  |  |  | 1662 | MW
ii) Chattogram area |  |  | 1338 |  | MW | ii) Barishal area |  |  |  | 478.4 | MW
iii) Cumilla area |  |  | 1390 |  | MW | iii) Rajshahi area |  |  |  | 1521.4 | MW
iv) Mymensingh area |  |  | 1216 |  | MW | iv) Rangpur area |  |  |  | 954 | MW
v) Sylhet area |  |  | 604 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14092.4 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 127 | 02:00 | 133 | Narshingdi | 184 | 00:00 | 199 | Uttara | 85 | 19:00
2 | AKSML | 136.5 | 03:00 | 68 | Hasnabad | 82 | 00:00 | 134 | Natore | 150 | 22:00 | 200 | UttaraNew | 50 | 13:00
3 | Aftabnagar | 40 | 00:00 | 69 | Hathazari | 82 | 22:00 | 135 | Nawabganj | 59.4 | 22:00 | 201 | Zigatola | 82 | 13:00
4 | Agargaon | 96 | 21:00 | 70 | Hatirjheel | 33 | 19:00 | 136 | Netrakona | 141 | 20:00
5 | Agrabad | 50 | 00:00 | 71 | Ishurdi | 74 | 00:00 | 137 | New | 70 | 00:00
6 | Amnura | 30 | 23:00 | 72 | Jaldhaka | 89 | 23:00 | 138 | Niamatpur | 82 | 21:00
7 | Ashuganj | 87 | 06:00 | 73 | Jamalpur | 140 | 21:00 | 139 | Noapara | 38 | 00:00
8 | BSRM | 193 | 08:00 | 74 | Jashore | 154 | 00:00 | 140 | PHP | 7 | 02:00
9 | Bagerhat | 83 | 01:00 | 75 | Jhenaidah | 94 | 00:00 | 141 | Pabna | 89 | 20:00
10 | Bajitpur | 92 | 21:00 | 76 | Joydebpur | 151 | 00:00 | 142 | Palashbari | 142 | 23:00
11 | Bakerganj | 15.4 | 21:00 | 77 | Joypurhat | 66 | 22:00 | 143 | Panchagarh | 69 | 20:00
12 | Bakulia | 83 | 20:00 | 78 | Juldah | 16 | 23:00 | 144 | Patiya | 11 | 19:00
13 | Banani | 111.7 | 21:00 | 79 | KSRM | 38 | 14:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 4 | 15:00 | 80 | Kabirpur | 197 | 20:00 | 146 | Patuakhali | 71 | 22:00
15 | Barapukuria | 64 | 00:00 | 81 | Kachua | 94 | 21:00 | 147 | Payra | 36 | 22:00
16 | Barguna | 22 | 22:00 | 82 | Kaliganj | 37 | 00:00 | 148 | Postogola | 60 | 00:00
17 | Barishal | 99 | 13:00 | 83 | Kallyanpur | 117 | 00:00 | 149 | Pubail | 41 | 00:00
18 | Barishal-230 | 96 | 21:00 | 84 | Kalurghat | 27 | 19:00 | 150 | Purbachal | 25 | 20:00
19 | Baroaulia | 38 | 06:00 | 85 | Kamrangirchar | 73 | 00:00 | 151 | Purbasadipur | 138 | 00:00
20 | Baroirhat | 62 | 19:30 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 42 | 21:00
21 | Bashundhara | 176 | 12:00 | 87 | Kasba | 37 | 19:30 | 153 | Rahim | 22 | 22:00
22 | BashundharaCement | 1 | 00:00 | 88 | Kazla | 104 | 00:00 | 154 | Rajbari | 85 | 00:00
23 | Beanibazar | 70 | 21:00 | 89 | Keranigonj | 78 | 00:00 | 155 | Rajendrapur | 114 | 00:00
24 | Benapole | 57 | 00:00 | 90 | Khagrachori | 30 | 00:00 | 156 | Rajshahi | 106 | 22:00
25 | Bhaluka | 163 | 21:00 | 91 | Khulna | 59 | 20:00 | 157 | Rajshahi-230 | 101 | 13:00
26 | Bhandaria | 57 | 01:00 | 92 | Khulshi | 181 | 13:00 | 158 | Ramganj | 116 | 22:00
27 | Bhangura | 38 | 19:30 | 93 | Kishoreganj | 136 | 22:00 | 159 | Rampur | 40 | 23:00
28 | Bheramara(GK) | 65 | 00:00 | 94 | Kodda | 244 | 02:00 | 160 | Rangamati | 14 | 19:00
29 | Bhulta | 200 | 00:00 | 95 | Kulaura | 60 | 20:00 | 161 | Rangpur | 136 | 19:30
30 | Bog-Sherpur | 78 | 23:00 | 96 | Kurigram | 74 | 20:00 | 162 | Ruppur | 3.6 | 10:00
31 | Bogura | 176 | 00:00 | 97 | Kushtia | 148 | 00:00 | 163 | SSM | 2 | 00:00
32 | Borhanuddin | 76 | 23:00 | 98 | Laksam | 35 | 22:00 | 164 | Saidpur | 96 | 00:00
33 | Brahmanbaria | 135 | 00:00 | 99 | Lakshmipur | 42 | 22:00 | 165 | Santhia | 36 | 19:30
34 | Cantonment | 114 | 13:00 | 100 | Lalbag | 69 | 00:00 | 166 | Satkhira | 129 | 20:00
35 | Chandina | 37 | 19:30 | 101 | Lalmonirhat | 66 | 20:00 | 167 | Satmasjid | 89 | 00:00
36 | Chandpur | 86 | 20:00 | 102 | MI_Cement | 17.4 | 11:00 | 168 | Savar | 176 | 00:00
37 | Chandraghona | 38 | 20:00 | 103 | Madanganj | 39 | 21:00 | 169 | SevenRings | 6.39 | 04:00
38 | Chapai | 78 | 21:00 | 104 | Madaripur | 116 | 22:00 | 170 | ShahCement | 22 | 00:00
39 | Charfasson | 35 | 23:00 | 105 | Madartek | 78 | 00:00 | 171 | Shahjadpur | 69 | 19:00
40 | Charsaidpur | 30 | 01:00 | 106 | Madunaghat | 48 | 20:00 | 172 | Shahjibazar | 130 | 00:00
41 | Chauddagram | 73 | 22:00 | 107 | Magura | 65 | 00:00 | 173 | Shahmirpur | 43 | 19:00
42 | Chhatak | 34 | 23:00 | 108 | Mahasthangarh | 82 | 00:00 | 174 | Shariatpur | 92 | 22:00
43 | Chowmuhani | 153 | 23:00 | 109 | Maijdee | 37 | 22:00 | 175 | Sherpur | 156 | 19:30
44 | Chuadanga | 123 | 00:00 | 110 | Manikganj | 132 | 02:00 | 176 | Shikalbaha | 32 | 01:00
45 | Coxsbazar | 137 | 23:00 | 111 | Maniknagar | 68 | 13:00 | 177 | Shitalakhya | 58 | 00:00
46 | Cumilla(N) | 132 | 22:00 | 112 | Matarbari | 46 | 02:00 | 178 | Sholosohor | 39 | 22:00
47 | Cumilla(S) | 140 | 00:00 | 113 | Matuail | 74 | 00:00 | 179 | Shomvuganj | 35 | 21:00
48 | Daganbhuiyan | 29 | 23:00 | 114 | Metrorail_Motijheel | 20 | 17:00 | 180 | Shyampur | 150 | 12:00
49 | Daudkandi | 140 | 00:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 110 | 00:00
50 | DhakaUniversity | 44 | 00:00 | 116 | Millgate | 74 | 02:00 | 182 | Sirajganj | 106 | 23:00
51 | Dhamrai | 100 | 00:00 | 117 | Mirpur | 139 | 12:00 | 183 | Sitakunda | 30 | 19:30
52 | Dhanmondi | 82 | 19:00 | 118 | Mirsorai | 42 | 07:00 | 184 | Sonargaon | 134 | 03:00
53 | Dohazari | 88 | 19:00 | 119 | Mirzapur | 42 | 22:00 | 185 | Sreemongol | 75 | 21:00
54 | Faridpur | 172 | 00:00 | 120 | Mithapukur | 78 | 19:30 | 186 | Sreepur | 117 | 00:00
55 | Fatullah | 87 | 00:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 49.7 | 22:00
56 | Fenchuganj | 41 | 22:00 | 122 | Mogbazar | 71 | 00:00 | 188 | Sunamganj | 60 | 21:00
57 | Feni | 104 | 23:00 | 123 | Mongla | 29 | 00:00 | 189 | Sylhet | 98 | 00:00
58 | GPH | 1 | 00:00 | 124 | Motijheel | 36 | 00:00 | 190 | Sylhet_(South) | 63 | 22:00
59 | Ghatail | 98 | 20:00 | 125 | Muktagacha | 41 | 21:00 | 191 | TK | 27 | 19:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 115 | 23:00 | 192 | Tangail | 186 | 21:00
61 | Ghorashal-230 | 99 | 00:00 | 127 | Muradnagar | 49 | 19:30 | 193 | Taraganj | 26 | 00:00
62 | Goalpara | 39 | 22:00 | 128 | Mymensingh | 128 | 21:00 | 194 | Tasnim | 48 | 04:00
63 | Gollamari | 92 | 00:00 | 129 | Nabinagar | 90 | 00:00 | 195 | Thakurgaon | 113 | 20:00
64 | Gopalganj | 101 | 19:30 | 130 | Naogaon | 137 | 21:00 | 196 | Tongi | 148 | 00:00
65 | Gulshan | 78 | 19:00 | 131 | Narail | 57 | 19:30 | 197 | Ullahpara | 38 | 20:00
66 | Halishahar | 65 | 23:00 | 132 | Narinda | 48 | 00:00 | 198 | Ullon | 55 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 10-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14735.6 | 342 |  | 15092.99
1:00 | 14272.82 | 316 |  | 14603.04
2:00 | 14215.58 | 151 |  | 14373.38
3:00 | 13755.78 | 137 |  | 13898.95
4:00 | 13302.59 | 114 |  | 13421.72
5:00 | 12643.74 | 97 |  | 12745.11
6:00 | 11843.34 | 53 |  | 11898.73
7:00 | 11509.2 | 45 |  | 11556.23
8:00 | 11329.86 | 72 |  | 11405.1
9:00 | 11404.37 | 68 |  | 11475.43
10:00 | 11366.59 | 126 |  | 11498.26
11:00 | 11648.96 | 0 |  | 11648.96
12:00 | 12175.54 | 0 |  | 12175.54
13:00 | 12924.47 | 38 |  | 12964.47
14:00 | 12484.42 | 10 |  | 12494.87
15:00 | 12272.81 | 14 |  | 12287.81
16:00 | 11566.55 | 10 |  | 11576.55
17:00 | 11459.86 | 10 |  | 11469.86
18:00 | 11576.38 | 10 |  | 11586.83
19:00 | 12969.35 | 22 |  | 12992.34
19:30 | 14031.32 | 25 |  | 14057.32
20:00 | 14229.29 | 15 |  | 14244.97
21:00 | 14358.07 | 30 |  | 14389.07
22:00 | 14516.88 | 0 |  | 14516.88
23:00 | 14744.53 | 0 |  | 14744.53
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 10-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 163 | 11 | 594 | 150 | 2348 | 534 | Ishurdi-Ghorashal Ckt-1 | Export | 3874036.36
1:00 | 160 | 11 | 600 | 126 | 2010 | 538
2:00 | 157 | 12 | 586 | 120 | 1984 | 552 |  | Import | 0
3:00 | 155 | 16 | 570 | 112 | 1946 | 538
4:00 | 171 | 25 | 612 | 122 | 2280 | 558 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 190 | 37 | 612 | 114 | 2338 | 608
6:00 | 176 | 18 | 864 | 100 | 1922 | 568 |  | Import | 0
7:00 | 172 | 17 | 536 | 100 | 1766 | 512
8:00 | 153 | 12 | 470 | 96 | 1606 | 474 | Sirajganj-Sreepur Ckt-1 | Export | 3098000
9:00 | 166 | 16 | 490 | 88 | 1644 | 486
10:00 | 182 | 22 | 456 | 56 | 1582 | 496 |  | Import | 0
11:00 | 164 | 9 | 484 | 90 | 1714 | 468
12:00 | 186 | 11 | 580 | 106 | 1904 | 510 | Sirajganj-Sreepur Ckt-2 | Export | 3109000
13:00 | 189 | 16 | 590 | 106 | 2038 | 502
14:00 | 176 | 17 | 508 | 84 | 1866 | 475 |  | Import | 0
15:00 | 186 | 23 | 526 | 88 | 1862 | 486
16:00 | 170 | 24 | 470 | 94 | 1576 | 488 | Gopalganj-Aminbazar Ckt-1 | Export | 22220000
17:00 | 164 | 18 | 410 | 52 | 1612 | 458
18:00 | 144 | 13 | 430 | 82 | 1534 | 414 |  | Import | 0
18:30 | 157 | 12 | 502 | 82 | 1814 | 428
19:00 | 152 | 3 | 510 | 100 | 1902 | 380 | Gopalganj-Aminbazar Ckt-2 | Export | 22280000
19:30 | 131 | 1 | 496 | 88 | 1888 | 314
20:00 | 132 | -2 | 520 | 108 | 1932 | 330 |  | Import | 0
21:00 | 144 | -1 | 570 | 140 | 1996 | 344
22:00 | 132 | -4 | 536 | 142 | 1866 | 366 |  | Total Export | 54581036.36
23:00 | 138 | -3 | 612 | 164 | 1878 | 390 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 10-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6782 | 7953.6 | 14735.6 | DAILY GENERATION CURVE
00:30 | 6771.43 | 7732.78 | 14504.21
01:00 | 6760.86 | 7511.96 | 14272.82 | 10-07-2026
01:30 | 6826.11 | 7418.09 | 14244.2
02:00 | 6891.36 | 7324.22 | 14215.58
02:30 | 6773.86 | 7211.82 | 13985.68
03:00 | 6656.36 | 7099.42 | 13755.78
03:30 | 6446.18 | 7083.005 | 13529.185
04:00 | 6236 | 7066.59 | 13302.59
04:30 | 6056.5 | 6916.665 | 12973.165
05:00 | 5877 | 6766.74 | 12643.74
05:30 | 5780.35 | 6463.19 | 12243.54
06:00 | 5683.7 | 6159.64 | 11843.34
06:30 | 5649.69 | 6026.58 | 11676.27
07:00 | 5615.68 | 5893.52 | 11509.2
07:30 | 5635.59 | 5783.94 | 11419.53
08:00 | 5655.5 | 5674.36 | 11329.86
08:30 | 5717.04 | 5650.075 | 11367.115
09:00 | 5778.58 | 5625.79 | 11404.37
09:30 | 5763.35 | 5622.13 | 11385.48
10:00 | 5748.12 | 5618.47 | 11366.59
10:30 | 5831.63 | 5676.145 | 11507.775
11:00 | 5915.14 | 5733.82 | 11648.96
11:30 | 5903.695 | 6008.555 | 11912.25
12:00 | 5892.25 | 6283.29 | 12175.54
12:30 | 5996.345 | 6553.66 | 12550.005
13:00 | 6100.44 | 6824.03 | 12924.47
13:30 | 6004.515 | 6699.93 | 12704.445
14:00 | 5908.59 | 6575.83 | 12484.42
14:30 | 5880.115 | 6498.5 | 12378.615
15:00 | 5851.64 | 6421.17 | 12272.81
15:30 | 5777.445 | 6142.235 | 11919.68
16:00 | 5703.25 | 5863.3 | 11566.55
16:30 | 5769.06 | 5744.145 | 11513.205
17:00 | 5834.87 | 5624.99 | 11459.86
17:30 | 5913.69 | 5604.43 | 11518.12
18:00 | 5992.51 | 5583.87 | 11576.38
18:30 | 6152.755 | 6120.11 | 12272.865
19:00 | 6313 | 6656.35 | 12969.35
19:30 | 6883 | 7148.32 | 14031.32
20:00 | 6915 | 7314.29 | 14229.29
20:30 | 6900.5 | 7393.18 | 14293.68 |  | Executive Engineer
21:00 | 6886 | 7472.07 | 14358.07 |  | Network Operation Division
21:30 | 6977.4 | 7460.075 | 14437.475
22:00 | 7068.8 | 7448.08 | 14516.88
22:30 | 7147.65 | 7483.055 | 14630.705
23:00 | 7226.5 | 7518.03 | 14744.53

## En-Curve
QF-LDC-12
Date | 10-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3237 | 1641 | 905 | 38 | 140 | 1485.6 | 94 | 5196 | 0 | 502 | 1489 | 0 | 0 | 8 | 342 | DAILY ENERGY CURVE
00:30 | 3275.5 | 1693.75 | 905 | 38 | 135 | 1486.28 | 126 | 4845 | 0 | 522 | 1473.68 | 0 | 0 | 4 | 329 | 10-07-2026
01:00 | 3314 | 1746.5 | 905 | 38 | 130 | 1486.96 | 158 | 4494 | 0 | 542 | 1458.36 | 0 | 0 | 0 | 316
01:30 | 3360 | 1752.75 | 905 | 38 | 130 | 1487.09 | 158.5 | 4434.5 | 0 | 479 | 1497.86 | 0 | 0 | 1.5 | 233.5 | Energy Generated | 310.2926 |  | MKWHr
02:00 | 3406 | 1759 | 905 | 38 | 130 | 1487.22 | 159 | 4375 | 0 | 416 | 1537.36 | 0 | 0 | 3 | 151 | Energy not Served | 1.68 |  | MKWHr
02:30 | 3415 | 1735 | 905 | 38 | 126 | 1424.82 | 160 | 4327 | 0 | 382 | 1439.86 | 0 | 0 | 33 | 144 | Total Energy Requirement | 311.9726 |  | MKWHr
03:00 | 3424 | 1711 | 905 | 38 | 122 | 1362.42 | 161 | 4279 | 0 | 348 | 1342.36 | 0 | 0 | 63 | 137
03:30 | 3391 | 1719.5 | 904.5 | 38 | 121 | 1368.505 | 162.5 | 4275 | 0 | 330 | 1155.18 | 0 | 0 | 64 | 125.5
04:00 | 3358 | 1728 | 904 | 38 | 120 | 1374.59 | 164 | 4271 | 0 | 312 | 968 | 0 | 0 | 65 | 114
04:30 | 3355 | 1734.5 | 904.5 | 38 | 121 | 1372.165 | 164 | 4274.5 | 0 | 302 | 645 | 0 | 0 | 62.5 | 105.5
05:00 | 3352 | 1741 | 905 | 38 | 122 | 1369.74 | 164 | 4278 | 0 | 292 | 322 | 0 | 0 | 60 | 97
05:30 | 3244.5 | 1796 | 905 | 38 | 116 | 1297.035 | 164 | 4097 | 3.005 | 279.5 | 247.5 | 0 | 0 | 56 | 75
06:00 | 3137 | 1851 | 905 | 38 | 110 | 1224.33 | 164 | 3916 | 6.01 | 267 | 173 | 0 | 0 | 52 | 53
06:30 | 3136 | 1853.5 | 905 | 38 | 105 | 1173.92 | 164 | 3799.5 | 35.85 | 257.5 | 152 | 0 | 0 | 56 | 49
07:00 | 3135 | 1856 | 905 | 38 | 100 | 1123.51 | 164 | 3683 | 65.69 | 248 | 131 | 0 | 0 | 60 | 45
07:30 | 3116 | 1897 | 905 | 38 | 97 | 1025.005 | 162 | 3650 | 98.025 | 248 | 130.5 | 0 | 0 | 53 | 58.5
08:00 | 3097 | 1938 | 905 | 38 | 94 | 926.5 | 160 | 3617 | 130.36 | 248 | 130 | 0 | 0 | 46 | 72
08:30 | 3103.5 | 1916.5 | 904.5 | 38 | 99 | 925.175 | 169.5 | 3625.5 | 164.94 | 248 | 130 | 0 | 0 | 42.5 | 70
09:00 | 3110 | 1895 | 904 | 38 | 104 | 923.85 | 179 | 3634 | 199.52 | 248 | 130 | 0 | 0 | 39 | 68
09:30 | 3130 | 1856.5 | 904 | 38 | 105 | 881.01 | 176.5 | 3607.5 | 249.47 | 230.5 | 167.5 | 0 | 0 | 39.5 | 97
10:00 | 3150 | 1818 | 904 | 38 | 106 | 838.17 | 174 | 3581 | 299.42 | 213 | 205 | 0 | 0 | 40 | 126
10:30 | 3244.5 | 1818 | 904 | 38 | 108 | 832.275 | 174.5 | 3610 | 344.5 | 179 | 205.5 | 0 | 0 | 49.5 | 63
11:00 | 3339 | 1818 | 904 | 38 | 110 | 826.38 | 175 | 3639 | 389.58 | 145 | 206 | 0 | 0 | 59 | 0
11:30 | 3361.5 | 1780.25 | 904.5 | 38 | 117 | 988.295 | 174 | 3785.5 | 376.705 | 112 | 214.5 | 0 | 0 | 60 | 0
12:00 | 3384 | 1742.5 | 905 | 38 | 124 | 1150.21 | 173 | 3932 | 363.83 | 79 | 223 | 0 | 0 | 61 | 0
12:30 | 3453 | 1746.25 | 905 | 38 | 130 | 1239.815 | 176.5 | 4080 | 388.44 | 78 | 253 | 0 | 0 | 62 | 19
13:00 | 3522 | 1750 | 905 | 38 | 136 | 1329.42 | 180 | 4228 | 413.05 | 77 | 283 | 0 | 0 | 63 | 38
13:30 | 3391 | 1702.5 | 905 | 38 | 129 | 1296.865 | 180.5 | 4271 | 364.58 | 78 | 286 | 0 | 0 | 62 | 24
14:00 | 3260 | 1655 | 905 | 38 | 122 | 1264.31 | 181 | 4314 | 316.11 | 79 | 289 | 0 | 0 | 61 | 10
14:30 | 3261 | 1687.5 | 905 | 38 | 123 | 1226.56 | 182 | 4258.5 | 323.555 | 59.5 | 269.5 | 0 | 0 | 44.5 | 12
15:00 | 3262 | 1720 | 905 | 38 | 124 | 1188.81 | 183 | 4203 | 331 | 40 | 250 | 0 | 0 | 28 | 14
15:30 | 3261.5 | 1733 | 905 | 38 | 118 | 1101.05 | 151 | 4053 | 264.13 | 32.5 | 232.5 | 0 | 0 | 30 | 12
16:00 | 3261 | 1746 | 905 | 38 | 112 | 1013.29 | 119 | 3903 | 197.26 | 25 | 215 | 0 | 0 | 32 | 10
16:30 | 3260.5 | 1845 | 904.5 | 38 | 108 | 935.875 | 124.5 | 3865.5 | 143.33 | 38 | 217 | 0 | 0 | 33 | 10
17:00 | 3260 | 1944 | 904 | 38 | 104 | 858.46 | 130 | 3828 | 89.4 | 51 | 219 | 0 | 0 | 34 | 10
17:30 | 3319 | 1926 | 904.5 | 38 | 102 | 877.185 | 132.5 | 3806 | 55.435 | 79.5 | 238 | 0 | 0 | 40 | 10
18:00 | 3378 | 1908 | 905 | 38 | 100 | 895.91 | 135 | 3784 | 21.47 | 108 | 257 | 0 | 0 | 46 | 10
18:30 | 3522.5 | 1972.5 | 905 | 38 | 109 | 1056.13 | 67.5 | 4003.5 | 10.735 | 170 | 373.5 | 0 | 0 | 44.5 | 16
19:00 | 3667 | 2037 | 905 | 38 | 118 | 1216.35 | 0 | 4223 | 0 | 232 | 490 | 0 | 0 | 43 | 22
19:30 | 3640 | 2106 | 904 | 38 | 126 | 1389.32 | 80 | 4434 | 0 | 294 | 988 | 0 | 0 | 32 | 25
20:00 | 3617 | 2103 | 905 | 38 | 122 | 1485.29 | 113 | 4495 | 0 | 261 | 1065 | 0 | 0 | 25 | 15
20:30 | 3571 | 2060.5 | 905 | 38 | 126 | 1479.18 | 131.5 | 4557.5 | 0 | 253 | 1155.5 | 0 | 0 | 16.5 | 22.5
21:00 | 3525 | 2018 | 905 | 38 | 130 | 1473.07 | 150 | 4620 | 0 | 245 | 1246 | 0 | 0 | 8 | 30
21:30 | 3490 | 1997.5 | 905 | 38 | 131 | 1477.575 | 181 | 4573.5 | 0 | 236.5 | 1385.4 | 0 | 0 | 22 | 15
22:00 | 3455 | 1977 | 905 | 38 | 132 | 1482.08 | 212 | 4527 | 0 | 228 | 1524.8 | 0 | 0 | 36 | 0
22:30 | 3493.5 | 2032 | 905.5 | 38 | 131 | 1486.555 | 192 | 4526.5 | 0 | 244 | 1540.65 | 0 | 0 | 41 | 0
23:00 | 3532 | 2087 | 906 | 38 | 130 | 1491.03 | 172 | 4526 | 0 | 260 | 1556.5 | 0 | 0 | 46 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 10-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 18:00 | 368 | 00:00 | Madunaghat | 395 | 03:00 | 390 | 00:00
Amtali | 414 | 08:00 | 405 | 00:00 | Meghnaghat | 390 | 18:00 | 369 | 00:00
Ashuganj | 397 | 08:00 | 376 | 00:00 | Payra | 416 | 08:00 | 406 | 00:00
Bhulta | 408 | 18:00 | 391 | 00:00 | Rahanpur | 409 | 17:00 | 391 | 00:00
Bibiana | 386 | 18:00 | 374 | 00:00 | Rampal | 404 | 08:00 | 381 | 00:00
BIPTC | 402 | 06:00 | 395 | 23:00
Bogura | 392 | 17:00 | 372 | 00:00
Gopalganj | 397 | 08:00 | 376 | 00:00
Kaliakoir | 373 | 08:00 | 356 | 00:00
Korerhat | 400 | 09:00 | 389 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 08:00 | 223 | 00:00 | Ishurdi | 236 | 05:00 | 221 | 00:00
AKSML | 238.4 | 01:00 | 230 | 23:00 | Jhenaidah | 232 | 10:00 | 211 | 00:00
Aminbazar | 237 | 17:00 | 226 | 00:00 | Kachua | 229 | 07:00 | 223 | 00:00
Ashuganj | 235 | 10:00 | 224 | 00:00 | Kaliakoir | 233 | 08:00 | 222 | 00:00
Ashuganj-400 | 235 | 10:00 | 224 | 00:00 | Keranigonj | 235 | 08:00 | 221 | 00:00
Baghabari | 236 | 07:00 | 226 | 00:00 | Khulna(S) | 238 | 10:00 | 214 | 00:00
Barapukuria | 227 | 17:00 | 218 | 00:00 | Korerhat | 229 | 09:00 | 222 | 00:00
Barapukuria-230 | 227 | 17:00 | 218 | 00:00 | Madunaghat | 240 | 01:00 | 235 | 19:00
Barishal | 229 | 18:00 | 220 | 00:00 | Madunaghat-400 | 242 | 02:00 | 237 | 21:00
Bheramara | 234 | 05:00 | 219 | 00:00 | Maniknagar | 235 | 18:00 | 223 | 00:00
Bhulta | 236 | 18:00 | 224 | 00:00 | Meghnaghat | 242 | 10:00 | 230 | 07:00
Bibiana | 225 | 08:00 | 218 | 00:00 | Meghnaghat-400 | 238 | 18:00 | 226 | 00:00
BIPTC | 237 | 05:00 | 219 | 00:00 | Mirsorai | 231 | 08:00 | 225 | 00:00
Bogura | 245 | 17:00 | 233 | 00:00 | Naogaon | 230 | 17:00 | 207 | 01:00
Bogura-400 | 245 | 10:00 | 233 | 00:00 | Purbasadipur | 224 | 17:00 | 216 | 00:00
Borhanuddin | 231 | 07:00 | 223 | 13:00 | Rajshahi | 232 | 05:00 | 217 | 22:00
BSRM | 230 | 10:00 | 224 | 19:00 | Rampal | 233 | 08:00 | 214 | 00:00
Charfasson | 231 | 06:00 | 225 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 08:00 | 222 | 00:00 | Rampura | 234 | 08:00 | 223 | 00:00
Cumilla(N) | 231 | 09:00 | 220 | 00:00 | Shikalbaha | 240 | 02:00 | 234 | 19:00
Faridpur | 227 | 17:00 | 211 | 00:00 | Shyampur | 236 | 10:00 | 223 | 00:00
Fenchuganj | 228 | 10:00 | 218 | 00:00 | Siddhirganj | 238 | 16:00 | 227 | 01:00
Feni | 228 | 10:00 | 221 | 00:00 | Sirajgonj | 242 | 09:00 | 234 | 00:00
Ghorashal | 238 | 17:00 | 230 | 00:00 | Sreepur | 231 | 09:00 | 218 | 00:00
Ghorashal-230 | 220 | 17:00 | 209 | 00:00 | Tongi | 225 | 18:30 | 213 | 00:00
Gopalganj | 228 | 18:00 | 214 | 00:00
GPH | 236 | 08:00 | 230 | 23:00
Haripur | 236 | 18:00 | 224 | 00:00
Hasnabad | 235 | 07:00 | 222 | 00:00
Hathazari | 237 | 07:00 | 232 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 140 | 08:00 | 133 | 12:00 | Madunaghat | 139 | 07:00 | 135 | 19:00
Agargaon | 139 | 09:00 | 131 | 00:00 | Magura | 132 | 09:00 | 116 | 22:00
Agrabad | 137 | 00:00 | 133 | 19:00 | Mahasthangarh | 137 | 17:00 | 129 | 00:00
AKS | 136 | 01:00 | 132 | 19:00 | Maijdee | 128 | 07:00 | 124 | 00:00
Aminbazar | 135 | 17:00 | 128 | 00:00 | Manikganj | 132 | 11:00 | 126 | 00:00
Amnura | 134 | 09:00 | 125 | 23:00 | Maniknagar | 139 | 18:00 | 130 | 00:00
Ashuganj | 135 | 10:00 | 127 | 00:00 | Matarbari | 130 | 09:00 | 118 | 21:00
Ashuganj-230 | 137 | 18:00 | 132 | 00:00 | Matuail | 137 | 17:00 | 130 | 00:00
Bagerhat | 133 | 06:00 | 121 | 22:00 | Metrorail_Motijheel | 139 | 17:00 | 125 | 03:00
Bajitpur | 129 | 18:00 | 119 | 23:00 | Metrorail_Uttara | 135 | 08:00 | 128 | 00:00
Bakerganj | 133 | 04:00 | 127 | 23:00 | Millgate | 136 | 07:00 | 128 | 00:00
Bakulia | 138 | 03:00 | 132 | 19:00 | Mirpur | 133 | 08:00 | 128 | 00:00
Banani | 140 | 08:00 | 132 | 13:00 | Mirzapur | 133 | 10:00 | 124 | 00:00
Bangabhaban | 139 | 18:00 | 130 | 00:00 | Mithapukur | 133 | 16:00 | 126 | 00:00
Barapukuria | 138 | 17:00 | 129 | 00:00 | MI_Cement | 139.7 | 18:00 | 130 | 00:00
Barguna | 133 | 07:00 | 127 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 133 | 04:00 | 127 | 13:00 | Mogbazar | 142 | 08:00 | 134 | 13:00
Barishal-230 | 133 | 04:00 | 127 | 13:00 | Mongla | 133 | 05:00 | 120 | 23:00
Baroaulia | 137 | 01:00 | 134 | 19:00 | Motijheel | 139 | 18:00 | 130 | 00:00
Baroirhat | 133 | 08:00 | 129 | 00:00 | Muktagacha | 127 | 10:00 | 114 | 13:00
Bashundhara | 141 | 08:00 | 128 | 00:00 | Munshiganj | 136 | 18:00 | 129 | 00:00
BashundharaCement | 137 | 18:00 | 130 | 01:00 | Muradnagar | 131 | 08:00 | 124 | 00:00
Beanibazar | 127 | 10:00 | 120 | 00:00 | Mymensingh | 127 | 10:00 | 109 | 23:00
Benapole | 137 | 06:00 | 117 | 00:00 | Nabinagar | 137 | 18:00 | 125 | 00:00
Bhaluka | 133 | 10:00 | 118 | 23:00 | Naogaon | 138 | 17:00 | 124 | 23:00
Bhandaria | 130 | 06:00 | 122 | 00:00 | Narail | 135 | 06:00 | 114 | 22:00
Bhangura | 136 | 17:00 | 129 | 00:00 | Narinda | 139 | 18:00 | 130 | 00:00
Bheramara | 138 | 10:00 | 128 | 00:00 | Narshingdi | 132 | 08:00 | 122 | 00:00
Bheramara(GK) | 137 | 04:00 | 127 | 00:00 | Natore | 135 | 10:00 | 126 | 22:00
Bhulta | 133 | 18:00 | 12 | 00:00 | Nawabganj | 141 | 18:00 | 131 | 00:00
Bog-Sherpur | 138 | 09:00 | 130 | 00:00 | Netrakona | 120 | 15:00 | 106 | 22:00
Bogura | 140 | 17:00 | 133 | 00:00 | New | 138 | 08:00 | 129 | 00:00
Bogura-230 | 141 | 17:00 | 134 | 00:00 | Niamatpur | 135 | 17:00 | 125 | 00:00
Brahmanbaria | 132 | 09:00 | 124 | 00:00 | Noapara | 137 | 06:00 | 123 | 00:00
Cantonment | 139 | 08:00 | 131 | 00:00 | Pabna | 136 | 10:00 | 127 | 22:00
Chandina | 133 | 08:00 | 127 | 00:00 | Palashbari | 133 | 17:00 | 123 | 00:00
Chandpur | 130 | 02:00 | 125 | 13:00 | Panchagarh | 138 | 21:00 | 128 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 139 | 02:00 | 135 | 19:00 | Patiya | 139 | 10:00 | 132 | 19:00
Chapai | 135 | 18:00 | 128 | 22:00 | Patnitala | 134 | 17:00 | 126 | 00:00
Charsaidpur | 137 | 18:00 | 130 | 00:00 | Patuakhali | 132 | 03:00 | 126 | 12:00
Chauddagram | 132 | 09:00 | 128 | 00:00 | Payra | 136 | 08:00 | 131 | 00:00
Chhatak | 126 | 18:00 | 117 | 00:00 | PHP | 132 | 03:00 | 130 | 00:00
Chowmuhani | 127 | 02:00 | 124 | 00:00 | Postogola | 141 | 08:00 | 132 | 00:00
Chuadanga | 140 | 07:00 | 118 | 00:00 | Pubail | 130 | 08:00 | 123 | 13:00
Coxsbazar | 129 | 16:00 | 121 | 21:00 | Purbachal | 140 | 08:00 | 133 | 13:00
Cumilla(N) | 134 | 18:00 | 128 | 00:00 | Purbasadipur | 135 | 04:00 | 129 | 00:00
Cumilla(S) | 133 | 07:00 | 126 | 12:00 | Rahanpur | 138 | 09:00 | 129 | 00:00
Daganbhuiyan | 131 | 08:00 | 18 | 22:00 | Rahanpur-400 | 137 | 17:00 | 130 | 00:00
Daudkandi | 131 | 18:00 | 121 | 00:00 | Rahim | 137 | 19:00 | 130 | 00:00
DhakaUniversity | 141 | 08:00 | 133 | 12:00 | Rajbari | 128 | 06:00 | 119 | 00:00
Dhamrai | 138 | 18:00 | 126 | 00:00 | Rajendrapur | 130 | 10:00 | 119 | 00:00
Dhanmondi | 140.5 | 08:00 | 134.5 | 13:00 | Rajshahi | 133 | 10:00 | 124 | 22:00
Dohazari | 135 | 08:00 | 128 | 19:00 | Rajshahi-230 | 133 | 05:00 | 123 | 23:00
Faridpur | 131 | 06:00 | 122 | 00:00 | Ramganj | 127 | 01:00 | 123 | 00:00
Fatullah | 143 | 18:30 | 131 | 00:00 | Rampur | 137 | 01:00 | 133 | 19:00
Fenchuganj | 134 | 09:00 | 128 | 00:00 | Rampura | 140 | 08:00 | 132 | 13:00
Feni | 131 | 08:00 | 128 | 00:00 | Rangamati | 138 | 01:00 | 133 | 19:00
Feni-230 | 132 | 08:00 | 128 | 13:00 | Rangpur | 132 | 17:00 | 124 | 00:00
Ghatail | 126 | 10:00 | 115 | 02:00 | Ruppur | 138 | 09:00 | 129 | 23:00
Ghorashal | 133 | 18:00 | 126 | 00:00 | Saidpur | 135 | 17:00 | 128 | 13:00
Goalpara | 140 | 06:00 | 127 | 00:00 | Santhia | 137 | 17:00 | 129 | 00:00
Gollamari | 138 | 06:00 | 125 | 11:00 | Satkhira | 144 | 10:00 | 120 | 23:00
Gopalganj | 134 | 06:00 | 125 | 00:00 | Satmasjid | 139 | 09:00 | 130 | 00:00
Gopalganj-400 | 134 | 06:00 | 126 | 00:00 | Savar | 133 | 19:30 | 125 | 00:00
Gulshan | 139 | 07:00 | 133 | 00:00 | SevenRings | 132 | 08:00 | 125 | 00:00
Halishahar | 139 | 02:00 | 133 | 19:00 | ShahCement | 137 | 18:00 | 130 | 00:00
Haripur | 138 | 18:00 | 131 | 00:00 | Shahjadpur | 140 | 17:00 | 132 | 00:00
HaripurSBU | 138 | 18:00 | 132 | 00:00 | Shahjibazar | 133 | 10:00 | 124 | 00:00
Hasnabad | 141 | 18:00 | 133 | 00:00 | Shahmirpur | 138 | 02:00 | 134 | 19:00
Hathazari | 138 | 00:00 | 134 | 19:30 | Shariatpur | 132 | 05:00 | 123 | 00:00
Hatirjheel | 141 | 08:00 | 133 | 13:00 | Sherpur | 124 | 18:00 | 111 | 02:00
Ishurdi | 140 | 10:00 | 130 | 00:00 | Shikalbaha | 127 | 00:00 | 122 | 19:00
Jaldhaka | 133 | 17:00 | 126 | 00:00 | Shikalbaha-230 | 139 | 02:00 | 135 | 19:00
Jamalpur | 129 | 21:00 | 115 | 08:00 | Shitalakhya | 139.7 | 18:00 | 130 | 00:00
Jashore | 138 | 06:00 | 120 | 00:00 | Sholosohor | 139 | 02:00 | 133 | 19:00
Jhenaidah | 141 | 09:00 | 118 | 22:00 | Shomvuganj | 124 | 09:00 | 112 | 23:00
Jhenaidah-230 | 141 | 06:00 | 127 | 00:00 | Shyampur | 140 | 08:00 | 132 | 00:00
Joydebpur | 128 | 08:00 | 121 | 00:00 | Shyampur-230 | 142 | 18:00 | 133 | 00:00
Joypurhat | 136 | 18:00 | 126 | 00:00 | Siddhirganj | 138 | 18:00 | 131 | 00:00
Juldah | 137 | 00:00 | 134 | 19:00 | Sirajganj | 136 | 10:00 | 128 | 00:00
Kabirpur | 135 | 08:00 | 127 | 13:00 | Sitakunda | 138 | 03:00 | 134 | 19:00
Kachua | 130 | 07:00 | 127 | 00:00 | Sonargaon | 135 | 10:00 | 128 | 00:00
Kaliakoir | 140 | 18:00 | 130 | 00:00 | Sreemongol | 131 | 06:00 | 124 | 00:00
Kaliganj | 140 | 05:00 | 121 | 00:00 | Sreepur | 134 | 10:00 | 122 | 00:00
Kallyanpur | 134 | 18:00 | 126 | 00:00 | Srinagar | 141 | 18:00 | 131 | 00:00
Kalurghat | 139 | 02:00 | 135 | 19:00 | SSM | 141 | 03:00 | 140 | 00:00
Kamrangirchar | 141 | 08:00 | 125 | 00:00 | Sunamganj | 123 | 15:00 | 114 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 127 | 07:00 | 122 | 00:00
Kasba | 131 | 08:00 | 123 | 00:00 | Sylhet_(South) | 128 | 08:00 | 122 | 00:00
Kazla | 138 | 18:00 | 130 | 00:00 | Tangail | 129 | 09:00 | 117 | 13:00
Keranigonj | 141 | 10:00 | 132 | 00:00 | Taraganj | 133 | 17:00 | 126 | 00:00
Khagrachori | 138 | 06:00 | 132 | 19:00 | Tasnim | 135 | 09:00 | 127 | 00:00
Khulna | 138 | 06:00 | 123 | 11:00 | Thakurgaon | 138 | 04:00 | 128 | 13:00
Khulna(S) | 145 | 10:00 | 126 | 23:00 | TK | 138 | 00:00 | 135 | 19:00
Khulshi | 137 | 01:00 | 133 | 19:30 | Tongi | 138 | 07:00 | 132 | 00:00
Kishoreganj | 127 | 07:00 | 115 | 22:00 | Ullahpara | 136 | 09:00 | 128 | 00:00
Kodda | 134 | 08:00 | 122 | 12:00 | Ullon | 140 | 08:00 | 132 | 13:00
Korerhat | 135 | 09:00 | 131 | 00:00 | Uttara | 136 | 08:00 | 127 | 13:00
KSRM | 138 | 00:00 | 13 | 07:00 | UttaraNew | 135 | 07:00 | 128 | 00:00
Kulaura | 133 | 08:00 | 126 | 00:00 | Zigatola | 142 | 18:00 | 132 | 00:00
Kurigram | 131 | 17:00 | 120 | 00:00
Kushtia | 136 | 09:00 | 123 | 00:00
Laksam | 129 | 07:00 | 122 | 16:00
Lakshmipur | 128 | 10:00 | 124 | 00:00
Lalbag | 140 | 08:00 | 131 | 00:00
Lalmonirhat | 130 | 17:00 | 120 | 01:00
Madanganj | 137 | 18:00 | 131 | 00:00
Madaripur | 131 | 05:00 | 125 | 00:00
Madartek | 139 | 07:00 | 132 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 10-07-2026 | [28 empty] | Date: | 10-07-2026 | [28 empty] | Date: | 10-07-2026 | [28 empty] | Date: | 10-07-2026 | [28 empty] | Date: | 10-07-2026 | [18 empty] | Date: | 10-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 17 | 43 | 64 | 195 | 55 | 35 | 54 | 0 | 0 | 295 | 460 | 0 | 17 | 295 | 0 | 0 | 0 | 143 | 15 | 21 | 0 | 0 | 15 | 16 | 0 | 0 | 8 | 34 | 0 | 39 | 12 | 12 | 0 | 94 | 110 | 30 | 930 | 0 | 0 | 38 | 0 | 87 | 160 | 0 | 0 | 0 | 303 | 0 | 13 | 0 | 250 | 300 | 280 | 51 | 1 | 196 | 40 | 21 | 95 | 76 | 28 | 19 | 98 | 140 | 16 | 0 | 0 | 300 | 0 | 230 | 29 | 0 | 134 | 0 | 15 | 0 | 80 | 25 | 143 | 0 | 103 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6782 | 905 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1206 | 0 | 0 | 0 | 1485.6 | 0 | 25 | 0 | 50 | 50 | 0 | 94 | 25 | 34 | 0 | 0 | 21 | 0 | 0 | 157 | 0 | 144 | 0 | 39 | 0 | 350 | 0 | 0 | 180 | 40 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 307 | 65 | 220 | 0 | 1050 | 1180 | 36 | 7953.6 | 14735.6 | 88.95
01:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 17 | 36 | 128 | 195 | 55 | 0 | 17 | 0 | 0 | 303 | 475 | 0 | 0 | 305 | 0 | 0 | 0 | 143 | 15.5 | 21 | 0 | 0 | 18 | 16 | 0 | 0 | 0 | 34 | 0 | 54.36 | 12 | 12 | 0 | 158 | 108 | 30 | 790 | 0 | 0 | 50 | 0 | 102 | 147 | 0 | 0 | 0 | 303 | 0 | 13 | 46 | 300 | 69 | 335 | 51 | 12 | 166 | 40 | 0 | 93 | 100 | 28 | 19 | 97 | 130 | 16 | 0 | 0 | 310 | 0 | 330 | 29 | 0 | 149 | 0 | 15 | 0 | 80 | 25 | 142 | 0 | 102 | 17 | 49 | 0 | 47 | 0 | 0 | 0 | 0 | 6760.86 | 905 | 0 | 0 | 0 | 30 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1204 | 0 | 0 | 0 | 1486.96 | 0 | 0 | 0 | 35 | 35 | 0 | 94 | 25 | 34 | 0 | 0 | 21 | 0 | 0 | 158 | 0 | 144 | 0 | 96 | 0 | 414 | 0 | 0 | 180 | 40 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 65 | 220 | 0 | 500 | 1170 | 36 | 7511.96 | 14272.82 | 89.13
02:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 21 | 34 | 126 | 195 | 55 | 0 | 0 | 0 | 0 | 297 | 500 | 0 | 0 | 300 | 0 | 0 | 0 | 143 | 16 | 21 | 0 | 0 | 84 | 16 | 0 | 0 | 3 | 0 | 0 | 54.36 | 12 | 12 | 0 | 159 | 107 | 30 | 760 | 0 | 0 | 48 | 2 | 98 | 146 | 0 | 0 | 0 | 302 | 0 | 13 | 45 | 393 | 0 | 342 | 51 | 20 | 198 | 40 | 0 | 95 | 151 | 28 | 19 | 95 | 130 | 25 | 0 | 0 | 305 | 0 | 330 | 29 | 0 | 140 | 0 | 15 | 0 | 80 | 25 | 142 | 0 | 102 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6891.36 | 905 | 0 | 0 | 0 | 30 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1150 | 0 | 0 | 0 | 1487.22 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 25 | 8 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 144 | 0 | 137 | 0 | 414 | 0 | 0 | 180 | 40 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 273 | 65 | 220 | 0 | 500 | 1170 | 36 | 7324.22 | 14215.58 | 89.28
03:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 6 | 0 | 28 | 34 | 128 | 195 | 55 | 0 | 0 | 0 | 0 | 308 | 425 | 0 | 0 | 310 | 0 | 0 | 0 | 143 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 54.36 | 0 | 12 | 0 | 161 | 107 | 34 | 705 | 0 | 0 | 46 | 0 | 97 | 134 | 0 | 0 | 0 | 302 | 0 | 13 | 45 | 390 | 0 | 342 | 51 | 20 | 206 | 40 | 0 | 94 | 100 | 27 | 19 | 95 | 122 | 0 | 0 | 0 | 310 | 0 | 343 | 29 | 0 | 141 | 0 | 15 | 0 | 80 | 25 | 143 | 0 | 103 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6656.36 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 0 | 0 | 1362.42 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 144 | 0 | 156 | 0 | 414 | 0 | 0 | 180 | 40 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 277 | 65 | 220 | 0 | 500 | 1170 | 36 | 7099.42 | 13755.78 | 89.43
04:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 6 | 0 | 28 | 34 | 127 | 145 | 55 | 0 | 0 | 0 | 0 | 295 | 465 | 0 | 0 | 300 | 0 | 0 | 0 | 143 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 35 | 0 | 12 | 0 | 164 | 106 | 30 | 705 | 0 | 0 | 0 | 0 | 96 | 133 | 0 | 0 | 0 | 302 | 0 | 13 | 45 | 393 | 0 | 342 | 51 | 20 | 192 | 40 | 0 | 95 | 0 | 0 | 19 | 0 | 120 | 0 | 0 | 0 | 305 | 0 | 343 | 29 | 0 | 140 | 0 | 15 | 0 | 80 | 25 | 142 | 0 | 103 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6236 | 904 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 0 | 0 | 0 | 1374.59 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 144 | 0 | 156 | 0 | 414 | 0 | 0 | 180 | 40 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 273 | 65 | 220 | 0 | 500 | 1170 | 36 | 7066.59 | 13302.59 | 89.58
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 120 | 0 | 17 | 34 | 132 | 0 | 30 | 0 | 0 | 0 | 0 | 301 | 370 | 0 | 0 | 298 | 0 | 0 | 0 | 143 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 12 | 0 | 164 | 34 | 30 | 710 | 0 | 0 | 0 | 0 | 34 | 133 | 0 | 0 | 0 | 302 | 0 | 13 | 45 | 393 | 0 | 342 | 51 | 20 | 199 | 40 | 0 | 96 | 0 | 0 | 19 | 0 | 122 | 0 | 0 | 0 | 305 | 0 | 343 | 29 | 0 | 128 | 0 | 15 | 0 | 80 | 25 | 140 | 0 | 102 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 5877 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 1369.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 144 | 0 | 154 | 0 | 414 | 0 | 0 | 180 | 40 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 65 | 220 | 0 | 500 | 1170 | 0 | 6766.74 | 12643.74 | 89.73
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 289 | 0 | 0 | 34 | 145 | 0 | 15 | 0 | 0 | 0 | 0 | 297 | 355 | 0 | 0 | 305 | 0 | 0 | 0 | 105 | 17 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 32 | 630 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 305 | 0 | 0 | 45 | 350 | 0 | 280 | 51 | 20 | 201 | 40 | 0 | 94 | 0 | 0 | 19 | 0 | 110 | 0 | 0 | 0 | 300 | 0 | 343 | 29 | 0 | 130 | 0 | 15 | 0 | 80 | 25 | 140 | 0 | 102 | 17 | 49 | 0.41 | 48 | 0 | 0 | 0.29 | 0 | 5683.7 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 971 | 0 | 0 | 0 | 1224.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0.12 | 157 | 0 | 144 | 0 | 150 | 0 | 300 | 0 | 0.03 | 180 | 40 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 5 | 0.01 | 0 | 170 | 65 | 180 | 0 | 500 | 1120 | 0 | 6159.64 | 11843.34 | 89.88
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 288 | 0 | 0 | 34 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 370 | 0 | 0 | 307 | 0 | 0 | 1 | 86 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 23 | 600 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 303 | 0 | 0 | 45 | 350 | 0 | 280 | 51 | 20 | 198 | 37 | 0 | 94 | 0 | 0 | 19 | 0 | 100 | 0 | 4 | 0 | 305 | 0 | 343 | 29 | 0 | 130 | 0 | 15 | 0 | 80 | 25 | 143 | 0 | 102 | 0 | 49 | 2.31 | 48 | 0 | 0.2 | 6.17 | 0 | 5615.68 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 862 | 0 | 0 | 0 | 1123.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.86 | 3 | 0 | 0 | 8.02 | 158 | 0 | 144 | 0 | 148 | 0 | 300 | 0 | 0.8 | 180 | 40 | 0 | 1 | 0 | 0 | 0 | 0 | 0.3 | 33 | 0.03 | 0 | 168 | 65 | 180 | 0 | 500 | 1030 | 0 | 5893.52 | 11509.2 | 90.03
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 262 | 0 | 0 | 34 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 455 | 0 | 0 | 298 | 0 | 0 | 3 | 86 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0.27 | 160 | 0 | 19 | 600 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 303 | 0.06 | 0 | 45 | 350 | 0 | 280 | 51 | 20 | 197 | 34 | 0 | 93 | 0 | 0 | 19 | 0 | 94 | 0 | 12 | 0 | 310 | 0 | 343 | 29 | 0 | 138 | 2 | 15 | 0 | 80 | 30 | 140 | 0 | 103 | 0 | 48 | 6.32 | 48 | 0 | 0.3 | 11.55 | 0 | 5655.5 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 796 | 0 | 0 | 0 | 926.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.51 | 11 | 0 | 0 | 17.02 | 160 | 0 | 144 | 0 | 147 | 0 | 300 | 0 | 1.28 | 180 | 43 | 0 | 2 | 0 | 0 | 0 | 0 | 1.9 | 55 | 0.15 | 0 | 170 | 65 | 180 | 0 | 500 | 1025 | 0 | 5674.36 | 11329.86 | 90.23
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 0 | 259 | 0 | 0 | 34 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 525 | 0 | 0 | 305 | 0 | 0 | 2 | 86 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 1.35 | 179 | 0 | 24 | 600 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 300 | 0.77 | 0 | 45 | 350 | 0 | 280 | 51 | 20 | 207 | 37 | 0 | 93 | 0 | 0 | 19 | 0 | 104 | 0 | 30 | 0 | 310 | 0 | 343 | 29 | 0 | 135 | 3 | 15 | 0 | 80 | 30 | 142 | 0 | 102 | 0 | 48 | 5.67 | 48 | 0 | 1.3 | 12.49 | 0 | 5778.58 | 904 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 787 | 0 | 0 | 0 | 923.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.63 | 17 | 0 | 0 | 12.64 | 160 | 0 | 149 | 0 | 147 | 0 | 300 | 0 | 1.58 | 190 | 42 | 0 | 4 | 0 | 0 | 0 | 0 | 1.9 | 95 | 0.19 | 0 | 172 | 65 | 62 | 0 | 500 | 1043 | 0 | 5625.79 | 11404.37 | 90.31
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 229 | 0 | 0 | 35 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 510 | 0 | 0 | 293 | 0 | 0 | 3 | 51 | 21 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 1.33 | 174 | 0 | 4 | 600 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 300 | 3 | 0 | 45 | 350 | 0 | 280 | 51 | 34 | 194 | 40 | 0 | 93 | 0 | 0 | 14 | 0 | 106 | 0 | 32 | 0 | 305 | 0 | 331 | 29 | 0 | 130 | 3 | 15 | 0 | 80 | 30 | 141 | 0 | 102 | 0 | 58 | 15.4 | 112 | 0 | 0.8 | 17.59 | 0 | 5748.12 | 904 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17 | 782 | 0 | 0 | 0 | 838.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4 | 21 | 0 | 0 | 28 | 160 | 0 | 150 | 0 | 147 | 0 | 350 | 0 | 0 | 190 | 42 | 0 | 9 | 0 | 0 | 0 | 0 | 0.7 | 140 | 0.2 | 0 | 168 | 65 | 62 | 0 | 500 | 999 | 0 | 5618.47 | 11366.59 | 90.41
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 269 | 0 | 0 | 35 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 530 | 0 | 0 | 315 | 0 | 0 | 10 | 17 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 1.19 | 175 | 0 | 7 | 660 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 300 | 9 | 0 | 45 | 350 | 0 | 280 | 51 | 43 | 201 | 40 | 0 | 93 | 0 | 0 | 14 | 0 | 110 | 0 | 9 | 0 | 310 | 0 | 331 | 29 | 0 | 138 | 2 | 0 | 0 | 60 | 30 | 140 | 0 | 102 | 0 | 58 | 11.5 | 113 | 0 | 1 | 26.45 | 0 | 5915.14 | 904 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 56 | 791 | 0 | 0 | 0 | 826.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.87 | 20 | 0 | 0 | 30 | 159 | 0 | 150 | 0 | 149 | 0 | 414 | 0 | 2.66 | 190 | 42 | 0 | 9 | 0 | 0 | 0 | 0 | 0.8 | 192 | 0.11 | 0 | 206 | 65 | 30 | 0 | 500 | 950 | 0 | 5733.82 | 11648.96 | 90.53
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 212 | 0 | 0 | 48 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 500 | 0 | 0 | 303 | 0 | 0 | 2 | 17 | 12.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 1.27 | 173 | 0 | 9 | 720 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 300 | 10 | 0 | 45 | 350 | 0 | 310 | 51 | 45 | 202 | 40 | 0 | 93 | 0 | 0 | 14 | 0 | 124 | 0 | 9 | 0 | 305 | 0 | 331 | 29 | 0 | 139 | 4 | 0 | 0 | 63 | 30 | 142 | 0 | 104 | 0 | 58 | 11.48 | 117 | 0 | 2.4 | 14.6 | 0 | 5892.25 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 70 | 908 | 0 | 0 | 0 | 1150.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.22 | 9 | 0 | 0 | 18 | 160 | 0 | 150 | 0 | 150 | 0 | 414 | 0 | 0 | 190 | 41 | 0 | 17 | 0 | 0 | 0 | 0 | 1.8 | 182 | 0.06 | 0 | 277 | 65 | 30 | 0 | 500 | 996 | 0 | 6283.29 | 12175.54 | 90.69
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 212 | 0 | 0 | 71 | 45 | 0 | 6 | 17 | 0 | 0 | 0 | 302 | 485 | 0 | 0 | 303 | 0 | 0 | 7 | 32 | 21 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 6 | 0 | 0 | 1.61 | 180 | 11 | 9 | 710 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 302 | 0 | 0 | 45 | 393 | 0 | 345 | 51 | 48 | 198 | 40 | 0 | 92 | 0 | 0 | 14 | 0 | 136 | 0 | 4 | 0 | 305 | 0 | 331 | 29 | 0 | 137 | 5 | 16 | 0 | 63 | 30 | 143 | 0 | 102 | 0 | 58 | 10.22 | 114 | 0 | 1.4 | 15.21 | 0 | 6100.44 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34 | 1125 | 0 | 0 | 0 | 1329.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.4 | 33 | 0 | 0 | 44.98 | 160 | 0 | 150 | 0 | 148 | 0 | 414 | 0 | 5.5 | 185 | 40 | 0 | 14 | 0 | 0 | 0 | 0 | 1.6 | 208 | 0.13 | 0 | 276 | 65 | 30 | 0 | 500 | 1090 | 0 | 6824.03 | 12924.47 | 90.83
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 238 | 0 | 0 | 71 | 45 | 0 | 15 | 0 | 0 | 0 | 0 | 301 | 385 | 0 | 0 | 323 | 0 | 0 | 10 | 34 | 21 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 12 | 1.26 | 181 | 17 | 14 | 720 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 300 | 8 | 0 | 45 | 340 | 0 | 300 | 51 | 48 | 203 | 40 | 0 | 92 | 0 | 0 | 11 | 0 | 122 | 0 | 8 | 0 | 295 | 0 | 293 | 29 | 0 | 128 | 4 | 16 | 0 | 62 | 30 | 141 | 0 | 102 | 0 | 58 | 10.7 | 116 | 0 | 1.8 | 18.83 | 0 | 5908.59 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 1145 | 0 | 0 | 0 | 1264.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.69 | 13 | 0 | 0 | 50.46 | 160 | 0 | 150 | 0 | 146 | 0 | 270 | 0 | 3.42 | 185 | 40 | 0 | 20 | 0 | 0 | 0 | 0 | 7.8 | 139 | 0.15 | 0 | 238 | 65 | 30 | 0 | 500 | 1186 | 0 | 6575.83 | 12484.42 | 90.97
15:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 211 | 0 | 0 | 71 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 475 | 0 | 0 | 313 | 0 | 0 | 10 | 17 | 21 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0.91 | 183 | 0 | 10 | 715 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 300 | 4 | 0 | 45 | 335 | 0 | 280 | 51 | 46 | 198 | 40 | 0 | 91 | 0 | 0 | 11 | 0 | 124 | 0 | 33 | 0 | 300 | 0 | 294 | 29 | 0 | 143 | 4 | 16 | 0 | 62 | 30 | 140 | 0 | 102 | 5 | 58 | 9.19 | 116 | 0 | 0.2 | 19.34 | 0 | 5851.64 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 1023 | 0 | 0 | 0 | 1188.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.86 | 49 | 0 | 0 | 4.59 | 160 | 0 | 150 | 0 | 146 | 0 | 300 | 0 | 0.36 | 185 | 41 | 0 | 11 | 0 | 0 | 0 | 0 | 3.5 | 153 | 0.05 | 0 | 219 | 65 | 30 | 0 | 600 | 1120 | 0 | 6421.17 | 12272.81 | 91.09
16:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 278 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 435 | 0 | 0 | 317 | 0 | 0 | 6 | 17 | 21 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0.94 | 119 | 0 | 3 | 715 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 300 | 0 | 0 | 45 | 340 | 0 | 280 | 51 | 44 | 206 | 40 | 0 | 91 | 0 | 0 | 11 | 0 | 112 | 0 | 22 | 0 | 295 | 0 | 303 | 29 | 0 | 137 | 1 | 16 | 0 | 62 | 30 | 141 | 0 | 101 | 17 | 45 | 8.48 | 95 | 0 | 0.1 | 1.73 | 0 | 5703.25 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.2 | 953 | 0 | 0 | 0 | 1013.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.81 | 19 | 0 | 0 | 8.45 | 160 | 0 | 150 | 0 | 149 | 0 | 300 | 0 | 0.63 | 185 | 40 | 0 | 10 | 0 | 0 | 0 | 0 | 1.9 | 112 | 0.02 | 0 | 170 | 65 | 38 | 0 | 500 | 1040 | 0 | 5863.3 | 11566.55 | 91.34
17:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 292 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 530 | 0 | 0 | 313 | 0 | 0 | 3 | 35 | 21 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0.51 | 130 | 0 | 13 | 715 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 300 | 0 | 0 | 45 | 330 | 0 | 280 | 51 | 46 | 202 | 40 | 0 | 92 | 0 | 0 | 11 | 0 | 104 | 0 | 9 | 0 | 300 | 0 | 319 | 29 | 0 | 148 | 1 | 16 | 0 | 62 | 30 | 142 | 0 | 102 | 17 | 45 | 1.13 | 96 | 0 | 0.1 | 2.13 | 9 | 5834.87 | 904 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.3 | 838 | 0 | 0 | 0 | 858.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.39 | 15 | 0 | 0 | 4.43 | 160 | 0 | 151 | 0 | 153 | 0 | 300 | 0 | 0.38 | 185 | 40 | 0 | 7 | 0 | 0 | 0 | 0 | 2 | 39 | 0.03 | 0 | 170 | 65 | 110 | 0 | 500 | 1080 | 0 | 5624.99 | 11459.86 | 91.44
18:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 271 | 0 | 0 | 55 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 500 | 0 | 0 | 309 | 0 | 0 | 1 | 68 | 21 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 21 | 715 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 300 | 0 | 0 | 45 | 340 | 87 | 280 | 51 | 46 | 206 | 41 | 0 | 93 | 0 | 0 | 11 | 0 | 100 | 0 | 1 | 0 | 300 | 0 | 319 | 29 | 0 | 140 | 0 | 11 | 0 | 62 | 30 | 142 | 0 | 102 | 17 | 58 | 0.09 | 115 | 0 | 0 | 0.42 | 12 | 5992.51 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.7 | 809 | 0 | 0 | 0 | 895.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63 | 0 | 0 | 0 | 0.3 | 160 | 0 | 156 | 0 | 156 | 0 | 300 | 0 | 0.02 | 180 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 16 | 0.01 | 0 | 170 | 65 | 120 | 0 | 500 | 1070 | 0 | 5583.87 | 11576.38 | 91.55
19:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 310 | 4 | 0 | 76 | 60 | 15 | 4 | 17 | 15 | 0 | 0 | 305 | 480 | 0 | 0 | 323 | 0 | 0 | 0 | 115 | 21 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 1 | 25 | 715 | 3 | 0 | 7 | 0 | 0 | 213 | 0 | 0 | 0 | 300 | 0 | 5 | 53 | 365 | 100 | 330 | 51 | 45 | 214 | 41 | 1 | 93 | 6 | 3 | 13 | 17 | 118 | 0 | 0 | 0 | 305 | 0 | 320 | 29 | 0 | 137 | 0 | 0 | 0 | 65 | 30 | 144 | 0 | 102 | 17 | 58 | 0 | 116 | 0 | 0 | 0 | 12 | 6313 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 963 | 0 | 0 | 0 | 1216.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 166 | 0 | 160 | 0 | 414 | 0 | 0 | 180 | 39 | 35 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 65 | 220 | 0 | 700 | 1048 | 0 | 6656.35 | 12969.35 | 91.85
19:30 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 309 | 16 | 0 | 114 | 76 | 55 | 30 | 35 | 35 | 0 | 0 | 310 | 535 | 0 | 0 | 315 | 0 | 0 | 0 | 143 | 21 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 12 | 12 | 0 | 80 | 17 | 25 | 715 | 16 | 0 | 31 | 0 | 0 | 213 | 0 | 0 | 0 | 300 | 0 | 40 | 26 | 390 | 100 | 295 | 51 | 45 | 200 | 41 | 36 | 93 | 31 | 27 | 14 | 34 | 126 | 0 | 0 | 0 | 310 | 0 | 320 | 29 | 0 | 148 | 0 | 5 | 0 | 80 | 30 | 142 | 0 | 102 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 12 | 6883 | 904 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1115 | 0 | 0 | 0 | 1389.32 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 167 | 0 | 160 | 0 | 414 | 0 | 0 | 180 | 39 | 72 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 65 | 220 | 0 | 700 | 1078 | 5 | 7148.32 | 14031.32
20:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 309 | 16 | 0 | 115 | 76 | 80 | 24 | 35 | 72 | 0 | 0 | 305 | 515 | 0 | 17 | 306 | 0 | 0 | 0 | 143 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 4 | 12 | 12 | 0 | 113 | 24 | 26 | 715 | 0 | 0 | 29 | 0 | 0 | 213 | 0 | 0 | 0 | 300 | 0 | 48 | 26 | 393 | 98 | 287 | 51 | 44 | 191 | 41 | 32 | 93 | 17 | 23 | 19 | 34 | 122 | 0 | 0 | 0 | 310 | 0 | 320 | 29 | 0 | 140 | 0 | 16 | 0 | 80 | 30 | 141 | 0 | 102 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 12 | 6915 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1188 | 0 | 0 | 0 | 1485.29 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 167 | 0 | 160 | 0 | 414 | 0 | 0 | 180 | 39 | 70 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 273 | 65 | 220 | 0 | 700 | 1100 | 17 | 7314.29 | 14229.29 | 91.94
21:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 293 | 16 | 0 | 115 | 60 | 80 | 30 | 35 | 72 | 0 | 0 | 304 | 460 | 0 | 17 | 316 | 0 | 0 | 0 | 143 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 17 | 12 | 12 | 0 | 150 | 50 | 30 | 715 | 0 | 0 | 33 | 4 | 0 | 213 | 0 | 0 | 0 | 300 | 0 | 88 | 8 | 350 | 40 | 290 | 51 | 36 | 190 | 41 | 69 | 93 | 16 | 26 | 19 | 33 | 130 | 0 | 0 | 0 | 315 | 0 | 320 | 29 | 0 | 144 | 0 | 16 | 0 | 80 | 30 | 141 | 0 | 102 | 17 | 68 | 0 | 156 | 0 | 0 | 0 | 12 | 6886 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 1473.07 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 165 | 0 | 160 | 0 | 414 | 0 | 0 | 180 | 38 | 70 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 65 | 220 | 0 | 700 | 1170 | 17 | 7472.07 | 14358.07 | 92.12
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 267 | 15.8 | 0 | 115 | 60 | 110 | 30 | 35 | 72 | 0 | 0 | 308 | 500 | 0 | 0 | 314 | 0 | 0 | 0 | 143 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 17 | 12 | 12 | 0 | 212 | 74 | 30 | 730 | 0 | 0 | 33 | 8 | 0 | 213 | 0 | 0 | 0 | 302 | 0 | 100 | 0 | 365 | 19 | 294 | 51 | 22 | 211 | 41 | 79 | 93 | 40 | 28 | 19 | 70 | 132 | 0 | 0 | 0 | 305 | 0 | 320 | 29 | 0 | 136 | 0 | 16 | 0 | 62 | 30 | 142 | 0 | 102 | 17 | 68 | 0 | 156 | 0 | 0 | 0 | 12 | 7068.8 | 905 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 1482.08 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 159 | 0 | 155 | 0 | 350 | 0 | 0 | 180 | 38 | 95 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 277 | 65 | 220 | 0 | 600 | 1190 | 72 | 7448.08 | 14516.88 | 92.15
23:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 296 | 16.5 | 0 | 115 | 92 | 110 | 30 | 35 | 72 | 0 | 0 | 312 | 540 | 0 | 0 | 322 | 0 | 0 | 0 | 143 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 18 | 12 | 12 | 0 | 172 | 92 | 42 | 730 | 0 | 0 | 33 | 8 | 0 | 213 | 0 | 0 | 0 | 302 | 0 | 98 | 0 | 370 | 18 | 305 | 51 | 20 | 206 | 41 | 89 | 93 | 51 | 27 | 19 | 68 | 130 | 0 | 0 | 0 | 315 | 0 | 320 | 29 | 0 | 153 | 0 | 16 | 0 | 62 | 30 | 143 | 0 | 103 | 17 | 68 | 0 | 155 | 0 | 0 | 0 | 12 | 7226.5 | 906 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 0 | 0 | 0 | 1491.03 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 157 | 0 | 157 | 0 | 414 | 0 | 0 | 180 | 38 | 95 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 278 | 65 | 220 | 0 | 600 | 1190 | 0 | 7518.03 | 14744.53 | 92.27
Total KWH | 0 | 413760 | 217920 | 0 | 0 | 0 | 0 | 0 | 7984800 | 0 | 5236254 | 100440 | 148320 | 1478592 | 2149920 | 1357920 | 486309 | 220181 | 354240 | 0 | 0 | 7283055 | 11347655 | 0 | 70050 | 7480021 | 0 | 0 | 56671 | 2338800 | 441600 | 404640 | 0 | 0 | 164345 | 42655 | 0 | 0 | 1046880 | 45178 | 0 | 330848 | 98880 | 128640 | 10680 | 3714320 | 951800 | 529440 | 16872727.27 | 6691 | 0 | 347520 | 46321.2 | 505163 | 4300403 | 0 | 0 | 0 | 7249090 | 43200 | 526909 | 903272.73 | 8671500 | 605100 | 7356000 | 1180888 | 753600 | 4942000 | 967752 | 365760 | 2217644 | 668160 | 244440 | 406020 | 648660 | 2805120 | 88282 | 172500 | 0 | 7407000 | 0 | 7961000 | 693000 | 0 | 3325172.73 | 31466 | 329088 | 0 | 1704960 | 681312 | 3283000 | 0 | 2396160 | 276120 | 1320000 | 73764 | 2220000 | 0 | 9100 | 144720 | 95760 | 151481159.93 | 21856000 | 0 | 0 | 0 | 62575 | 912000 | 0 | 0 | 0 | 0 | 72432 | 149040 | 24385450 | 0 | 0 | 0 | 28592000 | 0 | 25000 | 0 | 162816 | 592128 | 0 | 108544 | 51562 | 51278 | 111528 | 233880 | 33008 | 0 | 218400 | 3857727 | 0 | 3846245 | 0 | 3821327 | 0 | 8699855 | 0 | 16140 | 4492000 | 933382 | 981754 | 112881 | 707078 | 0 | 0 | 0 | 23081.64 | 1254240 | 1630 | 808032 | 5739000 | 1558000 | 3624560 | 0 | 13367273 | 27067636.36 | 282000 | 158811483 | 310292642.93