## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-07-2026 | during | 15-07-2026 | during | 15-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 352 | 381 | 412 | 412 | 330 | 330 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 290 | 308 | 335 | 335 | 306 | 306 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 42 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 310 | 317 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 104 | 143 | 149.36 | 149.36 | 48 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 14 | 14 | 33 | 33 | 15 | 15 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 24 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 195 | 260 | 300 | 300 | 64 | 130 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 17 | 149 | 149 | 17 | 17 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 105 | 105 | 51 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 15 | 0 | 15 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 510 | 560 | 583 | 583 | 524.7 | 524.7 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 496 | 618 | 718 | 718 | 598 | 598 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 120 | 143 | 143 | 143 | 143 | 143 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2585 | 3179 | 5790.22 | 5775.22 | 2616.7 | 2940.7
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 20 | 8 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 46 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 176 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 211 | 145 | 145 | 145 | 145 | Plant availability less
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 78 | 102 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 2 | 36 | 24 | 56 | 24 | 56 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 0 | 34 | 0 | 34 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 31 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 83 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 5.16 | 0 | 2.42 | 0 | 2.42 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 0 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 108 | 106 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 37 | 97 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 40 | 156 | 163 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 612 | 1224 | 1224 | 612 | 900 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 5 | 11 | 50 | 58 | 50 | 58 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 1125 | 1150 | 1150 | 1125 | 1125 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2499.16 | 2899.36 | 4069.28 | 4144.86 | 3221.42 | 3376
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 189 | 180 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 320 | 280 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 255 | 280 | 342.01 | 342.01 | 306 | 306 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 260 | 215 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 40 | 41.65 | 41.65 | 20 | 20 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 10 | 20 | 52.82 | 52.82 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 100 | 150 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 48 | 48 | 48 | 48 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 92 | 163 | 163 | 95 | 95 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 84 | 200 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 144 | 124 | 84 | 78 | 150 | 150 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 1 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 88 | 96 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 5 | 89 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 73 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1702 | 1929.2 | 2770.44 | 2704.44 | 1962.46 | 2148.46
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-07-2026 | during | 15-07-2026 | during | 15-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 18.21 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 152 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 30.38 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 240.59 | 232 | 536.6 | 516.5 | 267.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 28 | 0 | 0 | 29 | 29 | plant availability zero
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 143 | 146 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 137 | 141 | 142 | 142 | 142 | 142 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86 | 86 | 86 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 70 | 98 | 100 | 100 | 100 | 100 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 10 | 16 | 25 | 25 | 16 | 16 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 306 | 295 | 220 | 220 | 220 | 220 | machine problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1090 | 1125 | 1127 | 1127 | 1047 | 1047
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 451 | 355 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 34 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 43 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 105 | 105 | 32 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 67 | 0 | 50 | 0 | 50 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1208 | 1207 | 1234.2 | 1234.2 | 1194 | 1194 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1764 | 1709 | 3586.2 | 3536.2 | 2396 | 2346
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 700 | 1100 | 700 | 1050 | 700 | 1050 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 72 | 110 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 130 | 130 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1150 | 1175 | 1244 | 1244 | 1200 | 1200 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 54 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.49 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3407.64 | 2596.49 | 3096 | 2862 | 3211 | 2635 | 2984
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 34.23 | 0 | 45 | 0 | 45 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 25 | 13 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 134 | 146 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 141 | 132 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 142 | 141 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 375 | 363 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 4.47 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 752.72 | 677.26 | 748 | 748 | 748 | 748 | U-2 Under maint.
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 50.51 | 0 | 37 | 0 | 37 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 63 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1772.93 | 1770.46 | 2501.49 | 2313.99 | 2110.11 | 2099.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 39 | 37 | 40 | 40 | 40 | 40 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 182 | 182 | 200 | 200 | 200 | 200 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.5 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 80 | 115 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 193 | 0 | 168 | 0 | 168 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 536.5 | 404 | 653 | 482 | 520 | 384
System Total |  |  |  |  | 28843.2 | 29250.117 | 14786.67 | 16344.02 | 23896.23 | 23811.21 | 16775.79 | 17584.77
Forecast Scenario (15-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15720 |  | 1530 |  | 17250
|  |  |  | 1:00 | 15450 |  | 1080 |  | 16530
|  |  |  | 2:00 | 14900 |  | 270 |  | 15170
|  |  |  | 3:00 | 14340 |  | 250 |  | 14590
|  |  |  | 4:00 | 13940 |  | 490 |  | 14430
|  |  |  | 5:00 | 13640 |  | 550 |  | 14190
|  |  |  | 6:00 | 13320 |  | 300 |  | 13620
|  |  |  | 7:00 | 13190 |  | 450 |  | 13640
|  |  |  | 8:00 | 13100 |  | 276.95 |  | 13390
|  |  |  | 9:00 | 13270 |  | 315.15 |  | 13600
|  |  |  | 10:00 | 14020 |  | 238.75 |  | 14270
|  |  |  | 11:00 | 14280 |  | 181.45 |  | 14470
|  |  |  | 12:00 | 14790 |  | 391.55 |  | 15200
|  |  |  | 13:00 | 15000 |  | 305.6 |  | 15320
|  |  |  | 14:00 | 14990 |  | 305.6 |  | 15310
|  |  |  | 15:00 | 14960 |  | 410.65 |  | 15390
|  |  |  | 16:00 | 15210 |  | 401.1 |  | 15630
|  |  |  | 17:00 | 14850 |  | 324.7 |  | 15190
|  |  |  | 18:00 | 14500 |  | 200.55 |  | 14710
|  |  |  | 18:30 | 14900 |  | 191 |  | 15100
|  |  |  | 19:00 | 15360 |  | 276.95 |  | 15650
|  |  |  | 19:30 | 16300 |  | 802.2 |  | 17140
|  |  |  | 20:00 | 16340 |  | 668.5 |  | 17040
|  |  |  | 21:00 | 16350 |  | 916.8 |  | 17310
|  |  |  | 22:00 | 16310 |  | 773.55 |  | 17120
|  |  |  | 23:00 | 16000 |  | 764 |  | 16800
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 15200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 917
Probable Maximum Demand at Evening Peak: |  |  | 17310.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16350.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 353.83 MKWHr. |  | 142 | 87 | 104 | 150 | 46 | 129 | 49 | 127 | 83 | 917
*** This report is generated digitally from Operation Information System (OIS) at 08:06 hrs on 15-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-07-2026 | [28 empty] | Date: | 14-07-2026 | [28 empty] | Date: | 14-07-2026 | [28 empty] | Date: | 14-07-2026 | [28 empty] | Date: | 14-07-2026 | [18 empty] | Date: | 14-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [18 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 598 | 17 | 17 | 38 | 30 | 60 | 35 | 35 | 30 | 0 | 0 | 296 | 505 | 0 | 0 | 303 | 0 | 0 | 0 | 51 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 34 | 0 | 18 | 12 | 11 | 0 | 222 | 60 | 18 | 1125 | 0 | 0 | 0 | 0 | 16 | 213 | 0 | 0 | 0 | 580 | 0 | 20 | 0 | 230 | 280 | 240 | 51 | 20 | 203 | 20 | 88 | 93 | 0 | 7 | 19 | 17 | 132 | 0 | 0 | 34 | 310 | 0 | 312 | 28 | 0 | 150 | 0 | 16 | 0 | 86 | 0 | 143 | 0 | 102 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7454 | 776 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1206 | 0 | 0 | 0 | 1453.72 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 133 | 0 | 140 | 0 | 376 | 0 | 0 | 182 | 39 | 35 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 275 | 130 | 220 | 0 | 600 | 1088 | 17 | 7034.72 | 14488.72 | 101.64
01:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 493 | 17 | 0 | 35 | 30 | 0 | 55 | 35 | 32 | 0 | 0 | 297 | 465 | 0 | 0 | 306 | 0 | 0 | 0 | 34 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 12 | 0 | 0 | 217 | 103 | 21 | 1125 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 583 | 0 | 20 | 0 | 230 | 280 | 240 | 51 | 20 | 202 | 20 | 62 | 93 | 0 | 0 | 19 | 17 | 132 | 0 | 0 | 34 | 305 | 0 | 312 | 29 | 0 | 137 | 0 | 16 | 0 | 86 | 0 | 144 | 0 | 101 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7180 | 872 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1206 | 0 | 0 | 0 | 1387.16 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 133 | 0 | 140 | 0 | 320 | 0 | 0 | 182 | 40 | 35 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 275 | 130 | 220 | 0 | 600 | 1135 | 17 | 7189.16 | 14369.16 | 101.71
02:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 585 | 0 | 0 | 27 | 30 | 0 | 30 | 35 | 0 | 0 | 0 | 295 | 450 | 0 | 0 | 307 | 0 | 0 | 0 | 34 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 107 | 28 | 1125 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 583 | 0 | 18 | 0 | 230 | 280 | 240 | 51 | 20 | 202 | 20 | 0 | 93 | 0 | 0 | 19 | 0 | 134 | 0 | 0 | 34 | 310 | 0 | 312 | 29 | 0 | 143 | 0 | 16 | 0 | 86 | 0 | 143 | 0 | 101 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7054 | 777 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1204 | 0 | 0 | 0 | 1397.49 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 135 | 0 | 140 | 0 | 395 | 0 | 0 | 182 | 40 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 275 | 130 | 220 | 0 | 500 | 1105 | 0 | 6907.49 | 13961.49 | 101.78
03:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 526 | 0 | 0 | 17 | 30 | 0 | 15 | 0 | 0 | 0 | 0 | 294 | 455 | 0 | 0 | 313 | 0 | 0 | 0 | 34 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 68 | 28 | 1125 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 582 | 0 | 0 | 0 | 230 | 280 | 240 | 51 | 20 | 202 | 20 | 0 | 93 | 0 | 0 | 19 | 0 | 126 | 0 | 0 | 34 | 305 | 0 | 312 | 29 | 0 | 140 | 0 | 16 | 0 | 86 | 0 | 144 | 0 | 101 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6862 | 777 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1209 | 0 | 0 | 0 | 1347.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 135 | 0 | 140 | 0 | 402 | 0 | 0 | 182 | 40 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 130 | 220 | 0 | 500 | 1125 | 0 | 6689.03 | 13551.03 | 101.85
04:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 577 | 0 | 0 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 495 | 0 | 0 | 308 | 0 | 0 | 0 | 34 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 29 | 1125 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 455 | 0 | 0 | 0 | 230 | 280 | 240 | 51 | 20 | 202 | 20 | 0 | 93 | 0 | 0 | 19 | 0 | 126 | 0 | 0 | 25 | 310 | 0 | 314 | 29 | 0 | 141 | 0 | 16 | 0 | 86 | 0 | 144 | 0 | 70 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6701 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 0 | 0 | 0 | 1360.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 136 | 0 | 142 | 0 | 414 | 0 | 0 | 182 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 130 | 220 | 0 | 500 | 1085 | 0 | 6592.92 | 13293.92 | 101.92
05:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 540 | 0 | 0 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 505 | 0 | 0 | 306 | 0 | 0 | 0 | 34 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 28 | 1125 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 230 | 280 | 240 | 51 | 20 | 198 | 20 | 0 | 93 | 0 | 0 | 19 | 0 | 126 | 0 | 0 | 25 | 300 | 0 | 314 | 29 | 0 | 138 | 0 | 16 | 0 | 86 | 0 | 144 | 0 | 22 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 6577 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1009 | 0 | 0 | 0 | 1410.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 136 | 0 | 141 | 0 | 414 | 0 | 0 | 182 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 130 | 220 | 0 | 500 | 1105 | 0 | 6553.37 | 13130.37 | 101.99
06:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 564 | 0 | 0 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 500 | 0 | 0 | 305 | 0 | 0 | 0 | 34 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0.31 | 222 | 0 | 26 | 1015 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 450 | 1 | 0 | 0 | 230 | 280 | 240 | 51 | 20 | 215 | 20 | 0 | 93 | 0 | 0 | 19 | 0 | 114 | 0 | 4 | 25 | 300 | 0 | 314 | 29 | 0 | 132 | 0 | 16 | 0 | 86 | 0 | 144 | 0 | 22 | 17 | 49 | 1 | 48 | 0 | 0 | 2.66 | 0 | 6470.97 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 1004 | 0 | 0 | 0 | 1344.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.46 | 4 | 0 | 0 | 1.43 | 140 | 0 | 141 | 0 | 139 | 0 | 414 | 0 | 0.13 | 181 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 9 | 0.02 | 0 | 220 | 130 | 220 | 0 | 500 | 1085 | 0 | 6488.57 | 12959.54 | 102.06
07:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 552 | 0 | 0 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 505 | 0 | 0 | 307 | 0 | 0 | 3 | 34 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 1.33 | 222 | 0 | 18 | 1000 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 450 | 4 | 0 | 0 | 230 | 280 | 240 | 51 | 20 | 218 | 30 | 0 | 92 | 0 | 0 | 19 | 0 | 116 | 0 | 14 | 25 | 310 | 0 | 314 | 29 | 0 | 139 | 3 | 16 | 0 | 86 | 0 | 145 | 0 | 22 | 17 | 49 | 2.5 | 48 | 0 | 0.1 | 6.37 | 0 | 6488.3 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 930 | 0 | 0 | 0 | 1378.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.91 | 24 | 0 | 0 | 1.4 | 142 | 0 | 143 | 0 | 139 | 0 | 414 | 0 | 0.13 | 181 | 40 | 0 | 4 | 0 | 0 | 0 | 0 | 1.6 | 32 | 0.08 | 0 | 218 | 130 | 220 | 0 | 500 | 1065 | 0 | 6493.39 | 12981.69 | 102.13
08:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 0 | 578 | 0 | 0 | 17 | 30 | 0 | 4 | 17 | 0 | 0 | 0 | 305 | 505 | 0 | 0 | 315 | 0 | 0 | 6 | 35 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 1.14 | 222 | 1 | 5 | 945 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 515 | 10 | 0 | 0 | 230 | 280 | 240 | 51 | 20 | 215 | 30 | 0 | 91 | 0 | 0 | 19 | 0 | 104 | 0 | 35 | 25 | 315 | 0 | 314 | 29 | 0 | 138 | 2 | 16 | 0 | 85 | 0 | 144 | 0 | 22 | 17 | 49 | 5.5 | 48 | 0 | 0.3 | 13.72 | 0 | 6608.66 | 873 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44 | 956 | 0 | 0 | 0 | 994.29 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 12.94 | 42 | 0 | 0 | 6.81 | 142 | 0 | 145 | 0 | 142 | 0 | 414 | 0 | 0.85 | 182 | 39 | 0 | 7 | 0 | 0 | 0 | 0 | 3.5 | 60 | 0.23 | 0 | 281 | 130 | 220 | 0 | 500 | 1080 | 0 | 6319.62 | 12928.28 | 102.2
09:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 570 | 0 | 0 | 25 | 30 | 2 | 19 | 17 | 17 | 0 | 0 | 303 | 520 | 0 | 0 | 312 | 0 | 0 | 8 | 143 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 2.52 | 222 | 29 | 2 | 1125 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 530 | 14 | 6 | 0 | 280 | 280 | 275 | 51 | 15 | 210 | 30 | 0 | 91 | 0 | 0 | 19 | 0 | 110 | 0 | 29 | 0 | 305 | 0 | 314 | 29 | 0 | 130 | 8 | 8 | 0 | 82 | 0 | 142 | 0 | 22 | 17 | 58 | 10.8 | 48 | 0 | 0.8 | 13.85 | 0 | 7163.97 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 1132 | 0 | 0 | 0 | 764.92 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 38.2 | 45 | 0 | 0 | 17.39 | 142 | 0 | 145 | 0 | 142 | 0 | 350 | 0 | 1.6 | 181 | 40 | 0 | 4 | 0 | 0 | 0 | 0 | 2.7 | 104 | 0.2 | 16 | 214 | 130 | 180 | 0 | 500 | 1070 | 0 | 6190.01 | 13353.98 | 102.25
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 525 | 0 | 0 | 35 | 62 | 30 | 30 | 35 | 17 | 0 | 0 | 293 | 505 | 0 | 0 | 310 | 0 | 0 | 13 | 123 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 4.21 | 222 | 48 | 2 | 1125 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 545 | 17 | 24 | 0 | 314 | 280 | 270 | 51 | 10 | 201 | 33 | 0 | 91 | 5 | 0 | 19 | 11 | 134 | 0 | 46 | 0 | 310 | 0 | 306 | 29 | 0 | 145 | 7 | 0 | 0 | 78 | 0 | 143 | 0 | 22 | 17 | 58 | 10.01 | 112 | 0 | 0.5 | 29.54 | 0 | 7386.26 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 52 | 1139 | 0 | 0 | 0 | 751.99 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 23.59 | 68 | 0 | 0 | 10.89 | 140 | 0 | 145 | 0 | 142 | 0 | 380 | 0 | 1.35 | 182 | 39 | 0 | 5 | 0 | 0 | 0 | 0 | 1.9 | 72 | 0.22 | 16 | 227 | 130 | 220 | 0 | 700 | 1060 | 0 | 6468.94 | 13855.2 | 102.3
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 445 | 17 | 0 | 17 | 90 | 110 | 35 | 35 | 17 | 0 | 0 | 286 | 500 | 0 | 0 | 305 | 0 | 0 | 15 | 123 | 14 | 21 | 0 | 0 | 1 | 16 | 0 | 0 | 13 | 0 | 0 | 9 | 0 | 0 | 4.58 | 222 | 69 | 2 | 1125 | 3 | 0 | 0 | 2 | 35 | 212 | 0 | 0 | 0 | 570 | 19 | 43 | 0 | 360 | 320 | 250 | 43 | 8 | 215 | 36 | 0 | 91 | 32 | 0 | 19 | 52 | 140 | 0 | 35 | 0 | 305 | 0 | 306 | 28 | 0 | 149 | 6 | 0 | 0 | 79 | 0 | 143 | 0 | 67 | 17 | 58 | 16.8 | 115 | 0 | 0.8 | 52.21 | 0 | 7712.39 | 450 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 64 | 1195 | 0 | 0 | 0 | 751.27 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 14.54 | 75 | 0 | 0 | 46.35 | 137 | 0 | 142 | 0 | 142 | 0 | 386 | 0 | 4.16 | 182 | 40 | 50 | 23 | 0 | 0 | 0 | 0 | 4.5 | 172 | 0.28 | 48 | 276 | 130 | 220 | 0 | 700 | 1080 | 2 | 6408.1 | 14120.49 | 102.3
12:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 496 | 17 | 0 | 17 | 104 | 195 | 42 | 35 | 17 | 0 | 0 | 290 | 510 | 0 | 0 | 310 | 0 | 0 | 13 | 120 | 14 | 20 | 0 | 0 | 37 | 16 | 0 | 0 | 5 | 0 | 2 | 17 | 12 | 0 | 5.16 | 222 | 108 | 2 | 1125 | 40 | 0 | 0 | 20 | 78 | 212 | 0 | 0 | 0 | 580 | 18 | 100 | 0 | 260 | 320 | 255 | 43 | 10 | 189 | 20 | 5 | 91 | 84 | 0 | 19 | 88 | 144 | 1 | 73 | 0 | 305 | 0 | 306 | 28 | 0 | 143 | 7 | 10 | 0 | 84 | 0 | 137 | 0 | 70 | 17 | 58 | 18.21 | 116 | 0 | 1 | 30.38 | 0 | 8116.75 | 451 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 67 | 1208 | 0 | 0 | 0 | 752.72 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 25 | 16 | 34.23 | 63 | 0 | 0 | 50.51 | 134 | 0 | 141 | 0 | 142 | 0 | 375 | 0 | 4.47 | 182 | 39 | 80 | 38 | 0 | 0 | 0 | 0 | 4.5 | 193 | 0.49 | 72 | 307 | 130 | 220 | 0 | 700 | 1150 | 17 | 6669.92 | 14786.67 | 102.4
13:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 456 | 17 | 0 | 17 | 108 | 225 | 55 | 35 | 17 | 0 | 0 | 292 | 520 | 0 | 0 | 310 | 0 | 0 | 19 | 143 | 14 | 20 | 0 | 0 | 77 | 16 | 3 | 0 | 9 | 0 | 16 | 17 | 12 | 0 | 4.1 | 222 | 103 | 2 | 1125 | 81 | 0 | 0 | 17 | 95 | 208 | 0 | 0 | 0 | 580 | 4 | 100 | 0 | 260 | 280 | 260 | 43 | 10 | 202 | 20 | 35 | 90 | 152 | 0 | 19 | 97 | 142 | 16 | 74 | 0 | 310 | 0 | 306 | 28 | 0 | 123 | 12 | 16 | 0 | 83 | 0 | 134 | 0 | 72 | 17 | 58 | 21.32 | 115 | 0 | 1.1 | 43.58 | 0 | 8334.1 | 450 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 100 | 1207 | 0 | 0 | 0 | 752.27 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 16 | 53.65 | 85 | 0 | 0 | 25.83 | 128 | 0 | 134 | 0 | 142 | 0 | 320 | 0 | 5.29 | 182 | 40 | 113 | 13 | 0 | 0 | 0 | 0 | 6.7 | 207 | 0.69 | 99 | 279 | 130 | 180 | 0 | 700 | 1180 | 17 | 6657.43 | 14991.53 | 102.45
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 456 | 0 | 0 | 17 | 108 | 225 | 55 | 35 | 17 | 0 | 0 | 292 | 450 | 0 | 17 | 313 | 0 | 0 | 14 | 143 | 14 | 20 | 0 | 0 | 80 | 46 | 18 | 0 | 7 | 0 | 16 | 17 | 12 | 0 | 1.42 | 221 | 107 | 2 | 1125 | 106 | 0 | 0 | 17 | 96 | 209 | 0 | 0 | 0 | 580 | 9 | 100 | 0 | 260 | 280 | 255 | 43 | 10 | 196 | 20 | 34 | 90 | 147 | 0 | 19 | 97 | 158 | 16 | 62 | 0 | 305 | 0 | 306 | 28 | 0 | 135 | 10 | 16 | 0 | 84 | 0 | 134 | 0 | 77 | 17 | 57 | 20.35 | 115 | 0 | 2.1 | 31.65 | 0 | 8351.52 | 450 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 97 | 1168 | 0 | 0 | 0 | 759.49 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 16 | 56.54 | 103 | 0 | 0 | 52.11 | 129 | 0 | 134 | 0 | 141 | 0 | 363 | 0 | 2.2 | 182 | 40 | 115 | 11 | 0 | 0 | 0 | 0 | 6.7 | 126 | 0.19 | 105 | 276 | 130 | 180 | 0 | 700 | 1180 | 17 | 6631.23 | 14982.75 | 102.5
15:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 625 | 0 | 0 | 17 | 107 | 225 | 55 | 35 | 17 | 0 | 0 | 298 | 455 | 0 | 35 | 315 | 0 | 0 | 13 | 143 | 13.8 | 20 | 0 | 0 | 80 | 48 | 28 | 0 | 6 | 0 | 16 | 17 | 12 | 0 | 1.09 | 80 | 108 | 2 | 1125 | 104 | 0 | 14 | 17 | 101 | 209 | 0 | 0 | 0 | 597 | 13 | 100 | 0 | 240 | 280 | 300 | 43 | 10 | 192 | 20 | 35 | 90 | 156 | 0 | 19 | 97 | 156 | 16 | 39 | 0 | 310 | 0 | 291 | 28 | 0 | 143 | 9 | 16 | 0 | 82 | 0 | 138 | 0 | 89 | 17 | 19 | 16.21 | 126 | 0 | 1.7 | 40.8 | 0 | 8478.6 | 450 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 61 | 1162 | 0 | 0 | 0 | 750.7 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 16 | 41.98 | 30 | 0 | 0 | 25.55 | 129 | 0 | 134 | 0 | 141 | 0 | 364 | 0 | 0 | 182 | 40 | 115 | 15 | 0 | 0 | 0 | 0 | 4.5 | 97 | 0.24 | 110 | 281 | 130 | 220 | 0 | 700 | 1166 | 17 | 6473.97 | 14952.57 | 102.57
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 610 | 0 | 0 | 17 | 140 | 225 | 55 | 35 | 17 | 0 | 0 | 293 | 460 | 0 | 35 | 315 | 0 | 0 | 9 | 143 | 13.5 | 20 | 0 | 0 | 87 | 48 | 35 | 0 | 0 | 0 | 16 | 36 | 12 | 0 | 1.16 | 146 | 107 | 2 | 1125 | 104 | 0 | 33 | 17 | 102 | 210 | 0 | 0 | 0 | 612 | 10 | 100 | 0 | 230 | 280 | 270 | 43 | 10 | 200 | 20 | 34 | 89 | 169 | 0 | 19 | 97 | 152 | 52.2 | 37 | 0 | 315 | 0 | 280 | 28 | 0 | 146 | 3 | 16 | 0 | 82 | 0 | 141 | 0 | 94 | 17 | 28 | 4.1 | 140 | 0 | 0.4 | 27.28 | 0 | 8638.64 | 450 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 48 | 1209 | 0 | 0 | 0 | 759.3 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 20 | 52.2 | 21.18 | 58 | 0 | 0 | 15.51 | 130 | 0 | 132 | 0 | 140 | 0 | 357 | 0 | 0 | 182 | 40 | 115 | 15 | 10 | 0 | 0 | 0 | 3.5 | 63 | 0.43 | 110 | 307 | 128 | 220 | 0 | 700 | 1160 | 17 | 6566.12 | 15204.76 | 102.6
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 430 | 0 | 6 | 17 | 140 | 225 | 55 | 35 | 17 | 0 | 0 | 283 | 435 | 0 | 35 | 300 | 0 | 0 | 5 | 143 | 13 | 20 | 0 | 0 | 91 | 48 | 40 | 0 | 9 | 0 | 16 | 36 | 12 | 0 | 0.64 | 176 | 105 | 8 | 1125 | 130 | 0 | 46 | 17 | 96 | 212 | 0 | 0 | 0 | 591 | 4 | 100 | 0 | 230 | 280 | 250 | 43 | 10 | 205 | 20 | 34 | 89 | 176 | 0 | 19 | 97 | 144 | 52.2 | 17 | 0 | 305 | 0 | 280 | 28 | 0 | 129 | 1 | 16 | 0 | 84 | 0 | 142 | 0 | 104 | 17 | 58 | 6.1 | 119 | 0 | 0.6 | 13.6 | 7 | 8373.14 | 450 | 0 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 0 | 15 | 16 | 1210 | 0 | 0 | 0 | 717.78 | 0 | 0 | 0 | 20 | 35 | 0 | 94 | 20 | 52.2 | 18.4 | 36 | 0 | 0 | 15.79 | 137 | 0 | 132 | 0 | 140 | 0 | 363 | 0 | 0 | 182 | 40 | 115 | 6 | 16 | 0 | 0 | 0 | 2.6 | 31 | 0.22 | 110 | 275 | 128 | 220 | 0 | 700 | 1120 | 17 | 6474.99 | 14848.13 | 102.67
18:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 435 | 0 | 17 | 17 | 140 | 225 | 55 | 35 | 17 | 0 | 0 | 287 | 430 | 0 | 35 | 300 | 0 | 0 | 2 | 143 | 13 | 21 | 0 | 0 | 86 | 48 | 30 | 0 | 12 | 0 | 25 | 36 | 12 | 0 | 0.13 | 176 | 105 | 5 | 1125 | 155 | 0 | 45 | 23 | 94 | 211 | 0 | 0 | 0 | 490 | 1 | 100 | 0 | 230 | 280 | 250 | 43 | 10 | 209 | 20 | 35 | 90 | 113 | 0 | 19 | 96 | 132 | 52.2 | 3 | 32 | 300 | 0 | 280 | 28 | 0 | 121 | 1 | 16 | 0 | 84 | 0 | 142 | 0 | 98 | 0 | 58 | 0.93 | 114 | 0 | 0.3 | 4.21 | 12 | 8168.77 | 450 | 0 | 0 | 0 | 26 | 38 | 0 | 0 | 0 | 0 | 32 | 8 | 1135 | 0 | 0 | 0 | 664.2 | 0 | 0 | 0 | 50 | 35 | 0 | 94 | 20 | 52.2 | 2.34 | 6 | 0 | 0 | 2.65 | 141 | 0 | 132 | 0 | 140 | 0 | 300 | 0 | 0 | 182 | 40 | 115 | 2 | 68 | 0 | 0 | 0 | 0.8 | 11 | 0.06 | 110 | 224 | 130 | 180 | 0 | 700 | 1100 | 17 | 6208.25 | 14377.02 | 102.7
19:00 | 0 | 42 | 24 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 487 | 35 | 0 | 17 | 142 | 245 | 55 | 35 | 108 | 0 | 0 | 307 | 390 | 0 | 55 | 309 | 0 | 0 | 0 | 143 | 14 | 21 | 0 | 0 | 82 | 50 | 48 | 0 | 21 | 0 | 35 | 36 | 12 | 0 | 0 | 176 | 103 | 12 | 1125 | 154 | 0 | 45 | 25.5 | 90 | 211 | 0 | 0 | 0 | 550 | 0 | 102 | 0 | 250 | 280 | 270 | 43 | 10 | 211 | 20 | 43 | 91 | 118 | 0 | 19 | 96 | 154 | 52.2 | 0 | 40 | 305 | 0 | 292 | 28 | 0 | 121 | 0 | 16 | 0 | 85 | 0 | 143 | 0 | 98 | 0 | 59 | 0 | 114 | 0 | 0 | 0 | 12 | 8615.7 | 450 | 0 | 0 | 17 | 44 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1071 | 0 | 0 | 0 | 723.07 | 0 | 0 | 0 | 50 | 37 | 0 | 94 | 20 | 52.2 | 0 | 0 | 20 | 0 | 0 | 143 | 0 | 132 | 0 | 139 | 0 | 340 | 0 | 0 | 182 | 40 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 281 | 130 | 220 | 0 | 1100 | 1095 | 35 | 6780.27 | 15395.97 | 102.76
19:30 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 548 | 35 | 0 | 17 | 143 | 260 | 55 | 35 | 108 | 0 | 0 | 300 | 550 | 0 | 55 | 305 | 0 | 0 | 0 | 143 | 14 | 21 | 0 | 0 | 88 | 50 | 65 | 0 | 19 | 0 | 35 | 36 | 12 | 0 | 0 | 176 | 103 | 17 | 1125 | 152 | 0 | 45 | 25.5 | 95 | 211 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 265 | 280 | 265 | 43 | 20 | 190 | 40 | 90 | 91 | 198 | 0 | 19 | 96 | 156 | 52.2 | 0 | 40 | 305 | 0 | 293 | 28 | 0 | 147 | 0 | 16 | 0 | 85 | 0 | 142 | 0 | 98 | 0 | 68 | 0 | 150 | 0 | 0 | 0 | 12 | 9298.7 | 450 | 0 | 0 | 37 | 46 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1109 | 0 | 0 | 0 | 739.47 | 0 | 0 | 0 | 50 | 50 | 0 | 94 | 20 | 52.2 | 0 | 0 | 20 | 0 | 0 | 144 | 0 | 131 | 0 | 140 | 0 | 361 | 0 | 0 | 182 | 40 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 130 | 220 | 0 | 1100 | 1150 | 54 | 6991.67 | 16290.37
20:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 543 | 35 | 0 | 17 | 143 | 260 | 55 | 35 | 108 | 0 | 0 | 305 | 545 | 0 | 55 | 302 | 0 | 0 | 0 | 143 | 14 | 21 | 0 | 0 | 95 | 51 | 75 | 0 | 11 | 17 | 30 | 36 | 12 | 0 | 0 | 176 | 108 | 23 | 1125 | 145 | 0 | 46 | 25.5 | 98 | 211 | 0 | 0 | 0 | 612 | 0 | 135 | 0 | 220 | 280 | 270 | 43 | 18 | 189 | 40 | 86 | 91 | 194 | 0 | 19 | 96 | 134 | 52.2 | 0 | 47 | 310 | 0 | 295 | 28 | 0 | 145 | 0 | 16 | 0 | 85 | 0 | 141 | 0 | 98 | 0 | 68 | 0 | 151 | 0 | 0 | 0 | 12 | 9242.7 | 450 | 0 | 0 | 34 | 53 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1168 | 0 | 0 | 0 | 735.97 | 0 | 32 | 0 | 50 | 50 | 0 | 94 | 20 | 52.2 | 0 | 0 | 20 | 0 | 0 | 144 | 0 | 132 | 0 | 140 | 0 | 367 | 0 | 0 | 182 | 40 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 130 | 220 | 0 | 1100 | 1150 | 54 | 7090.17 | 16332.87 | 102.85
21:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 618 | 35 | 0 | 17 | 143 | 260 | 55 | 35 | 108 | 0 | 0 | 308 | 560 | 0 | 35 | 317 | 0 | 0 | 0 | 143 | 14 | 21 | 0 | 0 | 97 | 16 | 83 | 0 | 11 | 17 | 36 | 54.36 | 12 | 0 | 0 | 176 | 106 | 31 | 1125 | 156 | 0 | 46 | 8 | 102 | 211 | 0 | 0 | 0 | 612 | 0 | 150 | 0 | 215 | 280 | 280 | 43 | 20 | 180 | 40 | 89 | 92 | 200 | 0 | 19 | 96 | 124 | 52.2 | 0 | 49 | 315 | 0 | 295 | 28 | 0 | 146 | 0 | 16 | 0 | 86 | 0 | 141 | 0 | 98 | 0 | 68 | 0 | 152 | 0 | 0 | 0 | 12 | 9364.56 | 355 | 0 | 0 | 34 | 43 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1207 | 0 | 0 | 0 | 677.26 | 0 | 32 | 0 | 50 | 50 | 0 | 94 | 13 | 52.2 | 0 | 0 | 20 | 0 | 0 | 146 | 0 | 132 | 0 | 141 | 0 | 363 | 0 | 0 | 182 | 37 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 130 | 220 | 0 | 1100 | 1175 | 54 | 6979.46 | 16344.02 | 102.92
22:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 599 | 35 | 0 | 17 | 127 | 260 | 55 | 35 | 108 | 0 | 0 | 308 | 555 | 0 | 35 | 310 | 0 | 0 | 0 | 143 | 13.5 | 21 | 0 | 0 | 99 | 16 | 87 | 0 | 13 | 17 | 36 | 36 | 12 | 0 | 0 | 222 | 107 | 30 | 1125 | 157 | 0 | 50 | 8 | 96 | 211 | 0 | 0 | 0 | 612 | 0 | 68 | 0 | 215 | 280 | 270 | 43 | 20 | 176 | 40 | 73 | 92 | 200 | 0 | 19 | 96 | 132 | 52.2 | 0 | 49 | 315 | 0 | 295 | 28 | 0 | 151 | 0 | 16 | 0 | 85 | 0 | 142 | 0 | 98 | 0 | 68 | 0 | 152 | 0 | 0 | 0 | 12 | 9270.7 | 352 | 0 | 0 | 34 | 41 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1211 | 0 | 0 | 0 | 724.27 | 0 | 32 | 0 | 50 | 50 | 0 | 94 | 20 | 52.2 | 0 | 0 | 20 | 0 | 0 | 146 | 0 | 132 | 0 | 140 | 0 | 368 | 0 | 0 | 181 | 38 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 130 | 220 | 0 | 1100 | 1170 | 54 | 7031.47 | 16302.17 | 102.95
23:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 641 | 35 | 0 | 17 | 127 | 260 | 55 | 17 | 108 | 0 | 0 | 308 | 560 | 0 | 17 | 321 | 0 | 0 | 0 | 143 | 13.5 | 21 | 0 | 0 | 100 | 16 | 65 | 0 | 27 | 17 | 36 | 36 | 12 | 0 | 0 | 222 | 110 | 32 | 1125 | 156 | 0 | 50 | 8 | 105 | 212 | 0 | 0 | 0 | 612 | 0 | 13 | 0 | 215 | 280 | 300 | 43 | 20 | 171 | 40 | 69 | 92 | 197 | 0 | 19 | 100 | 130 | 52.2 | 0 | 49 | 315 | 0 | 295 | 28 | 0 | 152 | 0 | 16 | 0 | 86 | 0 | 142 | 0 | 98 | 0 | 68 | 0 | 152 | 0 | 0 | 0 | 12 | 9258.7 | 352 | 0 | 0 | 29 | 38 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1210 | 0 | 0 | 0 | 733.19 | 0 | 32 | 0 | 50 | 50 | 0 | 94 | 13 | 52.2 | 0 | 0 | 20 | 0 | 0 | 146 | 0 | 133 | 0 | 141 | 0 | 368 | 0 | 0 | 182 | 39 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 130 | 220 | 0 | 1100 | 1174 | 54 | 7032.39 | 16291.09 | 102.97
Total KWH | 0 | 1093440 | 258720 | 0 | 0 | 0 | 0 | 0 | 8082000 | 0 | 12842580 | 259560 | 31680 | 481680 | 2039520 | 3176760 | 934875 | 597369 | 830880 | 0 | 0 | 7143884 | 11891364 | 0 | 337414 | 7410812 | 0 | 0 | 112813 | 2522400 | 345600 | 506880 | 0 | 0 | 1116545 | 439091 | 576960 | 0 | 306720 | 127615 | 295104 | 445380 | 176640 | 0 | 24238 | 4975140 | 1878500 | 355200 | 26676363.64 | 1662691 | 0 | 433920 | 211278.6 | 1324799 | 4979691 | 0 | 0 | 0 | 13325453 | 130410 | 1323127 | 0 | 6045000 | 7229500 | 6284000 | 1126445 | 384960 | 4889000 | 657072 | 704640 | 2167004 | 2148480 | 11760 | 473560 | 1295040 | 3210240 | 504110 | 472127 | 539824 | 7466000 | 0 | 7426000 | 669000 | 0 | 3336463.64 | 69890 | 339312 | 0 | 2008320 | 0 | 3250000 | 0 | 1787250 | 318240 | 1274400 | 126680 | 2270400 | 0 | 10200 | 324910 | 93840 | 190598764.88 | 14751273 | 0 | 0 | 150240 | 243456 | 912000 | 0 | 0 | 0 | 0 | 228240 | 635040 | 27447280 | 0 | 0 | 0 | 22894761 | 0 | 130569 | 0 | 374784 | 948960 | 0 | 735232 | 209425 | 467549 | 314664 | 676520 | 104554 | 0 | 291680 | 3349636 | 0 | 3484664 | 0 | 3595376 | 0 | 8999272 | 0 | 21420 | 4515000 | 933382 | 1526824 | 181026 | 770448 | 0 | 0 | 0 | 44550.6 | 1129680 | 3715 | 1682976 | 6437000 | 3119000 | 5306850 | 0 | 17352727 | 27626181.82 | 427200 | 162023155.42 | 352621920.3

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14786.67 | MW | 12:00 Hr. | Energy Generated |  |  | 352.6219 |  | MKWHr.
| Day Peak Demand |  |  | 14941.67 | MW | 12:00 Hr. | Energy Unserverd |  |  | 6.979 |  | MKWHr.
| Evening Peak Generation |  |  | 16344.02 | MW | 21:00 Hr. | Energy Demand |  |  | 359.6009 |  | MKWHr.
| Evening Peak Demand |  |  | 17054.02 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.4 |  | °C
| Minimum Generation of the Day |  |  | 12928.28 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 983.08 |  | MMCFD
| Maximum Generation of the Day |  |  | 16344.02 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.6297 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 48.2231 | 0 | 12.5643 | 0 | 0 | 0.11281 | 0 | 0 | 60.9002 | Gas | 136.9517 | Gas | 463140270.7988
| Chattogram Zone |  |  | 5.3349 | 40.0018 | 8.6885 | 0 | 4.9751 | 0.15465 | 0 | 0.30672 | 59.4617 | Coal | 124.3134 | Coal | 829315224.5498
| Cumilla Zone |  |  | 29.2565 | 0 | 6.527 | 0 | 0 | 0.47213 | 3.2102 | 0 | 39.4659 | HFO | 39.7371 | HFO | 694979375.256
| Mymensingh Zone |  |  | 0 | 0 | 3.9569 | 0 | 0 | 0.46179 | 0 | 0 | 4.4187 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.2823 | 0 | 0 | 0 | 0 | 0.06989 | 0 | 0 | 26.3522 | Hydro | 4.9751 | Hydro | 18955283.4
| Khulna Zone |  |  | 0 | 27.4473 | 0.62194 | 0 | 0 | 0.63504 | 15.6633 | 0 | 44.3675 | Solar | 4.5696 | Solar | 73242850.112
| Barishal Zone |  |  | 8.4259 | 51.4159 | 2.1102 | 0 | 0 | 0.003715 | 0 | 0 | 61.9556 | Import | 41.7683 | Import | 253628124.39
| Rajshahi Zone |  |  | 19.4289 | 0 | 2.9711 | 0 | 0 | 1.3043 | 22.8948 | 0 | 46.5991 | Wind | 0.30672 | Wind | 4511851.2
| Rangpur Zone |  |  | 0 | 5.4484 | 2.2973 | 0 | 0 | 1.3553 | 0 | 0 | 9.1009
| Total |  |  | 136.9517 | 124.3134 | 39.7371 | 0 | 4.9751 | 4.5696 | 41.7683 | 0.30672 | 352.6219
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 463140270.7988 |  | Hydro | 18955283.4
|  |  |  | Coal | 829315224.5498 |  | Solar | 73242850.112
|  |  |  | HFO | 694979375.256 |  | Import | 253628124.39
|  |  |  | HSD | 0 |  | Wind | 4511851.2
[5 empty] | Total: | 233,77,72,979 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 43490.91 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 14.7513 | Peak Hr Flow | 355.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46370400 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.8948 | Peak Hr Flow | 677.26 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1490 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.2102 | Peak Hr Flow | 124.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2526 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.8563 | Peak Hr Flow | 1156.26 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 198 |  | 5895
|  |  |  | Chattogram |  | 0 |  | 1552
|  |  |  | Cumilla |  | 0 |  | 1548
|  |  |  | Mymensingh |  | 259 |  | 1451
|  |  |  | Sylhet |  | 78 |  | 717
|  |  |  | Khulna |  | 134 |  | 2027
|  |  |  | Barishal |  | 0 |  | 510
|  |  |  | Rajshahi |  | 10 |  | 1672
|  |  |  | Rangpur |  | 0 |  | 1109
|  |  |  | Total |  | 679 |  | 16481
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Fenchugonj CCPP Phase-2 GT-4 |  |  | 35
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Karnaphuli Hydro PP Unit-1 |  |  | 40
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Karnaphuli Hydro PP Unit-3 |  |  | 50
[5 empty] | Total | 300 |  |  |  | Total | 125
|  |  |  | Total Unavailable Capacity |  |  |  | 425
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:21 | Ishwardi-Natore 132kV Ckt-1 is restored.
|  | 08:22 | Natore 132/33kV S/S 132 KV MAIN BUS is restored.
|  | 08:22 | Ishwardi-Natore 132kV Ckt-2 is restored.
|  | 08:35 | Natore-Rajshahi 132kV Ckt-1 is restored.
|  | 08:41 | Bogura-Natore 132 kV Ckt-1 is restored.
|  | 08:42 | Bogura-Natore 132 kV Ckt-2 is restored.
|  | 09:17 | Shahjibazar 132/33kV S/S TR-06 HT is restored.
|  | 09:18 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
| 09:22 | 15:49 | Daudkandi-Sonargaon 132 kV Ckt-1 Project Work S/D from Daudkandi 132/33kV end Due to For
project work at bus section.
| 09:24 | 15:50 | Daudkandi-Sonargaon 132 kV Ckt-2 Project Work S/D from Daudkandi 132/33kV end Due to For
project work at bus section.
| 09:28 | 15:23 | Daudkandi 132/33kV S/S Titas 50 MW Power Plant Line Project Work S/D Due to For project
work at bus section.
| 09:30 | 10:59 | Sirajganj 132/33kV S/S T4-(445) LT Forced S/D Due to 33 KV Economic Zone feeder Bus DS
Red hot. ( T-4 33kv Bus ). DS bolt replacement at Economic Zone feeder.
| 09:31 | 10:59 | Sirajganj 132/33kV S/S T4-(445) HT Forced S/D Due to 33 KV Economic Zone feeder Bus DS | [7 empty] | 15.0MW load
|  |  | Red hot. ( T-4 33kv Bus ). DS bolt replacement at Economic Zone feeder. | [7 empty] | interrup.
|  | 09:40 | Thakurgaon 132/33kV S/S 33kV Bus is restored.
| 10:18 | 12:19 | Patiya 132/33kV S/S TRAFO-01 LT Scheduled S/D Due to Corrective maintenance | [7 empty] | 6.0MW load
interrup.
|  | 10:20 | Barishal-Barishal(N) 132 kV Ckt-2 is restored.
| 10:20 | 12:20 | Patiya 132/33kV S/S TRAFO-01 HT Scheduled S/D Due to Corrective maintenance | [7 empty] | 6.0MW load
interrup.
| 10:55 | 15:10 | Daudkandi 132/33kV S/S Main Project Work S/D Due to For project work at bus section.
| 11:25 |  | Bheramara P/S-Kustia 132 kV Ckt-2 Scheduled S/D from Kushtia 132/33kV end Due to Project
work and from Bheramara 230/132kV end Due to Erection and Stringing Work
| 11:30 | 18:51 | Korerhat 400/230/132kV S/S ATR-3(7303T)-Three Ph LT Project Work S/D Due to Due to
project work
| 11:31 | 18:50 | Korerhat 400/230/132kV S/S ATR-3(7303T)-Three Ph HT Project Work S/D Due to Due to
project work
| 12:00 |  | Day peak generation is 14787 MW.
| 12:17 | 12:55 | Ghorashal 230kV S/S TARFO-2 HT Tripped showing Inner differential relays Due to WTI & OTI | [7 empty] | 101.0MW load
interrup.
|  | 12:20 | Patiya 132/33kV S/S TRAFO-01 HT is restored.
|  | 13:02 | Natore-Rajshahi 132kV Ckt-2 is restored.
| 14:13 | 16:50 | Rajendrapur 132/33kV S/S MTR-2 LT Project Work S/D Due to Rajendrapur-Sreepur Bay
Extention Work.
| 14:13 | 16:50 | Rajendrapur 132/33kV S/S MTR-2 HT Project Work S/D Due to Rajendrapur-Sreepur Bay
Extention Work.
| 14:26 | 18:11 | Bogura 230/132kV S/S T-01 HT Scheduled S/D Due to Auxiliary transformer Oil Centrifuging.
| 14:26 | 18:11 | Bogura 230/132kV S/S T-01 LT Scheduled S/D Due to Auxiliary transformer Oil Centrifuging.
| 05:58 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 LT Scheduled S/D Due to Read Hot maintenance
| 06:00 |  | Minimum generation: 14052 MW
| 06:09 |  | Bhaluka-Mymensingh 132 kV Ckt-1 Scheduled S/D from Bhaluka 132/33kV end Due to High
temperature maintenance work
| 06:10 |  | Bhaluka 132/33kV S/S Bus A Scheduled S/D Due to High temperature maintenance work
| 06:32 |  | Bhulta-Haripur 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end. and from Haripur
230/132kV end Due to Relay Replacement work at Haripur.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 381 | 8082000 | DP High
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 308 | 7143884 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 934875 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 317 | 7410812 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 259560 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 2039520 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 597369 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 337414 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 14 | 345600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 506880 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 258720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 260 | 3176760 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 17 | 481680 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1093440 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 830880 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 112813 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 31680 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 560 | 11891364 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 618 | 12842580 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143 | 2522400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 3179 | 60900231
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 211278.6 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 130410 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 433920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 176 | 4975140 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 211 | 4979691 | Plant availability less
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 102 | 1324799 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 36 | 295104 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 127615 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 176640 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 31 | 355200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 83 | 576960 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24238 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 439091 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 445380 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 106 | 1878500 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 97 | 1116545 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 156 | 1662691 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13325453 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 11 | 306720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 26676363.64 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 2899.36 | 59461739.24
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 180 | 4889000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 280 | 7229500 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 280 | 6284000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 215 | 6045000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 657072 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 20 | 384960 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 1126445 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1323127 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 49 | 539824 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 92 | 2167004 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2148480 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 124 | 3210240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 504110 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 473560 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 96 | 1295040 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 11760 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 704640 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 472127 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1929.2 | 39465889
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 126680 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 152 | 2270400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1274400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 324910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 93840 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 318240 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 232 | 4418670
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 69890 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 669000 | plant availability zero
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 146 | 3336463.64 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 141 | 3250000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2008320 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 98 | 1787250 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 339312 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7466000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 295 | 7426000 | Plant availability less
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1125 | 26352235.64
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 355 | 14751273 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 34 | 150240 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 43 | 243456 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 228240 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 635040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1207 | 27447280 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1709 | 44367529
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 17352727 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 110 | 1682976 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 3119000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1175 | 27626181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5306850 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 427200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6437000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3715 | -
Barishal Area Total |  |  |  |  | 3407.64 | 3096 | 61955649.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 314664 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 130569 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 13 | 209425 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 146 | 3349636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 132 | 3484664 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 141 | 3595376 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 363 | 8999272 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 104554 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 467549 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 735232 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 948960 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 374784 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 21420 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 677.26 | 22894761 | U#2 withdrawn
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 291680 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 676520 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1770.46 | 46599066
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 37 | 933382 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 182 | 4515000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 770448 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44550.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1526824 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 181026 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1129680 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 404 | 9100910.6
Eastern Grid Total |  |  |  |  | 17438.042 | 9364.56 | 190598764.88
Western Grid Total |  |  |  |  | 11812.075 | 6979.46 | 162023155.42
National Grid Total |  |  |  |  | 29250.117 | 16344.02 | 352621920.3
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10677.05 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5173.6 | MW
i) Dhaka area |  |  | 5697.05 |  | MW | i) Khulna area |  |  |  | 1893 | MW
ii) Chattogram area |  |  | 1601 |  | MW | ii) Barishal area |  |  |  | 509.8 | MW
iii) Cumilla area |  |  | 1548 |  | MW | iii) Rajshahi area |  |  |  | 1661.8 | MW
iv) Mymensingh area |  |  | 1192 |  | MW | iv) Rangpur area |  |  |  | 1109 | MW
v) Sylhet area |  |  | 639 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15850.65 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 143 | 15:00 | 133 | Narshingdi | 200 | 21:00 | 199 | Uttara | 103 | 16:00
2 | AKSML | 150.9 | 03:00 | 68 | Hasnabad | 96 | 13:00 | 134 | Natore | 159 | 19:30 | 200 | UttaraNew | 55 | 13:00
3 | Aftabnagar | 44 | 13:00 | 69 | Hathazari | 98 | 19:00 | 135 | Nawabganj | 66.8 | 22:00 | 201 | Zigatola | 110 | 14:00
4 | Agargaon | 125 | 13:00 | 70 | Hatirjheel | 91 | 15:00 | 136 | Netrakona | 133 | 19:00
5 | Agrabad | 64 | 17:00 | 71 | Ishurdi | 84 | 21:00 | 137 | New | 86.8 | 12:00
6 | Amnura | 35 | 23:00 | 72 | Jaldhaka | 100 | 22:00 | 138 | Niamatpur | 84 | 21:00
7 | Ashuganj | 77 | 23:00 | 73 | Jamalpur | 126 | 21:00 | 139 | Noapara | 45 | 22:00
8 | BSRM | 196 | 21:00 | 74 | Jashore | 158 | 19:30 | 140 | PHP | 12 | 19:30
9 | Bagerhat | 83 | 23:00 | 75 | Jhenaidah | 94 | 19:00 | 141 | Pabna | 112 | 19:30
10 | Bajitpur | 88 | 20:00 | 76 | Joydebpur | 170 | 18:30 | 142 | Palashbari | 140 | 20:00
11 | Bakerganj | 16.4 | 21:00 | 77 | Joypurhat | 74 | 22:00 | 143 | Panchagarh | 69 | 22:00
12 | Bakulia | 102 | 21:00 | 78 | Juldah | 16 | 01:00 | 144 | Patiya | 12 | 19:30
13 | Banani | 75 | 13:00 | 79 | KSRM | 28 | 15:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 17 | 10:00 | 80 | Kabirpur | 260 | 11:00 | 146 | Patuakhali | 75 | 22:00
15 | Barapukuria | 77 | 19:30 | 81 | Kachua | 104 | 20:00 | 147 | Payra | 34 | 23:00
16 | Barguna | 24 | 22:00 | 82 | Kaliganj | 40 | 20:00 | 148 | Postogola | 62 | 13:00
17 | Barishal | 110 | 13:00 | 83 | Kallyanpur | 117 | 16:00 | 149 | Pubail | 30 | 12:00
18 | Barishal-230 | 108 | 23:00 | 84 | Kalurghat | 45 | 12:00 | 150 | Purbachal | 31 | 13:00
19 | Baroaulia | 45 | 13:00 | 85 | Kamrangirchar | 83 | 13:00 | 151 | Purbasadipur | 146 | 21:00
20 | Baroirhat | 71 | 20:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 42 | 22:00
21 | Bashundhara | 207 | 19:00 | 87 | Kasba | 41 | 22:00 | 153 | Rahim | 44 | 11:00
22 | BashundharaCement | 6 | 01:00 | 88 | Kazla | 125 | 13:00 | 154 | Rajbari | 95 | 19:30
23 | Beanibazar | 92 | 20:00 | 89 | Keranigonj | 89 | 19:30 | 155 | Rajendrapur | 118 | 11:00
24 | Benapole | 74 | 15:00 | 90 | Khagrachori | 36 | 20:00 | 156 | Rajshahi | 118 | 22:00
25 | Bhaluka | 157 | 16:00 | 91 | Khulna | 70 | 14:00 | 157 | Rajshahi-230 | 110 | 13:00
26 | Bhandaria | 60 | 22:00 | 92 | Khulshi | 212 | 19:00 | 158 | Ramganj | 124 | 23:00
27 | Bhangura | 43 | 19:00 | 93 | Kishoreganj | 134 | 00:00 | 159 | Rampur | 44 | 19:00
28 | Bheramara(GK) | 73 | 20:00 | 94 | Kodda | 288 | 15:00 | 160 | Rangamati | 17 | 19:00
29 | Bhulta | 196 | 05:00 | 95 | Kulaura | 64 | 19:00 | 161 | Rangpur | 150 | 19:30
30 | Bog-Sherpur | 88 | 21:00 | 96 | Kurigram | 77 | 20:00 | 162 | Ruppur | 4.8 | 16:00
31 | Bogura | 172 | 22:00 | 97 | Kushtia | 166 | 19:30 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 80 | 22:00 | 98 | Laksam | 39 | 23:00 | 164 | Saidpur | 116 | 22:00
33 | Brahmanbaria | 146 | 23:00 | 99 | Lakshmipur | 46 | 19:00 | 165 | Santhia | 38 | 22:00
34 | Cantonment | 128 | 13:00 | 100 | Lalbag | 76 | 13:00 | 166 | Satkhira | 140 | 22:00
35 | Chandina | 36 | 21:00 | 101 | Lalmonirhat | 74 | 21:00 | 167 | Satmasjid | 108 | 14:00
36 | Chandpur | 94 | 22:00 | 102 | MI_Cement | 13.5 | 01:00 | 168 | Savar | 234 | 15:00
37 | Chandraghona | 33 | 23:00 | 103 | Madanganj | 42 | 19:00 | 169 | SevenRings | 13.46 | 18:00
38 | Chapai | 75 | 00:00 | 104 | Madaripur | 126 | 22:00 | 170 | ShahCement | 34 | 12:00
39 | Charfasson | 35 | 23:00 | 105 | Madartek | 82 | 23:00 | 171 | Shahjadpur | 91 | 20:00
40 | Charsaidpur | 30 | 13:00 | 106 | Madunaghat | 63 | 15:00 | 172 | Shahjibazar | 138 | 00:00
41 | Chauddagram | 81 | 20:00 | 107 | Magura | 69 | 19:00 | 173 | Shahmirpur | 52 | 22:00
42 | Chhatak | 43 | 19:00 | 108 | Mahasthangarh | 86 | 19:30 | 174 | Shariatpur | 101 | 22:00
43 | Chowmuhani | 168 | 23:00 | 109 | Maijdee | 42 | 22:00 | 175 | Sherpur | 154 | 22:00
44 | Chuadanga | 118 | 19:30 | 110 | Manikganj | 127 | 22:00 | 176 | Shikalbaha | 29 | 18:00
45 | Coxsbazar | 138 | 19:00 | 111 | Maniknagar | 82 | 13:00 | 177 | Shitalakhya | 83.7 | 12:00
46 | Cumilla(N) | 160 | 23:00 | 112 | Matarbari | 55 | 19:00 | 178 | Sholosohor | 47 | 16:00
47 | Cumilla(S) | 158 | 14:00 | 113 | Matuail | 80 | 16:00 | 179 | Shomvuganj | 43 | 20:00
48 | Daganbhuiyan | 33 | 23:00 | 114 | Metrorail_Motijheel | 40 | 10:00 | 180 | Shyampur | 160 | 13:00
49 | Daudkandi | 156 | 23:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 134 | 16:00
50 | DhakaUniversity | 96 | 13:00 | 116 | Millgate | 108 | 12:00 | 182 | Sirajganj | 130 | 21:00
51 | Dhamrai | 108 | 19:00 | 117 | Mirpur | 160 | 19:00 | 183 | Sitakunda | 37 | 19:30
52 | Dhanmondi | 104 | 13:00 | 118 | Mirsorai | 46 | 12:00 | 184 | Sonargaon | 140 | 02:00
53 | Dohazari | 107 | 21:00 | 119 | Mirzapur | 44 | 19:00 | 185 | Sreemongol | 85 | 19:00
54 | Faridpur | 187 | 20:00 | 120 | Mithapukur | 88 | 00:00 | 186 | Sreepur | 128 | 21:00
55 | Fatullah | 102 | 12:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 53.4 | 22:00
56 | Fenchuganj | 45 | 00:00 | 122 | Mogbazar | 0 | 00:00 | 188 | Sunamganj | 62 | 20:00
57 | Feni | 120 | 22:00 | 123 | Mongla | 50 | 12:00 | 189 | Sylhet | 126 | 19:30
58 | GPH | 1 | 00:00 | 124 | Motijheel | 53 | 13:00 | 190 | Sylhet_(South) | 76 | 19:30
59 | Ghatail | 87 | 18:00 | 125 | Muktagacha | 39 | 12:00 | 191 | TK | 26 | 19:30
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 117 | 22:00 | 192 | Tangail | 168 | 20:00
61 | Ghorashal-230 | 108 | 01:00 | 127 | Muradnagar | 56 | 21:00 | 193 | Taraganj | 30 | 20:00
62 | Goalpara | 36 | 13:00 | 128 | Mymensingh | 176 | 20:00 | 194 | Tasnim | 45 | 06:00
63 | Gollamari | 102 | 13:00 | 129 | Nabinagar | 120 | 12:00 | 195 | Thakurgaon | 125 | 20:00
64 | Gopalganj | 122 | 20:00 | 130 | Naogaon | 142 | 20:00 | 196 | Tongi | 155 | 12:00
65 | Gulshan | 122 | 13:00 | 131 | Narail | 65 | 23:00 | 197 | Ullahpara | 45 | 19:30
66 | Halishahar | 108 | 11:00 | 132 | Narinda | 76 | 13:00 | 198 | Ullon | 68 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14488.72 | 435 |  | 14943.3
1:00 | 14369.16 | 442 |  | 14831.05
2:00 | 13961.49 | 420 |  | 14400.39
3:00 | 13551.03 | 402 |  | 13971.03
4:00 | 13293.92 | 393 |  | 13704.92
5:00 | 13130.37 | 387 |  | 13534.37
6:00 | 12959.54 | 348 |  | 13323.54
7:00 | 12981.69 | 311 |  | 13306.69
8:00 | 12928.28 | 301 |  | 13243.28
9:00 | 13353.98 | 232 |  | 13595.98
10:00 | 13855.2 | 157 |  | 14019.2
11:00 | 14120.49 | 90 |  | 14214.54
12:00 | 14786.67 | 148 |  | 14941.67
13:00 | 14991.53 | 71 |  | 15065.53
14:00 | 14982.75 | 71 |  | 15056.95
15:00 | 14952.57 | 178 |  | 15138.57
16:00 | 15204.76 | 161 |  | 15373.01
17:00 | 14848.13 | 85 |  | 14936.96
18:00 | 14377.02 | 77 |  | 14457.49
19:00 | 15395.97 | 0 |  | 15395.97
19:30 | 16290.37 | 571 |  | 16887.07
20:00 | 16332.87 | 432 |  | 16783.87
21:00 | 16344.02 | 679 |  | 17054.02
22:00 | 16302.17 | 548 |  | 16875.17
23:00 | 16291.09 | 611 |  | 16929.59
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7454 | 7034.72 | 14488.72 | DAILY GENERATION CURVE
00:30 | 7317 | 7111.94 | 14428.94
01:00 | 7180 | 7189.16 | 14369.16 | 14-07-2026
01:30 | 7117 | 7048.325 | 14165.325
02:00 | 7054 | 6907.49 | 13961.49
02:30 | 6958 | 6798.26 | 13756.26
03:00 | 6862 | 6689.03 | 13551.03
03:30 | 6781.5 | 6640.975 | 13422.475
04:00 | 6701 | 6592.92 | 13293.92
04:30 | 6639 | 6573.145 | 13212.145
05:00 | 6577 | 6553.37 | 13130.37
05:30 | 6523.985 | 6520.97 | 13044.955
06:00 | 6470.97 | 6488.57 | 12959.54
06:30 | 6479.635 | 6490.98 | 12970.615
07:00 | 6488.3 | 6493.39 | 12981.69
07:30 | 6548.48 | 6406.505 | 12954.985
08:00 | 6608.66 | 6319.62 | 12928.28
08:30 | 6886.315 | 6254.815 | 13141.13
09:00 | 7163.97 | 6190.01 | 13353.98
09:30 | 7275.115 | 6329.475 | 13604.59
10:00 | 7386.26 | 6468.94 | 13855.2
10:30 | 7549.325 | 6438.52 | 13987.845
11:00 | 7712.39 | 6408.1 | 14120.49
11:30 | 7914.57 | 6539.01 | 14453.58
12:00 | 8116.75 | 6669.92 | 14786.67
12:30 | 8225.425 | 6663.675 | 14889.1
13:00 | 8334.1 | 6657.43 | 14991.53
13:30 | 8342.81 | 6644.33 | 14987.14
14:00 | 8351.52 | 6631.23 | 14982.75
14:30 | 8415.06 | 6552.6 | 14967.66
15:00 | 8478.6 | 6473.97 | 14952.57
15:30 | 8558.62 | 6520.045 | 15078.665
16:00 | 8638.64 | 6566.12 | 15204.76
16:30 | 8505.89 | 6520.555 | 15026.445
17:00 | 8373.14 | 6474.99 | 14848.13
17:30 | 8270.955 | 6341.62 | 14612.575
18:00 | 8168.77 | 6208.25 | 14377.02
18:30 | 8392.235 | 6494.26 | 14886.495
19:00 | 8615.7 | 6780.27 | 15395.97
19:30 | 9298.7 | 6991.67 | 16290.37
20:00 | 9242.7 | 7090.17 | 16332.87
20:30 | 9303.63 | 7034.815 | 16338.445 |  | Executive Engineer
21:00 | 9364.56 | 6979.46 | 16344.02 |  | Network Operation Division
21:30 | 9317.63 | 7005.465 | 16323.095
22:00 | 9270.7 | 7031.47 | 16302.17
22:30 | 9264.7 | 7031.93 | 16296.63
23:00 | 9258.7 | 7032.39 | 16291.09

## En-Curve
QF-LDC-12
Date | 14-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3401 | 2325 | 776 | 38 | 132 | 1453.72 | 222 | 5095 | 0 | 183 | 852 | 0 | 0 | 11 | 435 | DAILY ENERGY CURVE
00:30 | 3374.5 | 2245.5 | 824 | 38 | 132 | 1420.44 | 219.5 | 5120.5 | 0 | 174.5 | 866 | 0 | 0 | 14 | 438.5 | 14-07-2026
01:00 | 3348 | 2166 | 872 | 38 | 132 | 1387.16 | 217 | 5146 | 0 | 166 | 880 | 0 | 0 | 17 | 442
01:30 | 3382.5 | 2212.5 | 824.5 | 38 | 133 | 1392.325 | 217 | 5080 | 0 | 149 | 723.5 | 0 | 0 | 13 | 431 | Energy Generated | 352.6219 |  | MKWHr
02:00 | 3417 | 2259 | 777 | 38 | 134 | 1397.49 | 217 | 5014 | 0 | 132 | 567 | 0 | 0 | 9 | 420 | Energy not Served | 6.979 |  | MKWHr
02:30 | 3414 | 2228 | 777 | 38 | 130 | 1372.26 | 218 | 5026.5 | 0 | 132 | 407.5 | 0 | 0 | 13 | 411 | Total Energy Requirement | 359.6009 |  | MKWHr
03:00 | 3411 | 2197 | 777 | 38 | 126 | 1347.03 | 219 | 5039 | 0 | 132 | 248 | 0 | 0 | 17 | 402
03:30 | 3399 | 2247 | 825.5 | 38 | 126 | 1353.975 | 219 | 4881 | 0 | 127.5 | 189.5 | 0 | 0 | 16 | 397.5
04:00 | 3387 | 2297 | 874 | 38 | 126 | 1360.92 | 219 | 4723 | 0 | 123 | 131 | 0 | 0 | 15 | 393
04:30 | 3356.5 | 2271.5 | 874 | 38 | 126 | 1385.645 | 220 | 4674.5 | 0 | 123 | 131 | 0 | 0 | 12 | 390
05:00 | 3326 | 2246 | 874 | 38 | 126 | 1410.37 | 221 | 4626 | 0 | 123 | 131 | 0 | 0 | 9 | 387
05:30 | 3322 | 2254 | 874 | 38 | 120 | 1377.3 | 221.5 | 4560.5 | 13.655 | 123 | 131 | 0 | 0 | 10 | 367.5
06:00 | 3318 | 2262 | 874 | 38 | 114 | 1344.23 | 222 | 4495 | 27.31 | 123 | 131 | 0 | 0 | 11 | 348
06:30 | 3319.5 | 2263 | 874 | 38 | 115 | 1361.25 | 222 | 4439.5 | 71.365 | 123 | 131 | 0 | 0 | 13 | 329.5
07:00 | 3321 | 2264 | 874 | 38 | 116 | 1378.27 | 222 | 4384 | 115.42 | 123 | 131 | 0 | 0 | 15 | 311
07:30 | 3331 | 2278.5 | 873.5 | 38 | 110 | 1186.28 | 222 | 4441 | 183.205 | 123.5 | 145 | 0 | 0 | 23 | 306
08:00 | 3341 | 2293 | 873 | 38 | 104 | 994.29 | 222 | 4498 | 250.99 | 124 | 159 | 0 | 0 | 31 | 301
08:30 | 3418.5 | 2256.5 | 873.5 | 38 | 107 | 879.605 | 222 | 4645 | 286.025 | 165.5 | 225 | 0 | 0 | 24.5 | 266.5
09:00 | 3496 | 2220 | 874 | 38 | 110 | 764.92 | 222 | 4792 | 321.06 | 207 | 291 | 0 | 0 | 18 | 232
09:30 | 3511 | 2206.5 | 874 | 38 | 122 | 758.455 | 222 | 4904.5 | 341.635 | 221 | 389.5 | 0 | 0 | 16 | 194.5
10:00 | 3526 | 2193 | 874 | 38 | 134 | 751.99 | 222 | 5017 | 362.21 | 235 | 488 | 0 | 0 | 14 | 157
10:30 | 3569.5 | 2142 | 662 | 38 | 137 | 751.63 | 222 | 5092.5 | 457.715 | 249 | 653 | 0 | 0 | 13.5 | 123.5
11:00 | 3613 | 2091 | 450 | 38 | 140 | 751.27 | 222 | 5168 | 553.22 | 263 | 818 | 0 | 0 | 13 | 90
11:30 | 3542.5 | 2128.5 | 450.5 | 38 | 142 | 751.995 | 222 | 5229.5 | 587.085 | 273.5 | 1079 | 0 | 0 | 9 | 119
12:00 | 3472 | 2166 | 451 | 38 | 144 | 752.72 | 222 | 5291 | 620.95 | 284 | 1340 | 0 | 0 | 5 | 148
12:30 | 3409 | 2127 | 450.5 | 38 | 143 | 752.495 | 222 | 5292 | 648.605 | 301 | 1498.5 | 0 | 0 | 7 | 109.5
13:00 | 3346 | 2088 | 450 | 38 | 142 | 752.27 | 222 | 5293 | 676.26 | 318 | 1657 | 0 | 0 | 9 | 71
13:30 | 3379.5 | 2057 | 450 | 38 | 150 | 755.88 | 221.5 | 5272 | 640.76 | 318 | 1696.5 | 0 | 0 | 8 | 71
14:00 | 3413 | 2026 | 450 | 38 | 158 | 759.49 | 221 | 5251 | 605.26 | 318 | 1736 | 0 | 0 | 7 | 71
14:30 | 3438.5 | 2141.4 | 450 | 38 | 157 | 755.095 | 150.5 | 5252 | 507.165 | 317.5 | 1754 | 0 | 0 | 6.5 | 124.5
15:00 | 3464 | 2256.8 | 450 | 38 | 156 | 750.7 | 80 | 5253 | 409.07 | 317 | 1772 | 0 | 0 | 6 | 178
15:30 | 3449.5 | 2253.15 | 450 | 38 | 154 | 755 | 113 | 5294 | 362.815 | 349.5 | 1856.7 | 0 | 0 | 3 | 169.5
16:00 | 3435 | 2249.5 | 450 | 38 | 152 | 759.3 | 146 | 5335 | 316.56 | 382 | 1941.4 | 0 | 0 | 0 | 161
16:30 | 3408.5 | 2132.25 | 450 | 38 | 148 | 738.54 | 161 | 5289 | 245.255 | 422.5 | 1988.9 | 0 | 0 | 4.5 | 123
17:00 | 3382 | 2015 | 450 | 38 | 144 | 717.78 | 176 | 5243 | 173.95 | 463 | 2036.4 | 0 | 0 | 9 | 85
17:30 | 3337 | 1989.5 | 450 | 38 | 138 | 690.99 | 176 | 5119.5 | 109.685 | 504 | 2049.4 | 0 | 0 | 10.5 | 81
18:00 | 3292 | 1964 | 450 | 38 | 132 | 664.2 | 176 | 4996 | 45.42 | 545 | 2062.4 | 0 | 0 | 12 | 77
18:30 | 3359 | 2007 | 450 | 38 | 143 | 693.635 | 176 | 5220 | 22.71 | 599 | 2161.65 | 0 | 0 | 16.5 | 38.5
19:00 | 3426 | 2050 | 450 | 38 | 154 | 723.07 | 176 | 5444 | 0 | 653 | 2260.9 | 0 | 0 | 21 | 0
19:30 | 3489 | 2305 | 450 | 38 | 156 | 739.47 | 176 | 5625 | 0 | 739 | 2553.9 | 0 | 0 | 19 | 571
20:00 | 3451 | 2307 | 450 | 38 | 134 | 735.97 | 176 | 5684 | 0 | 794 | 2551.9 | 0 | 0 | 11 | 432
20:30 | 3460.5 | 2362 | 402.5 | 38 | 129 | 706.615 | 176 | 5714.5 | 0 | 789.5 | 2548.83 | 0 | 0 | 11 | 555.5
21:00 | 3470 | 2417 | 355 | 38 | 124 | 677.26 | 176 | 5745 | 0 | 785 | 2545.76 | 0 | 0 | 11 | 679
21:30 | 3471 | 2406.25 | 353.5 | 38 | 128 | 700.765 | 199 | 5744.5 | 0 | 779.5 | 2490.58 | 0 | 0 | 12 | 613.5
22:00 | 3472 | 2395.5 | 352 | 38 | 132 | 724.27 | 222 | 5744 | 0 | 774 | 2435.4 | 0 | 0 | 13 | 548
22:30 | 3487.5 | 2421 | 352 | 38 | 131 | 728.73 | 222 | 5746.5 | 0 | 766.5 | 2383.4 | 0 | 0 | 20 | 579.5
23:00 | 3503 | 2446.5 | 352 | 38 | 130 | 733.19 | 222 | 5749 | 0 | 759 | 2331.4 | 0 | 0 | 27 | 611
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 14-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 114 | 34 | 450 | 190 | 1660 | 548 | Ishurdi-Ghorashal Ckt-1 | Export | 2410400
1:00 | 135 | 35 | 480 | 176 | 1718 | 572
2:00 | 125 | 44 | 480 | 186 | 1660 | 574 |  | Import | 43490.91
3:00 | 126 | 44 | 470 | 180 | 1644 | 574
4:00 | 138 | 36 | 500 | 168 | 1558 | 552 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 151 | 38 | 540 | 154 | 1670 | 494
6:00 | 157 | 38 | 550 | 152 | 1662 | 500 |  | Import | 0
7:00 | 160 | 36 | 560 | 162 | 1536 | 504
8:00 | 168 | 44 | 530 | 170 | 1736 | 506 | Sirajganj-Sreepur Ckt-1 | Export | 2221000
9:00 | 169 | 56 | 450 | 170 | 1696 | 606
10:00 | 170 | 54 | 470 | 188 | 1886 | 626 |  | Import | 0
11:00 | 128 | 66 | 420 | 180 | 1834 | 610
12:00 | 116 | 65 | 394 | 190 | 1816 | 616 | Sirajganj-Sreepur Ckt-2 | Export | 2229000
13:00 | 80 | 42 | 350 | 164 | 1690 | 540
14:00 | 90 | 46 | 340 | 164 | 1664 | 530 |  | Import | 0
15:00 | 104 | 61 | 370 | 188 | 1706 | 600
16:00 | 90 | 55 | 334 | 180 | 1668 | 576 | Gopalganj-Aminbazar Ckt-1 | Export | 19730000
17:00 | 104 | 48 | 370 | 172 | 1700 | 604
18:00 | 97 | 49 | 330 | 180 | 1636 | 510 |  | Import | 0
18:30 | 82 | 31 | 320 | 164 | 1628 | 538
19:00 | 52 | 20 | 240 | 174 | 1668 | 428 | Gopalganj-Aminbazar Ckt-2 | Export | 19780000
19:30 | -4 | 26 | 92 | 156 | 1468 | 322
20:00 | 2 | 31 | 116 | 144 | 1518 | 318 |  | Import | 0
21:00 | -18 | 38 | 80 | 166 | 1428 | 316
22:00 | -13 | 38 | 124 | 176 | 1406 | 292 |  | Total Export | 46370400
23:00 | -15 | 32 | 130 | 190 | 1460 | 290 |  | Total Import | 43490.91
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 377 | 06:00 | 365 | 00:00 | Madunaghat | 394 | 19:00 | 382 | 00:00
Amtali | 413 | 04:00 | 403 | 19:30 | Meghnaghat | 385 | 06:00 | 372 | 07:00
Ashuganj | 408 | 5:00 | 395 | 16:00 | Payra | 415 | 07:00 | 406 | 19:30
Bhulta | 400 | 05:00 | 385 | 12:00 | Rahanpur | 405 | 08:00 | 385 | 21:00
Bibiana | 379 | 06:00 | 373 | 00:00 | Rampal | 397 | 06:00 | 379 | 19:30
BIPTC | 407 | 18:30 | 399 | 01:00
Bogura | 389 | 18:00 | 369 | 23:00
Gopalganj | 391 | 06:00 | 376 | 19:30
Kaliakoir | 364 | 06:00 | 352 | 11:00
Korerhat | 396 | 18:30 | 383 | 02:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 06:00 | 219 | 12:00 | Ishurdi | 236 | 05:00 | 224 | 19:00
AKSML | 235 | 18:00 | 225.9 | 03:00 | Jhenaidah | 230 | 06:00 | 209 | 19:30
Aminbazar | 230 | 06:00 | 221 | 16:00 | Kachua | 227 | 18:00 | 216 | 02:00
Ashuganj | 229 | 06:00 | 222 | 00:00 | Kaliakoir | 227 | 06:00 | 218 | 10:00
Ashuganj-400 | 229 | 06:00 | 222 | 00:00 | Keranigonj | 229 | 06:00 | 217 | 12:00
Baghabari | 234 | 05:00 | 224 | 19:30 | Khulna(S) | 229 | 09:00 | 205 | 23:00
Barapukuria | 226 | 15:00 | 215 | 19:30 | Korerhat | 226 | 18:00 | 217 | 03:00
Barapukuria-230 | 226 | 15:00 | 215 | 19:30 | Madunaghat | 240 | 18:00 | 230 | 03:00
Barishal | 228 | 18:00 | 220 | 23:00 | Madunaghat-400 | 241 | 19:00 | 232 | 00:00
Bheramara | 235 | 05:00 | 222 | 19:00 | Maniknagar | 228 | 03:00 | 217 | 12:00
Bhulta | 230 | 06:00 | 219 | 12:00 | Meghnaghat | 235 | 05:00 | 227 | 12:00
Bibiana | 220 | 07:00 | 215 | 00:00 | Meghnaghat-400 | 231 | 06:00 | 222 | 12:00
BIPTC | 237 | 05:00 | 222 | 19:00 | Mirsorai | 233 | 18:00 | 221 | 02:00
Bogura | 244 | 18:00 | 231 | 23:00 | Naogaon | 228 | 18:30 | 202 | 23:00
Bogura-400 | 244 | 18:00 | 231 | 23:00 | Purbasadipur | 224 | 13:00 | 209 | 20:00
Borhanuddin | 231 | 18:00 | 220 | 14:00 | Rajshahi | 234 | 06:00 | 220 | 00:00
BSRM | 227 | 18:00 | 219 | 03:00 | Rampal | 228 | 09:00 | 208 | 19:30
Charfasson | 231 | 17:00 | 224 | 22:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 226 | 18:00 | 215 | 02:00 | Rampura | 229 | 06:00 | 217 | 12:00
Cumilla(N) | 224 | 06:00 | 218 | 00:00 | Shikalbaha | 240 | 18:00 | 229 | 04:00
Faridpur | 224 | 05:00 | 213 | 23:00 | Shyampur | 230 | 19:30 | 218 | 12:00
Fenchuganj | 222 | 10:00 | 216 | 00:00 | Siddhirganj | 229 | 06:00 | 220 | 12:00
Feni | 225 | 18:00 | 216 | 02:00 | Sirajgonj | 241 | 18:00 | 235 | 19:30
Ghorashal | 230 | 06:00 | 225 | 00:00 | Sreepur | 224 | 18:00 | 217 | 00:00
Ghorashal-230 | 215 | 05:00 | 203 | 12:00 | Tongi | 217 | 04:00 | 203 | 10:00
Gopalganj | 225 | 06:00 | 217 | 19:30
GPH | 230 | 06:00 | 226 | 01:00
Haripur | 229 | 05:00 | 219 | 12:00
Hasnabad | 229 | 04:00 | 218 | 09:00
Hathazari | 236 | 18:00 | 229 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 05:00 | 121 | 22:00 | Madunaghat | 138 | 18:00 | 132 | 03:00
Agargaon | 133 | 06:00 | 124 | 12:00 | Magura | 136 | 18:00 | 122 | 00:00
Agrabad | 136 | 18:00 | 130 | 00:00 | Mahasthangarh | 136 | 08:00 | 126 | 19:30
AKS | 133 | 17:00 | 129 | 00:00 | Maijdee | 127 | 18:30 | 120 | 02:00
Aminbazar | 132 | 05:00 | 124 | 16:00 | Manikganj | 127 | 09:00 | 122 | 00:00
Amnura | 139 | 18:00 | 125 | 21:00 | Maniknagar | 135 | 05:00 | 125 | 12:00
Ashuganj | 131 | 04:00 | 126 | 00:00 | Matarbari | 124 | 08:00 | 113 | 00:00
Ashuganj-230 | 134 | 05:00 | 130 | 00:00 | Matuail | 132 | 04:00 | 127 | 12:00
Bagerhat | 133 | 09:00 | 111 | 23:00 | Metrorail_Motijheel | 135 | 05:00 | 126 | 13:00
Bajitpur | 125 | 04:00 | 118 | 23:00 | Metrorail_Uttara | 131 | 05:00 | 122 | 10:00
Bakerganj | 131 | 09:00 | 126 | 23:00 | Millgate | 132 | 05:00 | 122 | 12:00
Bakulia | 137 | 18:00 | 130 | 10:00 | Mirpur | 131 | 06:00 | 123 | 12:00
Banani | 134 | 04:00 | 124 | 12:00 | Mirzapur | 128 | 06:00 | 123 | 00:00
Bangabhaban | 134 | 07:00 | 125 | 12:00 | Mithapukur | 133 | 18:00 | 122 | 20:00
Barapukuria | 138 | 18:30 | 125 | 19:30 | MI_Cement | 135 | 06:00 | 125.2 | 12:00
Barguna | 131 | 18:00 | 126 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 03:00 | 127 | 23:00 | Mogbazar | 0 | 00:00 | N/A | N/A
Barishal-230 | 132 | 18:00 | 127 | 22:00 | Mongla | 132 | 09:00 | 113 | 23:00
Baroaulia | 138 | 18:30 | 131 | 00:00 | Motijheel | 135 | 06:00 | 125 | 12:00
Baroirhat | 132 | 18:00 | 127 | 00:00 | Muktagacha | 126 | 13:00 | 114 | 01:00
Bashundhara | 134 | 05:00 | 121 | 10:00 | Munshiganj | 131 | 06:00 | 127 | 10:00
BashundharaCement | 132 | 01:00 | 127 | 16:00 | Muradnagar | 127 | 18:30 | 119 | 11:00
Beanibazar | 126 | 10:00 | 117 | 00:00 | Mymensingh | 126 | 09:00 | 107 | 23:00
Benapole | 138 | 06:00 | 112 | 23:00 | Nabinagar | 128 | 05:00 | 119 | 12:00
Bhaluka | 124 | 14:00 | 117 | 00:00 | Naogaon | 138 | 18:30 | 122 | 23:00
Bhandaria | 129 | 18:30 | 121 | 23:00 | Narail | 137 | 18:00 | 120 | 00:00
Bhangura | 135 | 11:00 | 126 | 19:00 | Narinda | 135 | 05:00 | 125 | 12:00
Bheramara | 138 | 14:00 | 130 | 19:30 | Narshingdi | 128 | 08:00 | 118 | 16:00
Bheramara(GK) | 137 | 06:00 | 130 | 00:00 | Natore | 137 | 18:00 | 128 | 00:00
Bhulta | 127 | 06:00 | 121 | 16:00 | Nawabganj | 132 | 05:00 | 125 | 12:00
Bog-Sherpur | 137 | 08:00 | 130 | 19:30 | Netrakona | 115 | 04:00 | 105 | 23:00
Bogura | 139 | 09:00 | 132 | 19:30 | New | 132 | 05:00 | 124 | 10:00
Bogura-230 | 140 | 17:00 | 132 | 19:30 | Niamatpur | 134 | 07:00 | 125 | 21:00
Brahmanbaria | 128 | 05:00 | 124 | 00:00 | Noapara | 135 | 06:00 | 118 | 19:30
Cantonment | 132 | 05:00 | 124 | 15:00 | Pabna | 135 | 05:00 | 127 | 19:30
Chandina | 130 | 18:30 | 124 | 00:00 | Palashbari | 132 | 18:30 | 120 | 19:30
Chandpur | 133 | 19:30 | 120 | 02:00 | Panchagarh | 139 | 18:00 | 127 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 138 | 18:00 | 134 | 00:00 | Patiya | 136 | 18:30 | 129 | 00:00
Chapai | 133 | 17:00 | 127 | 00:00 | Patnitala | 134 | 18:00 | 125 | 19:30
Charsaidpur | 132 | 05:00 | 127 | 12:00 | Patuakhali | 132 | 18:00 | 127 | 00:00
Chauddagram | 130 | 18:30 | 124 | 00:00 | Payra | 134 | 06:00 | 131 | 23:00
Chhatak | 125 | 10:00 | 114 | 00:00 | PHP | 131 | 18:00 | 125 | 02:00
Chowmuhani | 127 | 18:00 | 120 | 02:00 | Postogola | 137 | 07:00 | 128 | 12:00
Chuadanga | 137 | 05:00 | 120 | 19:30 | Pubail | 129 | 21:00 | 120 | 15:00
Coxsbazar | 125 | 18:00 | 112 | 00:00 | Purbachal | 134 | 05:00 | 124 | 12:00
Cumilla(N) | 129 | 18:00 | 125 | 00:00 | Purbasadipur | 136 | 18:00 | 126 | 20:00
Cumilla(S) | 130 | 18:00 | 122 | 14:00 | Rahanpur | 136 | 18:00 | 127 | 23:00
Daganbhuiyan | 130 | 18:30 | 123 | 02:00 | Rahanpur-400 | 136 | 08:00 | 128 | 21:00
Daudkandi | 125 | 18:00 | 114 | 12:00 | Rahim | 133 | 07:00 | 128 | 12:00
DhakaUniversity | 134 | 05:00 | 125 | 12:00 | Rajbari | 127 | 06:00 | 119 | 23:00
Dhamrai | 129 | 04:00 | 121 | 12:00 | Rajendrapur | 123 | 14:00 | 117 | 00:00
Dhanmondi | 134.7 | 06:00 | 127 | 16:00 | Rajshahi | 134 | 06:00 | 126 | 19:30
Dohazari | 131 | 17:00 | 124 | 00:00 | Rajshahi-230 | 134 | 06:00 | 126 | 00:00
Faridpur | 128 | 05:00 | 123 | 23:00 | Ramganj | 127 | 19:30 | 118 | 02:00
Fatullah | 135 | 05:00 | 126 | 12:00 | Rampur | 136 | 18:00 | 131 | 00:00
Fenchuganj | 131 | 10:00 | 126 | 00:00 | Rampura | 134 | 05:00 | 125 | 12:00
Feni | 130 | 18:00 | 126 | 00:00 | Rangamati | 137 | 18:30 | 133 | 00:00
Feni-230 | 131 | 18:00 | 125 | 00:00 | Rangpur | 132 | 18:30 | 121 | 23:00
Ghatail | 126 | 09:00 | 116 | 19:00 | Ruppur | 138 | 08:00 | 130 | 19:30
Ghorashal | 130 | 02:00 | 123 | 10:00 | Saidpur | 134 | 13:00 | 125 | 19:30
Goalpara | 137 | 09:00 | 120 | 19:30 | Santhia | 136 | 08:00 | 129 | 19:30
Gollamari | 138 | 09:00 | 122 | 23:00 | Satkhira | 136 | 09:00 | 113 | 19:30
Gopalganj | 132 | 18:30 | 123 | 00:00 | Satmasjid | 131 | 05:00 | 123 | 12:00
Gopalganj-400 | 131 | 05:00 | 126 | 22:00 | Savar | 130 | 06:00 | 122 | 12:00
Gulshan | 134 | 06:00 | 125 | 12:00 | SevenRings | 130 | 05:00 | 122 | 12:00
Halishahar | 137 | 18:30 | 131 | 00:00 | ShahCement | 132 | 05:00 | 127 | 12:00
Haripur | 133 | 05:00 | 128 | 12:00 | Shahjadpur | 138 | 18:00 | 131 | 19:30
HaripurSBU | 133 | 05:00 | 128 | 16:00 | Shahjibazar | 129 | 07:00 | 122 | 00:00
Hasnabad | 136 | 04:00 | 127 | 12:00 | Shahmirpur | 136 | 18:00 | 131 | 00:00
Hathazari | 139 | 20:00 | 133 | 00:00 | Shariatpur | 129 | 06:00 | 121 | 00:00
Hatirjheel | 134 | 05:00 | 125 | 12:00 | Sherpur | 128 | 09:00 | 110 | 02:00
Ishurdi | 139 | 06:00 | 131 | 19:30 | Shikalbaha | 136 | 18:00 | 131 | 00:00
Jaldhaka | 133 | 13:00 | 121 | 19:30 | Shikalbaha-230 | 138 | 18:00 | 132 | 00:00
Jamalpur | 130 | 20:00 | 113 | 19:00 | Shitalakhya | 135 | 06:00 | 125.2 | 12:00
Jashore | 140 | 09:00 | 115 | 22:00 | Sholosohor | 137 | 17:00 | 131 | 00:00
Jhenaidah | 142 | 09:00 | 123 | 00:00 | Shomvuganj | 118 | 05:00 | 112 | 23:00
Jhenaidah-230 | 141 | 06:00 | 126 | 19:30 | Shyampur | 133 | 04:00 | 126 | 12:00
Joydebpur | 128 | 19:30 | 117 | 11:00 | Shyampur-230 | 134 | 05:00 | 127 | 12:00
Joypurhat | 135 | 18:30 | 125 | 21:00 | Siddhirganj | 133 | 04:00 | 128 | 15:00
Juldah | 136 | 17:00 | 130 | 01:00 | Sirajganj | 134 | 11:00 | 125 | 19:30
Kabirpur | 129 | 06:00 | 118 | 11:00 | Sitakunda | 137 | 18:00 | 130 | 04:00
Kachua | 130 | 19:30 | 121 | 03:00 | Sonargaon | 130 | 05:00 | 125 | 16:00
Kaliakoir | 134 | 06:00 | 127 | 10:00 | Sreemongol | 128 | 07:00 | 122 | 00:00
Kaliganj | 141 | 09:00 | 124 | 19:30 | Sreepur | 126 | 13:00 | 121 | 00:00
Kallyanpur | 131 | 05:00 | 123 | 12:00 | Srinagar | 133 | 05:00 | 125 | 12:00
Kalurghat | 138 | 18:00 | 133 | 00:00 | SSM | 140 | 13:00 | 135 | 00:00
Kamrangirchar | 133 | 05:00 | 121 | 12:00 | Sunamganj | 125 | 10:00 | 111 | 01:00
Kaptai | 140 | 0:00 | 136 | 1:00 | Sylhet | 126 | 10:00 | 120 | 02:00
Kasba | 127 | 18:30 | 119 | 11:00 | Sylhet_(South) | 126 | 10:00 | 119 | 01:00
Kazla | 134 | 05:00 | 125 | 13:00 | Tangail | 127 | 09:00 | 116 | 19:00
Keranigonj | 134 | 06:00 | 125 | 12:00 | Taraganj | 133 | 18:00 | 122 | 19:30
Khagrachori | 136 | 17:00 | 131 | 02:00 | Tasnim | 130 | 05:00 | 125 | 16:00
Khulna | 137 | 09:00 | 119 | 23:00 | Thakurgaon | 138 | 13:00 | 126 | 10:00
Khulna(S) | 138 | 09:00 | 121 | 23:00 | TK | 138 | 18:00 | 133 | 00:00
Khulshi | 135 | 18:30 | 130 | 00:00 | Tongi | 134 | 04:00 | 125 | 10:00
Kishoreganj | 123 | 05:00 | 116 | 23:00 | Ullahpara | 135 | 11:00 | 127 | 19:30
Kodda | 130 | 17:00 | 119 | 15:00 | Ullon | 134 | 05:00 | 125 | 12:00
Korerhat | 133 | 18:00 | 128 | 02:00 | Uttara | 132 | 05:00 | 120 | 12:00
KSRM | 137 | 19:30 | 132 | 00:00 | UttaraNew | 131 | 05:00 | 122 | 10:00
Kulaura | 128 | 04:00 | 124 | 19:00 | Zigatola | 133 | 05:00 | 126 | 12:00
Kurigram | 130 | 13:00 | 117 | 19:30
Kushtia | 135 | 06:00 | 125 | 19:30
Laksam | 129 | 18:30 | 122 | 00:00
Lakshmipur | 126 | 18:00 | 119 | 02:00
Lalbag | 132 | 07:00 | 124 | 12:00
Lalmonirhat | 129 | 11:00 | 117 | 20:00
Madanganj | 132 | 01:00 | 127 | 16:00
Madaripur | 131 | 18:30 | 124 | 23:00
Madartek | 133 | 05:00 | 124 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division