## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-07-2026 | during | 19-07-2026 | during | 19-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 378 | 349 | 412 | 412 | 370.8 | 370.8 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 307 | 302 | 335 | 335 | 250 | 250 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 315 | 309 | 335 | 335 | 315 | 315 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 17 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 47 | 141 | 149.36 | 149.36 | 149.36 | 149.36 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 14 | 13 | 33 | 33 | 17 | 17 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 12 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 24 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 195 | 300 | 300 | 48 | 48 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 53 | 149 | 149 | 149 | 34 | 34 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 7 | 105 | 105 | 105 | 17 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 12 | 0 | 12 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 455 | 490 | 583 | 583 | 524.5 | 524.5 | AGC+FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 520 | 480 | 718 | 718 | 658 | 658 | AGC+FGMO
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 105 | 143 | 143 | 143 | 143 | 143 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2350 | 2830 | 5787.22 | 5775.22 | 2728.66 | 2946.66
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 10 | 0 | 11 | 0 | 11 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 220 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 208 | 180 | 215 | 220 | 0 | 0 | Tripped at 22:35(18/7/26)
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 24 | 56 | 24 | 56 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 34 | 0 | 34 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 8 | 6 | 5 | 24 | 30 | 40 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 24 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.45 | 0 | 5.25 | 0 | 5.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 17 | 54.36 | 54.36 | 54 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 33 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 15 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1130 | 1160 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 14 | 20 | 26 | 34 | 26 | 34 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 1125 | 1150 | 1150 | 1065 | 1065 | AGC
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2766.45 | 2885 | 4114.11 | 4195.86 | 3197.25 | 3307
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 210 | 185 | 221.25 | 221.25 | 221.25 | 221.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 290 | 270 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 220 | 220 | 342.01 | 342.01 | 230 | 230 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 210 | 210 | 393 | 393 | 240 | 240 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 37 | 10 | 41.65 | 41.65 | 40 | 40 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 5 | 5 | 52.82 | 52.82 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 20 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 24 | 24 | 32 | 32 | 48 | 48 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 92 | 163 | 163 | 95 | 95 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 16 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 140 | 134 | 84 | 76 | 150 | 150 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 2 | 28 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 32 | 115 | 115 | 34 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 58 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1351 | 1316 | 2754.44 | 2686.44 | 1761.46 | 1969.46
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-07-2026 | during | 19-07-2026 | during | 19-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 4.73 | 0 | 15 | 0 | 15 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 47 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 48 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 44.56 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 18 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 147.29 | 130 | 529.6 | 516.5 | 260.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 28 | 28 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 142 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 143 | 143 | 142 | 142 | 142 | 142 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 84 | 84 | 84 | 86 | 86 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 100 | 0 | 0 | 100 | 100 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 16 | 16 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 17 | 25 | 25 | 16 | 16 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 305 | 228 | 250 | 250 | 250 | 250 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1064 | 1082 | 1121 | 1121 | 1076 | 1076
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 896 | 849 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 65 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 32 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 69 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 955 | 1200 | 1234.2 | 1234.2 | 1194 | 1194 | AGC
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1958 | 2152 | 3616.2 | 3536.2 | 2426 | 2346
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 700 | 1050 | 700 | 1050 | 700 | 1050 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 924 | 1155 | 1163.05 | 1163.05 | 1184 | 1184 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 203 | 307 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.34 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3407.64 | 2167.34 | 2869 | 2781.05 | 3130.05 | 2649 | 2998
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 42.57 | 0 | 60 | 0 | 60 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 166 | 152 | 214 | 214 | 170 | 170 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 134 | 128 | 220 | 220 | 150 | 150 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 141 | 131 | 220 | 220 | 150 | 150 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 356 | 316 | 413.79 | 413.79 | 413.79 | 413.79 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 22 | 22 | 22 | 22 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 0 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1214.79 | 1491.5 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 44.57 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 44 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2142.93 | 2253.5 | 3259.72 | 3033.12 | 2681.52 | 2616.92
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 40 | 40 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 180 | 180 | 185 | 185 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.4 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 35 | 0 | 153.16 | 0 | 153.16 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 231.4 | 300 | 614.16 | 428 | 546.16 | 395
System Total |  |  |  |  | 28843.2 | 29250.117 | 14178.41 | 15817.5 | 24577.5 | 24422.39 | 17326 | 17914
Forecast Scenario (19-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15600 |  | 0 |  | 15600
|  |  |  | 1:00 | 15030 |  | 0 |  | 15030
|  |  |  | 2:00 | 14300 |  | 0 |  | 14300
|  |  |  | 3:00 | 13820 |  | 0 |  | 13820
|  |  |  | 4:00 | 13450 |  | 0 |  | 13450
|  |  |  | 5:00 | 13200 |  | 0 |  | 13200
|  |  |  | 6:00 | 12900 |  | 0 |  | 12900
|  |  |  | 7:00 | 12830 |  | 0 |  | 12830
|  |  |  | 8:00 | 12940 |  | 0 |  | 12940
|  |  |  | 9:00 | 13230 |  | 0 |  | 13230
|  |  |  | 10:00 | 13460 |  | 0 |  | 13460
|  |  |  | 11:00 | 13660 |  | 0 |  | 13660
|  |  |  | 12:00 | 14200 |  | 0 |  | 14200
|  |  |  | 13:00 | 14600 |  | 0 |  | 14600
|  |  |  | 14:00 | 14130 |  | 0 |  | 14130
|  |  |  | 15:00 | 14270 |  | 0 |  | 14270
|  |  |  | 16:00 | 14050 |  | 0 |  | 14050
|  |  |  | 17:00 | 14040 |  | 0 |  | 14040
|  |  |  | 18:00 | 14180 |  | 0 |  | 14180
|  |  |  | 18:30 | 14800 |  | 0 |  | 14800
|  |  |  | 19:00 | 15430 |  | 0 |  | 15430
|  |  |  | 19:30 | 16750 |  | 0 |  | 16750
|  |  |  | 20:00 | 16800 |  | 0 |  | 16800
|  |  |  | 21:00 | 16780 |  | 0 |  | 16780
|  |  |  | 22:00 | 16550 |  | 0 |  | 16550
|  |  |  | 23:00 | 16490 |  | 0 |  | 16490
Probable Maximum Temperature: |  |  | 32.90°C
Probable Maximum Demand at Day Peak: |  |  | 14200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 344.41501 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:56 hrs on 19-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-07-2026 | [28 empty] | Date: | 18-07-2026 | [28 empty] | Date: | 18-07-2026 | [28 empty] | Date: | 18-07-2026 | [28 empty] | Date: | 18-07-2026 | [18 empty] | Date: | 18-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [18 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 419 | 35 | 17 | 111 | 110 | 15 | 15 | 17 | 16 | 0 | 0 | 287 | 445 | 0 | 17 | 295 | 0 | 0 | 0 | 143 | 15 | 14 | 0 | 0 | 16 | 16 | 12 | 0 | 18 | 34 | 30 | 54.36 | 0 | 0 | 0 | 222 | 55 | 42 | 730 | 15 | 0 | 19 | 8 | 17 | 212 | 0 | 0 | 0 | 1160 | 0 | 40 | 0 | 220 | 290 | 77 | 51 | 35 | 203 | 40 | 61 | 93 | 17 | 0 | 19 | 17 | 126 | 0 | 0 | 24 | 305 | 0 | 306 | 40 | 0 | 145 | 0 | 17 | 0 | 86 | 0 | 143 | 16 | 122 | 17 | 48 | 0 | 153 | 0 | 0 | 0 | 0 | 7764.36 | 826 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1212 | 0 | 0 | 0 | 1419.85 | 0 | 40 | 0 | 35 | 50 | 0 | 52 | 27 | 8 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 145 | 0 | 149 | 0 | 393 | 0 | 0 | 180 | 0 | 89 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 270 | 120 | 220 | 0 | 800 | 1163 | 15 | 7472.85 | 15237.21 | 104.14
01:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 423 | 0 | 17 | 79 | 144 | 0 | 30 | 0 | 14 | 0 | 0 | 287 | 385 | 0 | 17 | 300 | 0 | 0 | 0 | 143 | 15 | 20 | 0 | 0 | 0 | 0 | 9 | 0 | 24 | 34 | 0 | 54.36 | 0 | 0 | 0 | 222 | 102 | 42 | 745 | 0 | 0 | 14 | 0 | 16 | 212 | 0 | 0 | 0 | 1143 | 0 | 40 | 0 | 220 | 290 | 125 | 51 | 30 | 219 | 40 | 89 | 93 | 17 | 0 | 19 | 0 | 128 | 0 | 0 | 24 | 300 | 0 | 306 | 40 | 0 | 122 | 0 | 17 | 0 | 86 | 0 | 143 | 16 | 0 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7377.36 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1212 | 0 | 0 | 0 | 1481.2 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 150 | 0 | 150 | 0 | 350 | 0 | 0 | 180 | 0 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 273 | 120 | 180 | 0 | 600 | 1163 | 15 | 7119.2 | 14496.56 | 104.11
02:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 455 | 0 | 0 | 37 | 144 | 0 | 30 | 0 | 0 | 0 | 0 | 294 | 400 | 0 | 0 | 307 | 0 | 0 | 0 | 143 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 65 | 42 | 730 | 0 | 0 | 0 | 0 | 15 | 207 | 0 | 0 | 0 | 1160 | 0 | 20 | 0 | 220 | 290 | 150 | 51 | 25 | 203 | 40 | 0 | 93 | 17 | 0 | 19 | 0 | 128 | 0 | 0 | 24 | 305 | 0 | 306 | 40 | 0 | 142 | 0 | 17 | 0 | 86 | 0 | 144 | 16 | 0 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7137 | 848 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1211 | 0 | 0 | 0 | 1428.37 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 150 | 0 | 152 | 0 | 404 | 0 | 0 | 180 | 0 | 69 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 120 | 220 | 0 | 500 | 1148 | 0 | 6974.37 | 14111.37 | 104.11
03:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 440 | 0 | 0 | 31 | 46 | 0 | 30 | 0 | 0 | 0 | 0 | 292 | 395 | 0 | 0 | 300 | 0 | 0 | 0 | 143 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 34 | 42 | 820 | 0 | 0 | 0 | 0 | 10 | 207 | 0 | 0 | 0 | 1153 | 0 | 0 | 0 | 220 | 290 | 250 | 51 | 25 | 198 | 40 | 0 | 93 | 0 | 0 | 19 | 0 | 122 | 0 | 0 | 24 | 305 | 0 | 306 | 40 | 0 | 129 | 0 | 17 | 0 | 86 | 0 | 143 | 16 | 0 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7057 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1194 | 0 | 0 | 0 | 1312.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 150 | 0 | 153 | 0 | 414 | 0 | 0 | 180 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 120 | 220 | 0 | 500 | 1070 | 0 | 6650.64 | 13707.64 | 104.11
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 486 | 0 | 0 | 34 | 46 | 0 | 30 | 0 | 0 | 0 | 0 | 302 | 400 | 0 | 0 | 310 | 0 | 0 | 0 | 143 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 42 | 820 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 1090 | 0 | 0 | 0 | 210 | 290 | 260 | 51 | 20 | 193 | 40 | 0 | 93 | 0 | 0 | 19 | 0 | 114 | 0 | 0 | 24 | 310 | 0 | 330 | 40 | 0 | 142 | 0 | 17 | 0 | 86 | 0 | 143 | 16 | 0 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7057 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1038 | 0 | 0 | 0 | 1310.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 156 | 0 | 154 | 0 | 414 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 120 | 220 | 0 | 500 | 1020 | 0 | 6400.26 | 13457.26 | 104.1
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 438 | 0 | 0 | 34 | 46 | 0 | 15 | 0 | 0 | 0 | 0 | 292 | 400 | 0 | 0 | 300 | 0 | 0 | 0 | 143 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 42 | 820 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 210 | 290 | 240 | 51 | 10 | 196 | 40 | 0 | 93 | 0 | 0 | 19 | 0 | 118 | 0 | 0 | 24 | 305 | 0 | 316 | 40 | 0 | 143 | 0 | 17 | 0 | 86 | 0 | 144 | 16 | 0 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 6891 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1019 | 0 | 0 | 0 | 1298.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 157 | 0 | 154 | 0 | 414 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 120 | 220 | 0 | 500 | 1026 | 0 | 6351.59 | 13242.59 | 104.1
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 445 | 0 | 0 | 34 | 46 | 0 | 15 | 0 | 0 | 0 | 0 | 296 | 390 | 0 | 0 | 306 | 0 | 0 | 0 | 143 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0.18 | 218 | 0 | 42 | 750 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 950 | 1 | 0 | 0 | 210 | 290 | 220 | 51 | 10 | 207 | 40 | 0 | 93 | 0 | 0 | 19 | 0 | 116 | 0 | 1 | 24 | 305 | 0 | 318 | 40 | 0 | 130 | 0 | 17 | 0 | 86 | 0 | 143 | 16 | 0 | 0 | 48 | 0.04 | 48 | 0 | 0.1 | 1.13 | 0 | 6698.45 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4.3 | 978 | 0 | 0 | 0 | 1204.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 0 | 0 | 0 | 0.6 | 163 | 0 | 157 | 0 | 154 | 0 | 414 | 0 | 0 | 180 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 0.03 | 0 | 170 | 120 | 220 | 0 | 500 | 992 | 0 | 6197.08 | 12895.53 | 104.1
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 447 | 0 | 0 | 34 | 46 | 0 | 15 | 0 | 0 | 0 | 0 | 294 | 395 | 0 | 0 | 306 | 0 | 0 | 0 | 123 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0.93 | 219 | 0 | 39 | 750 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 950 | 2 | 0 | 0 | 210 | 290 | 220 | 51 | 6 | 211 | 40 | 0 | 93 | 0 | 0 | 19 | 0 | 112 | 0 | 8 | 24 | 310 | 0 | 318 | 40 | 0 | 133 | 1 | 17 | 0 | 86 | 0 | 142 | 16 | 0 | 0 | 48 | 1.1 | 48 | 0 | 0.4 | 5.61 | 0 | 6726.04 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17.52 | 945 | 0 | 0 | 0 | 1127.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9 | 15 | 0 | 0 | 6.56 | 166 | 0 | 157 | 0 | 154 | 0 | 414 | 0 | 0.69 | 180 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.5 | 14 | 0.04 | 0 | 170 | 120 | 220 | 0 | 500 | 940 | 0 | 6094.83 | 12820.87 | 104.1
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 498 | 0 | 0 | 34 | 46 | 0 | 15 | 0 | 0 | 0 | 0 | 302 | 395 | 0 | 0 | 314 | 0 | 0 | 0 | 105 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 3.32 | 220 | 0 | 15 | 750 | 0 | 0 | 29 | 0 | 0 | 207 | 0 | 0 | 0 | 906 | 9 | 0 | 0 | 210 | 290 | 220 | 51 | 5 | 212 | 40 | 0 | 92 | 0 | 0 | 19 | 0 | 114 | 0 | 25 | 24 | 305 | 0 | 318 | 40 | 0 | 135 | 2 | 17 | 0 | 84 | 0 | 141 | 16 | 0 | 0 | 48 | 2.6 | 48 | 0 | 0.8 | 2.22 | 0 | 6740.94 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 29.7 | 917 | 0 | 0 | 0 | 1104.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.79 | 56 | 0 | 0 | 6.43 | 166 | 0 | 156 | 0 | 151 | 0 | 414 | 0 | 0.52 | 180 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0.2 | 38 | 0.21 | 0 | 171 | 120 | 220 | 0 | 500 | 915 | 0 | 6096.62 | 12837.56 | 104.09
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 450 | 0 | 0 | 44 | 46 | 0 | 15 | 0 | 0 | 0 | 0 | 291 | 445 | 0 | 0 | 314 | 0 | 0 | 0 | 105 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 2.59 | 220 | 0 | 4 | 880 | 0 | 0 | 50 | 0 | 0 | 208 | 0 | 0 | 0 | 1003 | 13 | 0 | 0 | 210 | 290 | 220 | 51 | 5 | 203 | 40 | 0 | 93 | 0 | 0 | 19 | 0 | 130 | 0 | 34 | 24 | 315 | 0 | 318 | 40 | 0 | 148 | 8 | 17 | 0 | 84 | 0 | 142 | 16 | 0 | 0 | 48 | 7.6 | 48 | 0 | 0.8 | 20.36 | 0 | 7082.35 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 60.14 | 935 | 0 | 0 | 0 | 1138.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.11 | 57 | 0 | 0 | 35.56 | 166 | 0 | 152 | 0 | 148 | 0 | 397 | 0 | 2.02 | 180 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0.3 | 47 | 0.43 | 0 | 170 | 120 | 220 | 0 | 500 | 970 | 0 | 6273.03 | 13355.38 | 104.09
10:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 491 | 17 | 0 | 53 | 47 | 0 | 10 | 13 | 0 | 0 | 0 | 303 | 450 | 0 | 0 | 314 | 0 | 0 | 0 | 105 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 3.21 | 220 | 0 | 5 | 1025 | 0 | 0 | 50 | 0 | 0 | 208 | 0 | 0 | 0 | 1005 | 1 | 0 | 0 | 210 | 290 | 220 | 51 | 5 | 208 | 36 | 0 | 92 | 0 | 0 | 19 | 0 | 122 | 0 | 47 | 24 | 305 | 0 | 318 | 40 | 0 | 135 | 5 | 8 | 0 | 84 | 0 | 143 | 16 | 0 | 0 | 48 | 9.37 | 48 | 0 | 1.1 | 11.16 | 0 | 7250.84 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 957 | 0 | 0 | 0 | 1091.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.34 | 90 | 0 | 0 | 42.34 | 166 | 0 | 142 | 0 | 145 | 0 | 384 | 0 | 2.71 | 180 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0.1 | 28 | 0.74 | 0 | 173 | 120 | 220 | 0 | 500 | 928 | 0 | 6155.63 | 13406.47 | 104.08
11:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 507 | 17 | 0 | 53 | 47 | 0 | 15 | 35 | 0 | 0 | 0 | 308 | 450 | 0 | 0 | 311 | 0 | 0 | 0 | 105 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 4.78 | 220 | 0 | 8 | 1125 | 0 | 0 | 50 | 0 | 0 | 208 | 0 | 0 | 0 | 1003 | 7 | 0 | 0 | 210 | 290 | 220 | 51 | 5 | 211 | 36 | 0 | 92 | 0 | 0 | 19 | 0 | 130 | 0 | 24 | 24 | 305 | 0 | 318 | 40 | 0 | 143 | 7 | 8 | 0 | 83 | 0 | 143 | 16 | 0 | 0 | 48 | 6.85 | 48 | 0 | 2 | 14.57 | 0 | 7421.2 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 955 | 0 | 0 | 0 | 1099.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 70 | 0 | 0 | 50.44 | 166 | 0 | 135 | 0 | 143 | 0 | 368 | 0 | 0 | 180 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0.3 | 81 | 0.89 | 0 | 171 | 120 | 220 | 0 | 500 | 917 | 0 | 6192.52 | 13613.72 | 104.07
12:00 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 520 | 17 | 0 | 53 | 47 | 45 | 15 | 35 | 0 | 0 | 0 | 307 | 455 | 0 | 0 | 315 | 0 | 0 | 0 | 105 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 1.45 | 220 | 0 | 8 | 1125 | 0 | 0 | 50 | 0 | 0 | 208 | 0 | 0 | 0 | 1130 | 10 | 0 | 0 | 210 | 290 | 220 | 51 | 5 | 210 | 37 | 0 | 90 | 0 | 2 | 14 | 0 | 140 | 0 | 58 | 24 | 310 | 0 | 305 | 40 | 0 | 152 | 7 | 8 | 0 | 83 | 0 | 143 | 16 | 0 | 0 | 49 | 4.73 | 48 | 0 | 1 | 44.56 | 0 | 7678.74 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69 | 955 | 0 | 0 | 0 | 1214.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.57 | 44 | 0 | 0 | 44.57 | 166 | 0 | 134 | 0 | 141 | 0 | 356 | 0 | 0 | 180 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0.4 | 35 | 0.34 | 0 | 203 | 120 | 220 | 0 | 700 | 924 | 0 | 6499.67 | 14178.41 | 103.92
13:00 | 0 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 418 | 17 | 0 | 53 | 47 | 145 | 15 | 35 | 17 | 0 | 0 | 295 | 445 | 0 | 0 | 290 | 0 | 0 | 0 | 105 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 1.78 | 220 | 0 | 8 | 1125 | 0 | 0 | 50 | 0 | 0 | 208 | 0 | 0 | 0 | 1120 | 5 | 0 | 0 | 210 | 290 | 220 | 51 | 5 | 211 | 37 | 0 | 91 | 0 | 0 | 19 | 0 | 140 | 0 | 47 | 24 | 300 | 0 | 305 | 40 | 0 | 138 | 3 | 8 | 0 | 83 | 0 | 143 | 16 | 0 | 0 | 48 | 17.25 | 48 | 0 | 1.2 | 27.6 | 0 | 7628.83 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 84 | 950 | 0 | 0 | 0 | 1489.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.95 | 82 | 0 | 0 | 60.67 | 166 | 0 | 130 | 0 | 138 | 0 | 353 | 0 | 0 | 180 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 1.3 | 56 | 0.23 | 0 | 212 | 120 | 220 | 0 | 700 | 924 | 0 | 6886.07 | 14514.9 | 103.92
14:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 453 | 20 | 0 | 53 | 47 | 195 | 0 | 35 | 17 | 0 | 0 | 306 | 450 | 0 | 17 | 307 | 0 | 0 | 0 | 105 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 2.45 | 220 | 0 | 4 | 1125 | 0 | 0 | 50 | 0 | 0 | 208 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 210 | 290 | 220 | 51 | 5 | 205 | 36 | 0 | 91 | 0 | 0 | 19 | 0 | 148 | 0 | 36 | 24 | 310 | 0 | 228 | 40 | 0 | 138 | 5 | 8 | 0 | 83 | 0 | 142 | 16 | 0 | 0 | 48 | 20.46 | 48 | 0 | 2.6 | 21.21 | 0 | 7700.72 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79 | 908 | 0 | 0 | 0 | 1420.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.92 | 23 | 0 | 0 | 58.31 | 165 | 0 | 128 | 0 | 137 | 0 | 342 | 0 | 0 | 180 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 2.8 | 82 | 0.75 | 0 | 247 | 120 | 220 | 0 | 700 | 925 | 0 | 6683.24 | 14383.96 | 103.9
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 449 | 26 | 9 | 53 | 47 | 245 | 0 | 35 | 17 | 0 | 0 | 302 | 450 | 0 | 0 | 311 | 0 | 0 | 0 | 105 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 1.91 | 222 | 0 | 4 | 1125 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 1161 | 5 | 0 | 0 | 210 | 290 | 220 | 51 | 5 | 208 | 36 | 0 | 90 | 0 | 0 | 19 | 0 | 150 | 0 | 43 | 0 | 305 | 0 | 228 | 40 | 0 | 142 | 1 | 8 | 0 | 83 | 0 | 144 | 16 | 0 | 0 | 48 | 17.74 | 47 | 0 | 1 | 45.56 | 0 | 7677.21 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 48 | 948 | 0 | 0 | 0 | 1438.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.16 | 50 | 0 | 0 | 12.28 | 156 | 0 | 128 | 0 | 135 | 0 | 328 | 0 | 0.58 | 180 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 1.5 | 80 | 0.17 | 0 | 247 | 115 | 220 | 0 | 700 | 935 | 0 | 6682.19 | 14359.4 | 103.9
16:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 442 | 17 | 17 | 69 | 48 | 245 | 0 | 50 | 17 | 0 | 0 | 299 | 450 | 0 | 0 | 304 | 0 | 0 | 0 | 105 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1.97 | 217 | 0 | 4 | 1125 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 1160 | 1 | 0 | 0 | 210 | 290 | 220 | 51 | 5 | 181 | 20 | 0 | 91 | 0 | 0 | 19 | 0 | 148 | 0 | 27 | 0 | 310 | 0 | 228 | 40 | 0 | 141 | 6 | 17 | 0 | 83 | 0 | 142 | 16 | 0 | 0 | 48 | 13.82 | 47 | 0 | 1.2 | 22.33 | 0 | 7607.32 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 47 | 975 | 0 | 0 | 0 | 1415.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.61 | 63 | 0 | 0 | 19.68 | 153 | 0 | 128 | 0 | 134 | 0 | 322 | 0 | 1.36 | 180 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0.9 | 95 | 0.03 | 0 | 248 | 115 | 220 | 0 | 700 | 985 | 0 | 6772.91 | 14380.23 | 103.9
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 461 | 17 | 17 | 69 | 48 | 245 | 0 | 55 | 17 | 0 | 0 | 300 | 350 | 0 | 0 | 309 | 0 | 0 | 0 | 105 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0.31 | 220 | 0 | 3 | 1000 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 210 | 270 | 220 | 51 | 5 | 176 | 20 | 0 | 91 | 0 | 0 | 19 | 0 | 130 | 0 | 12 | 0 | 305 | 0 | 228 | 40 | 0 | 147 | 2 | 0 | 0 | 83 | 0 | 141 | 16 | 40 | 0 | 48 | 2.22 | 47 | 0 | 0.2 | 1.69 | 12 | 7237.42 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 948 | 0 | 0 | 0 | 1420.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.85 | 33 | 0 | 0 | 10.75 | 152 | 0 | 128 | 0 | 134 | 0 | 322 | 0 | 0 | 180 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.4 | 19 | 0.28 | 0 | 248 | 115 | 180 | 0 | 700 | 1045 | 0 | 6588.69 | 13826.11 | 103.9
18:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 471 | 28 | 17 | 78 | 56 | 245 | 0 | 55 | 108 | 0 | 0 | 303 | 290 | 0 | 0 | 309 | 0 | 0 | 0 | 105 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0.07 | 220 | 0 | 7 | 1000 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 210 | 270 | 220 | 51 | 5 | 185 | 10 | 0 | 92 | 0 | 0 | 19 | 0 | 132 | 0 | 4 | 0 | 300 | 0 | 228 | 40 | 0 | 136 | 0 | 17 | 0 | 84 | 0 | 142 | 18 | 100 | 1 | 48 | 0.79 | 47 | 0 | 0.1 | 2.42 | 18 | 7346.38 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 925 | 0 | 0 | 0 | 1295.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.35 | 7 | 0 | 0 | 3.16 | 152 | 0 | 128 | 0 | 134 | 0 | 318 | 0 | 0.29 | 180 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 9 | 0.06 | 0 | 194 | 115 | 180 | 0 | 760 | 1050 | 0 | 6396.85 | 13743.23 | 103.89
19:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 477 | 30 | 17 | 122 | 124 | 195 | 0 | 55 | 108 | 0 | 0 | 307 | 295 | 0 | 40 | 311 | 0 | 0 | 0 | 143 | 13 | 21 | 0 | 0 | 0 | 15 | 0 | 0 | 24 | 34 | 0 | 17 | 0 | 0 | 0 | 220 | 18 | 2 | 1125 | 3 | 0 | 7 | 0 | 2 | 212 | 0 | 0 | 0 | 1140 | 0 | 10 | 0 | 210 | 270 | 220 | 51 | 5 | 184 | 10 | 3 | 92 | 5 | 4 | 19 | 0 | 156 | 0 | 0 | 15 | 290 | 0 | 228 | 40 | 0 | 130 | 0 | 17 | 0 | 84 | 0 | 142 | 18 | 101 | 17 | 48 | 0 | 47 | 0 | 0 | 0 | 18 | 7919 | 896 | 0 | 0 | 31 | 12 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 0 | 0 | 0 | 1267.8 | 0 | 0 | 0 | 0 | 5 | 0 | 93 | 28 | 0 | 0 | 0 | 20 | 0 | 0 | 152 | 0 | 128 | 0 | 131 | 0 | 317 | 0 | 0 | 162 | 0 | 110 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 120 | 220 | 0 | 1050 | 1040 | 10 | 7168.8 | 0 | 103.8
19:30 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 409 | 30 | 17 | 149 | 125 | 195 | 15 | 42 | 53 | 0 | 0 | 296 | 382 | 0 | 55 | 290 | 0 | 0 | 0 | 143 | 13 | 0 | 0 | 0 | 0 | 15 | 10 | 0 | 12 | 34 | 0 | 17 | 0 | 0 | 0 | 220 | 40 | 10 | 1125 | 14 | 0 | 18 | 0 | 17 | 181 | 0 | 0 | 0 | 1120 | 0 | 20 | 0 | 210 | 270 | 220 | 51 | 5 | 185 | 10 | 70 | 92 | 15 | 27 | 19 | 0 | 150 | 0 | 0 | 24 | 300 | 0 | 228 | 40 | 0 | 131 | 0 | 17 | 0 | 84 | 0 | 142 | 18 | 100 | 17 | 48 | 0 | 47 | 0 | 0 | 0 | 18 | 8049 | 896 | 0 | 0 | 37 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1168 | 0 | 0 | 0 | 1492.21 | 0 | 0 | 0 | 0 | 35 | 0 | 60 | 28 | 0 | 0 | 0 | 20 | 0 | 0 | 152 | 0 | 128 | 0 | 131 | 0 | 316 | 0 | 0 | 180 | 0 | 90 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 1050 | 1120 | 17 | 7735.21 | 15087.8 | 103.89
20:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 436 | 17 | 17 | 149 | 141 | 195 | 15 | 35 | 52 | 0 | 0 | 297 | 400 | 0 | 17 | 306 | 0 | 0 | 0 | 143 | 13 | 0 | 0 | 0 | 0 | 15 | 19 | 0 | 17 | 34 | 0 | 17 | 0 | 0 | 0 | 220 | 68 | 6 | 1125 | 15 | 0 | 18 | 0 | 17 | 181 | 0 | 0 | 0 | 1160 | 0 | 20 | 0 | 210 | 270 | 220 | 51 | 5 | 185 | 10 | 34 | 92 | 15 | 27 | 19 | 0 | 140 | 0 | 0 | 24 | 300 | 0 | 228 | 40 | 0 | 131 | 0 | 17 | 0 | 84 | 0 | 142 | 18 | 100 | 17 | 48 | 0 | 47 | 0 | 0 | 0 | 18 | 8116 | 896 | 0 | 0 | 34 | 43 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1185 | 0 | 0 | 0 | 1479.29 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 128 | 0 | 131 | 0 | 315 | 0 | 0 | 180 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 1050 | 1140 | 17 | 7590.29 | 15784.21 | 103.89
21:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 480 | 17 | 17 | 149 | 141 | 195 | 15 | 35 | 17 | 0 | 0 | 302 | 490 | 0 | 17 | 309 | 0 | 0 | 0 | 143 | 13 | 12 | 0 | 0 | 0 | 15 | 24 | 0 | 20 | 34 | 0 | 17 | 0 | 0 | 0 | 220 | 33 | 6 | 1125 | 15 | 0 | 19 | 0 | 17 | 180 | 0 | 0 | 0 | 1160 | 0 | 20 | 0 | 210 | 270 | 220 | 51 | 5 | 185 | 10 | 32 | 92 | 16 | 28 | 19 | 0 | 134 | 0 | 0 | 24 | 310 | 0 | 228 | 40 | 0 | 142 | 0 | 17 | 0 | 84 | 0 | 143 | 18 | 100 | 17 | 48 | 0 | 47 | 0 | 0 | 0 | 18 | 8243 | 849 | 0 | 0 | 0 | 65 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 1491.5 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 128 | 0 | 131 | 0 | 316 | 0 | 0 | 180 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 1050 | 1155 | 17 | 7574.5 | 15706.29 | 103.89
22:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 436 | 17 | 17 | 149 | 144 | 195 | 15 | 35 | 15 | 0 | 0 | 296 | 495 | 0 | 17 | 303 | 0 | 0 | 0 | 143 | 13 | 21 | 0 | 0 | 0 | 15 | 24 | 0 | 34 | 34 | 0 | 17 | 0 | 0 | 0 | 222 | 33 | 14 | 1125 | 15 | 0 | 19 | 0 | 16 | 180 | 0 | 0 | 0 | 1160 | 0 | 20 | 0 | 210 | 270 | 220 | 51 | 5 | 182 | 10 | 31 | 93 | 15 | 28 | 19 | 0 | 142 | 0 | 0 | 24 | 305 | 0 | 229 | 40 | 0 | 132 | 0 | 17 | 0 | 84 | 0 | 142 | 16 | 100 | 17 | 48 | 0 | 47 | 0 | 0 | 0 | 13 | 8190 | 849 | 0 | 0 | 0 | 54 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1191 | 0 | 0 | 0 | 1484.13 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 128 | 0 | 131 | 0 | 312 | 0 | 0 | 180 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 307 | 120 | 220 | 0 | 1050 | 1163 | 17 | 7560.13 | 15817.5 | 103.89
23:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 528 | 17 | 27 | 149 | 144 | 195 | 15 | 35 | 16 | 0 | 0 | 310 | 500 | 0 | 17 | 322 | 0 | 0 | 0 | 143 | 13 | 21 | 0 | 0 | 0 | 15 | 24 | 0 | 55 | 34 | 0 | 18 | 0 | 0 | 0 | 222 | 35 | 17 | 1125 | 16 | 0 | 19 | 0 | 17 | 0 | 0 | 0 | 0 | 1175 | 0 | 20 | 0 | 210 | 270 | 220 | 51 | 5 | 182 | 10 | 32 | 92 | 17 | 28 | 19 | 0 | 144 | 0 | 0 | 16 | 310 | 0 | 229 | 40 | 0 | 139 | 0 | 17 | 0 | 84 | 0 | 142 | 16 | 100 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 8193 | 896 | 0 | 0 | 0 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1192 | 0 | 0 | 0 | 1495.85 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 128 | 0 | 133 | 0 | 310 | 0 | 0 | 180 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 307 | 120 | 220 | 0 | 900 | 1163 | 17 | 7538.05 | 15750.13 | 103.88
Total KWH | 0 | 853440 | 201120 | 0 | 0 | 0 | 0 | 0 | 8715600 | 0 | 11168690 | 293040 | 212040 | 1792512 | 1778880 | 2479484 | 351434 | 604774 | 442080 | 0 | 0 | 7204771 | 10180895 | 0 | 227298 | 7395130 | 0 | 0 | 0 | 3075600 | 342000 | 448200 | 0 | 0 | 11291 | 110400 | 127680 | 0 | 660000 | 247995 | 18770 | 196541 | 0 | 0 | 23246 | 5309363 | 531091 | 463200 | 23258181.82 | 93673 | 0 | 485280 | 4350.6 | 173127 | 4866457 | 0 | 0 | 0 | 26034543 | 42795 | 222472 | 0 | 5237000 | 7193100 | 5288000 | 1239165 | 226560 | 4849000 | 726840 | 343680 | 2183818 | 177120 | 152040 | 465860 | 10260 | 3179520 | 0 | 355036 | 454032 | 7420000 | 0 | 6802000 | 946000 | 0 | 3332700 | 51289 | 333552 | 0 | 2025600 | 0 | 3253000 | 401000 | 729640 | 112320 | 1122000 | 81439 | 1152000 | 0 | 11350 | 191190 | 123840 | 180817395.42 | 20626909 | 0 | 0 | 54720 | 222080 | 912000 | 0 | 0 | 0 | 0 | 7776 | 497520 | 24887270 | 0 | 0 | 0 | 31346545 | 0 | 3334 | 0 | 46560 | 285984 | 0 | 143072 | 46134 | 82858 | 262776 | 561863 | 39862 | 0 | 334528 | 3855636 | 0 | 3559891 | 0 | 3645000 | 0 | 8654691 | 0 | 11040 | 4420000 | 0 | 560636 | 135897 | 542457 | 0 | 0 | 0 | 10547.16 | 708480 | 3745 | 84192 | 5585000 | 2858000 | 5332930 | 0 | 16560000 | 25412363.64 | 118800 | 162421096.8 | 343238492.22 | 103.88

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14178.41 | MW | 12:00 Hr. | Energy Generated |  |  | 343.2385 |  | MKWHr.
| Day Peak Demand |  |  | 14407.41 | MW | 12:00 Hr. | Energy Unserverd |  |  | 5.881 |  | MKWHr.
| Evening Peak Generation |  |  | 15817.5 | MW | 21:00 Hr. | Energy Demand |  |  | 349.1195 |  | MKWHr.
| Evening Peak Demand |  |  | 16355.5 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.4 |  | °C
| Minimum Generation of the Day |  |  | 12820.87 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 945.3 |  | MMCFD
| Maximum Generation of the Day |  |  | 15817.5 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.155 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 45.4553 | 0 | 12.3117 | 0 | 0 | 0 | 0 | 0 | 57.767 | Gas | 131.3439 | Gas | 465080406.35
| Chattogram Zone |  |  | 5.3297 | 49.2927 | 2.0002 | 0 | 5.3094 | 0.066041 | 0 | 0.66 | 62.658 | Coal | 126.1574 | Coal | 849277581.707
| Cumilla Zone |  |  | 27.4093 | 0 | 1.3596 | 0 | 0 | 0.35504 | 3.1795 | 0 | 32.3035 | HFO | 20.4201 | HFO | 382279127.064
| Mymensingh Zone |  |  | 0 | 0 | 2.5102 | 0 | 0 | 0.28398 | 0 | 0 | 2.7941 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.2435 | 0 | 0 | 0 | 0 | 0.051289 | 0 | 0 | 25.2948 | Hydro | 5.3094 | Hydro | 530936.3
| Khulna Zone |  |  | 0 | 24.8873 | 0.28458 | 0 | 0 | 0.49752 | 21.5389 | 0 | 47.2083 | Solar | 3.2827 | Solar | 51586212.1228
| Barishal Zone |  |  | 8.1909 | 47.5574 | 0.20299 | 0 | 0 | 0.003745 | 0 | 0 | 55.955 | Import | 56.065 | Import | 354179420.61
| Rajshahi Zone |  |  | 19.7152 | 0 | 0.6478 | 0 | 0 | 1.1702 | 31.3465 | 0 | 52.8798 | Wind | 0.66 | Wind | 9708600
| Rangpur Zone |  |  | 0 | 4.42 | 1.1031 | 0 | 0 | 0.85492 | 0 | 0 | 6.378
| Total |  |  | 131.3439 | 126.1574 | 20.4201 | 0 | 5.3094 | 3.2827 | 56.065 | 0.66 | 343.2385
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 465080406.35 |  | Hydro | 530936.3
|  |  |  | Coal | 849277581.707 |  | Solar | 51586212.1228
|  |  |  | HFO | 382279127.064 |  | Import | 354179420.61
|  |  |  | HSD | 0 |  | Wind | 9708600
[5 empty] | Total: | 211,26,42,284 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.6269 | Peak Hr Flow | 849.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47838909.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.3465 | Peak Hr Flow | 1491.50 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2284 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.1795 | Peak Hr Flow | 134.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2585 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 55.153 | Peak Hr Flow | 2474.50 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 15 |  | 5732
|  |  |  | Chattogram |  | 0 |  | 1371
|  |  |  | Cumilla |  | 20 |  | 1498
|  |  |  | Mymensingh |  | 428 |  | 1438
|  |  |  | Sylhet |  | 0 |  | 638
|  |  |  | Khulna |  | 52 |  | 1906
|  |  |  | Barishal |  | 0 |  | 505
|  |  |  | Rajshahi |  | 0 |  | 1606
|  |  |  | Rangpur |  | 0 |  | 1024
|  |  |  | Total |  | 515 |  | 15718
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Fenchugonj CCPP Phase-2 GT-4 |  |  | 35
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 124
|  |  |  | Total Unavailable Capacity |  |  |  | 424
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:03 | Faridpur 132/33kV S/S Transformer-2 LT is restored.
|  | 08:03 | Faridpur 132/33kV S/S Transformer-2 HT is restored.
|  | 08:20 | Natore 132/33kV S/S TR-1 (405 T) LT is restored.
|  | 08:20 | Natore 132/33kV S/S TR-1 (405 T) HT is restored.
|  | 08:21 | Natore 132/33kV S/S TR-2 (415 T) LT is restored.
|  | 08:21 | Natore 132/33kV S/S TR-2 (415 T) HT is restored.
|  | 09:35 | Jhenaidah 132/33kV S/S Transformer T-2 LT is restored.
|  | 09:35 | Jhenaidah 132/33kV S/S Transformer T-2 HT is restored.
| 09:38 | 14:47 | KSRM 132/33kV S/S Transformer-02 LT Forced S/D Due to red hot maintenance. check every
junction point., cleaning.
| 09:41 | 14:49 | KSRM 132/33kV S/S Transformer-02 HT Forced S/D Due to red hot maintenance. check every
junction point., cleaning.
| 10:23 | 16:27 | Khulna (S)-Satkhira 132kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end. and from
Satkhira 132/33kVend.
| 11:28 | 12:52 | Ishurdi 230/132kV S/S 230 kV Bus 2 Project Work S/D Due to 23 KV ISD-Ghorasal-2's
different equipments clamp changing
| 12:00 |  | Day Peak Generation: 14178 MW.
| 13:01 | 14:09 | Bhandaria 132/33kV S/S Transformer-1 HT Forced S/D Due to oil leakage maintenance work by
G2G.
| 13:01 | 14:09 | Bhandaria 132/33kV S/S Transformer-1 LT Forced S/D Due to oil leakage maintenance work by
G2G.
|  | 13:37 | Rampura-Ullon-2 132kV Ckt-2 is restored.
| 14:41 | 15:48 | Taraganj 132/33kV S/S TR-03 (404T) LT Forced S/D Due to Red hot HT Bushing
| 15:13 | 17:43 | Bagerhat-Goalpara 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end.
|  | 16:27 | Khulna (S)-Satkhira 132kV Ckt-1 is restored.
| 16:55 |  | Sylhet 225 MW CCPP GT was sync.
|  | 17:51 | Gallamari- Khulna (S) 132kV Ckt-2 is restored.
| 22:55 | 23:37 | Narshingdi 132/33kV S/S T-4 LT Scheduled S/D Due to T4 Transformer এর Hasnabad 33kV | [7 empty] | 35.0MW load
|  |  | Feeder R-Phase Red hot Maintenance Work. | [7 empty] | interrup.
| 22:56 | 23:36 | Narshingdi 132/33kV S/S T-4 HT Scheduled S/D Due to T4 Transformer এর Hasnabad 33kV
Feeder R-Phase Red hot Maintenance Work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 349 | 8715600 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 302 | 7204771 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 351434 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 309 | 7395130 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 293040 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 141 | 1778880 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 604774 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 227298 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 342000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 12 | 448200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 201120 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 2479484 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1792512 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 853440 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 442080 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 212040 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 490 | 10180895 | AGC+FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 480 | 11168690 | AGC+FGMO
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143 | 3075600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2830 | 57766988
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 4350.6 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 42795 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 485280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5309363 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 180 | 4866457 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 173127 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 18770 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 247995 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 6 | 463200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 24 | 127680 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23246 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 110400 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 196541 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 33 | 531091 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 11291 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 15 | 93673 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1160 | 26034543 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 20 | 660000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 23258181.82 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2885 | 62657984.42
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 185 | 4849000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 270 | 7193100 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 220 | 5288000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 210 | 5237000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 726840 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 226560 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1239165 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 20 | 222472 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 24 | 454032 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 92 | 2183818 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 16 | 177120 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 134 | 3179520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 465860 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 10260 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 152040 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 32 | 343680 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 355036 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1316 | 32303503
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 81439 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 47 | 1152000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 48 | 1122000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 191190 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 123840 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 112320 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 130 | 2794139
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 51289 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 946000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 142 | 3332700 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 143 | 3253000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 2025600 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 729640 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 401000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 333552 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7420000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 228 | 6802000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1082 | 25294781
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 849 | 20626909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 54720 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 65 | 222080 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 7776 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 497520 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1200 | 24887270 | AGC
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2152 | 47208275
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1050 | 16560000 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 84192 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2858000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1155 | 25412363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5332930 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 118800 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5585000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3745 | -
Barishal Area Total |  |  |  |  | 3407.64 | 2869 | 55955030.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 262776 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 3334 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 46134 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 152 | 3855636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 128 | 3559891 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 131 | 3645000 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 316 | 8654691 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 39862 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 82858 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 143072 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 285984 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 46560 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 11040 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1491.5 | 31346545 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 334528 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 561863 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2253.5 | 52879774
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4420000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 542457 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 10547.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 560636 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 135897 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 708480 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 300 | 6378017.16
Eastern Grid Total |  |  |  |  | 17438.042 | 8243 | 180817395.42
Western Grid Total |  |  |  |  | 11812.075 | 7574.5 | 162421096.8
National Grid Total |  |  |  |  | 29250.117 | 15817.5 | 343238492.22
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10263.1 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4988.8 | MW
i) Dhaka area |  |  | 5717.2 |  | MW | i) Khulna area |  |  |  | 1854 | MW
ii) Chattogram area |  |  | 1419.9 |  | MW | ii) Barishal area |  |  |  | 504.8 | MW
iii) Cumilla area |  |  | 1478 |  | MW | iii) Rajshahi area |  |  |  | 1606 | MW
iv) Mymensingh area |  |  | 1010 |  | MW | iv) Rangpur area |  |  |  | 1024 | MW
v) Sylhet area |  |  | 638 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15251.9 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 130 | 08:00 | 133 | Narshingdi | 185 | 00:00 | 199 | Uttara | 97 | 13:00
2 | AKSML | 148.6 | 13:00 | 68 | Hasnabad | 96 | 12:00 | 134 | Natore | 148 | 21:00 | 200 | UttaraNew | 54 | 13:00
3 | Aftabnagar | 44 | 13:00 | 69 | Hathazari | 90 | 19:30 | 135 | Nawabganj | 63.9 | 22:00 | 201 | Zigatola | 112 | 13:00
4 | Agargaon | 120 | 13:00 | 70 | Hatirjheel | 89 | 13:00 | 136 | Netrakona | 133 | 18:00
5 | Agrabad | 70 | 19:00 | 71 | Ishurdi | 84 | 19:30 | 137 | New | 87 | 12:00
6 | Amnura | 33 | 00:00 | 72 | Jaldhaka | 84 | 00:00 | 138 | Niamatpur | 84 | 23:00
7 | Ashuganj | 77 | 00:00 | 73 | Jamalpur | 122 | 00:00 | 139 | Noapara | 46 | 19:30
8 | BSRM | 165 | 01:00 | 74 | Jashore | 149 | 13:00 | 140 | PHP | 10 | 18:00
9 | Bagerhat | 91 | 22:00 | 75 | Jhenaidah | 94 | 19:00 | 141 | Pabna | 102 | 21:00
10 | Bajitpur | 90 | 00:00 | 76 | Joydebpur | 167 | 21:00 | 142 | Palashbari | 136 | 23:00
11 | Bakerganj | 15.6 | 22:00 | 77 | Joypurhat | 67 | 23:00 | 143 | Panchagarh | 61 | 00:00
12 | Bakulia | 96 | 19:00 | 78 | Juldah | 16 | 12:00 | 144 | Patiya | 11 | 00:00
13 | Banani | 64 | 13:00 | 79 | KSRM | 15 | 23:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 7 | 12:00 | 80 | Kabirpur | 264 | 21:00 | 146 | Patuakhali | 72.8 | 23:00
15 | Barapukuria | 76 | 22:00 | 81 | Kachua | 98 | 21:00 | 147 | Payra | 36 | 00:00
16 | Barguna | 22 | 00:00 | 82 | Kaliganj | 39 | 19:30 | 148 | Postogola | 63 | 13:00
17 | Barishal | 108 | 12:00 | 83 | Kallyanpur | 123 | 18:30 | 149 | Pubail | 45 | 19:00
18 | Barishal-230 | 108 | 22:00 | 84 | Kalurghat | 40 | 10:00 | 150 | Purbachal | 28 | 14:00
19 | Baroaulia | 39 | 06:00 | 85 | Kamrangirchar | 79 | 14:00 | 151 | Purbasadipur | 142 | 23:00
20 | Baroirhat | 65 | 19:30 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 43 | 00:00
21 | Bashundhara | 203 | 13:00 | 87 | Kasba | 40 | 22:00 | 153 | Rahim | 50 | 17:00
22 | BashundharaCement | 6 | 00:00 | 88 | Kazla | 124 | 14:00 | 154 | Rajbari | 92 | 19:30
23 | Beanibazar | 80 | 19:30 | 89 | Keranigonj | 88 | 19:00 | 155 | Rajendrapur | 115 | 18:30
24 | Benapole | 80 | 19:30 | 90 | Khagrachori | 36 | 19:30 | 156 | Rajshahi | 122 | 23:00
25 | Bhaluka | 152 | 18:30 | 91 | Khulna | 66 | 19:30 | 157 | Rajshahi-230 | 113 | 13:00
26 | Bhandaria | 60 | 23:00 | 92 | Khulshi | 162 | 19:00 | 158 | Ramganj | 120 | 00:00
27 | Bhangura | 40 | 00:00 | 93 | Kishoreganj | 138 | 00:00 | 159 | Rampur | 42 | 00:00
28 | Bheramara(GK) | 70 | 19:30 | 94 | Kodda | 299 | 19:30 | 160 | Rangamati | 18 | 20:00
29 | Bhulta | 215 | 12:00 | 95 | Kulaura | 54 | 22:00 | 161 | Rangpur | 142 | 19:30
30 | Bog-Sherpur | 84 | 22:00 | 96 | Kurigram | 72 | 19:30 | 162 | Ruppur | 2.8 | 10:00
31 | Bogura | 177 | 00:00 | 97 | Kushtia | 162 | 19:30 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 79 | 22:00 | 98 | Laksam | 36 | 19:30 | 164 | Saidpur | 108 | 19:30
33 | Brahmanbaria | 137 | 19:00 | 99 | Lakshmipur | 43 | 21:00 | 165 | Santhia | 40 | 00:00
34 | Cantonment | 122 | 13:00 | 100 | Lalbag | 67 | 13:00 | 166 | Satkhira | 133 | 23:00
35 | Chandina | 41 | 22:00 | 101 | Lalmonirhat | 68 | 20:00 | 167 | Satmasjid | 105 | 13:00
36 | Chandpur | 88 | 23:00 | 102 | MI_Cement | 18.1 | 15:00 | 168 | Savar | 224 | 12:00
37 | Chandraghona | 36 | 00:00 | 103 | Madanganj | 39 | 00:00 | 169 | SevenRings | 17.87 | 09:00
38 | Chapai | 80 | 21:00 | 104 | Madaripur | 122 | 20:00 | 170 | ShahCement | 29 | 01:00
39 | Charfasson | 34 | 22:00 | 105 | Madartek | 82 | 00:00 | 171 | Shahjadpur | 80 | 19:30
40 | Charsaidpur | 42 | 00:00 | 106 | Madunaghat | 56 | 19:00 | 172 | Shahjibazar | 135 | 22:00
41 | Chauddagram | 75 | 22:00 | 107 | Magura | 67 | 21:00 | 173 | Shahmirpur | 52 | 23:00
42 | Chhatak | 38 | 21:00 | 108 | Mahasthangarh | 86 | 23:00 | 174 | Shariatpur | 96 | 22:00
43 | Chowmuhani | 162 | 19:00 | 109 | Maijdee | 42 | 22:00 | 175 | Sherpur | 154 | 00:00
44 | Chuadanga | 118 | 00:00 | 110 | Manikganj | 134 | 00:00 | 176 | Shikalbaha | 28.5 | 19:30
45 | Coxsbazar | 149 | 19:00 | 111 | Maniknagar | 71 | 13:00 | 177 | Shitalakhya | 79.8 | 16:00
46 | Cumilla(N) | 123 | 20:00 | 112 | Matarbari | 52 | 19:30 | 178 | Sholosohor | 45 | 15:00
47 | Cumilla(S) | 153 | 19:00 | 113 | Matuail | 74 | 12:00 | 179 | Shomvuganj | 42 | 00:00
48 | Daganbhuiyan | 30 | 00:00 | 114 | Metrorail_Motijheel | 20 | 10:00 | 180 | Shyampur | 176 | 13:00
49 | Daudkandi | 141 | 01:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 128 | 10:00
50 | DhakaUniversity | 82 | 13:00 | 116 | Millgate | 104 | 12:00 | 182 | Sirajganj | 118 | 21:00
51 | Dhamrai | 104 | 15:00 | 117 | Mirpur | 156 | 19:00 | 183 | Sitakunda | 35 | 19:00
52 | Dhanmondi | 111 | 13:00 | 118 | Mirsorai | 37 | 09:00 | 184 | Sonargaon | 144 | 23:00
53 | Dohazari | 102 | 19:00 | 119 | Mirzapur | 38 | 00:00 | 185 | Sreemongol | 87 | 20:00
54 | Faridpur | 180 | 20:00 | 120 | Mithapukur | 78 | 19:30 | 186 | Sreepur | 134 | 19:00
55 | Fatullah | 103 | 15:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 50.8 | 22:00
56 | Fenchuganj | 45 | 22:00 | 122 | Mogbazar | 0 | 00:00 | 188 | Sunamganj | 61 | 00:00
57 | Feni | 113 | 22:00 | 123 | Mongla | 47 | 14:00 | 189 | Sylhet | 114 | 16:00
58 | GPH | 4 | 16:00 | 124 | Motijheel | 49 | 13:00 | 190 | Sylhet_(South) | 71 | 00:00
59 | Ghatail | 84 | 00:00 | 125 | Muktagacha | 40 | 00:00 | 191 | TK | 25 | 00:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 115 | 23:00 | 192 | Tangail | 172 | 00:00
61 | Ghorashal-230 | 105 | 16:00 | 127 | Muradnagar | 53 | 22:00 | 193 | Taraganj | 28 | 20:00
62 | Goalpara | 30 | 00:00 | 128 | Mymensingh | 162 | 19:00 | 194 | Tasnim | 45 | 17:00
63 | Gollamari | 106 | 23:00 | 129 | Nabinagar | 108 | 09:00 | 195 | Thakurgaon | 108 | 21:00
64 | Gopalganj | 114 | 21:00 | 130 | Naogaon | 145 | 21:00 | 196 | Tongi | 166 | 11:00
65 | Gulshan | 104 | 13:00 | 131 | Narail | 57 | 19:00 | 197 | Ullahpara | 37 | 00:00
66 | Halishahar | 91 | 10:00 | 132 | Narinda | 90 | 13:00 | 198 | Ullon | 66 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15237.21 | 65 |  | 15305.14
1:00 | 14496.56 | 185 |  | 14689.56
2:00 | 14111.37 | 167 |  | 14286.37
3:00 | 13707.64 | 174 |  | 13889.64
4:00 | 13457.26 | 170 |  | 13635.26
5:00 | 13242.59 | 157 |  | 13406.59
6:00 | 12895.53 | 182 |  | 13085.53
7:00 | 12820.87 | 161 |  | 12988.87
8:00 | 12837.56 | 156 |  | 13000.56
9:00 | 13355.38 | 172 |  | 13535.38
10:00 | 13406.47 | 218 |  | 13634.47
11:00 | 13613.72 | 166 |  | 13786.72
12:00 | 14178.41 | 219 |  | 14407.41
13:00 | 14514.9 | 335 |  | 14864.9
14:00 | 14383.96 | 327 |  | 14725.96
15:00 | 14359.4 | 321 |  | 14694.4
16:00 | 14380.23 | 242 |  | 14633.23
17:00 | 13826.11 | 208 |  | 14043.11
18:00 | 13743.23 | 202 |  | 13954.23
19:00 | 15087.8 | 241 |  | 15339.8
19:30 | 15784.21 | 394 |  | 16196.21
20:00 | 15706.29 | 394 |  | 16118.29
21:00 | 15817.5 | 515 |  | 16355.5
22:00 | 15750.13 | 445 |  | 16215.13
23:00 | 15731.05 | 459 |  | 16211.05
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7764.36 | 7472.85 | 15237.21 | DAILY GENERATION CURVE
00:30 | 7570.86 | 7296.025 | 14866.885
01:00 | 7377.36 | 7119.2 | 14496.56 | 18-07-2026
01:30 | 7257.18 | 7046.785 | 14303.965
02:00 | 7137 | 6974.37 | 14111.37
02:30 | 7097 | 6812.505 | 13909.505
03:00 | 7057 | 6650.64 | 13707.64
03:30 | 7057 | 6525.45 | 13582.45
04:00 | 7057 | 6400.26 | 13457.26
04:30 | 6974 | 6375.925 | 13349.925
05:00 | 6891 | 6351.59 | 13242.59
05:30 | 6794.725 | 6274.335 | 13069.06
06:00 | 6698.45 | 6197.08 | 12895.53
06:30 | 6712.245 | 6145.955 | 12858.2
07:00 | 6726.04 | 6094.83 | 12820.87
07:30 | 6733.49 | 6095.725 | 12829.215
08:00 | 6740.94 | 6096.62 | 12837.56
08:30 | 6911.645 | 6184.825 | 13096.47
09:00 | 7082.35 | 6273.03 | 13355.38
09:30 | 7166.595 | 6214.33 | 13380.925
10:00 | 7250.84 | 6155.63 | 13406.47
10:30 | 7336.02 | 6174.075 | 13510.095
11:00 | 7421.2 | 6192.52 | 13613.72
11:30 | 7549.97 | 6346.095 | 13896.065
12:00 | 7678.74 | 6499.67 | 14178.41
12:30 | 7653.785 | 6692.87 | 14346.655
13:00 | 7628.83 | 6886.07 | 14514.9
13:30 | 7664.775 | 6784.655 | 14449.43
14:00 | 7700.72 | 6683.24 | 14383.96
14:30 | 7688.965 | 6682.715 | 14371.68
15:00 | 7677.21 | 6682.19 | 14359.4
15:30 | 7642.265 | 6727.55 | 14369.815
16:00 | 7607.32 | 6772.91 | 14380.23
16:30 | 7422.37 | 6680.8 | 14103.17
17:00 | 7237.42 | 6588.69 | 13826.11
17:30 | 7291.9 | 6492.77 | 13784.67
18:00 | 7346.38 | 6396.85 | 13743.23
18:30 | 7632.69 | 6782.825 | 14415.515
19:00 | 7919 | 7168.8 | 15087.8
19:30 | 8049 | 7735.21 | 15784.21
20:00 | 8116 | 7590.29 | 15706.29
20:30 | 8179.5 | 7582.395 | 15761.895 |  | Executive Engineer
21:00 | 8243 | 7574.5 | 15817.5 |  | Network Operation Division
21:30 | 8216.5 | 7567.315 | 15783.815
22:00 | 8190 | 7560.13 | 15750.13
22:30 | 8191.5 | 7549.09 | 15740.59
23:00 | 8193 | 7538.05 | 15731.05

## En-Curve
QF-LDC-12
Date | 18-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3392 | 2100 | 826 | 38 | 126 | 1419.85 | 222 | 5515 | 0 | 527 | 1053.36 | 0 | 0 | 18 | 65 | DAILY ENERGY CURVE
00:30 | 3325.5 | 2038.5 | 860.5 | 38 | 127 | 1450.525 | 222 | 5415.5 | 0 | 461 | 907.36 | 0 | 0 | 21 | 125 | 18-07-2026
01:00 | 3259 | 1977 | 895 | 38 | 128 | 1481.2 | 222 | 5316 | 0 | 395 | 761.36 | 0 | 0 | 24 | 185
01:30 | 3313.5 | 2034 | 871.5 | 38 | 128 | 1454.785 | 222 | 5261 | 0 | 370 | 589.68 | 0 | 0 | 21.5 | 176 | Energy Generated | 343.2385 |  | MKWHr
02:00 | 3368 | 2091 | 848 | 38 | 128 | 1428.37 | 222 | 5206 | 0 | 345 | 418 | 0 | 0 | 19 | 167 | Energy not Served | 5.881 |  | MKWHr
02:30 | 3409.5 | 2073.5 | 872 | 38 | 125 | 1370.505 | 221 | 5170.5 | 0 | 287.5 | 322 | 0 | 0 | 20 | 170.5 | Total Energy Requirement | 349.1195 |  | MKWHr
03:00 | 3451 | 2056 | 896 | 38 | 122 | 1312.64 | 220 | 5135 | 0 | 230 | 226 | 0 | 0 | 21 | 174
03:30 | 3476.5 | 2093 | 896 | 38 | 118 | 1311.45 | 219.5 | 4988.5 | 0 | 221.5 | 193 | 0 | 0 | 27 | 172
04:00 | 3502 | 2130 | 896 | 38 | 114 | 1310.26 | 219 | 4842 | 0 | 213 | 160 | 0 | 0 | 33 | 170
04:30 | 3485 | 2094 | 896 | 38 | 116 | 1304.425 | 218.5 | 4803 | 0 | 213 | 152.5 | 0 | 0 | 29.5 | 163.5
05:00 | 3468 | 2058 | 896 | 38 | 118 | 1298.59 | 218 | 4764 | 0 | 213 | 145 | 0 | 0 | 26 | 157
05:30 | 3459 | 2052 | 896 | 38 | 117 | 1251.755 | 218 | 4642 | 6.805 | 213 | 145 | 0 | 0 | 30.5 | 169.5
06:00 | 3450 | 2046 | 896 | 38 | 116 | 1204.92 | 218 | 4520 | 13.61 | 213 | 145 | 0 | 0 | 35 | 182
06:30 | 3457.5 | 2049 | 896 | 38 | 114 | 1166.27 | 218.5 | 4477.5 | 49.93 | 203 | 145 | 0 | 0 | 43.5 | 171.5
07:00 | 3465 | 2052 | 896 | 38 | 112 | 1127.62 | 219 | 4435 | 86.25 | 193 | 145 | 0 | 0 | 52 | 161
07:30 | 3464 | 2066.5 | 896 | 38 | 113 | 1116.195 | 219.5 | 4387 | 139.52 | 184 | 159.5 | 0 | 0 | 46 | 158.5
08:00 | 3463 | 2081 | 896 | 38 | 114 | 1104.77 | 220 | 4339 | 192.79 | 175 | 174 | 0 | 0 | 40 | 156
08:30 | 3456.5 | 2082.5 | 896 | 38 | 122 | 1121.62 | 220 | 4488.5 | 260.85 | 175 | 189.5 | 0 | 0 | 46 | 164
09:00 | 3450 | 2084 | 896 | 38 | 130 | 1138.47 | 220 | 4638 | 328.91 | 175 | 205 | 0 | 0 | 52 | 172
09:30 | 3429.5 | 2097.5 | 896 | 38 | 126 | 1114.935 | 220 | 4703 | 310.99 | 183.5 | 222 | 0 | 0 | 39.5 | 195
10:00 | 3409 | 2111 | 896 | 38 | 122 | 1091.4 | 220 | 4768 | 293.07 | 192 | 239 | 0 | 0 | 27 | 218
10:30 | 3401 | 2126.5 | 896 | 38 | 126 | 1095.645 | 220 | 4809.5 | 321.45 | 192 | 252.5 | 0 | 0 | 31.5 | 192
11:00 | 3393 | 2142 | 896 | 38 | 130 | 1099.89 | 220 | 4851 | 349.83 | 192 | 266 | 0 | 0 | 36 | 166
11:30 | 3386 | 2155 | 896 | 38 | 135 | 1157.34 | 220 | 5034 | 364.225 | 195.5 | 290 | 0 | 0 | 25 | 192.5
12:00 | 3379 | 2168 | 896 | 38 | 140 | 1214.79 | 220 | 5217 | 378.62 | 199 | 314 | 0 | 0 | 14 | 219
12:30 | 3359 | 2093.5 | 896 | 38 | 140 | 1352.355 | 220 | 5214 | 425.3 | 211 | 371 | 0 | 0 | 26.5 | 277
13:00 | 3339 | 2019 | 896 | 38 | 140 | 1489.92 | 220 | 5211 | 471.98 | 223 | 428 | 0 | 0 | 39 | 335
13:30 | 3292.5 | 2047.5 | 896 | 38 | 144 | 1455.19 | 220 | 5228 | 408.24 | 228.5 | 455.5 | 0 | 0 | 36 | 331
14:00 | 3246 | 2076 | 896 | 38 | 148 | 1420.46 | 220 | 5245 | 344.5 | 234 | 483 | 0 | 0 | 33 | 327
14:30 | 3239 | 2074 | 896 | 38 | 149 | 1429.48 | 221 | 5270.5 | 338.7 | 205.5 | 481.5 | 0 | 0 | 29 | 324
15:00 | 3232 | 2072 | 896 | 38 | 150 | 1438.5 | 222 | 5296 | 332.9 | 177 | 480 | 0 | 0 | 25 | 321
15:30 | 3200 | 2073.5 | 896 | 38 | 149 | 1426.915 | 219.5 | 5334.5 | 334.9 | 186 | 495 | 0 | 0 | 16.5 | 281.5
16:00 | 3168 | 2075 | 896 | 38 | 148 | 1415.33 | 217 | 5373 | 336.9 | 195 | 510 | 0 | 0 | 8 | 242
16:30 | 3171 | 2006.5 | 895.5 | 38 | 139 | 1417.87 | 218.5 | 5272 | 219.3 | 199 | 518.5 | 0 | 0 | 8 | 225
17:00 | 3174 | 1938 | 895 | 38 | 130 | 1420.41 | 220 | 5171 | 101.7 | 203 | 527 | 0 | 0 | 8 | 208
17:30 | 3201 | 1917.5 | 895.5 | 38 | 131 | 1358.2 | 220 | 5140 | 69.97 | 211 | 586 | 0 | 0 | 16.5 | 205
18:00 | 3228 | 1897 | 896 | 38 | 132 | 1295.99 | 220 | 5109 | 38.24 | 219 | 645 | 0 | 0 | 25 | 202
18:30 | 3232 | 1914 | 896 | 38 | 144 | 1281.895 | 220 | 5432 | 19.12 | 388.5 | 825.5 | 0 | 0 | 24.5 | 221.5
19:00 | 3236 | 1931 | 896 | 38 | 156 | 1267.8 | 220 | 5755 | 0 | 558 | 1006 | 0 | 0 | 24 | 241
19:30 | 3148 | 1937 | 896 | 38 | 150 | 1492.21 | 220 | 6070 | 0 | 630 | 1191 | 0 | 0 | 12 | 394
20:00 | 3178 | 1979 | 896 | 38 | 140 | 1479.29 | 220 | 6147 | 0 | 548 | 1064 | 0 | 0 | 17 | 394
20:30 | 3189.5 | 2065 | 872.5 | 38 | 137 | 1485.395 | 220 | 6162 | 0 | 542 | 1032 | 0 | 0 | 18.5 | 454.5
21:00 | 3201 | 2151 | 849 | 38 | 134 | 1491.5 | 220 | 6177 | 0 | 536 | 1000 | 0 | 0 | 20 | 515
21:30 | 3193.5 | 2129.5 | 849 | 38 | 138 | 1487.815 | 221 | 6176.5 | 0 | 524 | 999.5 | 0 | 0 | 27 | 480
22:00 | 3186 | 2108 | 849 | 38 | 142 | 1484.13 | 222 | 6176 | 0 | 512 | 999 | 0 | 0 | 34 | 445
22:30 | 3104 | 2171 | 872.5 | 38 | 143 | 1489.99 | 222 | 6109 | 0 | 502 | 1044.6 | 0 | 0 | 44.5 | 452
23:00 | 3022 | 2234 | 896 | 38 | 144 | 1495.85 | 222 | 6042 | 0 | 492 | 1090.2 | 0 | 0 | 55 | 459
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 18-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 118 | 11 | 482 | 156 | 1692 | 338 | Ishurdi-Ghorashal Ckt-1 | Export | 3470909.09
1:00 | 122 | 3 | 484 | 148 | 1590 | 376
2:00 | 126 | 14 | 508 | 158 | 1558 | 406 |  | Import | 0
3:00 | 125 | 15 | 460 | 130 | 1376 | 432
4:00 | 129 | 19 | 466 | 130 | 1350 | 438 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 132 | 21 | 476 | 126 | 1368 | 426
6:00 | 139 | 27 | 466 | 120 | 1352 | 438 |  | Import | 0
7:00 | 136 | 31 | 444 | 122 | 1330 | 456
8:00 | 151 | 39 | 480 | 134 | 1416 | 500 | Sirajganj-Sreepur Ckt-1 | Export | 2983000
9:00 | 187 | 62 | 526 | 156 | 1512 | 560
10:00 | 193 | 71 | 508 | 146 | 1470 | 636 |  | Import | 0
11:00 | 184 | 72 | 502 | 172 | 1420 | 668
12:00 | 168 | 60 | 500 | 210 | 1528 | 718 | Sirajganj-Sreepur Ckt-2 | Export | 2995000
13:00 | 170 | 37 | 580 | 121 | 1656 | 740
14:00 | 153 | 30 | 546 | 220 | 1600 | 704 |  | Import | 0
15:00 | 167 | 42 | 570 | 236 | 1666 | 702
16:00 | 179 | 45 | 600 | 234 | 1776 | 726 | Gopalganj-Aminbazar Ckt-1 | Export | 19170000
17:00 | 175 | 46 | 590 | 220 | 1820 | 700
18:00 | 157 | 40 | 520 | 211 | 1674 | 652 |  | Import | 0
18:30 | 163 | 43 | 550 | 212 | 1770 | 630
19:00 | 154 | 37 | 520 | 232 | 1786 | 578 | Gopalganj-Aminbazar Ckt-2 | Export | 19220000
19:30 | 123 | 7 | 468 | 176 | 1860 | 472
20:00 | 104 | -5 | 440 | 162 | 1830 | 458 |  | Import | 0
21:00 | 98 | 3 | 420 | 170 | 1766 | 454
22:00 | 100 | -1 | 420 | 154 | 1776 | 440 |  | Total Export | 47838909.09
23:00 | 111 | 0 | 440 | 168 | 1632 | 462 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 378 | 03:00 | 353 | 12:00 | Madunaghat | 393 | 07:00 | 379 | 16:00
Amtali | 413 | 04:00 | 401 | 21:00 | Meghnaghat | 389 | 07:00 | 362 | 13:00
Ashuganj | 409 | 6:00 | 381 | 13:00 | Payra | 414 | 07:00 | 404 | 20:00
Bhulta | 402 | 06:00 | 373 | 14:00 | Rahanpur | 403 | 08:00 | 381 | 20:00
Bibiana | 381 | 06:00 | 369 | 13:00 | Rampal | 399 | 07:00 | 374 | 22:00
BIPTC | 399 | 04:00 | 392 | 23:00
Bogura | 385 | 07:00 | 358 | 20:00
Gopalganj | 394 | 07:00 | 369 | 20:00
Kaliakoir | 370 | 06:00 | 343 | 12:00
Korerhat | 396 | 07:00 | 376 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 07:00 | 214 | 13:00 | Ishurdi | 237 | 08:00 | 209 | 20:00
AKSML | 236 | 07:00 | 223 | 15:00 | Jhenaidah | 226 | 09:00 | 198 | 20:00
Aminbazar | 232 | 04:00 | 211 | 12:00 | Kachua | 225 | 07:00 | 212 | 15:00
Ashuganj | 230 | 07:00 | 216 | 15:00 | Kaliakoir | 230 | 06:00 | 210 | 12:00
Ashuganj-400 | 230 | 7:00 | 216 | 15:00 | Keranigonj | 231 | 06:00 | 210 | 13:00
Baghabari | 234 | 05:00 | 217 | 20:00 | Khulna(S) | 227 | 06:00 | 205 | 20:00
Barapukuria | 223 | 19:00 | 210 | 20:00 | Korerhat | 226 | 07:00 | 214 | 15:00
Barapukuria-230 | 223 | 19:00 | 212 | 20:00 | Madunaghat | 238 | 07:00 | 228 | 15:00
Barishal | 227 | 07:00 | 216 | 19:30 | Madunaghat-400 | 239 | 07:00 | 229 | 16:00
Bheramara | 234 | 07:00 | 207 | 20:00 | Maniknagar | 230 | 03:00 | 210 | 13:00
Bhulta | 231 | 06:00 | 212 | 12:00 | Meghnaghat | 238 | 08:00 | 220 | 13:00
Bibiana | 221 | 06:00 | 211 | 16:00 | Meghnaghat-400 | 233 | 06:00 | 215 | 13:00
BIPTC | 236 | 06:00 | 207 | 20:00 | Mirsorai | 230 | 07:00 | 218 | 13:00
Bogura | 241 | 10:00 | 224 | 21:00 | Naogaon | 0 | 00:00 | N/A | N/A
Bogura-400 | 241 | 07:00 | 224 | 20:00 | Purbasadipur | 220 | 06:00 | 206 | 20:00
Borhanuddin | 230 | 08:00 | 222 | 21:00 | Rajshahi | 232 | 07:00 | 204 | 20:00
BSRM | 227 | 07:00 | 215 | 21:00 | Rampal | 221 | 16:00 | 207 | 20:00
Charfasson | 231 | 04:00 | 222 | 22:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 225 | 00:00 | 210 | 14:00 | Rampura | 230 | 06:00 | 209 | 13:00
Cumilla(N) | 227 | 06:00 | 212 | 15:00 | Shikalbaha | 236 | 01:00 | 226 | 12:00
Faridpur | 226 | 07:00 | 209 | 21:00 | Shyampur | 232 | 06:00 | 211 | 13:00
Fenchuganj | 223 | 07:00 | 212 | 15:00 | Siddhirganj | 230 | 05:00 | 213 | 12:00
Feni | 224 | 06:00 | 212 | 13:00 | Sirajgonj | 240 | 06:00 | 228 | 21:00
Ghorashal | 230 | 00:00 | 218 | 14:00 | Sreepur | 227 | 07:00 | 211 | 21:00
Ghorashal-230 | 216 | 06:00 | 197 | 15:00 | Tongi | 222 | 07:00 | 200 | 11:00
Gopalganj | 227 | 07:00 | 212 | 21:00
GPH | 234 | 03:00 | 222 | 15:00
Haripur | 231 | 07:00 | 212 | 13:00
Hasnabad | 231 | 07:00 | 214 | 14:00
Hathazari | 234 | 00:00 | 224 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 121 | 12:00 | Madunaghat | 137 | 07:00 | 129 | 12:00
Agargaon | 134 | 06:00 | 121 | 13:00 | Magura | 133 | 08:00 | 115 | 20:00
Agrabad | 136 | 06:00 | 127 | 15:00 | Mahasthangarh | 135 | 09:00 | 123 | 20:00
AKS | 134 | 05:00 | 127 | 15:00 | Maijdee | 126 | 07:00 | 117 | 23:00
Aminbazar | 133 | 04:00 | 118 | 12:00 | Manikganj | 129 | 06:00 | 120 | 13:00
Amnura | 135 | 18:30 | 117 | 21:00 | Maniknagar | 136 | 06:00 | 121 | 13:00
Ashuganj | 131 | 06:00 | 123 | 21:00 | Matarbari | 126 | 10:00 | 112 | 21:00
Ashuganj-230 | 139 | 21:00 | 128 | 15:00 | Matuail | 134 | 06:00 | 122 | 12:00
Bagerhat | 127 | 06:00 | 113 | 20:00 | Metrorail_Motijheel | 136 | 06:00 | 121 | 13:00
Bajitpur | 125 | 07:00 | 118 | 00:00 | Metrorail_Uttara | 133 | 05:00 | 115 | 12:00
Bakerganj | 131 | 03:00 | 123 | 21:00 | Millgate | 135 | 05:00 | 119 | 12:00
Bakulia | 136 | 01:00 | 128 | 15:00 | Mirpur | 132 | 05:00 | 119 | 12:00
Banani | 135 | 05:00 | 121 | 12:00 | Mirzapur | 130 | 07:00 | 120 | 16:00
Bangabhaban | 135 | 04:00 | 121 | 13:00 | Mithapukur | 133 | 19:00 | 120 | 20:00
Barapukuria | 135 | 06:00 | 123 | 20:00 | MI_Cement | 137 | 06:00 | 121 | 13:00
Barguna | 131 | 08:00 | 122 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 07:00 | 121 | 20:00 | Mogbazar | 0 | 00:00 | N/A | N/A
Barishal-230 | 131 | 07:00 | 122 | 19:30 | Mongla | 128 | 08:00 | 112 | 19:30
Baroaulia | 136 | 00:00 | 128 | 16:00 | Motijheel | 135 | 04:00 | 121 | 13:00
Baroirhat | 131 | 06:00 | 124 | 20:00 | Muktagacha | 121 | 00:00 | 114 | 19:00
Bashundhara | 135 | 05:00 | 115 | 12:00 | Munshiganj | 132 | 03:00 | 121 | 12:00
BashundharaCement | 134 | 07:00 | 122 | 13:00 | Muradnagar | 128 | 06:00 | 118 | 13:00
Beanibazar | 124 | 07:00 | 113 | 15:00 | Mymensingh | 121 | 13:00 | 106 | 21:00
Benapole | 131 | 09:00 | 110 | 21:00 | Nabinagar | 132 | 05:00 | 115 | 12:00
Bhaluka | 125 | 08:00 | 116 | 21:00 | Naogaon | 136 | 09:00 | 120 | 21:00
Bhandaria | 128 | 08:00 | 116 | 19:30 | Narail | 135 | 09:00 | 113 | 21:00
Bhangura | 134 | 06:00 | 123 | 20:00 | Narinda | 136 | 6:00 | 121 | 13:00
Bheramara | 137 | 06:00 | 121 | 20:00 | Narshingdi | 130 | 05:00 | 115 | 13:00
Bheramara(GK) | 137 | 06:00 | 121 | 20:00 | Natore | 136 | 07:00 | 118 | 20:00
Bhulta | 130 | 06:00 | 118 | 12:00 | Nawabganj | 136 | 06:00 | 122 | 13:00
Bog-Sherpur | 136 | 07:00 | 124 | 20:00 | Netrakona | 120 | 10:00 | 105 | 21:00
Bogura | 138 | 07:00 | 127 | 21:00 | New | 134 | 03:00 | 120 | 12:00
Bogura-230 | 138 | 06:00 | 127 | 21:00 | Niamatpur | 133 | 18:30 | 123 | 21:00
Brahmanbaria | 128 | 05:00 | 121 | 15:00 | Noapara | 133 | 06:00 | 118 | 19:30
Cantonment | 134 | 06:00 | 120 | 13:00 | Pabna | 135 | 06:00 | 120 | 20:00
Chandina | 130 | 06:00 | 121 | 13:00 | Palashbari | 130 | 06:00 | 118 | 20:00
Chandpur | 126 | 00:00 | 119 | 13:00 | Panchagarh | 138 | 19:00 | 126 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 137 | 00:00 | 132 | 14:00 | Patiya | 134 | 01:00 | 127 | 16:00
Chapai | 132 | 09:00 | 123 | 22:00 | Patnitala | 133 | 02:00 | 119 | 21:00
Charsaidpur | 133 | 03:00 | 122 | 13:00 | Patuakhali | 130 | 05:00 | 124 | 19:30
Chauddagram | 129 | 06:00 | 121 | 13:00 | Payra | 134 | 06:00 | 129 | 22:00
Chhatak | 123 | 17:00 | 110 | 15:00 | PHP | 131 | 07:00 | 123 | 13:00
Chowmuhani | 126 | 00:00 | 118 | 22:00 | Postogola | 138 | 05:00 | 124 | 13:00
Chuadanga | 133 | 09:00 | 107 | 19:00 | Pubail | 127 | 01:00 | 115 | 15:00
Coxsbazar | 126 | 10:00 | 116 | 19:00 | Purbachal | 135 | 05:00 | 122 | 13:00
Cumilla(N) | 131 | 06:00 | 121 | 22:00 | Purbasadipur | 134 | 19:00 | 124 | 20:00
Cumilla(S) | 130 | 06:00 | 121 | 22:00 | Rahanpur | 135 | 10:00 | 127 | 21:00
Daganbhuiyan | 129 | 07:00 | 121 | 13:00 | Rahanpur-400 | 135 | 07:00 | 128 | 20:00
Daudkandi | 128 | 06:00 | 116 | 15:00 | Rahim | 135 | 06:00 | 122 | 13:00
DhakaUniversity | 135 | 05:00 | 123 | 12:00 | Rajbari | 128 | 07:00 | 117 | 20:00
Dhamrai | 133 | 04:00 | 128 | 23:00 | Rajendrapur | 125 | 06:00 | 117 | 21:00
Dhanmondi | 135.5 | 06:00 | 122 | 13:00 | Rajshahi | 134 | 07:00 | 117 | 20:00
Dohazari | 132 | 01:00 | 124 | 16:00 | Rajshahi-230 | 134 | 07:00 | 117 | 20:00
Faridpur | 129 | 06:00 | 121 | 20:00 | Ramganj | 124 | 09:00 | 115 | 21:00
Fatullah | 137 | 05:00 | 121 | 13:00 | Rampur | 135 | 02:00 | 127 | 16:00
Fenchuganj | 131 | 07:00 | 124 | 15:00 | Rampura | 135 | 05:00 | 122 | 12:00
Feni | 130 | 02:00 | 123 | 22:00 | Rangamati | 136 | 04:00 | 131 | 15:00
Feni-230 | 130 | 07:00 | 122 | 13:00 | Rangpur | 129 | 05:00 | 118 | 20:00
Ghatail | 120 | 07:00 | 114 | 01:00 | Ruppur | 138 | 07:00 | 122 | 20:00
Ghorashal | 129 | 02:00 | 118 | 14:00 | Saidpur | 137 | 14:00 | 121 | 20:00
Goalpara | 136 | 10:00 | 121 | 21:00 | Santhia | 136 | 07:00 | 122 | 20:00
Gollamari | 136 | 08:00 | 121 | 21:00 | Satkhira | 132 | 06:00 | 112 | 21:00
Gopalganj | 128 | 06:00 | 119 | 19:30 | Satmasjid | 133 | 06:00 | 119 | 13:00
Gopalganj-400 | 132 | 06:00 | 123 | 19:30 | Savar | 130 | 07:00 | 118 | 12:00
Gulshan | 135 | 06:00 | 121 | 12:00 | SevenRings | 129 | 06:00 | 118 | 15:00
Halishahar | 135 | 00:00 | 128 | 15:00 | ShahCement | 133 | 03:00 | 122 | 13:00
Haripur | 134 | 05:00 | 123 | 13:00 | Shahjadpur | 136 | 03:00 | 130 | 13:00
HaripurSBU | 135 | 06:00 | 124 | 15:00 | Shahjibazar | 130 | 07:00 | 121 | 15:00
Hasnabad | 138 | 05:00 | 123 | 13:00 | Shahmirpur | 135 | 07:00 | 129 | 15:00
Hathazari | 136 | 00:00 | 131 | 16:00 | Shariatpur | 130 | 07:00 | 119 | 19:30
Hatirjheel | 134 | 04:00 | 128 | 05:00 | Sherpur | 119 | 00:00 | 110 | 21:00
Ishurdi | 139 | 07:00 | 123 | 20:00 | Shikalbaha | 126 | 04:00 | 119 | 16:00
Jaldhaka | 131 | 06:00 | 119 | 20:00 | Shikalbaha-230 | 136 | 01:00 | 130 | 12:00
Jamalpur | 122 | 00:00 | 112 | 21:00 | Shitalakhya | 137 | 06:00 | 121 | 13:00
Jashore | 132 | 09:00 | 112 | 21:00 | Sholosohor | 136 | 00:00 | 129 | 16:00
Jhenaidah | 138 | 09:00 | 118 | 20:00 | Shomvuganj | 121 | 10:00 | 111 | 21:00
Jhenaidah-230 | 137 | 10:00 | 117 | 23:00 | Shyampur | 134 | 06:00 | 121 | 13:00
Joydebpur | 125 | 00:00 | 112 | 12:00 | Shyampur-230 | 136 | 06:00 | 122 | 13:00
Joypurhat | 133 | 09:00 | 119 | 21:00 | Siddhirganj | 135 | 06:00 | 123 | 13:00
Juldah | 135 | 01:00 | 128 | 16:00 | Sirajganj | 132 | 07:00 | 120 | 20:00
Kabirpur | 133 | 00:00 | 114 | 12:00 | Sitakunda | 136 | 07:00 | 129 | 15:00
Kachua | 127 | 06:00 | 120 | 15:00 | Sonargaon | 132 | 06:00 | 120 | 13:00
Kaliakoir | 136 | 05:00 | 122 | 12:00 | Sreemongol | 128 | 07:00 | 120 | 21:00
Kaliganj | 136 | 09:00 | 116 | 19:00 | Sreepur | 127 | 06:00 | 120 | 21:00
Kallyanpur | 132 | 07:00 | 120 | 12:00 | Srinagar | 136 | 05:00 | 124 | 13:00
Kalurghat | 137 | 07:00 | 131 | 15:00 | SSM | 140 | 00:00 | 135 | 14:00
Kamrangirchar | 136 | 05:00 | 117 | 16:00 | Sunamganj | 119 | 17:00 | 108 | 15:00
Kaptai | 138 | 9:00 | 135 | 15:00 | Sylhet | 125 | 05:00 | 116 | 12:00
Kasba | 128 | 06:00 | 117 | 15:00 | Sylhet_(South) | 125 | 08:00 | 115 | 15:00
Kazla | 135 | 05:00 | 121 | 13:00 | Tangail | 124 | 07:00 | 116 | 16:00
Keranigonj | 137 | 06:00 | 123 | 13:00 | Taraganj | 133 | 18:30 | 121 | 20:00
Khagrachori | 135 | 06:00 | 130 | 15:00 | Tasnim | 132 | 06:00 | 120 | 13:00
Khulna | 135 | 06:00 | 120 | 21:00 | Thakurgaon | 137 | 19:00 | 125 | 20:00
Khulna(S) | 136 | 06:00 | 121 | 20:00 | TK | 137 | 04:00 | 131 | 14:00
Khulshi | 133 | 00:00 | 126 | 16:00 | Tongi | 136 | 07:00 | 123 | 11:00
Kishoreganj | 124 | 10:00 | 115 | 19:00 | Ullahpara | 134 | 05:00 | 121 | 21:00
Kodda | 132 | 00:00 | 113 | 15:00 | Ullon | 135 | 06:00 | 122 | 13:00
Korerhat | 133 | 06:00 | 126 | 15:00 | Uttara | 133 | 06:00 | 117 | 12:00
KSRM | 136 | 05:00 | 129 | 15:00 | UttaraNew | 133 | 05:00 | 115 | 12:00
Kulaura | 130 | 07:00 | 123 | 15:00 | Zigatola | 138 | 06:00 | 123 | 13:00
Kurigram | 128 | 09:00 | 114 | 20:00
Kushtia | 133 | 07:00 | 115 | 20:00
Laksam | 127 | 07:00 | 118 | 22:00
Lakshmipur | 125 | 06:00 | 117 | 21:00
Lalbag | 137 | 05:00 | 123 | 13:00
Lalmonirhat | 127 | 09:00 | 116 | 20:00
Madanganj | 134 | 07:00 | 122 | 13:00
Madaripur | 131 | 07:00 | 122 | 21:00
Madartek | 134 | 05:00 | 122 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division