## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-07-2026 | during | 20-07-2026 | during | 20-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 365 | 330 | 412 | 412 | 370.8 | 370.8 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 297 | 299 | 335 | 335 | 310 | 310 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 30 | 30 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 308 | 310 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 15 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 95 | 128 | 149.36 | 149.36 | 48 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 13 | 13 | 33 | 33 | 15 | 15 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 20 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 24 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 195 | 195 | 300 | 300 | 48 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 106 | 85 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 34 | 105 | 105 | 17 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 35 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 27 | 27 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 400 | 461 | 583 | 583 | 524.5 | 524.5 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 453 | 450 | 718 | 718 | 658 | 658 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 105 | 143 | 143 | 143 | 143 | 143 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2606 | 2709 | 5775.22 | 5775.22 | 2692.3 | 3266.3
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 2 | 0 | 8 | 0 | 8 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 5 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 222 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 21 | 0 | 0 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 51 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 72 | 24 | 56 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 34 | 0 | 34 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 8 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 7 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.38 | 0 | 1.44 | 0 | 1.44 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 10 | 17 | 54.36 | 54.36 | 0 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 6 | 51 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 14 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 32 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1192 | 1090 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 26 | 28 | 24 | 26 | 24 | 26 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 1125 | 1150 | 1150 | 1125 | 1125 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2604.38 | 2713 | 3906.3 | 3979.86 | 3404.44 | 3574
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 210 | 197 | 221.25 | 221.25 | 215 | 215 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 270 | 278 | 350.01 | 350.01 | 270 | 270 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 220 | 220 | 342.01 | 342.01 | 220 | 220 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 210 | 210 | 393 | 393 | 210 | 210 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 40 | 50 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 25 | 42 | 42 | 42 | 42 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 93 | 163 | 163 | 95 | 95 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 15 | 17 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 146 | 130 | 84 | 80 | 150 | 150 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 14 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 26 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 26 | 90 | 115 | 115 | 34 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 16 | 0 | 40 | 0 | 40 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1313 | 1401 | 2744.44 | 2700.44 | 1557.2 | 1785.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-07-2026 | during | 20-07-2026 | during | 20-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 11.5 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.5 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 94 | 85 | 50 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 56 | 67 | 50 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 40.56 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 9 | 18 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 212.56 | 170 | 454.6 | 516.5 | 265.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 28 | 40 | 40 | 40 | 40 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 144 | 127 | 163 | 163 | 163 | 163 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 142 | 144 | 142 | 142 | 142 | 142 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 28 | 28 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 84 | 84 | 84 | 84 | 84 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | ST Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 14 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 229 | 319 | 250 | 250 | 230 | 230 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1111 | 1182 | 1195 | 1195 | 1083 | 1083
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 896 | 894 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 37 | 37 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 32 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 96.61 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1035 | 1086 | 550 | 1234.2 | 1234.2 | 1234.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2065.61 | 2066 | 2882 | 3491.2 | 2411.2 | 2336.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 634 | 1000 | 700 | 1050 | 800 | 800 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1075 | 1100 | 1163.05 | 1163.05 | 1163.05 | 1163.05 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 227 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.39 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3407.64 | 2299.39 | 2683 | 2781.05 | 3130.05 | 2737.05 | 2736.05
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 28.05 | 0 | 55 | 0 | 55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 152 | 144 | 214 | 214 | 170 | 170 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 126 | 129 | 220 | 220 | 150 | 150 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 133 | 128 | 220 | 220 | 150 | 150 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 323 | 290 | 413.79 | 413.79 | 305 | 305 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 93 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 6 | 50 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 0.75 | 0 | 5.6 | 0 | 5.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1353.36 | 1484.02 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 8 | 0 | 37 | 0 | 37 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 73 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2203.16 | 2368.02 | 3232.72 | 3035.12 | 2505.73 | 2470.13
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 180 | 180 | 180 | 180 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 108 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 90 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 10 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 87 | 0 | 146.79 | 0 | 146.79 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 281 | 378 | 619.79 | 442 | 506.79 | 364
System Total |  |  |  |  | 28843.2 | 29250.117 | 14696.1 | 15670.02 | 23591.12 | 24265.39 | 17162.81 | 17873.88
Forecast Scenario (20-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15650 |  | 47.75 |  | 15700
|  |  |  | 1:00 | 15250 |  | 57.3 |  | 15310
|  |  |  | 2:00 | 14570 |  | 191 |  | 14770
|  |  |  | 3:00 | 14370 |  | 248.3 |  | 14630
|  |  |  | 4:00 | 14130 |  | 286.5 |  | 14430
|  |  |  | 5:00 | 13960 |  | 286.5 |  | 14260
|  |  |  | 6:00 | 13560 |  | 334.25 |  | 13910
|  |  |  | 7:00 | 13540 |  | 305.6 |  | 13860
|  |  |  | 8:00 | 13550 |  | 382 |  | 13950
|  |  |  | 9:00 | 13760 |  | 429.75 |  | 14210
|  |  |  | 10:00 | 13920 |  | 410.65 |  | 14350
|  |  |  | 11:00 | 14330 |  | 353.35 |  | 14700
|  |  |  | 12:00 | 14700 |  | 477.5 |  | 15200
|  |  |  | 13:00 | 14930 |  | 439.3 |  | 15390
|  |  |  | 14:00 | 14570 |  | 611.2 |  | 15210
|  |  |  | 15:00 | 14630 |  | 735.35 |  | 15400
|  |  |  | 16:00 | 14230 |  | 706.7 |  | 14970
|  |  |  | 17:00 | 13860 |  | 592.1 |  | 14480
|  |  |  | 18:00 | 13580 |  | 582.55 |  | 14190
|  |  |  | 18:30 | 14750 |  | 47.75 |  | 14800
|  |  |  | 19:00 | 14920 |  | 611.2 |  | 15560
|  |  |  | 19:30 | 16050 |  | 335 |  | 16400
|  |  |  | 20:00 | 16100 |  | 114.6 |  | 16220
|  |  |  | 21:00 | 16000 |  | 191 |  | 16200
|  |  |  | 22:00 | 16000 |  | 152.8 |  | 16160
|  |  |  | 23:00 | 15900 |  | 47.75 |  | 15950
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 15200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 335
Probable Maximum Demand at Evening Peak: |  |  | 16400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 350.01 MKWHr. |  | 102 | 0 | 50 | 183 | 0 | 0 | 0 | 0 | 0 | 335
*** This report is generated digitally from Operation Information System (OIS) at 10:27 hrs on 20-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-07-2026 | [28 empty] | Date: | 19-07-2026 | [28 empty] | Date: | 19-07-2026 | [28 empty] | Date: | 19-07-2026 | [28 empty] | Date: | 19-07-2026 | [18 empty] | Date: | 19-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [18 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 449 | 17 | 27 | 149 | 46 | 195 | 22 | 35 | 48 | 0 | 0 | 302 | 505 | 0 | 35 | 304 | 0 | 0 | 0 | 143 | 13 | 21 | 0 | 0 | 0 | 45 | 24 | 0 | 45 | 34 | 0 | 18 | 0 | 0 | 0 | 222 | 56 | 18 | 1125 | 17 | 0 | 19 | 0 | 45 | 0 | 0 | 0 | 0 | 1160 | 0 | 20 | 0 | 210 | 270 | 220 | 51 | 5 | 186 | 10 | 60 | 91 | 67 | 27 | 19 | 0 | 144 | 0 | 0 | 16 | 315 | 0 | 229 | 40 | 0 | 149 | 0 | 17 | 0 | 84 | 0 | 142 | 15 | 100 | 17 | 9 | 0 | 48 | 0 | 0 | 0 | 12 | 8125 | 896 | 0 | 0 | 0 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1203 | 0 | 0 | 0 | 1486.79 | 0 | 0 | 0 | 20 | 45 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 128 | 0 | 135 | 0 | 317 | 0 | 0 | 180 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 120 | 220 | 0 | 800 | 1163 | 17 | 7481.99 | 15606.99 | 103.87
01:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 435 | 0 | 27 | 46 | 31 | 195 | 30 | 35 | 53 | 0 | 0 | 288 | 450 | 0 | 35 | 300 | 0 | 0 | 0 | 143 | 13 | 21 | 0 | 0 | 0 | 0 | 24 | 0 | 27 | 34 | 0 | 0 | 0 | 0 | 0 | 222 | 67 | 18 | 1125 | 0 | 0 | 19 | 0 | 66 | 0 | 0 | 0 | 0 | 1150 | 0 | 20 | 0 | 210 | 270 | 220 | 51 | 5 | 191 | 10 | 65 | 93 | 80 | 28 | 19 | 0 | 142 | 0 | 0 | 16 | 305 | 0 | 229 | 40 | 0 | 138 | 0 | 17 | 0 | 84 | 0 | 142 | 15 | 101 | 0 | 9 | 0 | 48 | 0 | 0 | 0 | 0 | 7784 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1205 | 0 | 0 | 0 | 1484.66 | 0 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 128 | 0 | 136 | 0 | 318 | 0 | 0 | 180 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 307 | 120 | 220 | 0 | 800 | 1163 | 17 | 7435.66 | 15219.66 | 103.88
02:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 506 | 0 | 27 | 34 | 31 | 60 | 15 | 0 | 0 | 0 | 0 | 299 | 445 | 0 | 0 | 309 | 0 | 0 | 0 | 143 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 12 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 0 | 0 | 210 | 270 | 220 | 51 | 5 | 191 | 10 | 65 | 93 | 0 | 0 | 19 | 0 | 142 | 0 | 0 | 16 | 305 | 0 | 229 | 40 | 0 | 132 | 0 | 17 | 0 | 84 | 0 | 142 | 15 | 101 | 0 | 9 | 0 | 48 | 0 | 0 | 0 | 0 | 7167 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1149 | 0 | 0 | 0 | 1439.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 130 | 0 | 138 | 0 | 333 | 0 | 0 | 180 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1050 | 1163 | 0 | 7402.97 | 14569.97 | 103.87
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 458 | 0 | 27 | 34 | 31 | 30 | 15 | 0 | 0 | 0 | 0 | 294 | 450 | 0 | 0 | 304 | 0 | 0 | 0 | 143 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 11 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 0 | 0 | 210 | 270 | 220 | 51 | 5 | 191 | 10 | 0 | 93 | 0 | 0 | 19 | 0 | 136 | 0 | 0 | 16 | 310 | 0 | 229 | 40 | 0 | 145 | 0 | 17 | 0 | 84 | 0 | 143 | 15 | 100 | 1 | 9 | 0 | 48 | 0 | 0 | 0 | 0 | 7094 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1051 | 0 | 0 | 0 | 1435.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 130 | 0 | 139 | 0 | 339 | 0 | 0 | 180 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 1050 | 1163 | 0 | 7270.37 | 14364.37 | 103.86
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 483 | 0 | 26 | 34 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 450 | 0 | 0 | 304 | 0 | 0 | 0 | 143 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 16 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1045 | 0 | 0 | 0 | 210 | 270 | 220 | 51 | 5 | 191 | 10 | 0 | 93 | 0 | 0 | 19 | 0 | 130 | 0 | 0 | 16 | 305 | 0 | 229 | 40 | 0 | 140 | 0 | 17 | 0 | 84 | 0 | 143 | 15 | 100 | 17 | 9 | 0 | 48 | 0 | 0 | 0 | 0 | 7001 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 999 | 0 | 0 | 0 | 1434.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 131 | 0 | 139 | 0 | 340 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 1050 | 1115 | 0 | 7121.71 | 14122.71 | 103.85
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 459 | 0 | 17 | 34 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 445 | 0 | 0 | 307 | 0 | 0 | 0 | 143 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 5 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 210 | 270 | 220 | 51 | 5 | 191 | 10 | 0 | 93 | 0 | 0 | 19 | 0 | 128 | 0 | 0 | 16 | 310 | 0 | 229 | 40 | 0 | 139 | 0 | 17 | 0 | 84 | 0 | 145 | 15 | 100 | 17 | 9 | 0 | 48 | 0 | 0 | 0 | 0 | 6918 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 954 | 0 | 0 | 0 | 1395.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 131 | 0 | 139 | 0 | 349 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 1050 | 1103 | 0 | 7035.74 | 13953.74 | 103.84
06:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 475 | 0 | 17 | 34 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 450 | 0 | 0 | 307 | 0 | 0 | 0 | 143 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0.03 | 222 | 0 | 9 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 1 | 0 | 0 | 210 | 270 | 220 | 51 | 5 | 197 | 10 | 0 | 93 | 0 | 0 | 19 | 0 | 124 | 0 | 4 | 16 | 300 | 0 | 229 | 40 | 0 | 142 | 0 | 17 | 0 | 84 | 0 | 144 | 15 | 101 | 0 | 9 | 0.45 | 48 | 0 | 0 | 0.49 | 0 | 6901.97 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.12 | 958 | 0 | 0 | 0 | 1381.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0.35 | 152 | 0 | 131 | 0 | 139 | 0 | 352 | 0 | 0.04 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0.01 | 0 | 307 | 120 | 220 | 0 | 700 | 1069 | 0 | 6652.08 | 13554.05 | 103.83
07:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 511 | 0 | 17 | 34 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 450 | 0 | 0 | 315 | 0 | 0 | 0 | 143 | 14 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0.53 | 222 | 0 | 15 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 2 | 0 | 0 | 210 | 270 | 220 | 51 | 5 | 195 | 10 | 0 | 92 | 0 | 0 | 19 | 0 | 118 | 0 | 8 | 16 | 305 | 0 | 229 | 40 | 0 | 145 | 1 | 17 | 0 | 84 | 0 | 144 | 15 | 101 | 0 | 9 | 2 | 48 | 0 | 0.2 | 2.92 | 0 | 6995.65 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 962 | 0 | 0 | 0 | 1432.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.17 | 11 | 0 | 0 | 4.27 | 152 | 0 | 131 | 0 | 139 | 0 | 347 | 0 | 0.41 | 170 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 8 | 0.05 | 0 | 307 | 120 | 220 | 0 | 500 | 1068 | 0 | 6535.88 | 13531.53 | 103.82
08:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 476 | 0 | 17 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 450 | 0 | 0 | 303 | 0 | 0 | 0 | 143 | 13.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0.73 | 222 | 0 | 2 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 3 | 0 | 0 | 210 | 270 | 220 | 51 | 5 | 191 | 10 | 0 | 92 | 0 | 0 | 19 | 0 | 120 | 0 | 14 | 0 | 310 | 0 | 229 | 40 | 0 | 151 | 1 | 17 | 0 | 84 | 0 | 144 | 15 | 100 | 0 | 9 | 3.69 | 48 | 0 | 0.6 | 5.69 | 0 | 6908.21 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24 | 957 | 0 | 0 | 0 | 1452.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.19 | 23 | 0 | 0 | 12.26 | 153 | 0 | 131 | 0 | 139 | 0 | 348 | 0 | 1.41 | 180 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.2 | 11 | 0.11 | 0 | 307 | 120 | 220 | 0 | 500 | 1120 | 0 | 6640.19 | 13548.4 | 103.81
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 480 | 17 | 17 | 49 | 32 | 45 | 4 | 4 | 17 | 0 | 0 | 290 | 450 | 0 | 0 | 306 | 0 | 0 | 0 | 143 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0.8 | 222 | 0 | 0 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1051 | 4 | 0 | 0 | 210 | 270 | 220 | 51 | 0 | 197 | 0 | 0 | 93 | 0 | 0 | 19 | 0 | 124 | 0 | 14 | 0 | 310 | 0 | 229 | 40 | 0 | 143 | 5 | 17 | 0 | 84 | 0 | 140 | 15 | 100 | 0 | 9 | 9.4 | 48 | 0 | 0.5 | 28.12 | 0 | 7049.82 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 47 | 1020 | 0 | 0 | 0 | 1405.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.44 | 32 | 0 | 0 | 20.57 | 152 | 0 | 131 | 0 | 138 | 0 | 343 | 0 | 1.98 | 180 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.4 | 22 | 0.29 | 0 | 307 | 120 | 180 | 0 | 500 | 1140 | 0 | 6704.03 | 13753.85 | 103.8
10:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 436 | 30 | 17 | 52 | 94 | 45 | 15 | 17 | 17 | 0 | 0 | 290 | 450 | 0 | 0 | 305 | 0 | 0 | 0 | 143 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 2.11 | 222 | 0 | 0 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 0.5 | 0 | 0 | 210 | 270 | 220 | 51 | 0 | 210 | 0 | 0 | 92 | 0 | 0 | 19 | 0 | 132 | 0 | 29 | 0 | 315 | 0 | 219 | 40 | 0 | 142 | 6 | 17 | 0 | 84 | 5 | 142 | 15 | 100 | 0 | 9 | 4.24 | 48 | 0 | 1.3 | 19.48 | 0 | 7203.63 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 35.59 | 1052 | 0 | 0 | 0 | 1407.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.41 | 47 | 0 | 0 | 21.82 | 153 | 0 | 131 | 0 | 136 | 0 | 331 | 0 | 2.96 | 180 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1.2 | 40 | 0.27 | 0 | 307 | 120 | 180 | 0 | 500 | 1100 | 0 | 6710.15 | 13913.78 | 103.79
11:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 523 | 0 | 25 | 81 | 95 | 145 | 15 | 35 | 17 | 0 | 0 | 306 | 415 | 0 | 0 | 317 | 0 | 0 | 0 | 105 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 1.41 | 222 | 0 | 0 | 1125 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 1145 | 2 | 18 | 0 | 210 | 270 | 220 | 51 | 0 | 210 | 0 | 1 | 91 | 0 | 0 | 19 | 0 | 138 | 0 | 12 | 0 | 305 | 0 | 229 | 40 | 0 | 137 | 10 | 17 | 0 | 81 | 30 | 142 | 15 | 100 | 0 | 30 | 6.55 | 48 | 0 | 1.2 | 32.27 | 0 | 7523.43 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 70.61 | 1005 | 0 | 0 | 0 | 1334.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.33 | 58 | 0 | 0 | 55.6 | 152 | 0 | 129 | 0 | 135 | 0 | 311 | 0 | 3.45 | 180 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1 | 64 | 0.6 | 0 | 251 | 120 | 220 | 0 | 698 | 1050 | 0 | 6800.77 | 14324.2 | 103.78
12:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 453 | 15 | 27 | 106 | 95 | 195 | 30 | 35 | 72 | 0 | 0 | 297 | 400 | 0 | 0 | 308 | 0 | 0 | 0 | 105 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 10 | 0 | 0 | 2.38 | 222 | 6 | 0 | 1125 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1192 | 2 | 40 | 0 | 210 | 270 | 220 | 51 | 0 | 210 | 0 | 26 | 90 | 15 | 0 | 19 | 0 | 146 | 0 | 16 | 0 | 305 | 0 | 229 | 40 | 0 | 144 | 9 | 17 | 0 | 83 | 28 | 142 | 14 | 100 | 0 | 56 | 11.5 | 94 | 0 | 1.5 | 40.56 | 9 | 7846.94 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 96.61 | 1035 | 0 | 0 | 0 | 1353.36 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 28.05 | 73 | 0 | 0 | 8 | 152 | 0 | 126 | 0 | 133 | 0 | 323 | 0 | 0.75 | 180 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 4 | 87 | 0.39 | 0 | 250 | 120 | 220 | 0 | 634 | 1075 | 0 | 6849.16 | 14696.1 | 103.77
13:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 459 | 16 | 27 | 106 | 92 | 225 | 55 | 35 | 72 | 0 | 0 | 290 | 400 | 0 | 17 | 299 | 0 | 0 | 0 | 123 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 17 | 0 | 0 | 2.59 | 172 | 42 | 5 | 1125 | 0 | 0 | 29 | 0 | 33 | 0 | 0 | 0 | 0 | 1152 | 0 | 80 | 0 | 210 | 270 | 220 | 51 | 0 | 207 | 0 | 34 | 91 | 48 | 0 | 19 | 0 | 142 | 0 | 32 | 0 | 305 | 0 | 229 | 40 | 0 | 141 | 5 | 17 | 0 | 83 | 25 | 142 | 12 | 100 | 0 | 57 | 17.15 | 94 | 0 | 2 | 6.69 | 12 | 7978.43 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34.07 | 1147 | 0 | 0 | 0 | 1367.53 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 48.38 | 27 | 0 | 0 | 8.91 | 149 | 0 | 125 | 0 | 132 | 0 | 307 | 0 | 0.9 | 180 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 4.2 | 105 | 0.48 | 0 | 269 | 120 | 220 | 0 | 666 | 1050 | 0 | 6942.47 | 14920.9 | 103.77
14:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 444 | 17 | 27 | 82 | 30 | 225 | 55 | 35 | 17 | 0 | 0 | 299 | 395 | 0 | 17 | 307 | 0 | 0 | 0 | 123 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 17 | 0 | 0 | 1.42 | 172 | 34 | 5 | 1125 | 0 | 0 | 32 | 0 | 33 | 0 | 0 | 0 | 0 | 1156 | 6 | 80 | 0 | 210 | 270 | 220 | 51 | 0 | 204 | 0 | 34 | 91 | 51 | 0 | 19 | 0 | 142 | 0 | 35 | 7 | 305 | 0 | 229 | 40 | 0 | 135 | 3 | 17 | 0 | 83 | 28 | 142 | 0 | 100 | 0 | 48 | 7.5 | 47 | 0 | 2 | 13.57 | 12 | 7694.49 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 99.51 | 1155 | 0 | 0 | 0 | 1345.53 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 38.42 | 22 | 0 | 0 | 8.05 | 144 | 0 | 125 | 0 | 131 | 0 | 307 | 0 | 0.76 | 180 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 3.4 | 89 | 0.37 | 0 | 278 | 120 | 180 | 0 | 628 | 1030 | 0 | 6866.04 | 14560.53 | 103.77
15:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 466 | 35 | 27 | 50 | 30 | 225 | 55 | 35 | 17 | 0 | 0 | 293 | 405 | 0 | 17 | 307 | 0 | 0 | 0 | 123 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 17 | 0 | 0 | 1.29 | 222 | 33 | 0 | 1125 | 0 | 0 | 32 | 0 | 16 | 0 | 0 | 0 | 0 | 1157 | 3 | 80 | 0 | 210 | 270 | 220 | 51 | 0 | 205 | 0 | 34 | 93 | 49 | 0 | 19 | 0 | 134 | 0 | 25 | 25 | 315 | 0 | 229 | 40 | 0 | 148 | 3 | 17 | 0 | 83 | 28 | 144 | 0 | 100 | 0 | 49 | 2.32 | 47 | 0 | 2.1 | 16.09 | 12 | 7775.8 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 69.46 | 1102 | 0 | 0 | 0 | 1367.99 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 18 | 41 | 0 | 0 | 23.34 | 144 | 0 | 124 | 0 | 131 | 0 | 296 | 0 | 2.06 | 180 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 3.7 | 57 | 0.08 | 0 | 276 | 120 | 180 | 0 | 661 | 1070 | 0 | 6851.63 | 14627.43 | 103.76
16:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 444 | 17 | 0 | 34 | 30 | 225 | 55 | 35 | 17 | 0 | 0 | 295 | 395 | 0 | 35 | 307 | 0 | 0 | 0 | 123 | 13 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 17 | 0 | 0 | 1.15 | 222 | 32 | 2 | 1125 | 0 | 0 | 32 | 0 | 15 | 0 | 0 | 0 | 0 | 1157 | 2 | 80 | 0 | 210 | 270 | 220 | 51 | 0 | 205 | 0 | 35 | 94 | 48 | 0 | 19 | 0 | 136 | 0 | 5 | 25 | 305 | 0 | 229 | 40 | 0 | 132 | 4 | 8 | 0 | 83 | 30 | 142 | 0 | 100 | 0 | 49 | 4.67 | 47 | 0 | 0.4 | 9.06 | 9 | 7597.28 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30.12 | 1095 | 0 | 0 | 0 | 1278.8 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 10.22 | 32 | 0 | 0 | 28.36 | 144 | 0 | 128 | 0 | 131 | 0 | 286 | 0 | 2.39 | 180 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 2.8 | 54 | 0.16 | 0 | 277 | 120 | 180 | 0 | 619 | 1046 | 0 | 6626.85 | 14224.13 | 103.76
17:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 447 | 17 | 15 | 34 | 30 | 195 | 15 | 55 | 35 | 0 | 0 | 293 | 395 | 0 | 35 | 295 | 0 | 0 | 0 | 123 | 13 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0.5 | 222 | 17 | 7 | 1125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1122 | 1 | 30 | 0 | 210 | 270 | 220 | 51 | 0 | 208 | 0 | 0 | 94 | 17 | 5 | 6 | 0 | 122 | 0 | 2 | 25 | 305 | 0 | 305 | 40 | 0 | 129 | 1 | 8 | 0 | 83 | 30 | 142 | 0 | 100 | 0 | 49 | 0.8 | 47 | 0 | 0.2 | 9.78 | 15 | 7403.28 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16.35 | 1080 | 0 | 0 | 0 | 1264.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.23 | 14 | 0 | 0 | 6.97 | 144 | 0 | 128 | 0 | 131 | 0 | 284 | 0 | 0.72 | 180 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1.3 | 38 | 0.05 | 0 | 276 | 120 | 180 | 0 | 615 | 1028 | 0 | 6449.85 | 13853.13 | 103.75
18:00 | 0 | 18 | 24 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 499 | 30 | 27 | 34 | 30 | 195 | 15 | 35 | 35 | 0 | 0 | 302 | 395 | 0 | 35 | 308 | 0 | 0 | 0 | 123 | 13 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0.05 | 219 | 0 | 5 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 1 | 18 | 0 | 210 | 270 | 220 | 51 | 0 | 205 | 0 | 0 | 94 | 0 | 26 | 11 | 0 | 122 | 0 | 0 | 25 | 300 | 0 | 315 | 28 | 0 | 135 | 0 | 17 | 0 | 84 | 30 | 141 | 0 | 100 | 0 | 49 | 0.44 | 47 | 0 | 0 | 1.11 | 18 | 7209.6 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5.54 | 974 | 0 | 0 | 0 | 1317.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.81 | 8 | 0 | 0 | 1.53 | 144 | 0 | 129 | 0 | 131 | 0 | 286 | 0 | 0.17 | 180 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.9 | 10 | 0.06 | 0 | 198 | 120 | 180 | 0 | 705 | 1030 | 0 | 6358.28 | 13567.88 | 103.74
19:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 415 | 35 | 27 | 36 | 116 | 260 | 30 | 55 | 72 | 0 | 0 | 286 | 390 | 0 | 35 | 306 | 0 | 0 | 0 | 137 | 13 | 20 | 0 | 0 | 6 | 15 | 0 | 0 | 20 | 34 | 0 | 27 | 0 | 0 | 0 | 222 | 24 | 8 | 1125 | 17 | 0 | 9 | 3 | 22 | 0 | 0 | 0 | 0 | 1050 | 0 | 38 | 0 | 210 | 270 | 220 | 51 | 0 | 202 | 0 | 40 | 94 | 20 | 26 | 14 | 17 | 132 | 0 | 0 | 25 | 305 | 0 | 319 | 28 | 0 | 132 | 0 | 17 | 0 | 83 | 28 | 142 | 0 | 100 | 0 | 49 | 0 | 70 | 0 | 0 | 0 | 18 | 7823 | 895 | 0 | 0 | 16 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 982 | 0 | 0 | 0 | 1487.82 | 0 | 0 | 0 | 35 | 12 | 0 | 7 | 20 | 16 | 0 | 0 | 12 | 0 | 0 | 144 | 0 | 130 | 0 | 130 | 0 | 284 | 0 | 0 | 180 | 0 | 90 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 227 | 100 | 180 | 0 | 915 | 1062 | 11 | 7092.82 | 14915.82 | 103.73
19:30 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 450 | 35 | 27 | 85 | 128 | 195 | 30 | 55 | 35 | 0 | 0 | 299 | 461 | 0 | 35 | 310 | 0 | 0 | 0 | 143 | 13 | 20 | 0 | 0 | 14 | 0 | 7 | 0 | 28 | 34 | 0 | 17 | 0 | 0 | 0 | 222 | 51 | 8 | 1125 | 32 | 0 | 5 | 8 | 51 | 21 | 0 | 0 | 0 | 1090 | 0 | 50 | 0 | 210 | 278 | 220 | 51 | 0 | 197 | 0 | 90 | 93 | 17 | 26 | 14 | 0 | 130 | 0 | 0 | 25 | 315 | 0 | 319 | 28 | 20 | 127 | 0 | 17 | 0 | 84 | 28 | 144 | 0 | 100 | 0 | 67 | 0 | 85 | 0 | 0 | 0 | 18 | 8175 | 894 | 0 | 0 | 33 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1086 | 0 | 0 | 0 | 1484.02 | 0 | 0 | 0 | 0 | 50 | 5 | 93 | 25 | 0 | 0 | 0 | 20 | 0 | 0 | 144 | 0 | 129 | 0 | 128 | 0 | 290 | 0 | 0 | 180 | 0 | 90 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 227 | 120 | 220 | 0 | 1000 | 1100 | 0 | 7495.02 | 15670.02
20:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 425 | 35 | 27 | 112 | 129 | 160 | 30 | 55 | 35 | 0 | 0 | 290 | 425 | 0 | 35 | 300 | 0 | 0 | 0 | 143 | 13 | 20 | 0 | 0 | 0 | 0 | 14 | 0 | 28 | 34 | 30 | 0 | 0 | 0 | 0 | 222 | 34 | 12 | 1125 | 0 | 0 | 0 | 0 | 20 | 144 | 0 | 0 | 0 | 1100 | 0 | 50 | 0 | 210 | 280 | 220 | 51 | 0 | 188 | 0 | 50 | 94 | 17 | 28 | 14 | 0 | 134 | 0 | 0 | 25 | 305 | 0 | 319 | 28 | 20 | 129 | 0 | 17 | 0 | 84 | 25 | 142 | 0 | 100 | 0 | 68 | 0 | 85 | 0 | 0 | 0 | 18 | 8083 | 896 | 0 | 0 | 38 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1116 | 0 | 0 | 0 | 1477.38 | 0 | 0 | 0 | 0 | 0 | 10 | 43 | 28 | 0 | 0 | 0 | 20 | 0 | 0 | 144 | 0 | 129 | 0 | 128 | 0 | 285 | 0 | 0 | 180 | 0 | 95 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 120 | 180 | 0 | 1100 | 1120 | 0 | 7547.38 | 15630.38 | 103.71
21:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 449 | 17 | 27 | 149 | 137 | 220 | 15 | 35 | 17 | 0 | 0 | 292 | 475 | 0 | 17 | 310 | 0 | 0 | 0 | 143 | 13 | 20 | 0 | 0 | 0 | 0 | 64 | 0 | 22 | 34 | 0 | 0.5 | 0 | 0 | 0 | 222 | 28 | 18 | 1125 | 0 | 0 | 0 | 0 | 11 | 144 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 184 | 0 | 33 | 94 | 0 | 0 | 19 | 0 | 130 | 0 | 0 | 25 | 305 | 0 | 319 | 28 | 20 | 138 | 0 | 17 | 0 | 84 | 25 | 144 | 0 | 100 | 0 | 68 | 0 | 87 | 0 | 0 | 0 | 18 | 8216.5 | 879 | 0 | 0 | 30 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 580 | 0 | 0 | 0 | 1482.18 | 0 | 0 | 0 | 20 | 3 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 129 | 0 | 129 | 0 | 289 | 0 | 0 | 180 | 0 | 110 | 0 | 113 | 0 | 120 | 0 | 0 | 0 | 0 | 2 | 275 | 120 | 220 | 0 | 1100 | 1163 | 0 | 7154.18 | 15370.68 | 103.7
22:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 436 | 17 | 27 | 149 | 144 | 225 | 50 | 35 | 15 | 0 | 0 | 290 | 545 | 0 | 17 | 301 | 0 | 0 | 0 | 143 | 13 | 20 | 0 | 0 | 0 | 0 | 73 | 0 | 27 | 34 | 0 | 32 | 0 | 0 | 0 | 222 | 33 | 30 | 1125 | 0 | 0 | 0 | 0 | 48 | 144 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 179 | 0 | 68 | 94 | 44 | 0 | 19 | 0 | 130 | 0 | 0 | 25 | 310 | 0 | 317 | 28 | 20 | 136 | 0 | 0 | 0 | 84 | 25 | 141 | 0 | 100 | 0 | 68 | 0 | 87 | 0 | 0 | 0 | 18 | 8439 | 849 | 0 | 0 | 30 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 475 | 0 | 0 | 0 | 1494.4 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 130 | 0 | 129 | 0 | 290 | 0 | 0 | 180 | 0 | 90 | 0 | 113 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 277 | 120 | 220 | 0 | 1100 | 1163 | 0 | 7158.4 | 15597.4 | 103.69
23:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 447 | 17 | 27 | 149 | 144 | 225 | 55 | 35 | 16 | 0 | 0 | 296 | 545 | 0 | 17 | 310 | 0 | 0 | 0 | 143 | 13 | 20 | 0 | 0 | 0 | 0 | 73 | 0 | 16 | 34 | 0 | 35 | 0 | 0 | 0 | 222 | 32 | 33 | 1125 | 0 | 0 | 0 | 0 | 50 | 144 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 181 | 0 | 63 | 94 | 48 | 0 | 19 | 0 | 132 | 0 | 0 | 25 | 300 | 0 | 317 | 28 | 20 | 131 | 0 | 8 | 0 | 84 | 25 | 142 | 0 | 100 | 0 | 68 | 0 | 87 | 0 | 0 | 0 | 19 | 8479 | 849 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 475 | 0 | 0 | 0 | 1499.09 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 130 | 0 | 129 | 0 | 290 | 0 | 0 | 180 | 0 | 90 | 0 | 113 | 0 | 40 | 0 | 0 | 0 | 0 | 32 | 276 | 120 | 220 | 0 | 1100 | 1163 | 0 | 7031.09 | 15510.09 | 103.7
Total KWH | 0 | 711360 | 290880 | 0 | 0 | 0 | 0 | 0 | 8420400 | 0 | 11201270 | 326160 | 571680 | 1707264 | 1509120 | 3270349 | 654677 | 603731 | 570240 | 0 | 0 | 7091695 | 10701086 | 0 | 338120 | 7381121 | 0 | 0 | 0 | 3325200 | 306600 | 487080 | 0 | 0 | 23836 | 52691 | 327360 | 0 | 519360 | 235453 | 10752 | 283193 | 0 | 0 | 13121 | 5199920 | 562036 | 241440 | 26923636.36 | 55200 | 0 | 208800 | 7218 | 420690 | 538334 | 0 | 0 | 0 | 26656361 | 31590 | 600509 | 0 | 5196500 | 6929500 | 5474000 | 1260762 | 48000 | 4844000 | 95472 | 712320 | 2193494 | 530880 | 144480 | 430330 | 12540 | 3137280 | 0 | 177936 | 359728 | 7433000 | 0 | 6322000 | 869000 | 81120 | 3334581.82 | 48707 | 359808 | 0 | 1994880 | 379104 | 3270000 | 224000 | 2401460 | 43560 | 842400 | 69696 | 1408800 | 0 | 10450 | 178380 | 205440 | 183403142.18 | 21474909 | 0 | 0 | 140160 | 30592 | 912000 | 0 | 0 | 0 | 0 | 91584 | 531360 | 23156369 | 0 | 0 | 0 | 33763273 | 0 | 0 | 0 | 201696 | 519840 | 7863 | 57312 | 86656 | 59088 | 189832 | 371890 | 22072 | 0 | 186128 | 3592182 | 0 | 3300255 | 0 | 3461873 | 0 | 7564072 | 0 | 16020 | 4415000 | 0 | 588627 | 92441 | 885158 | 0 | 326025 | 0 | 22078.56 | 615600 | 2865 | 195744 | 6786000 | 2875000 | 5239630 | 0 | 19352727 | 27109818.18 | 468000 | 168711739.74 | 352114881.92

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14696.1 | MW | 12:00 Hr. | Energy Generated |  |  | 352.1149 |  | MKWHr.
| Day Peak Demand |  |  | 14951.1 | MW | 12:00 Hr. | Energy Unserverd |  |  | 9.732 |  | MKWHr.
| Evening Peak Generation |  |  | 15670.02 | MW | 19:30 Hr. | Energy Demand |  |  | 361.8469 |  | MKWHr.
| Evening Peak Demand |  |  | 16130.02 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.2 |  | °C
| Minimum Generation of the Day |  |  | 13531.53 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 939.61 |  | MMCFD
| Maximum Generation of the Day |  |  | 15670.02 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.3005 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 45.5893 | 0 | 13.8788 | 0 | 0 | 0 | 0 | 0 | 59.468 | Gas | 125.543 | Gas | 443795460.8044
| Chattogram Zone |  |  | 0.77977 | 53.58 | 2.1872 | 0 | 5.1999 | 0.044711 | 0 | 0.51936 | 62.311 | Coal | 134.3999 | Coal | 900240372.7196
| Cumilla Zone |  |  | 26.4721 | 0 | 2.3605 | 0 | 0 | 0.17794 | 3.1373 | 0 | 32.1477 | HFO | 24.2811 | HFO | 439191492.16
| Mymensingh Zone |  |  | 0 | 0 | 2.5002 | 0 | 0 | 0.25853 | 0 | 0 | 2.7587 | HSD | 0.32603 | HSD | 10067652
| Sylhet Zone |  |  | 26.669 | 0 | 0 | 0 | 0 | 0.048707 | 0 | 0 | 26.7177 | Hydro | 5.1999 | Hydro | 519992
| Khulna Zone |  |  | 0 | 23.1564 | 0.26234 | 0 | 0 | 0.53136 | 22.3869 | 0 | 46.337 | Solar | 2.5581 | Solar | 41483699.8348
| Barishal Zone |  |  | 8.1146 | 53.2485 | 0.66374 | 0 | 0 | 0.002865 | 0 | 0 | 62.0298 | Import | 59.2875 | Import | 375552420.21
| Rajshahi Zone |  |  | 17.9184 | 0 | 0.95453 | 0 | 0 | 0.76387 | 33.7633 | 0 | 53.4001 | Wind | 0.51936 | Wind | 7639785.6
| Rangpur Zone |  |  | 0 | 4.415 | 1.4738 | 0.32603 | 0 | 0.73012 | 0 | 0 | 6.9449
| Total |  |  | 125.543 | 134.3999 | 24.2811 | 0.32603 | 5.1999 | 2.5581 | 59.2875 | 0.51936 | 352.1149
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 443795460.8044 |  | Hydro | 519992
|  |  |  | Coal | 900240372.7196 |  | Solar | 41483699.8348
|  |  |  | HFO | 439191492.16 |  | Import | 375552420.21
|  |  |  | HSD | 10067652 |  | Wind | 7639785.6
[5 empty] | Total: | 221,84,90,875 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4749 | Peak Hr Flow | 894.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 49283472.73 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.7633 | Peak Hr Flow | 1484.02 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2200 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.1373 | Peak Hr Flow | 130.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2632 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 58.3755 | Peak Hr Flow | 2508.02 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 159 |  | 5831
|  |  |  | Chattogram |  | 0 |  | 1498
|  |  |  | Cumilla |  | 24 |  | 1335
|  |  |  | Mymensingh |  | 257 |  | 1403
|  |  |  | Sylhet |  | 0 |  | 626
|  |  |  | Khulna |  | 0 |  | 1891
|  |  |  | Barishal |  | 0 |  | 493
|  |  |  | Rajshahi |  | 0 |  | 1540
|  |  |  | Rangpur |  | 0 |  | 1107
|  |  |  | Total |  | 440 |  | 15724
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 89
|  |  |  | Total Unavailable Capacity |  |  |  | 389
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:26 | 11:45 | Haripur 230/132kV S/S Auto TR-3 LT Scheduled S/D Due to High temperature maintenance .
| 08:27 | 11:45 | Haripur 230/132kV S/S Auto TR-3 HT Scheduled S/D Due to High temperature maintenance .
| 09:14 | 19:26 | Korerhat 400/230/132kV S/S Hathajari-1 Project Work S/D Due to Project work
| 09:27 | 20:09 | Madunaghat-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Taken by korerhat
| 09:30 | 10:43 | BIPTC S/S 20DF24 Scheduled S/D
| 09:33 | 20:08 | Korerhat 400/230/132kV S/S Meghnaghat-2 Project Work S/D Due to Project work
| 09:50 | 10:47 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Forced S/D Due to High temperature maintenance
| 10:13 | 10:18 | Muradnagar 132/33kV S/S 132KV Transformar-01 LT Tripped showing TR Backup Relay relays
Due to PBS 33 kv PT blast
| 10:20 |  | Muradnagar 132/33kV S/S 132KV Transformar-01 LT Scheduled S/D Due to PBS 33 KV PT
Replacement work
| 10:34 |  | Bheramara 230/132kV S/S GTG (NW) Forced S/D Due to Concrete slub for cable tray
reinstallation
| 10:36 |  | Bheramara 230/132kV S/S STG (NW) Forced S/D Due to Concrete slub for cable tray
reinstallation
| 12:00 |  | Day peak generation is 14696 MW.
| 12:59 | 15:16 | Taraganj 132/33kV S/S TR-03 (404T) LT Forced S/D Due to Loose bushing Connection
rectification (33KV Side)
| 14:04 | 15:18 | Daganbhuiyan 132/33kV S/S Transformer-1 LT Forced S/D Due to 33 KV Feeder Line DS red hot | [7 empty] | 12.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 14:05 | 15:17 | Daganbhuiyan 132/33kV S/S Transformer-1 HT Forced S/D Due to 33 KV Feeder Line DS red hot | [7 empty] | 12.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 14:23 | 14:43 | Cumilla(S) 132/33kV S/S TR-4 LT Tripped showing RET670,REF615 relays Due to 33 KV | [7 empty] | 40.0MW load
|  |  | Donaotori feeder fault(PDB) | [7 empty] | interrup.
| 14:23 | 14:43 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing RET670,REF615 relays Due to 33 KV | [7 empty] | 40.0MW load
|  |  | Donaitori feeder fault(PDB) | [7 empty] | interrup.
|  | 15:15 | Moghbazar-Rampura 132kV Ckt-1 is restored.
| 15:23 | 17:39 | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to Red Hot maintanence of 33 kV | [7 empty] | 85.0MW load
|  |  | kashimpur-2 feeder | [7 empty] | interrup.
| 15:23 | 17:38 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to Red Hot maintanence of 33 kV | [7 empty] | 85.0MW load
|  |  | Kashimpur -2 feeder | [7 empty] | interrup.
| 15:30 | 17:23 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Scheduled S/D Due to Cable termination
| 16:16 | 18:02 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Forced S/D Due to Porsha 33 Kv feeder red | [7 empty] | 16.0MW load
|  |  | hot maintenance. | [7 empty] | interrup.
| 16:18 | 18:01 | Niamatpur 132/33kV S/S Transformer-1(407T) HT Forced S/D Due to Porsha 33 Kv feeder red | [7 empty] | 16.0MW load
|  |  | hot maintenance | [7 empty] | interrup.
| 16:20 |  | Muradnagar 132/33kV S/S 132KV Transformar-01 HT Scheduled S/D Due to PBS 33 KV PT
Replacement work
| 17:20 |  | Bashundhara-Tongi 132 kV Ckt-2 Tripped from Tongi 230/132/33kV end showing Distance, Z-2,
Phase-Y relays Due to THUNDER.
| 20:18 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- Unit-2
| 20:18 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- Unit-2
| 20:19 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- Unit-1 Running
| 02:57 | 04:32 | Rangpur 132/33kV S/S Rangpur-Teesta Solar-1 Tripped showing Distance Relay relays Due to
Zone-1 Phase-A & B
| 02:57 | 04:34 | Rangpur 132/33kV S/S Rangpur-Teesta Solar-2 Tripped showing Distance Relay relays Due to
Zone-1 Phase A & B
| 06:15 |  | Munshiganj 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Shifting of 33/.4 KV | [7 empty] | 30.0MW load
|  |  | Auxiliary -01 and 33KV bus PT | [7 empty] | interrup.
| 06:15 |  | Munshiganj 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Shifting of 33/.4 kv | [7 empty] | 30.0MW load
|  |  | Auxiliary -01 Transformer and 33kv bus PT | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 330 | 8420400 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 299 | 7091695 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 654677 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 310 | 7381121 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 326160 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 128 | 1509120 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 603731 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 338120 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 306600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 487080 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 290880 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 3270349 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 85 | 1707264 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 711360 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 570240 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 27 | 571680 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 461 | 10701086 | AGC+FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 450 | 11201270 | AGC+FGMO
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143 | 3325200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2709 | 59468033
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 7218 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 31590 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 5 | 208800 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5199920 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 21 | 538334 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 420690 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 10752 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 235453 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 241440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 7 | 327360 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 13121 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 52691 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 283193 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 562036 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 14 | 23836 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 32 | 55200 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1090 | 26656361 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 28 | 519360 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 26923636.36 | AGC
Chattogram Area Total |  |  |  |  | 4898.863 | 2713 | 62310991.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 197 | 4844000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 278 | 6929500 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 220 | 5474000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 210 | 5196500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 95472 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 48000 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1260762 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 600509 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 25 | 359728 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 93 | 2193494 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 530880 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 130 | 3137280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 430330 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 12540 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 144480 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 712320 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 177936 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1401 | 32147731
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 69696 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 85 | 1408800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 842400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 178380 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 205440 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 43560 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 170 | 2758726
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 48707 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 869000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 81120 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 127 | 3334581.82 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 144 | 3270000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 379104 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1994880 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2401460 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 224000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 359808 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7433000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 319 | 6322000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1182 | 26717660.82
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 894 | 21474909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 140160 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 30592 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 91584 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 531360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1086 | 23156369 | AGC
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2066 | 46336974
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1000 | 19352727 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 195744 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2875000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1100 | 27109818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5239630 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 468000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 227 | 6786000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2865 | -
Barishal Area Total |  |  |  |  | 3407.64 | 2683 | 62029784.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 189832 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 7863 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 86656 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 144 | 3592182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 129 | 3300255 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 128 | 3461873 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 290 | 7564072 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 22072 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 59088 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 57312 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 519840 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 201696 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 16020 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1484.02 | 33763273 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 186128 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 371890 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2368.02 | 53400052
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 326025 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | U-2 Under maint.
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4415000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 885158 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 22078.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 90 | 588627 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 92441 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 615600 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 378 | 6944929.56
Eastern Grid Total |  |  |  |  | 17438.042 | 8175 | 183403142.18
Western Grid Total |  |  |  |  | 11812.075 | 7495.02 | 168711739.74
National Grid Total |  |  |  |  | 29250.117 | 15670.02 | 352114881.92
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-07-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10305.02 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5031.4 | MW
i) Dhaka area |  |  | 5671.72 |  | MW | i) Khulna area |  |  |  | 1891 | MW
ii) Chattogram area |  |  | 1550.3 |  | MW | ii) Barishal area |  |  |  | 493 | MW
iii) Cumilla area |  |  | 1311 |  | MW | iii) Rajshahi area |  |  |  | 1540.4 | MW
iv) Mymensingh area |  |  | 1146 |  | MW | iv) Rangpur area |  |  |  | 1107 | MW
v) Sylhet area |  |  | 626 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15336.42 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 150 | 15:00 | 133 | Narshingdi | 194 | 00:00 | 199 | Uttara | 99 | 16:00
2 | AKSML | 153.3 | 00:00 | 68 | Hasnabad | 91 | 00:00 | 134 | Natore | 155 | 22:00 | 200 | UttaraNew | 55 | 13:00
3 | Aftabnagar | 42 | 00:00 | 69 | Hathazari | 89 | 00:00 | 135 | Nawabganj | 63.7 | 22:00 | 201 | Zigatola | 111 | 13:00
4 | Agargaon | 128 | 13:00 | 70 | Hatirjheel | 106 | 13:00 | 136 | Netrakona | 143 | 22:00
5 | Agrabad | 70 | 12:00 | 71 | Ishurdi | 81 | 19:30 | 137 | New | 86 | 09:00
6 | Amnura | 32 | 00:00 | 72 | Jaldhaka | 88 | 19:30 | 138 | Niamatpur | 82 | 22:00
7 | Ashuganj | 84 | 00:00 | 73 | Jamalpur | 110 | 22:00 | 139 | Noapara | 52 | 19:30
8 | BSRM | 192 | 08:00 | 74 | Jashore | 145 | 13:00 | 140 | PHP | 9 | 10:00
9 | Bagerhat | 94 | 19:30 | 75 | Jhenaidah | 97 | 19:30 | 141 | Pabna | 103 | 19:30
10 | Bajitpur | 87 | 00:00 | 76 | Joydebpur | 177 | 11:00 | 142 | Palashbari | 134 | 00:00
11 | Bakerganj | 15.2 | 19:00 | 77 | Joypurhat | 68 | 00:00 | 143 | Panchagarh | 63 | 20:00
12 | Bakulia | 92 | 11:00 | 78 | Juldah | 16 | 00:00 | 144 | Patiya | 11 | 00:00
13 | Banani | 82 | 13:00 | 79 | KSRM | 23 | 10:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 18 | 11:00 | 80 | Kabirpur | 259 | 19:30 | 146 | Patuakhali | 70.8 | 00:00
15 | Barapukuria | 77 | 22:00 | 81 | Kachua | 98 | 00:00 | 147 | Payra | 36 | 00:00
16 | Barguna | 22 | 22:00 | 82 | Kaliganj | 37 | 19:30 | 148 | Postogola | 63 | 13:00
17 | Barishal | 109 | 12:00 | 83 | Kallyanpur | 123 | 00:00 | 149 | Pubail | 39 | 06:00
18 | Barishal-230 | 106 | 22:00 | 84 | Kalurghat | 41 | 12:00 | 150 | Purbachal | 32 | 13:00
19 | Baroaulia | 31 | 19:00 | 85 | Kamrangirchar | 81 | 13:00 | 151 | Purbasadipur | 144 | 00:00
20 | Baroirhat | 71 | 19:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 44 | 22:00
21 | Bashundhara | 207 | 13:00 | 87 | Kasba | 37 | 00:00 | 153 | Rahim | 50 | 22:00
22 | BashundharaCement | 6 | 00:00 | 88 | Kazla | 106 | 13:00 | 154 | Rajbari | 90 | 20:00
23 | Beanibazar | 78 | 00:00 | 89 | Keranigonj | 89 | 19:30 | 155 | Rajendrapur | 119 | 00:00
24 | Benapole | 71 | 22:00 | 90 | Khagrachori | 38 | 19:00 | 156 | Rajshahi | 125 | 00:00
25 | Bhaluka | 155 | 19:30 | 91 | Khulna | 66 | 19:30 | 157 | Rajshahi-230 | 107 | 13:00
26 | Bhandaria | 60 | 22:00 | 92 | Khulshi | 174 | 15:00 | 158 | Ramganj | 116 | 00:00
27 | Bhangura | 39 | 19:30 | 93 | Kishoreganj | 133 | 20:00 | 159 | Rampur | 42 | 00:00
28 | Bheramara(GK) | 68 | 01:00 | 94 | Kodda | 319 | 20:00 | 160 | Rangamati | 16 | 19:00
29 | Bhulta | 221 | 15:00 | 95 | Kulaura | 52 | 00:00 | 161 | Rangpur | 152 | 19:30
30 | Bog-Sherpur | 84 | 00:00 | 96 | Kurigram | 74 | 18:30 | 162 | Ruppur | 4.4 | 11:00
31 | Bogura | 180 | 22:00 | 97 | Kushtia | 165 | 01:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 78 | 00:00 | 98 | Laksam | 33 | 00:00 | 164 | Saidpur | 110 | 19:30
33 | Brahmanbaria | 137 | 00:00 | 99 | Lakshmipur | 44 | 00:00 | 165 | Santhia | 38 | 00:00
34 | Cantonment | 120 | 13:00 | 100 | Lalbag | 81 | 13:00 | 166 | Satkhira | 138 | 20:00
35 | Chandina | 39 | 00:00 | 101 | Lalmonirhat | 70 | 19:30 | 167 | Satmasjid | 107 | 13:00
36 | Chandpur | 90 | 00:00 | 102 | MI_Cement | 18.1 | 03:00 | 168 | Savar | 219 | 20:00
37 | Chandraghona | 36 | 21:00 | 103 | Madanganj | 35 | 12:00 | 169 | SevenRings | 12.74 | 17:00
38 | Chapai | 78 | 22:00 | 104 | Madaripur | 124 | 22:00 | 170 | ShahCement | 7 | 00:00
39 | Charfasson | 33 | 20:00 | 105 | Madartek | 81 | 00:00 | 171 | Shahjadpur | 82 | 20:00
40 | Charsaidpur | 40 | 01:00 | 106 | Madunaghat | 54 | 19:00 | 172 | Shahjibazar | 134 | 21:00
41 | Chauddagram | 74 | 00:00 | 107 | Magura | 68 | 20:00 | 173 | Shahmirpur | 54 | 23:00
42 | Chhatak | 37 | 00:00 | 108 | Mahasthangarh | 86 | 00:00 | 174 | Shariatpur | 97 | 00:00
43 | Chowmuhani | 157 | 00:00 | 109 | Maijdee | 39 | 01:00 | 175 | Sherpur | 130 | 20:00
44 | Chuadanga | 117 | 22:00 | 110 | Manikganj | 145 | 20:00 | 176 | Shikalbaha | 27 | 20:00
45 | Coxsbazar | 149 | 23:00 | 111 | Maniknagar | 78 | 13:00 | 177 | Shitalakhya | 84.5 | 12:00
46 | Cumilla(N) | 120 | 02:00 | 112 | Matarbari | 55 | 22:00 | 178 | Sholosohor | 46 | 15:00
47 | Cumilla(S) | 145 | 00:00 | 113 | Matuail | 76 | 10:00 | 179 | Shomvuganj | 46 | 21:00
48 | Daganbhuiyan | 32 | 19:30 | 114 | Metrorail_Motijheel | 28 | 10:00 | 180 | Shyampur | 174 | 00:00
49 | Daudkandi | 144 | 19:30 | 115 | Metrorail_Uttara | 6 | 02:00 | 181 | Siddhirganj | 131 | 12:00
50 | DhakaUniversity | 96 | 12:00 | 116 | Millgate | 114 | 15:00 | 182 | Sirajganj | 120 | 21:00
51 | Dhamrai | 106 | 22:00 | 117 | Mirpur | 155 | 13:00 | 183 | Sitakunda | 34 | 19:00
52 | Dhanmondi | 122 | 13:00 | 118 | Mirsorai | 40 | 02:00 | 184 | Sonargaon | 154 | 23:00
53 | Dohazari | 103 | 21:00 | 119 | Mirzapur | 44 | 22:00 | 185 | Sreemongol | 84 | 00:00
54 | Faridpur | 180 | 21:00 | 120 | Mithapukur | 78 | 21:00 | 186 | Sreepur | 135 | 19:30
55 | Fatullah | 103 | 12:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 50 | 23:00
56 | Fenchuganj | 42 | 00:00 | 122 | Mogbazar | 0 | 00:00 | 188 | Sunamganj | 59 | 00:00
57 | Feni | 113 | 00:00 | 123 | Mongla | 46 | 11:00 | 189 | Sylhet | 120 | 15:00
58 | GPH | 9 | 19:00 | 124 | Motijheel | 54 | 13:00 | 190 | Sylhet_(South) | 64 | 00:00
59 | Ghatail | 74 | 12:00 | 125 | Muktagacha | 37 | 14:00 | 191 | TK | 25 | 19:30
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 115 | 00:00 | 192 | Tangail | 164 | 21:00
61 | Ghorashal-230 | 107 | 04:00 | 127 | Muradnagar | 50 | 00:00 | 193 | Taraganj | 29 | 19:30
62 | Goalpara | 30 | 00:00 | 128 | Mymensingh | 167 | 00:00 | 194 | Tasnim | 37 | 18:30
63 | Gollamari | 108 | 13:00 | 129 | Nabinagar | 106 | 12:00 | 195 | Thakurgaon | 116 | 20:00
64 | Gopalganj | 122 | 19:30 | 130 | Naogaon | 145 | 00:00 | 196 | Tongi | 152 | 11:00
65 | Gulshan | 120 | 12:00 | 131 | Narail | 60 | 19:30 | 197 | Ullahpara | 40 | 19:30
66 | Halishahar | 97 | 10:00 | 132 | Narinda | 78 | 13:00 | 198 | Ullon | 64 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15606.99 | 654 |  | 16290.42
1:00 | 15219.66 | 576 |  | 15821.66
2:00 | 14569.97 | 622 |  | 15219.97
3:00 | 14364.37 | 616 |  | 15008.37
4:00 | 14122.71 | 582 |  | 14730.71
5:00 | 13953.74 | 517 |  | 14493.74
6:00 | 13554.05 | 502 |  | 14079.05
7:00 | 13531.53 | 402 |  | 13951.53
8:00 | 13548.4 | 406 |  | 13972.4
9:00 | 13753.85 | 391 |  | 14162.85
10:00 | 13913.78 | 304 |  | 14231.78
11:00 | 14324.2 | 188 |  | 14520.2
12:00 | 14696.1 | 244 |  | 14951.1
13:00 | 14920.9 | 206 |  | 15135.9
14:00 | 14560.53 | 373 |  | 14950.32
15:00 | 14627.43 | 484 |  | 15133.43
16:00 | 14224.13 | 457 |  | 14702.13
17:00 | 13853.13 | 345 |  | 14214.13
18:00 | 13567.88 | 339 |  | 13921.88
19:00 | 14915.82 | 360 |  | 15291.82
19:30 | 15670.02 | 440 |  | 16130.02
20:00 | 15630.38 | 300 |  | 15944.38
21:00 | 15370.68 | 295 |  | 15678.68
22:00 | 15597.4 | 272 |  | 15881.4
23:00 | 15510.09 | 297 |  | 15820.09
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8125 | 7481.99 | 15606.99 | DAILY GENERATION CURVE
00:30 | 7954.5 | 7458.825 | 15413.325
01:00 | 7784 | 7435.66 | 15219.66 | 19-07-2026
01:30 | 7475.5 | 7419.315 | 14894.815
02:00 | 7167 | 7402.97 | 14569.97
02:30 | 7130.5 | 7336.67 | 14467.17
03:00 | 7094 | 7270.37 | 14364.37
03:30 | 7047.5 | 7196.04 | 14243.54
04:00 | 7001 | 7121.71 | 14122.71
04:30 | 6959.5 | 7078.725 | 14038.225
05:00 | 6918 | 7035.74 | 13953.74
05:30 | 6909.985 | 6843.91 | 13753.895
06:00 | 6901.97 | 6652.08 | 13554.05
06:30 | 6948.81 | 6593.98 | 13542.79
07:00 | 6995.65 | 6535.88 | 13531.53
07:30 | 6951.93 | 6588.035 | 13539.965
08:00 | 6908.21 | 6640.19 | 13548.4
08:30 | 6979.015 | 6672.11 | 13651.125
09:00 | 7049.82 | 6704.03 | 13753.85
09:30 | 7126.725 | 6707.09 | 13833.815
10:00 | 7203.63 | 6710.15 | 13913.78
10:30 | 7363.53 | 6755.46 | 14118.99
11:00 | 7523.43 | 6800.77 | 14324.2
11:30 | 7685.185 | 6824.965 | 14510.15
12:00 | 7846.94 | 6849.16 | 14696.1
12:30 | 7912.685 | 6895.815 | 14808.5
13:00 | 7978.43 | 6942.47 | 14920.9
13:30 | 7836.46 | 6904.255 | 14740.715
14:00 | 7694.49 | 6866.04 | 14560.53
14:30 | 7735.145 | 6858.835 | 14593.98
15:00 | 7775.8 | 6851.63 | 14627.43
15:30 | 7686.54 | 6739.24 | 14425.78
16:00 | 7597.28 | 6626.85 | 14224.13
16:30 | 7500.28 | 6538.35 | 14038.63
17:00 | 7403.28 | 6449.85 | 13853.13
17:30 | 7306.44 | 6404.065 | 13710.505
18:00 | 7209.6 | 6358.28 | 13567.88
18:30 | 7516.3 | 6725.55 | 14241.85
19:00 | 7823 | 7092.82 | 14915.82
19:30 | 8175 | 7495.02 | 15670.02
20:00 | 8083 | 7547.38 | 15630.38
20:30 | 8149.75 | 7350.78 | 15500.53 |  | Executive Engineer
21:00 | 8216.5 | 7154.18 | 15370.68 |  | Network Operation Division
21:30 | 8327.75 | 7156.29 | 15484.04
22:00 | 8439 | 7158.4 | 15597.4
22:30 | 8459 | 7094.745 | 15553.745
23:00 | 8479 | 7031.09 | 15510.09

## En-Curve
QF-LDC-12
Date | 19-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3048 | 2168 | 896 | 38 | 144 | 1486.79 | 222 | 5938 | 0 | 323 | 1298.2 | 0 | 0 | 45 | 654 | DAILY ENERGY CURVE
00:30 | 3036 | 2116 | 896 | 38 | 143 | 1485.725 | 222 | 5934 | 0 | 290.5 | 1216.1 | 0 | 0 | 36 | 615 | 19-07-2026
01:00 | 3024 | 2064 | 896 | 38 | 142 | 1484.66 | 222 | 5930 | 0 | 258 | 1134 | 0 | 0 | 27 | 576
01:30 | 3030.5 | 2096.5 | 896 | 38 | 142 | 1462.315 | 222 | 6004.5 | 0 | 241 | 739 | 0 | 0 | 23 | 599 | Energy Generated | 352.1149 |  | MKWHr
02:00 | 3037 | 2129 | 896 | 38 | 142 | 1439.97 | 222 | 6079 | 0 | 224 | 344 | 0 | 0 | 19 | 622 | Energy not Served | 9.732 |  | MKWHr
02:30 | 3056 | 2113.5 | 896 | 38 | 139 | 1437.67 | 222 | 6028.5 | 0 | 232 | 278.5 | 0 | 0 | 26 | 619 | Total Energy Requirement | 361.8469 |  | MKWHr
03:00 | 3075 | 2098 | 896 | 38 | 136 | 1435.37 | 222 | 5978 | 0 | 240 | 213 | 0 | 0 | 33 | 616
03:30 | 3073 | 2109 | 896 | 38 | 133 | 1435.04 | 221 | 5899.5 | 0 | 240 | 173.5 | 0 | 0 | 25.5 | 599
04:00 | 3071 | 2120 | 896 | 38 | 130 | 1434.71 | 220 | 5821 | 0 | 240 | 134 | 0 | 0 | 18 | 582
04:30 | 3076.5 | 2099.5 | 896.5 | 38 | 129 | 1415.225 | 220 | 5770 | 0 | 240 | 129.5 | 0 | 0 | 24 | 549.5
05:00 | 3082 | 2079 | 897 | 38 | 128 | 1395.74 | 220 | 5719 | 0 | 240 | 125 | 0 | 0 | 30 | 517
05:30 | 3086.5 | 2087.5 | 896.5 | 38 | 126 | 1388.7 | 221 | 5529 | 7.195 | 232 | 116.5 | 0 | 0 | 25 | 509.5
06:00 | 3091 | 2096 | 896 | 38 | 124 | 1381.66 | 222 | 5339 | 14.39 | 224 | 108 | 0 | 0 | 20 | 502
06:30 | 3092 | 2127 | 896 | 38 | 121 | 1407.32 | 222 | 5239.5 | 41.97 | 224 | 108 | 0 | 0 | 26 | 452
07:00 | 3093 | 2158 | 896 | 38 | 118 | 1432.98 | 222 | 5140 | 69.55 | 224 | 108 | 0 | 0 | 32 | 402
07:30 | 3082 | 2135.25 | 896 | 38 | 119 | 1442.5 | 222 | 5165.5 | 88.715 | 216.5 | 108 | 0 | 0 | 26.5 | 404
08:00 | 3071 | 2112.5 | 896 | 38 | 120 | 1452.02 | 222 | 5191 | 107.88 | 209 | 108 | 0 | 0 | 21 | 406
08:30 | 3064.5 | 2085.25 | 896 | 38 | 122 | 1428.685 | 222 | 5257 | 161.69 | 200.5 | 159 | 0 | 0 | 16.5 | 398.5
09:00 | 3058 | 2058 | 896 | 38 | 124 | 1405.35 | 222 | 5323 | 215.5 | 192 | 210 | 0 | 0 | 12 | 391
09:30 | 3056.5 | 2034.5 | 896 | 38 | 128 | 1406.625 | 222 | 5347 | 228.19 | 235 | 230 | 0 | 0 | 12 | 347.5
10:00 | 3055 | 2011 | 896 | 38 | 132 | 1407.9 | 222 | 5371 | 240.88 | 278 | 250 | 0 | 0 | 12 | 304
10:30 | 3061.5 | 2059.5 | 896 | 38 | 135 | 1371.04 | 222 | 5412.5 | 293.95 | 277 | 338 | 0 | 0 | 14.5 | 246
11:00 | 3068 | 2108 | 896 | 38 | 138 | 1334.18 | 222 | 5454 | 347.02 | 276 | 426 | 0 | 0 | 17 | 188
11:30 | 3074 | 2062 | 896 | 38 | 142 | 1343.77 | 222 | 5472.5 | 368.88 | 276 | 593.5 | 0 | 0 | 21.5 | 216
12:00 | 3080 | 2016 | 896 | 38 | 146 | 1353.36 | 222 | 5491 | 390.74 | 276 | 761 | 0 | 0 | 26 | 244
12:30 | 3061.5 | 2020 | 896.5 | 38 | 144 | 1360.445 | 197 | 5540 | 348.055 | 283.5 | 897.5 | 0 | 0 | 22 | 225
13:00 | 3043 | 2024 | 897 | 38 | 142 | 1367.53 | 172 | 5589 | 305.37 | 291 | 1034 | 0 | 0 | 18 | 206
13:30 | 3028 | 1995.5 | 896.5 | 38 | 142 | 1356.53 | 172 | 5570.5 | 323.685 | 229.5 | 966 | 0 | 0 | 22.5 | 289.5
14:00 | 3013 | 1967 | 896 | 38 | 142 | 1345.53 | 172 | 5552 | 342 | 168 | 898 | 0 | 0 | 27 | 373
14:30 | 3024 | 1989 | 896.5 | 38 | 138 | 1356.76 | 197 | 5561.5 | 312.22 | 177 | 881.5 | 0 | 0 | 22.5 | 428.5
15:00 | 3035 | 2011 | 897 | 38 | 134 | 1367.99 | 222 | 5571 | 282.44 | 186 | 865 | 0 | 0 | 18 | 484
15:30 | 3016 | 1979 | 896.5 | 38 | 135 | 1323.395 | 222 | 5535 | 240.885 | 186 | 841 | 0 | 0 | 13 | 470.5
16:00 | 2997 | 1947 | 896 | 38 | 136 | 1278.8 | 222 | 5499 | 199.33 | 186 | 817 | 0 | 0 | 8 | 457
16:30 | 3024 | 1942 | 896 | 38 | 129 | 1271.515 | 222 | 5462.5 | 150.115 | 190 | 699 | 0 | 0 | 14.5 | 401
17:00 | 3051 | 1937 | 896 | 38 | 122 | 1264.23 | 222 | 5426 | 100.9 | 194 | 581 | 0 | 0 | 21 | 345
17:30 | 3050 | 1974.5 | 896 | 38 | 122 | 1290.75 | 220.5 | 5256.5 | 66.755 | 207 | 572.5 | 0 | 0 | 16 | 342
18:00 | 3049 | 2012 | 896 | 38 | 122 | 1317.27 | 219 | 5087 | 32.61 | 220 | 564 | 0 | 0 | 11 | 339
18:30 | 3028 | 1963 | 895.5 | 38 | 127 | 1402.545 | 220.5 | 5314 | 16.305 | 330 | 891.5 | 0 | 0 | 15.5 | 349.5
19:00 | 3007 | 1914 | 895 | 38 | 132 | 1487.82 | 222 | 5541 | 0 | 440 | 1219 | 0 | 0 | 20 | 360
19:30 | 3109 | 2079 | 894 | 38 | 130 | 1484.02 | 222 | 5808 | 0 | 579 | 1299 | 0 | 0 | 28 | 440
20:00 | 3203 | 1965 | 896 | 38 | 134 | 1477.38 | 222 | 6016 | 0 | 573 | 1078 | 0 | 0 | 28 | 300
20:30 | 3210.5 | 2033 | 887.5 | 38 | 132 | 1479.78 | 222 | 5831.5 | 0 | 515 | 1066.25 | 60 | 0 | 25 | 297.5
21:00 | 3218 | 2101 | 879 | 38 | 130 | 1482.18 | 222 | 5647 | 0 | 457 | 1054.5 | 120 | 0 | 22 | 295
21:30 | 3206.5 | 2127.5 | 864 | 38 | 130 | 1488.29 | 222 | 5595.5 | 0 | 455 | 1190.25 | 142.5 | 0 | 24.5 | 283.5
22:00 | 3195 | 2154 | 849 | 38 | 130 | 1494.4 | 222 | 5544 | 0 | 453 | 1326 | 165 | 0 | 27 | 272
22:30 | 3208 | 2160.5 | 849 | 38 | 131 | 1496.745 | 222 | 5543.5 | 0 | 450 | 1331 | 102.5 | 0 | 21.5 | 284.5
23:00 | 3221 | 2167 | 849 | 38 | 132 | 1499.09 | 222 | 5543 | 0 | 447 | 1336 | 40 | 0 | 16 | 297
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 19-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 115 | 4 | 460 | 160 | 1666 | 454 | Ishurdi-Ghorashal Ckt-1 | Export | 3442472.73
1:00 | 121 | 5 | 460 | 142 | 1710 | 456
2:00 | 121 | 9 | 454 | 148 | 1800 | 480 |  | Import | 0
3:00 | 135 | 20 | 456 | 152 | 1826 | 492
4:00 | 140 | 29 | 480 | 156 | 1762 | 520 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 140 | 30 | 480 | 150 | 1764 | 502
6:00 | 141 | 35 | 470 | 142 | 1546 | 504 |  | Import | 0
7:00 | 138 | 32 | 450 | 138 | 1454 | 512
8:00 | 163 | 44 | 510 | 140 | 1700 | 600 | Sirajganj-Sreepur Ckt-1 | Export | 2901000
9:00 | 191 | 63 | 580 | 172 | 1820 | 630
10:00 | 200 | 76 | 590 | 192 | 1842 | 740 |  | Import | 0
11:00 | 182 | 62 | 570 | 208 | 1786 | 790
12:00 | 178 | 61 | 550 | 238 | 1768 | 780 | Sirajganj-Sreepur Ckt-2 | Export | 2910000
13:00 | 159 | 44 | 510 | 208 | 1744 | 732
14:00 | 155 | 40 | 510 | 200 | 1738 | 758 |  | Import | 0
15:00 | 167 | 52 | 520 | 206 | 1770 | 750
16:00 | 153 | 43 | 490 | 184 | 1714 | 730 | Gopalganj-Aminbazar Ckt-1 | Export | 19990000
17:00 | 159 | 51 | 490 | 172 | 1686 | 736
18:00 | 164 | 53 | 520 | 184 | 1688 | 692 |  | Import | 0
18:30 | 159 | 59 | 550 | 184 | 1728 | 644
19:00 | 157 | 36 | 570 | 194 | 1796 | 600 | Gopalganj-Aminbazar Ckt-2 | Export | 20040000
19:30 | 120 | 16 | 430 | 172 | 1650 | 486
20:00 | 114 | 10 | 420 | 168 | 1780 | 446 |  | Import | 0
21:00 | 107 | 9 | 440 | 192 | 1342 | 358
22:00 | 99 | 8 | 410 | 174 | 1294 | 316 |  | Total Export | 49283472.73
23:00 | 98 | 9 | 400 | 184 | 1274 | 320 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 391 | 00:00 | 352 | 12:00 | Madunaghat | 389 | 19:00 | 381 | 03:00
Amtali | 410 | 07:00 | 402 | 03:00 | Meghnaghat | 380 | 07:00 | 361 | 12:00
Ashuganj | 402 | 7:00 | 381 | 12:00 | Payra | 412 | 07:00 | 403 | 19:30
Bhulta | 394 | 06:00 | 371 | 12:00 | Rahanpur | 398 | 17:00 | 384 | 20:00
Bibiana | 377 | 07:00 | 370 | 12:00 | Rampal | 393 | 08:00 | 369 | 21:00
BIPTC | 406 | 18:30 | 393 | 00:00
Bogura | 381 | 19:00 | 364 | 02:00
Gopalganj | 385 | 07:00 | 369 | 21:00
Kaliakoir | 356 | 07:00 | 341 | 15:00
Korerhat | 390 | 18:30 | 379 | 01:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 06:00 | 213 | 12:00 | Ishurdi | 235 | 18:30 | 213 | 00:00
AKSML | 233 | 19:00 | 224 | 11:00 | Jhenaidah | 227 | 18:30 | 200 | 21:00
Aminbazar | 226 | 06:00 | 211 | 12:00 | Kachua | 222 | 18:30 | 214 | 03:00
Ashuganj | 225 | 06:00 | 216 | 12:00 | Kaliakoir | 221 | 06:00 | 211 | 11:00
Ashuganj-400 | 225 | 6:00 | 216 | 12:00 | Keranigonj | 224 | 06:00 | 210 | 13:00
Baghabari | 231 | 17:00 | 218 | 20:00 | Khulna(S) | 224 | 18:00 | 203 | 21:00
Barapukuria | 224 | 18:30 | 212 | 00:00 | Korerhat | 223 | 18:30 | 216 | 00:00
Barapukuria-230 | 224 | 18:00 | 212 | 23:00 | Madunaghat | 236 | 19:00 | 228 | 03:00
Barishal | 225 | 09:00 | 216 | 21:00 | Madunaghat-400 | 236 | 07:00 | 230 | 03:00
Bheramara | 234 | 18:30 | 211 | 00:00 | Maniknagar | 224 | 06:00 | 210 | 12:00
Bhulta | 226 | 06:00 | 211 | 12:00 | Meghnaghat | 230 | 04:00 | 218 | 13:00
Bibiana | 219 | 06:00 | 214 | 00:00 | Meghnaghat-400 | 226 | 06:00 | 214 | 12:00
BIPTC | 236 | 18:30 | 211 | 00:00 | Mirsorai | 227 | 19:00 | 219 | 03:00
Bogura | 239 | 18:30 | 226 | 20:00 | Naogaon | 0 | 00:00 | N/A | N/A
Bogura-400 | 240 | 19:00 | 227 | 02:00 | Purbasadipur | 221 | 18:30 | 207 | 20:00
Borhanuddin | 229 | 06:00 | 222 | 21:00 | Rajshahi | 233 | 18:30 | 208 | 00:00
BSRM | 224 | 18:30 | 214 | 04:00 | Rampal | 223 | 18:30 | 206 | 21:00
Charfasson | 230 | 08:00 | 222 | 05:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 223 | 19:00 | 214 | 11:00 | Rampura | 226 | 07:00 | 210 | 12:00
Cumilla(N) | 221 | 07:00 | 213 | 12:00 | Shikalbaha | 236 | 18:30 | 228 | 03:00
Faridpur | 221 | 09:00 | 210 | 21:00 | Shyampur | 224 | 06:00 | 211 | 12:00
Fenchuganj | 221 | 07:00 | 216 | 00:00 | Siddhirganj | 226 | 05:00 | 219 | 00:00
Feni | 220 | 06:00 | 213 | 12:00 | Sirajgonj | 238 | 18:30 | 230 | 00:00
Ghorashal | 230 | 01:00 | 215 | 14:00 | Sreepur | 222 | 06:00 | 214 | 00:00
Ghorashal-230 | 208 | 18:30 | 197 | 12:00 | Tongi | 210 | 04:00 | 198 | 11:00
Gopalganj | 222 | 07:00 | 212 | 21:00
GPH | 230 | 19:00 | 223 | 00:00
Haripur | 226 | 07:00 | 211 | 13:00
Hasnabad | 225 | 06:00 | 211 | 12:00
Hathazari | 233 | 18:00 | 224 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 06:00 | 121 | 13:00 | Madunaghat | 136 | 18:30 | 132 | 03:00
Agargaon | 130 | 18:30 | 120 | 12:00 | Magura | 136 | 18:00 | 117 | 01:00
Agrabad | 133 | 06:00 | 129 | 10:00 | Mahasthangarh | 136 | 18:30 | 124 | 20:00
AKS | 131 | 07:00 | 128 | 10:00 | Maijdee | 124 | 18:30 | 118 | 03:00
Aminbazar | 128 | 06:00 | 120 | 10:00 | Manikganj | 125 | 09:00 | 119 | 12:00
Amnura | 133 | 18:00 | 119 | 20:00 | Maniknagar | 132 | 06:00 | 120 | 13:00
Ashuganj | 129 | 08:00 | 123 | 12:00 | Matarbari | 125 | 07:00 | 115 | 01:00
Ashuganj-230 | 132 | 19:00 | 128 | 12:00 | Matuail | 130 | 06:00 | 122 | 12:00
Bagerhat | 125 | 09:00 | 111 | 21:00 | Metrorail_Motijheel | 132 | 06:00 | 120 | 13:00
Bajitpur | 124 | 17:00 | 118 | 12:00 | Metrorail_Uttara | 125 | 01:00 | 116 | 10:00
Bakerganj | 130 | 18:30 | 123 | 20:00 | Millgate | 128 | 05:00 | 117 | 10:00
Bakulia | 134 | 19:00 | 130 | 03:00 | Mirpur | 127 | 06:00 | 119 | 11:00
Banani | 132 | 07:00 | 121 | 12:00 | Mirzapur | 124 | 00:00 | 120 | 02:00
Bangabhaban | 132 | 07:00 | 121 | 12:00 | Mithapukur | 134 | 18:30 | 122 | 00:00
Barapukuria | 136 | 18:30 | 125 | 20:00 | MI_Cement | 132 | 06:00 | 120 | 13:00
Barguna | 129 | 09:00 | 122 | 21:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 129 | 09:00 | 122 | 21:00 | Mogbazar | 130 | 22:00 | 125 | 16:00
Barishal-230 | 129 | 07:00 | 123 | 00:00 | Mongla | 125 | 18:30 | 110 | 21:00
Baroaulia | 133 | 04:00 | 130 | 10:00 | Motijheel | 132 | 07:00 | 121 | 12:00
Baroirhat | 129 | 18:30 | 124 | 05:00 | Muktagacha | 123 | 18:30 | 112 | 01:00
Bashundhara | 133 | 06:00 | 117 | 13:00 | Munshiganj | 129 | 19:00 | 121 | 11:00
BashundharaCement | 130 | 07:00 | 123 | 12:00 | Muradnagar | 124 | 06:00 | 118 | 12:00
Beanibazar | 124 | 07:00 | 117 | 00:00 | Mymensingh | 123 | 18:30 | 106 | 21:00
Benapole | 135 | 18:30 | 108 | 21:00 | Nabinagar | 124 | 06:00 | 116 | 11:00
Bhaluka | 124 | 08:00 | 116 | 21:00 | Naogaon | 136 | 18:30 | 122 | 00:00
Bhandaria | 125 | 07:00 | 115 | 22:00 | Narail | 137 | 18:00 | 115 | 20:00
Bhangura | 133 | 18:30 | 124 | 02:00 | Narinda | 132 | 6:00 | 120 | 13:00
Bheramara | 137 | 18:30 | 124 | 00:00 | Narshingdi | 126 | 05:00 | 115 | 00:00
Bheramara(GK) | 137 | 18:30 | 123 | 21:00 | Natore | 135 | 18:30 | 122 | 21:00
Bhulta | 125 | 19:00 | 119 | 12:00 | Nawabganj | 132 | 06:00 | 123 | 12:00
Bog-Sherpur | 135 | 08:00 | 126 | 00:00 | Netrakona | 117 | 17:00 | 104 | 21:00
Bogura | 138 | 18:30 | 130 | 00:00 | New | 129 | 04:00 | 118 | 12:00
Bogura-230 | 138 | 18:30 | 129 | 02:00 | Niamatpur | 131 | 08:00 | 124 | 21:00
Brahmanbaria | 126 | 07:00 | 121 | 12:00 | Noapara | 131 | 18:00 | 115 | 21:00
Cantonment | 130 | 18:00 | 120 | 11:00 | Pabna | 134 | 18:30 | 122 | 01:00
Chandina | 127 | 07:00 | 121 | 12:00 | Palashbari | 132 | 18:30 | 119 | 00:00
Chandpur | 126 | 18:30 | 119 | 03:00 | Panchagarh | 138 | 18:30 | 128 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 07:00 | 132 | 03:00 | Patiya | 133 | 21:00 | 129 | 10:00
Chapai | 130 | 10:00 | 124 | 00:00 | Patnitala | 131 | 10:00 | 120 | 00:00
Charsaidpur | 130 | 19:00 | 122 | 11:00 | Patuakhali | 129 | 07:00 | 123 | 19:30
Chauddagram | 127 | 18:30 | 122 | 00:00 | Payra | 133 | 07:00 | 130 | 00:00
Chhatak | 123 | 08:00 | 114 | 00:00 | PHP | 128 | 06:00 | 124 | 02:00
Chowmuhani | 124 | 18:30 | 120 | 00:00 | Postogola | 134 | 06:00 | 123 | 12:00
Chuadanga | 134 | 18:00 | 113 | 21:00 | Pubail | 123 | 02:00 | 116 | 10:00
Coxsbazar | 127 | 08:00 | 118 | 23:00 | Purbachal | 133 | 05:00 | 121 | 12:00
Cumilla(N) | 128 | 18:30 | 122 | 00:00 | Purbasadipur | 134 | 18:30 | 125 | 20:00
Cumilla(S) | 130 | 05:00 | 121 | 12:00 | Rahanpur | 134 | 18:00 | 127 | 20:00
Daganbhuiyan | 126 | 06:00 | 122 | 00:00 | Rahanpur-400 | 133 | 09:00 | 128 | 20:00
Daudkandi | 123 | 06:00 | 115 | 12:00 | Rahim | 136 | 07:00 | 123 | 11:00
DhakaUniversity | 133 | 05:00 | 122 | 12:00 | Rajbari | 125 | 08:00 | 117 | 00:00
Dhamrai | 126 | 04:00 | 118 | 11:00 | Rajendrapur | 126 | 08:00 | 117 | 20:00
Dhanmondi | 133 | 06:00 | 121.5 | 12:00 | Rajshahi | 133 | 18:30 | 120 | 00:00
Dohazari | 132 | 06:00 | 126 | 19:30 | Rajshahi-230 | 133 | 18:30 | 119 | 21:00
Faridpur | 129 | 08:00 | 121 | 21:00 | Ramganj | 123 | 18:30 | 117 | 10:00
Fatullah | 133 | 07:00 | 121 | 12:00 | Rampur | 134 | 18:30 | 129 | 02:00
Fenchuganj | 130 | 07:00 | 126 | 00:00 | Rampura | 133 | 06:00 | 122 | 12:00
Feni | 127 | 05:00 | 123 | 15:00 | Rangamati | 135 | 07:00 | 132 | 01:00
Feni-230 | 128 | 18:30 | 123 | 02:00 | Rangpur | 132 | 18:30 | 121 | 00:00
Ghatail | 121 | 18:30 | 113 | 01:00 | Ruppur | 137 | 18:30 | 124 | 00:00
Ghorashal | 125 | 03:00 | 119 | 14:00 | Saidpur | 134 | 18:30 | 124 | 00:00
Goalpara | 134 | 18:00 | 120 | 21:00 | Santhia | 134 | 18:30 | 124 | 00:00
Gollamari | 134 | 18:30 | 119 | 21:00 | Satkhira | 130 | 18:00 | 110 | 21:00
Gopalganj | 128 | 18:00 | 117 | 21:00 | Satmasjid | 129 | 05:00 | 118 | 13:00
Gopalganj-400 | 130 | 18:30 | 123 | 21:00 | Savar | 126 | 07:00 | 118 | 14:00
Gulshan | 134 | 07:00 | 121 | 12:00 | SevenRings | 126 | 06:00 | 118 | 13:00
Halishahar | 133 | 00:00 | 129 | 02:00 | ShahCement | 130 | 06:00 | 122 | 11:00
Haripur | 130 | 06:00 | 123 | 11:00 | Shahjadpur | 136 | 00:00 | 128 | 20:00
HaripurSBU | 132 | 01:00 | 123 | 00:00 | Shahjibazar | 127 | 08:00 | 121 | 00:00
Hasnabad | 133 | 04:00 | 123 | 12:00 | Shahmirpur | 134 | 06:00 | 130 | 02:00
Hathazari | 135 | 05:00 | 132 | 00:00 | Shariatpur | 128 | 18:30 | 119 | 21:00
Hatirjheel | 133 | 06:00 | 128 | 23:00 | Sherpur | 119 | 18:30 | 106 | 06:00
Ishurdi | 138 | 18:30 | 125 | 02:00 | Shikalbaha | 125 | 03:00 | 120 | 10:00
Jaldhaka | 132 | 18:30 | 122 | 00:00 | Shikalbaha-230 | 136 | 20:00 | 131 | 03:00
Jamalpur | 123 | 18:30 | 109 | 02:00 | Shitalakhya | 132 | 06:00 | 120 | 13:00
Jashore | 136 | 18:00 | 111 | 21:00 | Sholosohor | 135 | 07:00 | 129 | 02:00
Jhenaidah | 138 | 18:00 | 119 | 01:00 | Shomvuganj | 118 | 08:00 | 113 | 21:00
Jhenaidah-230 | 139 | 18:00 | 120 | 22:00 | Shyampur | 130 | 06:00 | 121 | 12:00
Joydebpur | 122 | 07:00 | 112 | 15:00 | Shyampur-230 | 131 | 06:00 | 122 | 12:00
Joypurhat | 133 | 18:30 | 116 | 00:00 | Siddhirganj | 130 | 04:00 | 122 | 11:00
Juldah | 134 | 01:00 | 130 | 12:00 | Sirajganj | 132 | 06:00 | 123 | 00:00
Kabirpur | 129 | 18:30 | 114 | 10:00 | Sitakunda | 134 | 06:00 | 130 | 02:00
Kachua | 127 | 19:00 | 120 | 03:00 | Sonargaon | 127 | 01:00 | 118 | 11:00
Kaliakoir | 131 | 18:30 | 122 | 11:00 | Sreemongol | 126 | 07:00 | 121 | 00:00
Kaliganj | 138 | 18:00 | 119 | 21:00 | Sreepur | 128 | 08:00 | 121 | 22:00
Kallyanpur | 127 | 05:00 | 119 | 15:00 | Srinagar | 132 | 06:00 | 123 | 12:00
Kalurghat | 136 | 18:30 | 132 | 03:00 | SSM | 140 | 18:30 | 135 | 00:00
Kamrangirchar | 131 | 06:00 | 117 | 11:00 | Sunamganj | 119 | 08:00 | 111 | 01:00
Kaptai | 137 | 7:00 | 134 | 12:00 | Sylhet | 124 | 07:00 | 120 | 00:00
Kasba | 124 | 07:00 | 116 | 12:00 | Sylhet_(South) | 125 | 08:00 | 120 | 00:00
Kazla | 132 | 05:00 | 120 | 13:00 | Tangail | 123 | 18:30 | 118 | 04:00
Keranigonj | 132 | 06:00 | 123 | 12:00 | Taraganj | 133 | 18:30 | 123 | 00:00
Khagrachori | 134 | 06:00 | 130 | 02:00 | Tasnim | 127 | 06:00 | 118 | 11:00
Khulna | 133 | 18:00 | 118 | 21:00 | Thakurgaon | 137 | 18:30 | 127 | 20:00
Khulna(S) | 134 | 18:00 | 119 | 21:00 | TK | 136 | 18:30 | 132 | 00:00
Khulshi | 133 | 18:30 | 129 | 10:00 | Tongi | 130 | 04:00 | 122 | 11:00
Kishoreganj | 122 | 08:00 | 115 | 12:00 | Ullahpara | 133 | 18:30 | 123 | 20:00
Kodda | 128 | 19:30 | 112 | 15:00 | Ullon | 133 | 06:00 | 121 | 13:00
Korerhat | 138 | 04:00 | 127 | 11:00 | Uttara | 127 | 06:00 | 116 | 12:00
KSRM | 135 | 18:30 | 130 | 01:00 | UttaraNew | 125 | 06:00 | 116 | 10:00
Kulaura | 131 | 17:00 | 124 | 00:00 | Zigatola | 132 | 06:00 | 122 | 13:00
Kurigram | 125 | 10:00 | 117 | 00:00
Kushtia | 133 | 18:30 | 118 | 00:00
Laksam | 125 | 18:30 | 121 | 00:00
Lakshmipur | 124 | 18:30 | 118 | 02:00
Lalbag | 131 | 06:00 | 122 | 12:00
Lalmonirhat | 130 | 00:00 | 119 | 19:30
Madanganj | 130 | 05:00 | 123 | 12:00
Madaripur | 129 | 18:00 | 122 | 21:00
Madartek | 133 | 06:00 | 122 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division