## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-07-2026 | during | 21-07-2026 | during | 21-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 350 | 259 | 412 | 412 | 405 | 405 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 302 | 307 | 335 | 335 | 310 | 310 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 30 | 35 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 308 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 18 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 94 | 145 | 149.36 | 149.36 | 48 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 12 | 33 | 33 | 12 | 12 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 15 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 95 | 300 | 300 | 48 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 16 | 96 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 88 | 105 | 105 | 17 | 105 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 104 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 3 | 0 | 5 | 0 | 5 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 27 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 395 | 550 | 583 | 583 | 524.5 | 524.5 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 486 | 463 | 718 | 718 | 658 | 658 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143 | 143 | 143 | 143 | 143 | 143 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2352 | 2750 | 5780.22 | 5775.22 | 2728.5 | 3297.5
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 12 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 219 | 220 | 220 | 220 | 220 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 66 | 0 | 145 | 145 | 70 | 70 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 68 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 24 | 56 | 24 | 56 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 34 | 0 | 34 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 18 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.98 | 0 | 2.37 | 0 | 2.37 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 30 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 45 | 54.36 | 54.36 | 54 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 83 | 51 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 25 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 30 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1192 | 1170 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 28 | 5 | 28 | 26 | 28 | 26 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1050 | 1125 | 1150 | 1150 | 1125 | 1125 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2743.98 | 2903 | 4036.23 | 4106.86 | 3314.37 | 3427
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 172 | 193 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 280 | 280 | 350.01 | 350.01 | 280 | 280 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 220 | 210 | 342.01 | 342.01 | 220 | 220 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 210 | 210 | 393 | 393 | 210 | 210 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 10 | 40 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 24 | 25 | 25 | 25 | 25 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 20 | 163 | 163 | 92 | 92 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 88 | 65 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 134 | 146 | 84 | 80 | 150 | 150 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 27 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 5 | 68 | 115 | 115 | 34 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 36 | 0 | 40 | 0 | 40 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1277 | 1353 | 2727.44 | 2683.44 | 1537.45 | 1765.45
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-07-2026 | during | 21-07-2026 | during | 21-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 15.88 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.9 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 130 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 67 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 23.07 | 0 | 19.63 | 0 | 19.63 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 148.85 | 209 | 508.23 | 516.5 | 238.73 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 28 | 28 | 28 | 28 | 28 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 30 | 0 | 0 | 20 | 20 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 131 | 142 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 143 | 142 | 142 | 142 | 142 | 142 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 28 | 30 | 30 | 30 | 30 | 30 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 33 | 52 | 84 | 84 | 33 | 33 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 101 | 100 | 100 | 100 | 100 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 15 | 15 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 17 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 314 | 395 | 385 | 385 | 395 | 395 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1105 | 1237 | 1318 | 1318 | 1234 | 1234
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 895 | 894 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 32 | 32 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 13 | 0 | 55 | 0 | 55 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 550 | 550 | 1000 | 1234.2 | 550 | 550 | U-2 Under maint.
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1496 | 1497 | 3307 | 3486.2 | 1707 | 1652
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 650 | 976 | 700 | 1050 | 700 | 1050 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 71 | 55 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 1070 | 1160 | 1163.05 | 1163.05 | 1103.05 | 1103.05 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 54 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 248 | 217 | 307 | 307 | 307 | 307 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.05 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2396.05 | 2802 | 2781.05 | 3130.05 | 2567.05 | 2916.05
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 12.6 | 0 | 55 | 0 | 55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 144 | 142 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 129 | 123 | 220 | 220 | 140 | 140 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 129 | 118 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 296 | 280 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 22 | 22 | 22 | 22 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 92 | 92 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 70 | 50 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 0.12 | 0 | 0 | 0 | 0 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1359.35 | 1491.1 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 0.59 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 62 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2202.66 | 2254.1 | 3249.12 | 3033.12 | 2737.74 | 2683.74
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 180 | 180 | 180 | 180 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 77 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.9 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 78 | 0 | 117 | 0 | 117 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 268.9 | 327 | 556 | 408 | 443 | 330
System Total |  |  |  |  | 28843.2 | 29169.167 | 13990.44 | 15332.1 | 24263.29 | 24457.39 | 16507.84 | 17564.74
Forecast Scenario (21-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15190 |  | 300 |  | 15504.1361
|  |  |  | 1:00 | 15000 |  | 209 |  | 15218.8482
|  |  |  | 2:00 | 14600 |  | 187 |  | 14795.8115
|  |  |  | 3:00 | 14200 |  | 179 |  | 14387.4346
|  |  |  | 4:00 | 14050 |  | 122 |  | 14177.7487
|  |  |  | 5:00 | 14100 |  | 119 |  | 14224.6073
|  |  |  | 6:00 | 13370 |  | 131 |  | 13507.1728
|  |  |  | 7:00 | 13300 |  | 158 |  | 13465.445
|  |  |  | 8:00 | 13500 |  | 152 |  | 13659.1623
|  |  |  | 9:00 | 13700 |  | 132 |  | 13838.2199
|  |  |  | 10:00 | 13700 |  | 200 |  | 13909.4241
|  |  |  | 11:00 | 14100 |  | 180 |  | 14288.4817
|  |  |  | 12:00 | 14580 |  | 220 |  | 14810.3665
|  |  |  | 13:00 | 14880 |  | 206 |  | 15095.7068
|  |  |  | 14:00 | 14700 |  | 300 |  | 15014.1361
|  |  |  | 15:00 | 14900 |  | 400 |  | 15318.8482
|  |  |  | 16:00 | 14500 |  | 410 |  | 14929.3194
|  |  |  | 17:00 | 14070 |  | 320 |  | 14405.0785
|  |  |  | 18:00 | 13800 |  | 310 |  | 14124.6073
|  |  |  | 18:30 | 14470 |  | 330 |  | 14815.5497
|  |  |  | 19:00 | 15100 |  | 300 |  | 15414.1361
|  |  |  | 19:30 | 15960 |  | 280 |  | 16253.1937
|  |  |  | 20:00 | 15800 |  | 250 |  | 16061.7801
|  |  |  | 21:00 | 15500 |  | 230 |  | 15740.8377
|  |  |  | 22:00 | 15700 |  | 210 |  | 15919.8953
|  |  |  | 23:00 | 15700 |  | 300 |  | 16014.1361
Probable Maximum Temperature: |  |  | 30 °C
Probable Maximum Demand at Day Peak: |  |  | 14600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 280
Probable Maximum Demand at Evening Peak: |  |  | 16253.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15960.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 348.04 MKWHr. |  | 90 | 0 | 30 | 160 | 0 | 0 | 0 | 0 | 0 | 280
*** This report is generated digitally from Operation Information System (OIS) at 09:14 hrs on 21-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 20-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13990.44 | MW | 12:00 Hr. | Energy Generated |  |  | 342.0169 |  | MKWHr.
| Day Peak Demand |  |  | 14071.95 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.659 |  | MKWHr.
| Evening Peak Generation |  |  | 15332.1 | MW | 19:30 Hr. | Energy Demand |  |  | 344.6759 |  | MKWHr.
| Evening Peak Demand |  |  | 15511.1 | MW | 19:30 Hr. | Maximum Temperature |  |  | 30 |  | °C
| Minimum Generation of the Day |  |  | 13146.57 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 926.78 |  | MMCFD
| Maximum Generation of the Day |  |  | 15401.9 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.3063 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 44.2099 | 0 | 13.7972 | 0 | 0 | 0.032614 | 0 | 0 | 58.0397 | Gas | 125.5677 | Gas | 442420360.7604
| Chattogram Zone |  |  | 2.2288 | 54.4291 | 3.6175 | 0 | 5.2545 | 0.081376 | 0 | 0.42768 | 66.039 | Coal | 122.878 | Coal | 813557290.4994
| Cumilla Zone |  |  | 25.5375 | 0 | 2.1471 | 0 | 0 | 0.36486 | 3.1133 | 0 | 31.1628 | HFO | 26.9661 | HFO | 490156630.59
| Mymensingh Zone |  |  | 0 | 0 | 3.6185 | 0 | 0 | 0.18702 | 0 | 0 | 3.8055 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.6608 | 0 | 0 | 0 | 0 | 0.02627 | 0 | 0 | 28.6871 | Hydro | 5.2545 | Hydro | 525448
| Khulna Zone |  |  | 0 | 12.8509 | 0.11102 | 0 | 0 | 0.12672 | 22.5287 | 0 | 35.6174 | Solar | 2.0791 | Solar | 32330899.9612
| Barishal Zone |  |  | 7.9306 | 51.147 | 1.1571 | 0 | 0 | 0.001585 | 0 | 0 | 60.2363 | Import | 58.8438 | Import | 371590918.23
| Rajshahi Zone |  |  | 17 | 0 | 1.1978 | 0 | 0 | 0.65071 | 33.2018 | 0 | 52.0503 | Wind | 0.42768 | Wind | 6291172.8
| Rangpur Zone |  |  | 0 | 4.451 | 1.3198 | 0 | 0 | 0.60799 | 0 | 0 | 6.3788
| Total |  |  | 125.5677 | 122.878 | 26.9661 | 0 | 5.2545 | 2.0791 | 58.8438 | 0.42768 | 342.0169
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 442420360.7604 |  | Hydro | 525448
|  |  |  | Coal | 813557290.4994 |  | Solar | 32330899.9612
|  |  |  | HFO | 490156630.59 |  | Import | 371590918.23
|  |  |  | HSD | 0 |  | Wind | 6291172.8
[5 empty] | Total: | 215,68,72,720 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6167 | Peak Hr Flow | 894.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 42644600 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.2018 | Peak Hr Flow | 1491.10 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2021 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.1133 | Peak Hr Flow | 146.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2348 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 57.9318 | Peak Hr Flow | 2531.10 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 7 |  | 5526
|  |  |  | Chattogram |  | 0 |  | 1572
|  |  |  | Cumilla |  | 26 |  | 1422
|  |  |  | Mymensingh |  | 138 |  | 1294
|  |  |  | Sylhet |  | 0 |  | 569
|  |  |  | Khulna |  | 0 |  | 1770
|  |  |  | Barishal |  | 0 |  | 451
|  |  |  | Rajshahi |  | 0 |  | 1467
|  |  |  | Rangpur |  | 0 |  | 1011
|  |  |  | Total |  | 171 |  | 15082
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 89
|  |  |  | Total Unavailable Capacity |  |  |  | 389
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:58 | 18:07 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 LT Scheduled S/D Due to Maintenance
| 08:59 | 17:58 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 HT Scheduled S/D Due to Maintenance
| 09:36 | 18:42 | Madunaghat-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Requested by NLDC
| 09:42 | 13:37 | Hathazari-Raozan 230kV Ckt-1 Project Work S/D from Hathazari 230/132/33kV end Due to G2G
project work
| 09:46 | 16:24 | Hathazari 230/132/33kV S/S 230KV MAIN BUS-02 Project Work S/D Due to G2G project work.
| 09:46 |  | Hathazari 230/132/33kV S/S Raojan-02 Project Work S/D Due to G2G project work
| 09:51 | 18:43 | Korerhat 400/230/132kV S/S Meghnaghat-2 Project Work S/D Due to Project work (shunt
reactor)
| 09:58 | 17:44 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Scheduled S/D from Purbasadipur 230/132/33kV end
Due to RTU Interconnection work
| 10:07 | 18:52 | Korerhat 400/230/132kV S/S Chowmuhani-1 Project Work S/D Due to Project work (DFDR)
|  | 10:40 | Munshiganj 132/33kV S/S Transformer-1 HT is restored.
|  | 10:40 | Munshiganj 132/33kV S/S Transformer-1 LT is restored.
| 11:29 | 12:21 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Tree
trimming work of Tower 9-10 span of 132kv Bagerhat -Bhandaria Line.
| 11:30 | 12:20 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Shutdown
by ALDC
| 12:00 |  | Day Peak Generation: 13990 MW.
|  | 12:55 | Bheramara 230/132kV S/S STG (NW) is restored.
|  | 13:11 | Bheramara 230/132kV S/S GTG (NW) is restored.
| 14:43 |  | Sirajganj 225 MW CCPP unit-3 ST tripped.
| 16:12 |  | Sikalbaha 225 MW CCPP ST was synchronized.
| 16:21 | 18:31 | Joypurhat 132/33kV S/S Transformer T-3 (427 T) LT Scheduled S/D Due to Red hot | [7 empty] | 20.0MW load
|  |  | Maintenance work is doing by Joypurhat PBS | [7 empty] | interrup.
| 16:21 | 19:09 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT Scheduled S/D Due to Red hot | [7 empty] | 20.0MW load
|  |  | Maintenance work is doing by Joypurhat PBS | [7 empty] | interrup.
| 16:22 | 19:07 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT Scheduled S/D Due to Red hot
Maintenance work is doing by Joypurhat PBS
| 16:22 | 18:29 | Joypurhat 132/33kV S/S Transformer T-3 (427 T) HT Scheduled S/D Due to Red hot
Maintenance work is doing by Joypurhat PBS
| 17:12 |  | Sikalbaha 225 MW CCPP tripped due to HRSG trip.
| 17:13 |  | Sirajganj 225 MW CCPP unit-3 ST was synchronized.
| 19:30 |  | Evening peak generation is 15332 MW.
|  | 20:42 | Muradnagar 132/33kV S/S 132KV Transformar-01 HT is restored.
|  | 20:44 | Muradnagar 132/33kV S/S 132KV Transformar-01 LT is restored.
| 21:13 | 23:02 | Barishal 230/132kV S/S T-5 LT Forced S/D Due to 33 kV Mehendiganj Feeder red hot | [7 empty] | 46.0MW load
|  |  | maintenance work by PBS | [7 empty] | interrup.
| 21:14 | 22:59 | Barishal 230/132kV S/S T-5 HT Forced S/D Due to Red hot maintenance or 33 kV Mehendiganj | [7 empty] | 46.0MW load
|  |  | Feeder Work by PBS | [7 empty] | interrup.
| 04:19 | 04:58 | Shahjibazar-Sreemangal 132kV Ckt-2 Tripped from Sreemongol 132/33kV end showing Distance
Relay relays Due to R phase LA blast. and from Shahjibazar 132/33kV end showing Distance
relay relays Due to LA blast of Sreemangal Grid.
| 04:19 | 04:40 | Shahjibazar-Sreemangal 132kV Ckt-1 Tripped from Sreemongol 132/33kV end showing Distance
relay relays Due to Due to the LA blast in Sreemangal-Shahjibazar circuit 2
| 04:24 | 04:24 | Shahjibazar-Sreemangal 132kV Ckt-2 Forced S/D from Sreemongol 132/33kV end Due to R
phase LA blast
| 04:45 |  | Shahjibazar-Sreemangal 132kV Ckt-2 Forced S/D from Sreemongol 132/33kV end Due to LA
Blust
| 06:00 |  | Minimum Generation: 12697 MW.
| 06:21 | 06:44 | Barishal 230/132kV S/S T-5 LT Tripped showing Over current relays Due to Over current | [7 empty] | 36.0MW load
|  |  | tripping due to 33kv Sarupkathi-2 feeder fault | [7 empty] | interrup.
| 06:21 | 06:46 | Barishal 230/132kV S/S T-4 LT Tripped showing Over current relays Due to Over current | [7 empty] | 36.0MW load
|  |  | Tripping due to 33kv Sarupkhathi-2 feeder fault. | [7 empty] | interrup.
| 06:32 |  | Payra 400/132/33kV S/S 132/33 kV Transformer-04 HT Scheduled S/D Due to Maintenance
| 06:32 |  | Payra 400/132/33kV S/S 132/33 kV Transformer-04 LT Scheduled S/D Due to Maintenance
| 06:41 |  | Patuakhali-Payra 132kV Ckt-2 Scheduled S/D from Patuakhali 132/33kV end Due to Payra
grid end side red hot maintenance. and from Payra 400/132/33kV end Due to High
temperature maintenance
| 07:35 |  | Madaripur 132/33kV S/S T2-415T LT Tripped showing O/c relays. | [7 empty] | 61.0MW load
interrup.
| 07:35 |  | Madaripur 132/33kV S/S T2-415T HT Tripped showing O/c relays. | [7 empty] | 61.0MW load
interrup.
| 07:35 |  | Madaripur 132/33kV S/S T1-405T LT Tripped showing O/c relays.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 259 | 7736400 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 307 | 7165295 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 35 | 510933 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 308 | 7355194 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 261360 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 145 | 2968800 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 604867 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 341266 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 12 | 303600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 371520 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 352800 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 1767905 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 96 | 1628640 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 982080 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 104 | 656640 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 32614 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 378720 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 550 | 10056696 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 463 | 11221150 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143 | 3343200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2750 | 58039680
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 64935 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 313920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 219 | 5254480 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 1800192 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 508509 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 320095 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 168960 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 18 | 428640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 144960 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 16441 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 55200 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 45 | 451306 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 1259563 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 333120 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 20073 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 30 | 41818 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1170 | 27774543 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 5 | 427680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 26654545.46 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 2903 | 66038980.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 193 | 4644000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 280 | 7160100 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 210 | 5366000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 210 | 5209000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1262456.3 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 40 | 147200 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 24 | 420640 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 20 | 1418042 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 65 | 686400 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 146 | 3113280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 57346 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 477930 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 125160 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 710400 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 364864 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1353 | 31162818.3
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 58629 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 4700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 130 | 1867200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 1339200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 123690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 337920 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 74160 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 209 | 3805499
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 26270 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 28 | 669000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 597000 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 142 | 3319527.27 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 3269000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 684672 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 52 | 1309440 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2423520 | ST Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 272688 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7397000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 395 | 8719000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1237 | 28687117.27
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 894 | 21616727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 63360 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 47664 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 126720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 550 | 12850909 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1497 | 35617380
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 976 | 18690909 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 55 | 737088 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2747000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 1160 | 26413090.91 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5183630 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 420000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 217 | 6043000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1585 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2802 | 60236302.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 116696 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 47258 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 142 | 3481364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 123 | 3270000 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 118 | 3055804 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 280 | 7192797 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 2704 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 957408 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 190464 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 11100 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1491.1 | 33201819 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 104368 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 418550 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2254.1 | 52050332
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4451000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 77 | 750864 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30044.64 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 568954 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 78261 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 499680 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 327 | 6378803.64
Eastern Grid Total |  |  |  |  | 17438.042 | 8452 | 187734095.03
Western Grid Total |  |  |  |  | 11731.125 | 6880.1 | 154282818.55
National Grid Total |  |  |  |  | 29169.167 | 15332.1 | 342016913.58
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-07-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10260.27 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4699 | MW
i) Dhaka area |  |  | 5519.27 |  | MW | i) Khulna area |  |  |  | 1770 | MW
ii) Chattogram area |  |  | 1620 |  | MW | ii) Barishal area |  |  |  | 450.6 | MW
iii) Cumilla area |  |  | 1396 |  | MW | iii) Rajshahi area |  |  |  | 1467.4 | MW
iv) Mymensingh area |  |  | 1156 |  | MW | iv) Rangpur area |  |  |  | 1011 | MW
v) Sylhet area |  |  | 569 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14959.27 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 150 | 11:00 | 133 | Narshingdi | 187 | 20:00 | 199 | Uttara | 88 | 12:00
2 | AKSML | 147 | 14:00 | 68 | Hasnabad | 93 | 00:00 | 134 | Natore | 153 | 21:00 | 200 | UttaraNew | 51 | 00:00
3 | Aftabnagar | 42 | 13:00 | 69 | Hathazari | 90 | 19:30 | 135 | Nawabganj | 60.1 | 00:00 | 201 | Zigatola | 106 | 13:00
4 | Agargaon | 116 | 10:00 | 70 | Hatirjheel | 96 | 15:00 | 136 | Netrakona | 129 | 19:30
5 | Agrabad | 72 | 12:00 | 71 | Ishurdi | 80 | 13:00 | 137 | New | 84 | 10:00
6 | Amnura | 32 | 00:00 | 72 | Jaldhaka | 80 | 19:30 | 138 | Niamatpur | 81 | 00:00
7 | Ashuganj | 74 | 02:00 | 73 | Jamalpur | 131 | 04:00 | 139 | Noapara | 48 | 00:00
8 | BSRM | 198 | 22:00 | 74 | Jashore | 142 | 19:30 | 140 | PHP | 12 | 13:00
9 | Bagerhat | 94 | 00:00 | 75 | Jhenaidah | 94 | 19:30 | 141 | Pabna | 100 | 19:30
10 | Bajitpur | 92 | 02:00 | 76 | Joydebpur | 168 | 10:00 | 142 | Palashbari | 128 | 00:00
11 | Bakerganj | 14.6 | 00:00 | 77 | Joypurhat | 68 | 00:00 | 143 | Panchagarh | 59 | 21:00
12 | Bakulia | 94 | 19:30 | 78 | Juldah | 17 | 15:00 | 144 | Patiya | 11 | 19:30
13 | Banani | 70.8 | 11:00 | 79 | KSRM | 31 | 12:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 17 | 10:00 | 80 | Kabirpur | 265 | 18:30 | 146 | Patuakhali | 69.7 | 00:00
15 | Barapukuria | 72 | 00:00 | 81 | Kachua | 88 | 00:00 | 147 | Payra | 34 | 01:00
16 | Barguna | 22 | 00:00 | 82 | Kaliganj | 36 | 19:00 | 148 | Postogola | 57 | 00:00
17 | Barishal | 104 | 12:00 | 83 | Kallyanpur | 114 | 00:00 | 149 | Pubail | 42 | 12:00
18 | Barishal-230 | 102 | 00:00 | 84 | Kalurghat | 40 | 12:00 | 150 | Purbachal | 28 | 13:00
19 | Baroaulia | 42 | 13:00 | 85 | Kamrangirchar | 76 | 13:00 | 151 | Purbasadipur | 142 | 00:00
20 | Baroirhat | 60 | 19:30 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 42 | 00:00
21 | Bashundhara | 187 | 11:00 | 87 | Kasba | 37 | 19:00 | 153 | Rahim | 49 | 00:00
22 | BashundharaCement | 6 | 00:00 | 88 | Kazla | 113 | 11:00 | 154 | Rajbari | 84 | 19:30
23 | Beanibazar | 66 | 00:00 | 89 | Keranigonj | 81 | 19:00 | 155 | Rajendrapur | 119 | 14:00
24 | Benapole | 74 | 00:00 | 90 | Khagrachori | 32 | 19:00 | 156 | Rajshahi | 107 | 01:00
25 | Bhaluka | 156 | 19:30 | 91 | Khulna | 65 | 09:00 | 157 | Rajshahi-230 | 106 | 13:00
26 | Bhandaria | 60 | 00:00 | 92 | Khulshi | 175 | 16:00 | 158 | Ramganj | 108 | 19:00
27 | Bhangura | 38 | 19:30 | 93 | Kishoreganj | 133 | 21:00 | 159 | Rampur | 41 | 19:00
28 | Bheramara(GK) | 66 | 00:00 | 94 | Kodda | 313 | 18:30 | 160 | Rangamati | 18 | 20:00
29 | Bhulta | 217 | 10:00 | 95 | Kulaura | 48 | 19:00 | 161 | Rangpur | 136 | 00:00
30 | Bog-Sherpur | 68 | 00:00 | 96 | Kurigram | 66 | 00:00 | 162 | Ruppur | 4.2 | 10:00
31 | Bogura | 176 | 00:00 | 97 | Kushtia | 158 | 10:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 74 | 02:00 | 98 | Laksam | 35 | 23:00 | 164 | Saidpur | 105 | 01:00
33 | Brahmanbaria | 133 | 19:00 | 99 | Lakshmipur | 40 | 19:00 | 165 | Santhia | 34 | 19:30
34 | Cantonment | 114 | 14:00 | 100 | Lalbag | 82 | 13:00 | 166 | Satkhira | 123 | 06:00
35 | Chandina | 36 | 21:00 | 101 | Lalmonirhat | 64 | 19:30 | 167 | Satmasjid | 102 | 13:00
36 | Chandpur | 84 | 00:00 | 102 | MI_Cement | 16.6 | 02:00 | 168 | Savar | 224 | 12:00
37 | Chandraghona | 32 | 19:00 | 103 | Madanganj | 41 | 13:00 | 169 | SevenRings | 13.14 | 19:30
38 | Chapai | 77 | 00:00 | 104 | Madaripur | 119 | 00:00 | 170 | ShahCement | 6 | 02:00
39 | Charfasson | 32 | 00:00 | 105 | Madartek | 78 | 00:00 | 171 | Shahjadpur | 80 | 20:00
40 | Charsaidpur | 30 | 12:00 | 106 | Madunaghat | 55 | 19:00 | 172 | Shahjibazar | 130 | 00:00
41 | Chauddagram | 73 | 22:00 | 107 | Magura | 64 | 19:30 | 173 | Shahmirpur | 54 | 01:00
42 | Chhatak | 33 | 00:00 | 108 | Mahasthangarh | 84 | 00:00 | 174 | Shariatpur | 90 | 00:00
43 | Chowmuhani | 149 | 19:30 | 109 | Maijdee | 42 | 03:00 | 175 | Sherpur | 152 | 01:00
44 | Chuadanga | 116 | 00:00 | 110 | Manikganj | 138 | 01:00 | 176 | Shikalbaha | 23 | 18:30
45 | Coxsbazar | 138 | 19:00 | 111 | Maniknagar | 74 | 13:00 | 177 | Shitalakhya | 76.6 | 13:00
46 | Cumilla(N) | 114 | 21:00 | 112 | Matarbari | 54 | 02:00 | 178 | Sholosohor | 47 | 12:00
47 | Cumilla(S) | 144 | 19:30 | 113 | Matuail | 76 | 10:00 | 179 | Shomvuganj | 44 | 00:00
48 | Daganbhuiyan | 35 | 22:00 | 114 | Metrorail_Motijheel | 21 | 12:00 | 180 | Shyampur | 146 | 00:00
49 | Daudkandi | 141 | 22:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 134 | 12:00
50 | DhakaUniversity | 86 | 13:00 | 116 | Millgate | 105 | 10:00 | 182 | Sirajganj | 110 | 20:00
51 | Dhamrai | 106 | 00:00 | 117 | Mirpur | 144 | 19:00 | 183 | Sitakunda | 34 | 19:00
52 | Dhanmondi | 109.8 | 13:00 | 118 | Mirsorai | 41 | 14:00 | 184 | Sonargaon | 145 | 11:00
53 | Dohazari | 96 | 22:00 | 119 | Mirzapur | 42 | 00:00 | 185 | Sreemongol | 74 | 21:00
54 | Faridpur | 180 | 00:00 | 120 | Mithapukur | 74 | 00:00 | 186 | Sreepur | 140 | 12:00
55 | Fatullah | 100 | 10:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 49.1 | 00:00
56 | Fenchuganj | 39 | 00:00 | 122 | Mogbazar | 10.8 | 19:00 | 188 | Sunamganj | 59 | 00:00
57 | Feni | 109 | 19:00 | 123 | Mongla | 49 | 12:00 | 189 | Sylhet | 106 | 19:00
58 | GPH | 71 | 22:00 | 124 | Motijheel | 48 | 13:00 | 190 | Sylhet_(South) | 59 | 23:00
59 | Ghatail | 85 | 01:00 | 125 | Muktagacha | 36 | 01:00 | 191 | TK | 24 | 00:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 109 | 00:00 | 192 | Tangail | 182 | 20:00
61 | Ghorashal-230 | 105 | 00:00 | 127 | Muradnagar | 44 | 00:00 | 193 | Taraganj | 27 | 00:00
62 | Goalpara | 30 | 00:00 | 128 | Mymensingh | 151 | 01:00 | 194 | Tasnim | 39 | 23:00
63 | Gollamari | 106 | 00:00 | 129 | Nabinagar | 104 | 19:00 | 195 | Thakurgaon | 111 | 19:30
64 | Gopalganj | 112 | 00:00 | 130 | Naogaon | 144 | 00:00 | 196 | Tongi | 162 | 12:00
65 | Gulshan | 106 | 11:00 | 131 | Narail | 57 | 20:00 | 197 | Ullahpara | 38 | 20:00
66 | Halishahar | 93 | 09:00 | 132 | Narinda | 70 | 13:00 | 198 | Ullon | 61 | 14:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15401.9 | 253 |  | 15666.29
1:00 | 15280.94 | 73 |  | 15357.23
2:00 | 14796.94 | 43 |  | 14841.88
3:00 | 14296.94 | 33 |  | 14331.43
4:00 | 14059.42 | 22 |  | 14082.41
5:00 | 13959.72 | 165 |  | 14131.72
6:00 | 13211.86 | 152 |  | 13370.86
7:00 | 13151.91 | 188 |  | 13347.91
8:00 | 13291.39 | 209 |  | 13509.8
9:00 | 13463.22 | 221 |  | 13694.17
10:00 | 13594.27 | 104 |  | 13702.95
11:00 | 13712.2 | 59 |  | 13773.86
12:00 | 13990.44 | 78 |  | 14071.95
13:00 | 14073.36 | 74 |  | 14150.36
14:00 | 13921.15 | 108 |  | 14034.01
15:00 | 13816.59 | 139 |  | 13961.59
16:00 | 13433.83 | 138 |  | 13577.83
17:00 | 13146.57 | 135 |  | 13287.65
18:00 | 13033.83 | 160 |  | 13200.83
19:00 | 14270.1 | 199 |  | 14478.1
19:30 | 15332.1 | 171 |  | 15511.1
20:00 | 15213.57 | 36 |  | 15251.57
21:00 | 15284.33 | 14 |  | 15298.96
22:00 | 15068.55 | 24 |  | 15093.63
23:00 | 14825.38 | 32 |  | 14858.82
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 20-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 90 | 1 | 400 | 172 | 1326 | 286 | Ishurdi-Ghorashal Ckt-1 | Export | 3477600
1:00 | 96 | 4 | 390 | 164 | 1316 | 312
2:00 | 93 | 10 | 360 | 148 | 1210 | 312 |  | Import | 0
3:00 | 94 | 15 | 340 | 136 | 1174 | 306
4:00 | 99 | 21 | 320 | 130 | 1126 | 352 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 121 | 27 | 400 | 134 | 1286 | 338
6:00 | 147 | 36 | 470 | 130 | 1164 | 418 |  | Import | 0
7:00 | 146 | 37 | 460 | 122 | 1032 | 424
8:00 | 161 | 48 | 490 | 138 | 1186 | 466 | Sirajganj-Sreepur Ckt-1 | Export | 2784000
9:00 | 179 | 64 | 520 | 152 | 1348 | 562
10:00 | 181 | 65 | 550 | 170 | 1492 | 678 |  | Import | 0
11:00 | 183 | 67 | 550 | 176 | 1538 | 694
12:00 | 178 | 69 | 530 | 186 | 1536 | 680 | Sirajganj-Sreepur Ckt-2 | Export | 2793000
13:00 | 169 | 55 | 510 | 166 | 1518 | 660
14:00 | 167 | 53 | 520 | 166 | 1598 | 662 |  | Import | 0
15:00 | 178 | 69 | 530 | 180 | 1640 | 686
16:00 | 178 | 72 | 506 | 190 | 1600 | 678 | Gopalganj-Aminbazar Ckt-1 | Export | 16780000
17:00 | 178 | 73 | 510 | 200 | 1564 | 686
18:00 | 166 | 58 | 520 | 184 | 1634 | 604 |  | Import | 0
18:30 | 166 | 60 | 510 | 168 | 1648 | 582
19:00 | 150 | 45 | 520 | 180 | 1584 | 480 | Gopalganj-Aminbazar Ckt-2 | Export | 16810000
19:30 | 127 | 29 | 440 | 162 | 1454 | 386
20:00 | 122 | 24 | 440 | 164 | 1424 | 392 |  | Import | 0
21:00 | 126 | 27 | 470 | 194 | 1500 | 396
22:00 | 121 | 23 | 450 | 180 | 1398 | 360 |  | Total Export | 42644600
23:00 | 144 | 34 | 500 | 180 | 1408 | 408 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 20-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8428 | 6973.9 | 15401.9 | DAILY GENERATION CURVE
00:30 | 8362.5 | 6978.92 | 15341.42
01:00 | 8297 | 6983.94 | 15280.94 | 20-07-2026
01:30 | 8216.5 | 6822.44 | 15038.94
02:00 | 8136 | 6660.94 | 14796.94
02:30 | 8015.5 | 6531.44 | 14546.94
03:00 | 7895 | 6401.94 | 14296.94
03:30 | 7882.5 | 6295.68 | 14178.18
04:00 | 7870 | 6189.42 | 14059.42
04:30 | 7792.5 | 6217.07 | 14009.57
05:00 | 7715 | 6244.72 | 13959.72
05:30 | 7515.65 | 6070.14 | 13585.79
06:00 | 7316.3 | 5895.56 | 13211.86
06:30 | 7332.925 | 5848.96 | 13181.885
07:00 | 7349.55 | 5802.36 | 13151.91
07:30 | 7363.02 | 5858.63 | 13221.65
08:00 | 7376.49 | 5914.9 | 13291.39
08:30 | 7384.59 | 5992.715 | 13377.305
09:00 | 7392.69 | 6070.53 | 13463.22
09:30 | 7418.94 | 6109.805 | 13528.745
10:00 | 7445.19 | 6149.08 | 13594.27
10:30 | 7478.085 | 6175.15 | 13653.235
11:00 | 7510.98 | 6201.22 | 13712.2
11:30 | 7568.905 | 6282.415 | 13851.32
12:00 | 7626.83 | 6363.61 | 13990.44
12:30 | 7672.335 | 6359.565 | 14031.9
13:00 | 7717.84 | 6355.52 | 14073.36
13:30 | 7660.805 | 6336.45 | 13997.255
14:00 | 7603.77 | 6317.38 | 13921.15
14:30 | 7566.605 | 6302.265 | 13868.87
15:00 | 7529.44 | 6287.15 | 13816.59
15:30 | 7458.935 | 6166.275 | 13625.21
16:00 | 7388.43 | 6045.4 | 13433.83
16:30 | 7329.405 | 5960.795 | 13290.2
17:00 | 7270.38 | 5876.19 | 13146.57
17:30 | 7167.745 | 5922.455 | 13090.2
18:00 | 7065.11 | 5968.72 | 13033.83
18:30 | 7374.555 | 6277.41 | 13651.965
19:00 | 7684 | 6586.1 | 14270.1
19:30 | 8452 | 6880.1 | 15332.1
20:00 | 8368 | 6845.57 | 15213.57
20:30 | 8336.18 | 6912.77 | 15248.95 |  | Executive Engineer
21:00 | 8304.36 | 6979.97 | 15284.33 |  | Network Operation Division
21:30 | 8307.36 | 6869.08 | 15176.44
22:00 | 8310.36 | 6758.19 | 15068.55
22:30 | 8257.43 | 6689.535 | 14946.965
23:00 | 8204.5 | 6620.88 | 14825.38

## En-Curve
QF-LDC-12
Date | 20-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3229 | 2169 | 848 | 38 | 140 | 1478.9 | 222 | 5542 | 0 | 420 | 1299 | 0 | 0 | 16 | 253 | DAILY ENERGY CURVE
00:30 | 3229.5 | 2094 | 871.5 | 38 | 138 | 1478.92 | 222 | 5535.5 | 0 | 472.5 | 1246.5 | 0 | 0 | 15 | 163 | 20-07-2026
01:00 | 3230 | 2019 | 895 | 38 | 136 | 1478.94 | 222 | 5529 | 0 | 525 | 1194 | 0 | 0 | 14 | 73
01:30 | 3244.5 | 1968.5 | 895 | 38 | 135 | 1422.44 | 221.5 | 5473.5 | 0 | 517.5 | 1103 | 0 | 0 | 20 | 58 | Energy Generated | 342.0169 |  | MKWHr
02:00 | 3259 | 1918 | 895 | 38 | 134 | 1365.94 | 221 | 5418 | 0 | 510 | 1012 | 0 | 0 | 26 | 43 | Energy not Served | 2.659 |  | MKWHr
02:30 | 3271.5 | 1891 | 895 | 38 | 130 | 1338.94 | 220.5 | 5343 | 0 | 488 | 907.5 | 0 | 0 | 23.5 | 38 | Total Energy Requirement | 344.6759 |  | MKWHr
03:00 | 3284 | 1864 | 895 | 38 | 126 | 1311.94 | 220 | 5268 | 0 | 466 | 803 | 0 | 0 | 21 | 33
03:30 | 3292 | 1895.5 | 895 | 38 | 125 | 1285.18 | 220 | 5197.5 | 0 | 466 | 747.5 | 0 | 0 | 16.5 | 27.5
04:00 | 3300 | 1927 | 895 | 38 | 124 | 1258.42 | 220 | 5127 | 0 | 466 | 692 | 0 | 0 | 12 | 22
04:30 | 3317.5 | 2021 | 895 | 38 | 126 | 1221.07 | 220 | 5227.5 | 0 | 448.5 | 480.5 | 0 | 0 | 14.5 | 93.5
05:00 | 3335 | 2115 | 895 | 38 | 128 | 1183.72 | 220 | 5328 | 0 | 431 | 269 | 0 | 0 | 17 | 165
05:30 | 3298.5 | 2056.5 | 895 | 38 | 125 | 1252.695 | 220 | 5087.5 | 2.595 | 359 | 217.5 | 0 | 0 | 33.5 | 158.5
06:00 | 3262 | 1998 | 895 | 38 | 122 | 1321.67 | 220 | 4847 | 5.19 | 287 | 166 | 0 | 0 | 50 | 152
06:30 | 3222.5 | 2047.5 | 895 | 38 | 117 | 1398.03 | 220 | 4719.5 | 23.855 | 287 | 166 | 0 | 0 | 47.5 | 170
07:00 | 3183 | 2097 | 895 | 38 | 112 | 1474.39 | 220 | 4592 | 42.52 | 287 | 166 | 0 | 0 | 45 | 188
07:30 | 3184 | 2109 | 895 | 38 | 113 | 1471.865 | 220 | 4632 | 70.285 | 287 | 166 | 0 | 0 | 35.5 | 198.5
08:00 | 3185 | 2121 | 895 | 38 | 114 | 1469.34 | 220 | 4672 | 98.05 | 287 | 166 | 0 | 0 | 26 | 209
08:30 | 3226.5 | 2108.5 | 895 | 38 | 116 | 1465.58 | 220 | 4704.5 | 121.225 | 287 | 166 | 0 | 0 | 29 | 215
09:00 | 3268 | 2096 | 895 | 38 | 118 | 1461.82 | 220 | 4737 | 144.4 | 287 | 166 | 0 | 0 | 32 | 221
09:30 | 3243.5 | 2040.5 | 894.5 | 38 | 122 | 1451.76 | 219.5 | 4808 | 173.985 | 278 | 225.5 | 0 | 0 | 33.5 | 162.5
10:00 | 3219 | 1985 | 894 | 38 | 126 | 1441.7 | 219 | 4879 | 203.57 | 269 | 285 | 0 | 0 | 35 | 104
10:30 | 3193.5 | 1971 | 894.5 | 38 | 130 | 1419.62 | 220 | 4834.5 | 244.115 | 269.5 | 407 | 0 | 0 | 31.5 | 81.5
11:00 | 3168 | 1957 | 895 | 38 | 134 | 1397.54 | 221 | 4790 | 284.66 | 270 | 529 | 0 | 0 | 28 | 59
11:30 | 3124 | 1963.5 | 895 | 38 | 134 | 1378.445 | 221 | 4865 | 277.375 | 281 | 646 | 0 | 0 | 28 | 68.5
12:00 | 3080 | 1970 | 895 | 38 | 134 | 1359.35 | 221 | 4940 | 270.09 | 292 | 763 | 0 | 0 | 28 | 78
12:30 | 3089.5 | 1954 | 895 | 38 | 138 | 1356.34 | 220.5 | 4978 | 288.06 | 288.5 | 766.5 | 0 | 0 | 19.5 | 76
13:00 | 3099 | 1938 | 895 | 38 | 142 | 1353.33 | 220 | 5016 | 306.03 | 285 | 770 | 0 | 0 | 11 | 74
13:30 | 3105.5 | 1897 | 895 | 38 | 143 | 1340.72 | 221 | 5013 | 283.535 | 285.5 | 768 | 0 | 0 | 7 | 91
14:00 | 3112 | 1856 | 895 | 38 | 144 | 1328.11 | 222 | 5010 | 261.04 | 286 | 766 | 0 | 0 | 3 | 108
14:30 | 3090 | 1897 | 895 | 38 | 141 | 1323.16 | 222 | 5005.5 | 245.71 | 286 | 720.5 | 0 | 0 | 5 | 123.5
15:00 | 3068 | 1938 | 895 | 38 | 138 | 1318.21 | 222 | 5001 | 230.38 | 286 | 675 | 0 | 0 | 7 | 139
15:30 | 3040.5 | 1955.5 | 895 | 38 | 138 | 1304.82 | 222 | 5008 | 178.89 | 258 | 579 | 0 | 0 | 7.5 | 138.5
16:00 | 3013 | 1973 | 895 | 38 | 138 | 1291.43 | 222 | 5015 | 127.4 | 230 | 483 | 0 | 0 | 8 | 138
16:30 | 3014 | 1983.5 | 895 | 38 | 135 | 1265.735 | 221 | 4942.5 | 96.965 | 230 | 458.5 | 0 | 0 | 10 | 136.5
17:00 | 3015 | 1994 | 895 | 38 | 132 | 1240.04 | 220 | 4870 | 66.53 | 230 | 434 | 0 | 0 | 12 | 135
17:30 | 2973.5 | 1938 | 894.5 | 38 | 126 | 1238.82 | 219.5 | 4934.5 | 42.88 | 237.5 | 440.5 | 0 | 0 | 6.5 | 147.5
18:00 | 2932 | 1882 | 894 | 38 | 120 | 1237.6 | 219 | 4999 | 19.23 | 245 | 447 | 0 | 0 | 1 | 160
18:30 | 2973 | 1913 | 894.5 | 38 | 132 | 1350.85 | 219 | 5089.5 | 9.615 | 353.5 | 677 | 0 | 0 | 2 | 179.5
19:00 | 3014 | 1944 | 895 | 38 | 144 | 1464.1 | 219 | 5180 | 0 | 462 | 907 | 0 | 0 | 3 | 199
19:30 | 2989 | 2166 | 894 | 38 | 146 | 1491.1 | 219 | 5378 | 0 | 474 | 1532 | 0 | 0 | 5 | 171
20:00 | 2968 | 2092 | 894 | 38 | 134 | 1488.57 | 219 | 5371 | 0 | 473 | 1534 | 0 | 0 | 2 | 36
20:30 | 2964.5 | 2064.5 | 895 | 38 | 137 | 1490.77 | 219.5 | 5438.5 | 0 | 466.5 | 1530.18 | 0 | 0 | 4.5 | 25
21:00 | 2961 | 2037 | 896 | 38 | 140 | 1492.97 | 220 | 5506 | 0 | 460 | 1526.36 | 0 | 0 | 7 | 14
21:30 | 2973.5 | 2078.5 | 895.5 | 38 | 136 | 1493.08 | 220.5 | 5439.5 | 0 | 451 | 1439.86 | 0 | 0 | 11 | 19
22:00 | 2986 | 2120 | 895 | 38 | 132 | 1493.19 | 221 | 5373 | 0 | 442 | 1353.36 | 0 | 0 | 15 | 24
22:30 | 2991.5 | 2131.75 | 895 | 38 | 133 | 1488.035 | 220.5 | 5309 | 0 | 411.5 | 1311.18 | 0 | 0 | 17.5 | 28
23:00 | 2997 | 2143.5 | 895 | 38 | 134 | 1482.88 | 220 | 5245 | 0 | 381 | 1269 | 0 | 0 | 20 | 32
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 20-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 377 | 05:00 | 362 | 10:00 | Madunaghat | 390 | 07:00 | 384 | 00:00
Amtali | 412 | 07:00 | 403 | 00:00 | Meghnaghat | 385 | 07:00 | 368 | 11:00
Ashuganj | 388 | 07:00 | 373 | 00:00 | Payra | 413 | 07:00 | 405 | 00:00
Bhulta | 398 | 07:00 | 381 | 11:00 | Rahanpur | 402 | 18:00 | 386 | 00:00
Bibiana | 380 | 03:00 | 372 | 12:00 | Rampal | 391 | 18:00 | 371 | 00:00
BIPTC | 401 | 06:00 | 395 | 00:00
Bogura | 384 | 18:00 | 367 | 00:00
Gopalganj | 388 | 07:00 | 373 | 00:00
Kaliakoir | 363 | 03:00 | 348 | 12:00
Korerhat | 392 | 07:00 | 383 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 04:00 | 217 | 12:00 | Ishurdi | 236 | 17:00 | 216 | 00:00
AKSML | 234 | 06:00 | 226 | 10:00 | Jhenaidah | 228 | 17:00 | 204 | 00:00
Aminbazar | 231 | 05:00 | 219 | 10:00 | Kachua | 222 | 18:30 | 217 | 00:00
Ashuganj | 227 | 04:00 | 220 | 12:00 | Kaliakoir | 227 | 03:00 | 213 | 12:00
Ashuganj-400 | 227 | 04:00 | 220 | 12:00 | Keranigonj | 228 | 04:00 | 215 | 12:00
Baghabari | 232 | 15:00 | 221 | 00:00 | Khulna(S) | 225 | 17:00 | 206 | 00:00
Barapukuria | 225 | 06:00 | 215 | 00:00 | Korerhat | 223 | 07:00 | 218 | 00:00
Barapukuria-230 | 225 | 06:00 | 215 | 00:00 | Madunaghat | 236 | 20:00 | 232 | 00:00
Barishal | 226 | 12:00 | 218 | 00:00 | Madunaghat-400 | 237 | 04:00 | 233 | 11:00
Bheramara | 234 | 17:00 | 214 | 00:00 | Maniknagar | 227 | 04:00 | 215 | 11:00
Bhulta | 229 | 06:00 | 217 | 11:00 | Meghnaghat | 233 | 04:00 | 225 | 11:00
Bibiana | 220 | 04:00 | 215 | 00:00 | Meghnaghat-400 | 231 | 07:00 | 220 | 11:00
BIPTC | 236 | 17:00 | 214 | 00:00 | Mirsorai | 227 | 07:00 | 222 | 00:00
Bogura | 240 | 17:00 | 229 | 00:00 | Naogaon | 0 | 00:00 | N/A | N/A
Bogura-400 | 240 | 17:00 | 230 | 00:00 | Purbasadipur | 223 | 06:00 | 212 | 00:00
Borhanuddin | 229 | 09:00 | 222 | 00:00 | Rajshahi | 233 | 17:00 | 211 | 00:00
BSRM | 225 | 07:00 | 219 | 00:00 | Rampal | 224 | 17:00 | 207 | 00:00
Charfasson | 232 | 12:00 | 224 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 221 | 18:00 | 217 | 00:00 | Rampura | 230 | 07:00 | 216 | 11:00
Cumilla(N) | 224 | 06:00 | 217 | 00:00 | Shikalbaha | 236 | 19:30 | 230 | 15:00
Faridpur | 222 | 08:00 | 212 | 00:00 | Shyampur | 229 | 04:00 | 217 | 12:00
Fenchuganj | 224 | 07:00 | 217 | 00:00 | Siddhirganj | 229 | 05:00 | 218 | 11:00
Feni | 223 | 07:00 | 216 | 00:00 | Sirajgonj | 238 | 06:00 | 231 | 00:00
Ghorashal | 230 | 02:00 | 220 | 16:00 | Sreepur | 224 | 06:00 | 216 | 00:00
Ghorashal-230 | 216 | 04:00 | 199 | 12:00 | Tongi | 217 | 04:00 | 200 | 11:00
Gopalganj | 223 | 06:00 | 214 | 00:00
GPH | 231 | 07:00 | 226 | 11:00
Haripur | 229 | 07:00 | 217 | 11:00
Hasnabad | 229 | 06:00 | 216 | 12:00
Hathazari | 233 | 07:00 | 228 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 06:00 | 126 | 11:00 | Madunaghat | 136 | 18:30 | 132 | 01:00
Agargaon | 135 | 03:00 | 127 | 11:00 | Magura | 138 | 17:00 | 119 | 00:00
Agrabad | 135 | 20:00 | 131 | 09:00 | Mahasthangarh | 135 | 06:00 | 127 | 00:00
AKS | 132 | 19:30 | 128 | 18:30 | Maijdee | 124 | 07:00 | 121 | 00:00
Aminbazar | 132 | 23:00 | 123 | 11:00 | Manikganj | 131 | 04:00 | 121 | 11:00
Amnura | 134 | 17:00 | 121 | 00:00 | Maniknagar | 135 | 07:00 | 125 | 11:00
Ashuganj | 131 | 07:00 | 125 | 00:00 | Matarbari | 122 | 07:00 | 116 | 00:00
Ashuganj-230 | 133 | 08:00 | 130 | 00:00 | Matuail | 133 | 04:00 | 12 | 10:00
Bagerhat | 127 | 17:00 | 111 | 00:00 | Metrorail_Motijheel | 135 | 07:00 | 125 | 11:00
Bajitpur | 125 | 08:00 | 118 | 00:00 | Metrorail_Uttara | 130 | 03:00 | 119 | 12:00
Bakerganj | 131 | 14:00 | 124 | 00:00 | Millgate | 133 | 03:00 | 119 | 12:00
Bakulia | 135 | 06:00 | 131 | 16:00 | Mirpur | 129 | 04:00 | 122 | 12:00
Banani | 135 | 04:00 | 126 | 11:00 | Mirzapur | 130 | 04:00 | 122 | 10:00
Bangabhaban | 134 | 05:00 | 125 | 11:00 | Mithapukur | 135 | 07:00 | 125 | 00:00
Barapukuria | 137 | 06:00 | 128 | 00:00 | MI_Cement | 135 | 04:00 | 124 | 12:00
Barguna | 131 | 14:00 | 123 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 131 | 12:00 | 124 | 00:00 | Mogbazar | 137 | 06:00 | 129 | 11:00
Barishal-230 | 131 | 12:00 | 124 | 00:00 | Mongla | 127 | 17:00 | 112 | 00:00
Baroaulia | 135 | 12:00 | 132 | 00:00 | Motijheel | 134 | 05:00 | 125 | 11:00
Baroirhat | 130 | 08:00 | 126 | 00:00 | Muktagacha | 124 | 19:30 | 115 | 00:00
Bashundhara | 136 | 06:00 | 119 | 12:00 | Munshiganj | 132 | 04:00 | 124 | 11:00
BashundharaCement | 132 | 19:00 | 126 | 11:00 | Muradnagar | 127 | 07:00 | 121 | 00:00
Beanibazar | 126 | 18:00 | 119 | 00:00 | Mymensingh | 122 | 19:30 | 108 | 00:00
Benapole | 137 | 17:00 | 112 | 00:00 | Nabinagar | 127 | 02:00 | 118 | 12:00
Bhaluka | 126 | 05:00 | 118 | 00:00 | Naogaon | 137 | 18:30 | 122 | 00:00
Bhandaria | 129 | 16:00 | 117 | 00:00 | Narail | 139 | 17:00 | 118 | 00:00
Bhangura | 135 | 12:00 | 126 | 00:00 | Narinda | 135 | 07:00 | 125 | 11:00
Bheramara | 137 | 17:00 | 126 | 00:00 | Narshingdi | 128 | 05:00 | 120 | 00:00
Bheramara(GK) | 138 | 17:00 | 125 | 00:00 | Natore | 135 | 18:00 | 123 | 00:00
Bhulta | 128 | 08:00 | 122 | 00:00 | Nawabganj | 133 | 04:00 | 126 | 11:00
Bog-Sherpur | 136 | 10:00 | 127 | 00:00 | Netrakona | 122 | 11:00 | 106 | 00:00
Bogura | 138 | 12:00 | 131 | 00:00 | New | 130 | 01:00 | 122 | 12:00
Bogura-230 | 138 | 10:00 | 131 | 00:00 | Niamatpur | 133 | 07:00 | 124 | 00:00
Brahmanbaria | 127 | 04:00 | 122 | 21:00 | Noapara | 133 | 18:00 | 118 | 00:00
Cantonment | 134 | 03:00 | 34 | 06:00 | Pabna | 135 | 17:00 | 127 | 01:00
Chandina | 129 | 06:00 | 123 | 00:00 | Palashbari | 132 | 11:00 | 121 | 00:00
Chandpur | 126 | 20:00 | 122 | 01:00 | Panchagarh | 139 | 06:00 | 131 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 06:00 | 134 | 00:00 | Patiya | 133 | 00:00 | 130 | 15:00
Chapai | 132 | 15:00 | 128 | 00:00 | Patnitala | 136 | 17:00 | 122 | 00:00
Charsaidpur | 132 | 03:00 | 125 | 11:00 | Patuakhali | 131 | 15:00 | 125 | 00:00
Chauddagram | 128 | 06:00 | 124 | 00:00 | Payra | 134 | 11:00 | 130 | 00:00
Chhatak | 124 | 09:00 | 116 | 00:00 | PHP | 129 | 06:00 | 126 | 00:00
Chowmuhani | 124 | 18:00 | 121 | 00:00 | Postogola | 136 | 03:00 | 127 | 12:00
Chuadanga | 137 | 16:00 | 117 | 00:00 | Pubail | 129 | 02:00 | 116 | 12:00
Coxsbazar | 127 | 15:00 | 118 | 23:00 | Purbachal | 135 | 05:00 | 125 | 11:00
Cumilla(N) | 129 | 07:00 | 124 | 00:00 | Purbasadipur | 135 | 06:00 | 128 | 00:00
Cumilla(S) | 129 | 01:00 | 124 | 00:00 | Rahanpur | 135 | 17:00 | 128 | 00:00
Daganbhuiyan | 127 | 07:00 | 124 | 00:00 | Rahanpur-400 | 135 | 18:00 | 128 | 00:00
Daudkandi | 125 | 18:00 | 118 | 11:00 | Rahim | 134 | 04:00 | 126 | 11:00
DhakaUniversity | 136 | 07:00 | 125 | 11:00 | Rajbari | 130 | 09:00 | 118 | 00:00
Dhamrai | 131 | 04:00 | 120 | 12:00 | Rajendrapur | 126 | 03:00 | 119 | 00:00
Dhanmondi | 136 | 05:00 | 126 | 11:00 | Rajshahi | 133 | 17:00 | 126 | 21:00
Dohazari | 130 | 02:00 | 127 | 00:00 | Rajshahi-230 | 134 | 17:00 | 121 | 00:00
Faridpur | 128 | 06:00 | 122 | 00:00 | Ramganj | 122 | 18:00 | 119 | 02:00
Fatullah | 135 | 03:00 | 125 | 12:00 | Rampur | 135 | 06:00 | 130 | 15:00
Fenchuganj | 132 | 07:00 | 127 | 00:00 | Rampura | 136 | 07:00 | 126 | 11:00
Feni | 127 | 05:00 | 124 | 00:00 | Rangamati | 136 | 06:00 | 132 | 18:30
Feni-230 | 129 | 07:00 | 125 | 00:00 | Rangpur | 131 | 07:00 | 124 | 00:00
Ghatail | 122 | 03:00 | 115 | 00:00 | Ruppur | 137 | 17:00 | 125 | 00:00
Ghorashal | 129 | 02:00 | 121 | 09:00 | Saidpur | 135 | 06:00 | 127 | 01:00
Goalpara | 135 | 16:00 | 122 | 00:00 | Santhia | 135 | 05:00 | 126 | 00:00
Gollamari | 135 | 17:00 | 122 | 00:00 | Satkhira | 132 | 18:30 | 114 | 00:00
Gopalganj | 129 | 17:00 | 119 | 00:00 | Satmasjid | 135 | 04:00 | 126 | 12:00
Gopalganj-400 | 130 | 06:00 | 124 | 00:00 | Savar | 129 | 03:00 | 120 | 12:00
Gulshan | 135 | 04:00 | 126 | 11:00 | SevenRings | 131 | 04:00 | 119 | 10:00
Halishahar | 135 | 04:00 | 131 | 10:00 | ShahCement | 132 | 03:00 | 125 | 11:00
Haripur | 134 | 04:00 | 126 | 11:00 | Shahjadpur | 135 | 07:00 | 130 | 00:00
HaripurSBU | 134 | 04:00 | 126 | 11:00 | Shahjibazar | 134 | 12:00 | 121 | 21:00
Hasnabad | 136 | 04:00 | 127 | 12:00 | Shahmirpur | 134 | 01:00 | 131 | 14:00
Hathazari | 137 | 05:00 | 133 | 00:00 | Shariatpur | 129 | 18:00 | 120 | 00:00
Hatirjheel | 135 | 04:00 | 126 | 11:00 | Sherpur | 123 | 22:00 | 108 | 07:00
Ishurdi | 139 | 17:00 | 127 | 00:00 | Shikalbaha | 123 | 22:00 | 121 | 00:00
Jaldhaka | 135 | 06:00 | 124 | 00:00 | Shikalbaha-230 | 136 | 19:30 | 132 | 14:00
Jamalpur | 127 | 22:00 | 113 | 08:00 | Shitalakhya | 135 | 04:00 | 124 | 12:00
Jashore | 138 | 17:00 | 114 | 00:00 | Sholosohor | 135 | 03:00 | 131 | 11:00
Jhenaidah | 140 | 16:00 | 122 | 00:00 | Shomvuganj | 121 | 09:00 | 113 | 00:00
Jhenaidah-230 | 140 | 17:00 | 122 | 00:00 | Shyampur | 132 | 06:00 | 124 | 12:00
Joydebpur | 128 | 03:00 | 113 | 12:00 | Shyampur-230 | 134 | 04:00 | 125 | 15:00
Joypurhat | 135 | 17:00 | 122 | 00:00 | Siddhirganj | 133 | 04:00 | 126 | 11:00
Juldah | 135 | 06:00 | 131 | 14:00 | Sirajganj | 133 | 14:00 | 123 | 00:00
Kabirpur | 134 | 02:00 | 116 | 12:00 | Sitakunda | 135 | 06:00 | 132 | 00:00
Kachua | 126 | 18:30 | 123 | 00:00 | Sonargaon | 130 | 03:00 | 123 | 02:00
Kaliakoir | 135 | 03:00 | 124 | 12:00 | Sreemongol | 128 | 07:00 | 122 | 22:00
Kaliganj | 139 | 16:00 | 122 | 00:00 | Sreepur | 129 | 04:00 | 122 | 00:00
Kallyanpur | 130 | 05:00 | 122 | 12:00 | Srinagar | 133 | 03:00 | 126 | 12:00
Kalurghat | 136 | 19:30 | 133 | 00:00 | SSM | 140 | 01:00 | 136 | 10:00
Kamrangirchar | 134 | 03:00 | 120 | 11:00 | Sunamganj | 120 | 07:00 | 113 | 00:00
Kaptai | 133 | 06:00 | 129 | 16:00 | Sylhet | 125 | 08:00 | 121 | 00:00
Kasba | 126 | 04:00 | 121 | 00:00 | Sylhet_(South) | 126 | 07:00 | 121 | 00:00
Kazla | 134 | 07:00 | 125 | 11:00 | Tangail | 125 | 04:00 | 116 | 12:00
Keranigonj | 134 | 04:00 | 127 | 11:00 | Taraganj | 134 | 06:00 | 121 | 21:00
Khagrachori | 135 | 07:00 | 132 | 00:00 | Tasnim | 130 | 08:00 | 123 | 11:00
Khulna | 134 | 17:00 | 121 | 00:00 | Thakurgaon | 137 | 06:00 | 130 | 00:00
Khulna(S) | 135 | 17:00 | 121 | 00:00 | TK | 136 | 07:00 | 132 | 13:00
Khulshi | 133 | 06:00 | 129 | 16:00 | Tongi | 134 | 04:00 | 123 | 11:00
Kishoreganj | 124 | 07:00 | 115 | 00:00 | Ullahpara | 133 | 04:00 | 126 | 00:00
Kodda | 134 | 20:00 | 115 | 11:00 | Ullon | 135 | 03:00 | 125 | 11:00
Korerhat | 132 | 06:00 | 129 | 00:00 | Uttara | 131 | 06:00 | 118 | 12:00
KSRM | 136 | 19:30 | 131 | 14:00 | UttaraNew | 130 | 03:00 | 119 | 12:00
Kulaura | 130 | 08:00 | 126 | 00:00 | Zigatola | 134 | 04:00 | 127 | 11:00
Kurigram | 131 | 06:00 | 121 | 00:00
Kushtia | 133 | 17:00 | 120 | 00:00
Laksam | 125 | 07:00 | 122 | 00:00
Lakshmipur | 124 | 07:00 | 120 | 00:00
Lalbag | 133 | 05:00 | 126 | 11:00
Lalmonirhat | 130 | 05:00 | 121 | 00:00
Madanganj | 132 | 19:00 | 126 | 11:00
Madaripur | 130 | 07:00 | 123 | 00:00
Madartek | 135 | 05:00 | 125 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-07-2026 | [28 empty] | Date: | 20-07-2026 | [28 empty] | Date: | 20-07-2026 | [28 empty] | Date: | 20-07-2026 | [28 empty] | Date: | 20-07-2026 | [18 empty] | Date: | 20-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 56 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 433 | 17 | 27 | 149 | 95 | 225 | 55 | 35 | 16 | 0 | 0 | 288 | 550 | 0 | 0 | 305 | 0 | 0 | 0 | 143 | 0 | 21 | 0 | 0 | 0 | 0 | 71 | 0 | 16 | 34 | 0 | 35 | 0 | 0 | 0 | 222 | 33 | 34 | 1125 | 0 | 0 | 0 | 0 | 49 | 145 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 187 | 0 | 64 | 93 | 49 | 0 | 19 | 0 | 140 | 0 | 0 | 25 | 310 | 0 | 318 | 28 | 20 | 142 | 0 | 17 | 0 | 84 | 25 | 142 | 0 | 100 | 0 | 49 | 0 | 78 | 0 | 0 | 0 | 22 | 8428 | 848 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 475 | 0 | 0 | 0 | 1478.9 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 130 | 0 | 129 | 0 | 290 | 0 | 0 | 180 | 0 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 275 | 120 | 220 | 0 | 1100 | 1163 | 5 | 6973.9 | 15401.9 | 103.69
01:00 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 427 | 17 | 27 | 149 | 144 | 145 | 30 | 35 | 15 | 0 | 0 | 288 | 460 | 0 | 5 | 304 | 0 | 0 | 0 | 143 | 13 | 21 | 0 | 0 | 0 | 0 | 69 | 0 | 14 | 34 | 0 | 17 | 0 | 0 | 0 | 222 | 32 | 33 | 1125 | 0 | 0 | 0 | 0 | 17 | 144 | 0 | 0 | 0 | 1182 | 0 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 189 | 0 | 50 | 93 | 17 | 0 | 19 | 0 | 136 | 13 | 0 | 25 | 300 | 0 | 330 | 28 | 20 | 126 | 0 | 17 | 0 | 84 | 28 | 142 | 0 | 100 | 13 | 78 | 0 | 125 | 0 | 0 | 0 | 24 | 8297 | 895 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 475 | 0 | 0 | 0 | 1478.94 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 128 | 0 | 129 | 0 | 295 | 0 | 0 | 180 | 0 | 70 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 100 | 180 | 0 | 1100 | 1160 | 17 | 6983.94 | 15280.94 | 103.68
02:00 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 468 | 17 | 27 | 149 | 144 | 95 | 15 | 17 | 16 | 0 | 0 | 301 | 300 | 0 | 17 | 310 | 0 | 0 | 0 | 143 | 13 | 21 | 0 | 0 | 0 | 0 | 35 | 0 | 26 | 34 | 0 | 17 | 0 | 0 | 0 | 221 | 34 | 26 | 1125 | 0 | 0 | 0 | 0 | 17 | 144 | 0 | 0 | 0 | 1192 | 0 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 198 | 0 | 30 | 93 | 17 | 0 | 19 | 0 | 134 | 25 | 0 | 25 | 305 | 0 | 340 | 28 | 20 | 133 | 0 | 17 | 0 | 84 | 28 | 143 | 0 | 100 | 17 | 79 | 0 | 125 | 0 | 0 | 0 | 24 | 8136 | 895 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 475 | 0 | 0 | 0 | 1365.94 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 130 | 0 | 129 | 0 | 296 | 0 | 0 | 180 | 0 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 276 | 100 | 180 | 0 | 1100 | 1070 | 17 | 6660.94 | 14796.94 | 103.67
03:00 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 435 | 17 | 27 | 149 | 144 | 45 | 15 | 17 | 15 | 0 | 0 | 292 | 295 | 0 | 17 | 300 | 0 | 0 | 0 | 143 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 34 | 0 | 17 | 5 | 0 | 0 | 220 | 33 | 28 | 1055 | 0 | 0 | 0 | 0 | 17 | 144 | 0 | 0 | 0 | 1192 | 0 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 206 | 0 | 29 | 93 | 17 | 0 | 19 | 0 | 126 | 0 | 0 | 25 | 300 | 0 | 342 | 28 | 20 | 129 | 0 | 17 | 0 | 84 | 28 | 142 | 0 | 100 | 17 | 79 | 0 | 126 | 0 | 0 | 0 | 24 | 7895 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 1311.94 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 130 | 0 | 129 | 0 | 317 | 0 | 0 | 180 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 275 | 100 | 180 | 0 | 1046 | 1020 | 17 | 6401.94 | 14296.94 | 103.66
04:00 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 486 | 17 | 27 | 149 | 144 | 0 | 15 | 17 | 0 | 0 | 0 | 293 | 295 | 0 | 17 | 300 | 0 | 0 | 0 | 143 | 13 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 34 | 0 | 17 | 12 | 0 | 0 | 220 | 34 | 29 | 1055 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1192 | 0 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 207 | 0 | 31 | 93 | 0 | 0 | 19 | 0 | 124 | 0 | 0 | 25 | 305 | 0 | 342 | 28 | 20 | 134 | 0 | 17 | 0 | 84 | 30 | 143 | 0 | 100 | 17 | 79 | 0 | 126 | 0 | 0 | 0 | 24 | 7870 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 0 | 1258.42 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 132 | 0 | 129 | 0 | 324 | 0 | 0 | 180 | 0 | 35 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 100 | 180 | 0 | 903 | 1010 | 0 | 6189.42 | 14059.42 | 103.65
05:00 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 452 | 0 | 27 | 62 | 143 | 0 | 15 | 0 | 0 | 0 | 0 | 288 | 455 | 0 | 0 | 299 | 0 | 0 | 0 | 143 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 10 | 0 | 220 | 0 | 29 | 1125 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1187 | 0 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 207 | 0 | 0 | 94 | 0 | 0 | 19 | 0 | 128 | 0 | 0 | 25 | 315 | 0 | 342 | 28 | 20 | 150 | 0 | 17 | 0 | 84 | 30 | 143 | 0 | 101 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7715 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 0 | 1183.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 132 | 0 | 129 | 0 | 334 | 0 | 0 | 180 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 120 | 220 | 0 | 1021 | 1030 | 0 | 6244.72 | 13959.72 | 103.64
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 410 | 0 | 17 | 16 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 455 | 0 | 0 | 285 | 0 | 0 | 0 | 143 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 12 | 0.1 | 220 | 0 | 33 | 1125 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1090 | 0 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 202 | 0 | 0 | 94 | 0 | 0 | 19 | 0 | 122 | 0 | 2 | 0 | 300 | 0 | 342 | 28 | 20 | 124 | 0 | 17 | 0 | 84 | 30 | 143 | 0 | 101 | 0 | 49 | 0.1 | 48 | 0 | 0 | 0.1 | 12 | 7316.3 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 510 | 0 | 0 | 0 | 1321.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53 | 0 | 0 | 0 | 1.35 | 143 | 0 | 132 | 0 | 131 | 0 | 300 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 272 | 120 | 180 | 0 | 700 | 970 | 0 | 5895.56 | 13211.86 | 103.63
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 496 | 0 | 17 | 16 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 299 | 450 | 0 | 0 | 300 | 0 | 0 | 0 | 143 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 12 | 12 | 0.39 | 220 | 0 | 28 | 1125 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 200 | 0 | 0 | 94 | 0 | 0 | 19 | 0 | 112 | 0 | 18 | 0 | 305 | 0 | 342 | 28 | 20 | 141 | 0 | 17 | 0 | 84 | 30 | 143 | 0 | 101 | 0 | 49 | 0.69 | 48 | 0 | 0.1 | 3.37 | 12 | 7349.55 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5.04 | 510 | 0 | 0 | 0 | 1474.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.98 | 8 | 0 | 0 | 1.35 | 143 | 0 | 132 | 0 | 133 | 0 | 300 | 0 | 0.11 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 1 | 0.09 | 0 | 277 | 120 | 180 | 0 | 500 | 900 | 0 | 5802.36 | 13151.91 | 103.62
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 526 | 0 | 17 | 16 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 450 | 0 | 0 | 308 | 0 | 0 | 0 | 143 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 12 | 12 | 0.77 | 220 | 0 | 6 | 1125 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 1106 | 1 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 195 | 0 | 0 | 93 | 0 | 0 | 19 | 0 | 114 | 0 | 22 | 0 | 310 | 0 | 342 | 28 | 20 | 150 | 0 | 8 | 0 | 84 | 30 | 143 | 0 | 101 | 0 | 49 | 3.3 | 48 | 0 | 0.2 | 7.22 | 12 | 7376.49 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 520 | 0 | 0 | 0 | 1469.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.45 | 20 | 0 | 0 | 6.19 | 143 | 0 | 132 | 0 | 133 | 0 | 300 | 0 | 0.68 | 180 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.9 | 3 | 0.34 | 0 | 281 | 120 | 180 | 0 | 500 | 960 | 0 | 5914.9 | 13291.39 | 103.61
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 469 | 0 | 17 | 16 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 452 | 0 | 0 | 308 | 0 | 0 | 1 | 143 | 13 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 12 | 12 | 1.43 | 220 | 0 | 2 | 1125 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 1105 | 3 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 184 | 0 | 0 | 92 | 0 | 0 | 19 | 0 | 118 | 0 | 28 | 0 | 310 | 0 | 330 | 28 | 20 | 150 | 1 | 8 | 0 | 84 | 30 | 142 | 0 | 101 | 0 | 49 | 5.4 | 48 | 0 | 0.2 | 12.66 | 12 | 7392.69 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 540 | 0 | 0 | 0 | 1461.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.27 | 32 | 0 | 0 | 7.61 | 143 | 0 | 132 | 0 | 132 | 0 | 330 | 0 | 1.02 | 180 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1.5 | 15 | 0.31 | 0 | 277 | 120 | 220 | 0 | 500 | 1010 | 0 | 6070.53 | 13463.22 | 103.6
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 427 | 0 | 17 | 16 | 93 | 80 | 0 | 17 | 0 | 0 | 0 | 300 | 405 | 0 | 0 | 297 | 0 | 0 | 1 | 143 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 4 | 0 | 12 | 1.88 | 219 | 1 | 0 | 1125 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 1192 | 6 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 178 | 0 | 0 | 92 | 4 | 0 | 19 | 0 | 126 | 0 | 48 | 0 | 315 | 0 | 314 | 28 | 20 | 138 | 2 | 0 | 0 | 84 | 28 | 140 | 0 | 101 | 0 | 49 | 4.4 | 48 | 0 | 0.4 | 14.51 | 12 | 7445.19 | 894 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17 | 550 | 0 | 0 | 0 | 1441.7 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 8.42 | 30 | 0 | 0 | 2.36 | 143 | 0 | 132 | 0 | 130 | 0 | 318 | 0 | 0.16 | 180 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 2.1 | 56 | 0.34 | 16 | 272 | 120 | 220 | 0 | 500 | 1060 | 0 | 6149.08 | 13594.27 | 103.59
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 461 | 0 | 19 | 16 | 94 | 95 | 5 | 35 | 0 | 0 | 0 | 308 | 395 | 0 | 0 | 310 | 0 | 0 | 2 | 143 | 12 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 17 | 0 | 12 | 2.79 | 221 | 47 | 2 | 1050 | 0 | 0 | 0 | 0 | 17 | 66 | 0 | 0 | 0 | 1192 | 7 | 12 | 0 | 210 | 280 | 220 | 51 | 0 | 177 | 0 | 0 | 92 | 48 | 0 | 19 | 0 | 134 | 0 | 69 | 0 | 305 | 0 | 314 | 28 | 20 | 130 | 2 | 17 | 0 | 33 | 30 | 144 | 0 | 101 | 0 | 49 | 11.45 | 48 | 0 | 0.6 | 15.14 | 12 | 7510.98 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 550 | 0 | 0 | 0 | 1397.54 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 19.84 | 49 | 0 | 0 | 3.94 | 143 | 0 | 131 | 0 | 129 | 0 | 308 | 0 | 0.95 | 180 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 3.9 | 68 | 0.05 | 44 | 248 | 120 | 220 | 0 | 500 | 1070 | 17 | 6201.22 | 13712.2 | 103.58
12:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 486 | 0 | 27 | 16 | 94 | 95 | 30 | 35 | 17 | 0 | 0 | 302 | 395 | 0 | 0 | 300 | 0 | 0 | 3 | 143 | 12 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 28 | 0 | 0 | 17 | 0 | 12 | 2.98 | 221 | 83 | 2 | 1050 | 0 | 0 | 12 | 0 | 34 | 66 | 0 | 0 | 0 | 1192 | 9 | 10 | 0 | 210 | 280 | 220 | 51 | 0 | 172 | 0 | 5 | 30 | 88 | 0 | 19 | 0 | 134 | 0 | 36 | 22 | 305 | 0 | 314 | 28 | 20 | 131 | 2 | 0 | 0 | 33 | 28 | 143 | 0 | 101 | 0 | 49 | 15.88 | 48 | 0 | 0.9 | 23.07 | 12 | 7626.83 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13 | 550 | 0 | 0 | 0 | 1359.35 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 12.6 | 62 | 0 | 0 | 0.59 | 144 | 0 | 129 | 0 | 129 | 0 | 296 | 0 | 0.12 | 180 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 3.9 | 78 | 0.05 | 71 | 248 | 120 | 220 | 0 | 650 | 1070 | 17 | 6363.61 | 13990.44 | 103.57
13:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 465 | 0 | 0 | 16 | 95 | 135 | 30 | 35 | 17 | 0 | 0 | 296 | 420 | 0 | 17 | 298 | 0 | 0 | 7 | 143 | 12 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 17 | 0 | 12 | 3.9 | 220 | 103 | 8 | 1125 | 0 | 0 | 19 | 0 | 17 | 66 | 0 | 0 | 0 | 1190 | 13 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 172 | 0 | 25 | 30 | 51 | 0 | 19 | 0 | 142 | 0 | 40 | 22 | 305 | 0 | 314 | 28 | 30 | 135 | 5 | 0 | 0 | 33 | 28 | 143 | 0 | 101 | 0 | 49 | 5.4 | 48 | 0 | 1 | 17.54 | 12 | 7717.84 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 550 | 0 | 0 | 0 | 1353.33 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 14.61 | 83 | 0 | 0 | 8.67 | 143 | 0 | 127 | 0 | 127 | 0 | 291 | 0 | 1.08 | 180 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 3.8 | 86 | 0.03 | 80 | 218 | 120 | 180 | 0 | 633 | 1120 | 17 | 6355.52 | 14073.36 | 103.56
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 449 | 0 | 0 | 16 | 95 | 145 | 30 | 55 | 17 | 0 | 0 | 299 | 350 | 0 | 17 | 308 | 0 | 0 | 8 | 143 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 17 | 0 | 12 | 1.3 | 222 | 102 | 5 | 1070 | 0 | 0 | 19 | 0 | 16 | 66 | 0 | 0 | 0 | 1192 | 8 | 0 | 0 | 210 | 280 | 220 | 51 | 0 | 172 | 0 | 34 | 30 | 17 | 0 | 19 | 0 | 144 | 0 | 41 | 23 | 310 | 0 | 340 | 28 | 30 | 133 | 4 | 0 | 0 | 33 | 30 | 142 | 0 | 101 | 0 | 49 | 10.05 | 48 | 0 | 0.8 | 14.62 | 12 | 7603.77 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.3 | 550 | 0 | 0 | 0 | 1328.11 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 14.22 | 43 | 0 | 0 | 16.84 | 143 | 0 | 125 | 0 | 126 | 0 | 281 | 0 | 1.8 | 180 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 4.1 | 83 | 0.01 | 73 | 218 | 120 | 180 | 0 | 637 | 1163 | 17 | 6317.38 | 13921.15 | 103.56
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 486 | 17 | 0 | 16 | 95 | 110 | 30 | 55 | 17 | 0 | 0 | 304 | 350 | 0 | 17 | 300 | 0 | 0 | 5 | 143 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 17 | 0 | 12 | 0.52 | 222 | 74 | 2 | 1070 | 0 | 0 | 19 | 0 | 15 | 66 | 0 | 0 | 0 | 1162 | 13 | 0 | 0 | 210 | 280 | 210 | 51 | 0 | 175 | 0 | 34 | 30 | 17 | 0 | 19 | 0 | 138 | 0 | 15 | 23 | 310 | 0 | 385 | 28 | 30 | 136 | 5 | 0 | 0 | 33 | 28 | 144 | 0 | 101 | 0 | 49 | 3.5 | 48 | 0 | 0.3 | 8.12 | 12 | 7529.44 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 550 | 0 | 0 | 0 | 1318.21 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 17.19 | 23 | 0 | 0 | 16.72 | 143 | 0 | 124 | 0 | 110 | 0 | 274 | 0 | 2 | 180 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1.9 | 94 | 0.13 | 64 | 217 | 100 | 220 | 0 | 659 | 1163 | 17 | 6287.15 | 13816.59 | 103.56
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 470 | 17 | 0 | 34 | 95 | 75 | 14 | 35 | 17 | 0 | 0 | 292 | 400 | 0 | 17 | 303 | 0 | 0 | 4 | 86 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 17 | 0 | 12 | 0.72 | 222 | 33 | 3 | 1125 | 0 | 0 | 19 | 0 | 0 | 67 | 0 | 0 | 0 | 1130 | 4 | 0 | 0 | 210 | 280 | 210 | 51 | 0 | 183 | 0 | 34 | 20 | 17 | 0 | 19 | 0 | 138 | 0 | 24 | 24 | 310 | 0 | 393 | 28 | 30 | 140 | 3 | 8 | 0 | 33 | 28 | 143 | 0 | 101 | 0 | 49 | 1.84 | 48 | 0 | 0.2 | 7.67 | 12 | 7388.43 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 550 | 0 | 0 | 0 | 1291.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.21 | 8 | 0 | 0 | 20.35 | 143 | 0 | 124 | 0 | 65 | 0 | 274 | 0 | 2.03 | 180 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 2.3 | 13 | 0.08 | 16 | 217 | 120 | 220 | 0 | 663 | 1150 | 17 | 6045.4 | 13433.83 | 103.56
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 496 | 17 | 0 | 45 | 95 | 60 | 10 | 35 | 35 | 0 | 0 | 299 | 370 | 0 | 17 | 306 | 0 | 0 | 2 | 86 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0.52 | 220 | 31 | 12 | 1125 | 0 | 0 | 19 | 0 | 0 | 67 | 0 | 0 | 0 | 1050 | 3 | 0 | 0 | 210 | 280 | 210 | 51 | 0 | 184 | 0 | 34 | 30 | 0 | 0 | 19 | 0 | 132 | 0 | 7 | 24 | 310 | 0 | 395 | 28 | 30 | 140 | 2 | 17 | 0 | 33 | 28 | 143 | 0 | 101 | 0 | 49 | 1.55 | 48 | 0 | 0.1 | 2.21 | 8 | 7270.38 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 538 | 0 | 0 | 0 | 1240.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 9 | 0 | 0 | 8.85 | 143 | 0 | 124 | 0 | 59 | 0 | 280 | 0 | 0.89 | 180 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 2.1 | 11 | 0.11 | 14 | 217 | 120 | 220 | 0 | 650 | 1110 | 0 | 5876.19 | 13146.57 | 103.56
18:00 | 0 | 17 | 13 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 484 | 17 | 0 | 52 | 95 | 60 | 15 | 35 | 35 | 0 | 0 | 296 | 325 | 0 | 17 | 310 | 0 | 0 | 0 | 96 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 12 | 0.06 | 219 | 31 | 2 | 1125 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1015 | 1 | 0 | 0 | 210 | 280 | 210 | 51 | 0 | 160 | 0 | 34 | 30 | 0 | 0 | 19 | 0 | 120 | 0 | 2 | 24 | 305 | 0 | 395 | 28 | 30 | 143 | 1 | 17 | 0 | 33 | 28 | 142 | 0 | 101 | 0 | 49 | 0.55 | 47 | 0 | 0.1 | 1.4 | 10 | 7065.11 | 894 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.9 | 510 | 0 | 0 | 0 | 1237.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 3 | 0 | 0 | 3.04 | 143 | 0 | 124 | 0 | 86 | 0 | 280 | 0 | 0.33 | 180 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.33 | 2 | 0.03 | 14 | 217 | 100 | 180 | 0 | 848 | 1104 | 0 | 5968.72 | 13033.83 | 103.56
19:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 473 | 35 | 0 | 92 | 146 | 95 | 19 | 35 | 84 | 0 | 0 | 302 | 330 | 0 | 25 | 314 | 0 | 0 | 0 | 130 | 12 | 15 | 0 | 0 | 3 | 20 | 4 | 0 | 3 | 34 | 0 | 9 | 12 | 25 | 0 | 219 | 37 | 13 | 1125 | 10 | 0 | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 1035 | 0 | 11 | 0 | 210 | 280 | 210 | 51 | 0 | 197 | 0 | 47 | 30 | 10 | 14 | 19 | 0 | 144 | 0 | 0 | 24 | 300 | 0 | 395 | 28 | 30 | 140 | 0 | 17 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 49 | 0 | 77 | 0 | 0 | 0 | 12 | 7684 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 533 | 0 | 0 | 0 | 1464.1 | 0 | 0 | 0 | 20 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 123 | 0 | 117 | 0 | 280 | 0 | 0 | 180 | 0 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 216 | 120 | 220 | 0 | 977 | 1114 | 9 | 6586.1 | 14270.1 | 103.56
19:30 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 259 | 0 | 463 | 35 | 0 | 96 | 145 | 95 | 35 | 35 | 104 | 0 | 0 | 307 | 550 | 0 | 35 | 308 | 0 | 0 | 0 | 143 | 12 | 15 | 0 | 0 | 15 | 30 | 12 | 0 | 5 | 34 | 0 | 45 | 24 | 25 | 0 | 219 | 51 | 18 | 1125 | 30 | 0 | 32 | 0 | 68 | 0 | 0 | 0 | 0 | 1170 | 0 | 40 | 0 | 210 | 280 | 210 | 51 | 0 | 193 | 0 | 68 | 20 | 65 | 27 | 19 | 0 | 146 | 0 | 0 | 24 | 300 | 0 | 395 | 28 | 30 | 142 | 0 | 17 | 0 | 52 | 30 | 142 | 0 | 101 | 0 | 67 | 0 | 130 | 0 | 0 | 0 | 12 | 8452 | 894 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 550 | 0 | 0 | 0 | 1491.1 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 123 | 0 | 118 | 0 | 280 | 0 | 0 | 180 | 0 | 70 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 217 | 120 | 220 | 0 | 976 | 1160 | 54 | 6880.1 | 15332.1
20:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 259 | 0 | 423 | 35 | 0 | 99 | 144 | 110 | 35 | 35 | 98 | 0 | 0 | 307 | 515 | 0 | 35 | 295 | 0 | 0 | 0 | 143 | 12 | 15 | 0 | 0 | 0 | 15 | 12 | 0 | 2 | 34 | 0 | 45 | 24 | 36 | 0 | 219 | 73 | 20 | 1125 | 17 | 0 | 32 | 0 | 65 | 0 | 0 | 0 | 0 | 1192 | 0 | 40 | 0 | 210 | 280 | 210 | 51 | 0 | 189 | 0 | 69 | 15 | 49 | 26 | 19 | 0 | 134 | 0 | 0 | 24 | 300 | 0 | 395 | 28 | 30 | 140 | 0 | 17 | 0 | 53 | 30 | 144 | 0 | 101 | 0 | 68 | 0 | 150 | 0 | 0 | 0 | 12 | 8368 | 894 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 550 | 0 | 0 | 0 | 1488.57 | 0 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 123 | 0 | 118 | 0 | 279 | 0 | 0 | 180 | 0 | 70 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 217 | 120 | 220 | 0 | 944 | 1163 | 54 | 6845.57 | 15213.57 | 103.56
21:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 420 | 35 | 0 | 114 | 146 | 75 | 40 | 35 | 70 | 0 | 0 | 302 | 505 | 0 | 35 | 290 | 0 | 0 | 0 | 143 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 34 | 0 | 54.36 | 37 | 36 | 0 | 220 | 102 | 25 | 1125 | 0 | 0 | 33 | 0 | 64 | 0 | 0 | 0 | 0 | 1224 | 0 | 20 | 0 | 210 | 280 | 210 | 51 | 0 | 189 | 0 | 69 | 15 | 61 | 26 | 19 | 0 | 140 | 0 | 0 | 24 | 305 | 0 | 395 | 28 | 30 | 124 | 0 | 17 | 0 | 22 | 28 | 143 | 0 | 101 | 0 | 68 | 0 | 152 | 0 | 0 | 0 | 12 | 8304.36 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 0 | 1492.97 | 0 | 0 | 0 | 35 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 123 | 0 | 119 | 0 | 284 | 0 | 0 | 180 | 0 | 50 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 214 | 120 | 220 | 0 | 1050 | 1163 | 54 | 6979.97 | 15284.33 | 103.55
22:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 485 | 17 | 26 | 114 | 145 | 75 | 40 | 17 | 66 | 0 | 0 | 310 | 540 | 0 | 35 | 308 | 0 | 0 | 0 | 143 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 34 | 0 | 54.36 | 12 | 36 | 0 | 221 | 101 | 30 | 1125 | 0 | 0 | 33 | 0 | 34 | 0 | 0 | 0 | 0 | 1181 | 0 | 12 | 0 | 210 | 280 | 210 | 51 | 0 | 190 | 0 | 66 | 15 | 63 | 26 | 19 | 0 | 132 | 0 | 0 | 24 | 305 | 0 | 395 | 28 | 30 | 134 | 0 | 17 | 0 | 22 | 28 | 143 | 0 | 102 | 0 | 69 | 0 | 155 | 0 | 0 | 0 | 12 | 8310.36 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 0 | 1493.19 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 123 | 0 | 120 | 0 | 290 | 0 | 0 | 180 | 0 | 50 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 213 | 120 | 180 | 0 | 961 | 1163 | 54 | 6758.19 | 15068.55 | 103.55
23:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 500 | 17 | 27 | 114 | 146 | 75 | 40 | 17 | 69 | 0 | 0 | 302 | 505 | 0 | 17 | 310 | 0 | 0 | 0 | 143 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 0 | 18 | 12 | 36 | 0 | 220 | 103 | 33 | 1125 | 0 | 0 | 32 | 0 | 33 | 0 | 0 | 0 | 0 | 1202 | 0 | 12 | 0 | 210 | 280 | 210 | 51 | 0 | 194 | 0 | 51 | 15 | 66 | 25 | 19 | 0 | 134 | 0 | 0 | 24 | 310 | 0 | 396 | 28 | 30 | 152 | 0 | 17 | 0 | 22 | 28 | 144 | 0 | 102 | 0 | 69 | 0 | 155 | 0 | 0 | 0 | 12 | 8204.5 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 0 | 1482.88 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 123 | 0 | 121 | 0 | 291 | 0 | 0 | 180 | 0 | 50 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 225 | 120 | 220 | 0 | 800 | 1163 | 35 | 6620.88 | 14825.38 | 103.55
Total KWH | 0 | 982080 | 352800 | 0 | 0 | 0 | 0 | 0 | 7736400 | 0 | 11221150 | 261360 | 378720 | 1628640 | 2968800 | 1767905 | 510933 | 604867 | 656640 | 0 | 0 | 7165295 | 10056696 | 0 | 341266 | 7355194 | 0 | 0 | 32614 | 3343200 | 303600 | 371520 | 0 | 0 | 20073 | 55200 | 144960 | 0 | 427680 | 320095 | 0 | 451306 | 168960 | 333120 | 16441 | 5254480 | 1259563 | 428640 | 26654545.46 | 41818 | 0 | 313920 | 0 | 508509 | 1800192 | 0 | 0 | 0 | 27774543 | 64935 | 147200 | 0 | 5209000 | 7160100 | 5366000 | 1262456.3 | 0 | 4644000 | 0 | 710400 | 1418042 | 686400 | 125160 | 477930 | 0 | 3113280 | 57346 | 364864 | 420640 | 7397000 | 0 | 8719000 | 669000 | 597000 | 3319527.27 | 26270 | 272688 | 0 | 1309440 | 684672 | 3269000 | 0 | 2423520 | 74160 | 1339200 | 58629 | 1867200 | 0 | 4700 | 123690 | 337920 | 187734095.03 | 21616727 | 0 | 0 | 63360 | 0 | 912000 | 0 | 0 | 0 | 0 | 47664 | 126720 | 12850909 | 0 | 0 | 0 | 33201819 | 0 | 0 | 0 | 190464 | 957408 | 0 | 2704 | 47258 | 0 | 116696 | 418550 | 0 | 0 | 104368 | 3481364 | 0 | 3270000 | 0 | 3055804 | 0 | 7192797 | 0 | 11100 | 4451000 | 0 | 568954 | 78261 | 750864 | 0 | 0 | 0 | 30044.64 | 499680 | 1585 | 737088 | 6043000 | 2747000 | 5183630 | 0 | 18690909 | 26413090.91 | 420000 | 154282818.55 | 342016913.58