## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-07-2026 | [28 empty] | Date: | 22-07-2026 | [28 empty] | Date: | 22-07-2026 | [28 empty] | Date: | 22-07-2026 | [28 empty] | Date: | 22-07-2026 | [18 empty] | Date: | 22-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [18 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 207 | 0 | 17 | 149 | 45 | 210 | 55 | 35 | 54 | 0 | 0 | 130 | 295 | 0 | 0 | 250 | 0 | 0 | 0 | 68 | 9 | 22 | 0 | 0 | 75 | 16 | 42 | 0 | 0 | 34 | 0 | 17 | 12 | 25 | 0 | 202 | 103 | 14 | 1125 | 17 | 0 | 50 | 20 | 68 | 204 | 0 | 0 | 0 | 1150 | 0 | 95 | 0 | 0 | 300 | 240 | 51 | 0 | 190 | 0 | 57 | 142 | 176 | 0 | 19 | 80 | 142 | 16 | 0 | 32 | 310 | 0 | 358 | 42 | 0 | 129 | 0 | 0 | 0 | 42 | 20 | 142 | 0 | 101 | 17 | 48 | 0 | 47 | 0 | 0 | 0 | 12 | 7865 | 890 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 1471.17 | 0 | 0 | 0 | 70 | 90 | 0 | 101 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 128 | 0 | 0 | 0 | 250 | 0 | 0 | 185 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 275 | 120 | 180 | 0 | 790 | 1163 | 17 | 7026.37 | 14891.37 | 103.39
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 207 | 0 | 17 | 135 | 45 | 175 | 55 | 35 | 54 | 0 | 0 | 130 | 300 | 0 | 0 | 250 | 0 | 0 | 0 | 51 | 9 | 14 | 0 | 0 | 45 | 16 | 43 | 0 | 15 | 34 | 0 | 0 | 12 | 25 | 0 | 203 | 104 | 22 | 1125 | 16 | 0 | 33 | 25.5 | 67 | 205 | 0 | 0 | 0 | 1175 | 0 | 100 | 0 | 0 | 300 | 240 | 51 | 0 | 197 | 0 | 52 | 142 | 177 | 0 | 19 | 37 | 138 | 25 | 0 | 32 | 305 | 0 | 371 | 42 | 0 | 139 | 0 | 6 | 0 | 42 | 20 | 142 | 0 | 20 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 7685.5 | 890 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 775 | 0 | 0 | 0 | 1436.08 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 128 | 0 | 0 | 0 | 297 | 0 | 0 | 185 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 276 | 120 | 220 | 0 | 776 | 1150 | 16 | 6825.28 | 14510.78 | 103.38
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 207 | 0 | 17 | 113 | 45 | 175 | 55 | 35 | 0 | 0 | 0 | 130 | 285 | 0 | 0 | 250 | 0 | 0 | 0 | 51 | 9 | 22 | 0 | 0 | 46 | 16 | 44 | 0 | 18 | 34 | 0 | 0 | 12 | 25 | 0 | 203 | 105 | 27 | 1125 | 16 | 0 | 33 | 0 | 65 | 205 | 0 | 0 | 0 | 1190 | 0 | 35 | 0 | 0 | 300 | 260 | 51 | 0 | 215 | 0 | 0 | 142 | 179 | 0 | 19 | 0 | 124 | 25 | 0 | 32 | 305 | 0 | 367 | 42 | 0 | 143 | 0 | 16 | 0 | 42 | 25 | 142 | 0 | 26 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 7473 | 890 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 775 | 0 | 0 | 0 | 1417.02 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 128 | 0 | 0 | 0 | 290 | 0 | 0 | 185 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 277 | 120 | 220 | 0 | 767 | 1130 | 16 | 6721.02 | 14194.02 | 103.37
03:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 208 | 0 | 17 | 113 | 45 | 145 | 55 | 0 | 0 | 0 | 0 | 130 | 285 | 0 | 0 | 250 | 0 | 0 | 0 | 51 | 9 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 203 | 104 | 28 | 1125 | 0 | 0 | 22 | 0 | 65 | 205 | 0 | 0 | 0 | 1190 | 0 | 12 | 0 | 0 | 300 | 260 | 51 | 0 | 207 | 0 | 0 | 142 | 179 | 0 | 8 | 0 | 130 | 8 | 0 | 32 | 300 | 0 | 375 | 42 | 0 | 137 | 0 | 16 | 0 | 42 | 25 | 142 | 0 | 66 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 7243 | 890 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 775 | 0 | 0 | 0 | 1371.96 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 128 | 0 | 0 | 0 | 292 | 0 | 0 | 185 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 276 | 120 | 220 | 0 | 737 | 1120 | 16 | 6565.96 | 13808.96 | 103.36
04:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 201 | 0 | 17 | 113 | 15 | 145 | 55 | 0 | 0 | 0 | 0 | 130 | 285 | 0 | 0 | 250 | 0 | 0 | 0 | 51 | 9 | 22 | 0 | 0 | 0 | 0 | 12 | 0 | 33 | 0 | 0 | 0 | 0 | 25 | 0 | 205 | 106 | 28 | 1125 | 0 | 0 | 19 | 0 | 65 | 205 | 0 | 0 | 0 | 1190 | 0 | 12 | 0 | 0 | 300 | 260 | 51 | 0 | 202 | 0 | 0 | 144 | 177 | 0 | 19 | 0 | 126 | 8 | 0 | 32 | 310 | 0 | 375 | 42 | 0 | 139 | 0 | 16 | 0 | 42 | 25 | 142 | 0 | 65 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 7218 | 890 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 775 | 0 | 0 | 0 | 1385.82 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 128 | 0 | 0 | 0 | 291 | 0 | 0 | 185 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 307 | 120 | 220 | 0 | 500 | 1120 | 16 | 6374.82 | 13592.82 | 103.35
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 202 | 0 | 2 | 50 | 15 | 145 | 40 | 0 | 0 | 0 | 0 | 130 | 285 | 0 | 0 | 250 | 0 | 0 | 0 | 51 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 25 | 0 | 205 | 101 | 31 | 1125 | 0 | 0 | 19 | 0 | 34 | 205 | 0 | 0 | 0 | 1175 | 0 | 12 | 0 | 0 | 280 | 220 | 51 | 0 | 216 | 0 | 0 | 144 | 100 | 0 | 19 | 0 | 122 | 0 | 0 | 32 | 305 | 0 | 358 | 42 | 0 | 141 | 0 | 16 | 0 | 42 | 25 | 144 | 0 | 100 | 0 | 47 | 0 | 48 | 0 | 0 | 0 | 12 | 6953 | 890 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 785 | 0 | 0 | 0 | 1391.47 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 128 | 0 | 0 | 0 | 290 | 0 | 0 | 185 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 301 | 120 | 220 | 0 | 500 | 1120 | 14 | 6345.47 | 13298.47 | 103.34
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 204 | 0 | 14 | 17 | 15 | 45 | 30 | 0 | 0 | 0 | 0 | 130 | 280 | 0 | 0 | 250 | 0 | 0 | 0 | 51 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 12 | 0.29 | 205 | 33 | 30 | 1125 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 1150 | 1 | 6 | 0 | 0 | 280 | 220 | 51 | 0 | 199 | 0 | 0 | 144 | 0 | 0 | 19 | 0 | 120 | 0 | 1 | 16 | 305 | 0 | 380 | 42 | 0 | 129 | 1 | 16 | 0 | 42 | 25 | 142 | 0 | 101 | 0 | 47 | 0.39 | 48 | 0 | 0.1 | 0.65 | 12 | 6506.43 | 890 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.29 | 900 | 0 | 0 | 0 | 1380.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.21 | 2 | 0 | 0 | 1.19 | 159 | 0 | 126 | 0 | 0 | 0 | 290 | 0 | 0.1 | 185 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 14 | 0.04 | 0 | 218 | 120 | 180 | 0 | 500 | 1110 | 0 | 6119.82 | 12626.25 | 103.33
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 203 | 0 | 17 | 17 | 15 | 30 | 30 | 0 | 0 | 0 | 0 | 130 | 290 | 0 | 0 | 250 | 0 | 0 | 3 | 51 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 12 | 0.64 | 203 | 0 | 26 | 1125 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 1150 | 1 | 0 | 0 | 0 | 280 | 220 | 51 | 0 | 194 | 0 | 0 | 143 | 0 | 0 | 19 | 0 | 118 | 0 | 4 | 16 | 310 | 0 | 397 | 42 | 0 | 149 | 2 | 8 | 0 | 42 | 25 | 141 | 0 | 101 | 0 | 47 | 3.66 | 48 | 0 | 0.2 | 7.53 | 12 | 6507.03 | 890 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 1015 | 0 | 0 | 0 | 1455.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.34 | 8 | 0 | 0 | 9.16 | 149 | 0 | 125 | 0 | 0 | 0 | 281 | 0 | 0.95 | 185 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 1.2 | 43 | 0.07 | 0 | 217 | 120 | 220 | 0 | 500 | 1155 | 0 | 6442.51 | 12949.54 | 103.32
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 202 | 0 | 17 | 17 | 15 | 60 | 30 | 0 | 0 | 0 | 0 | 130 | 285 | 0 | 0 | 250 | 0 | 0 | 2 | 51 | 8.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 12 | 1.01 | 212 | 0 | 5 | 1050 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 1150 | 2 | 1 | 0 | 0 | 280 | 220 | 51 | 0 | 200 | 0 | 0 | 143 | 0 | 0 | 19 | 0 | 118 | 0 | 13 | 16 | 310 | 0 | 331 | 29 | 0 | 138 | 3 | 8 | 0 | 42 | 25 | 142 | 0 | 100 | 0 | 47 | 14 | 47 | 0 | 0.6 | 14.07 | 12 | 6417.18 | 890 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 1069 | 0 | 0 | 0 | 1422.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.31 | 7 | 0 | 0 | 7.22 | 145 | 0 | 124 | 0 | 0 | 0 | 250 | 0 | 1.02 | 185 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 2.7 | 110 | 0.17 | 4 | 249 | 100 | 180 | 0 | 500 | 1135 | 0 | 6464.08 | 12881.26 | 103.31
09:00 | 0 | 17 | 4 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 233 | 0 | 17 | 17 | 44 | 60 | 30 | 0 | 0 | 0 | 0 | 130 | 285 | 0 | 0 | 250 | 0 | 0 | 1 | 86 | 7.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 0 | 12 | 1.46 | 222 | 16 | 2 | 1050 | 0 | 0 | 0 | 0 | 13 | 205 | 0 | 0 | 0 | 1066 | 3 | 12 | 0 | 0 | 280 | 240 | 10 | 0 | 188 | 0 | 0 | 142 | 16 | 0 | 19 | 0 | 122 | 0 | 17 | 16 | 305 | 0 | 377 | 29 | 0 | 142 | 2 | 17 | 0 | 42 | 25 | 142 | 0 | 100 | 0 | 47 | 5.08 | 48 | 0 | 0.8 | 24.45 | 12 | 6509.29 | 889 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 55 | 1061 | 0 | 0 | 0 | 1422.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.67 | 28 | 0 | 0 | 8.68 | 143 | 0 | 122 | 0 | 0 | 0 | 248 | 0 | 1.22 | 185 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 3.6 | 73 | 0.32 | 14 | 197 | 120 | 220 | 0 | 691 | 1130 | 0 | 6690.13 | 13199.42 | 103.31
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 229 | 0 | 17 | 42 | 141 | 145 | 31 | 17 | 17 | 0 | 0 | 130 | 280 | 0 | 0 | 250 | 0 | 0 | 5 | 143 | 7.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 17 | 0 | 12 | 2.1 | 222 | 15 | 0 | 1125 | 0 | 0 | 0 | 0 | 17 | 205 | 0 | 0 | 0 | 1070 | 3 | 12 | 0 | 0 | 280 | 260 | 19 | 0 | 188 | 0 | 0 | 142 | 19 | 0 | 19 | 0 | 122 | 0 | 63 | 16 | 315 | 0 | 317 | 28 | 0 | 146 | 3 | 17 | 0 | 42 | 25 | 142 | 0 | 100 | 0 | 57 | 9.2 | 103 | 0 | 1.2 | 16.13 | 12 | 7029.13 | 889 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 66.31 | 1015 | 0 | 0 | 0 | 1440.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.53 | 46 | 0 | 0 | 23.54 | 135 | 0 | 122 | 0 | 0 | 0 | 224 | 0 | 1.5 | 185 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 7.5 | 106 | 0.24 | 0 | 247 | 120 | 220 | 0 | 638 | 1150 | 0 | 6730.17 | 13759.3 | 103.31
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 236 | 17 | 17 | 90 | 125 | 278 | 55 | 17 | 17 | 0 | 0 | 130 | 275 | 0 | 0 | 270 | 0 | 0 | 6 | 143 | 7.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 17 | 0 | 25 | 0.77 | 222 | 39 | 0 | 1125 | 0 | 0 | 13 | 0 | 30 | 205 | 0 | 0 | 0 | 1100 | 2 | 20 | 0 | 0 | 280 | 260 | 51 | 0 | 189 | 0 | 0 | 141 | 45 | 0 | 19 | 0 | 138 | 0 | 46 | 16 | 265 | 0 | 346 | 28 | 0 | 131 | 11 | 0 | 0 | 11 | 22 | 144 | 0 | 100 | 0 | 58 | 16.71 | 115 | 0 | 1.8 | 27.24 | 12 | 7373.02 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 65.73 | 1042 | 0 | 0 | 0 | 1355.24 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 24.92 | 27 | 0 | 0 | 24.72 | 135 | 0 | 122 | 0 | 0 | 0 | 204 | 0 | 2.38 | 186 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0.1 | 97 | 0.23 | 0 | 248 | 100 | 220 | 0 | 637 | 1110 | 0 | 6574.32 | 13947.34 | 103.3
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 243 | 17 | 17 | 96 | 110 | 294 | 55 | 17 | 17 | 0 | 0 | 130 | 285 | 0 | 0 | 270 | 0 | 0 | 6 | 143 | 7.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 17 | 0 | 25 | 1.57 | 222 | 50 | 0 | 1050 | 0 | 0 | 26 | 0 | 32 | 205 | 0 | 0 | 0 | 1100 | 4 | 50 | 0 | 0 | 280 | 260 | 51 | 0 | 184 | 0 | 6 | 140 | 47 | 16 | 19 | 0 | 134 | 0 | 79 | 16 | 290 | 0 | 346 | 28 | 0 | 143 | 6 | 0 | 0 | 11 | 0 | 143 | 0 | 70 | 0 | 58 | 20 | 115 | 0 | 2.2 | 42.26 | 12 | 7438.53 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 42.99 | 1002 | 0 | 0 | 0 | 1386.08 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 11.04 | 6 | 0 | 0 | 43.5 | 135 | 0 | 115 | 0 | 0 | 0 | 179 | 0 | 3.63 | 185 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 2.3 | 170 | 0.33 | 0 | 251 | 120 | 220 | 0 | 900 | 1095 | 0 | 6851.87 | 14290.4 | 103.3
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 226 | 17 | 17 | 96 | 125 | 294 | 55 | 17 | 17 | 0 | 0 | 130 | 285 | 0 | 35 | 270 | 0 | 0 | 6 | 143 | 7.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 17 | 0 | 25 | 4 | 222 | 51 | 0 | 1125 | 5 | 0 | 26 | 0 | 31 | 205 | 0 | 0 | 0 | 1150 | 3 | 50 | 0 | 0 | 280 | 260 | 43 | 0 | 171 | 0 | 35 | 140 | 68 | 56 | 19 | 17 | 134 | 1 | 30 | 24 | 300 | 0 | 339 | 14 | 0 | 137 | 11 | 8 | 0 | 5 | 0 | 140 | 0 | 100 | 0 | 58 | 20.5 | 114 | 0 | 2.3 | 32.99 | 12 | 7655.29 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 55.01 | 903 | 0 | 0 | 0 | 1323.61 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 8.68 | 8 | 0 | 0 | 46.12 | 134 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 4.8 | 185 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 5.4 | 182 | 0.11 | 0 | 277 | 120 | 220 | 0 | 950 | 1115 | 0 | 6736.73 | 14392.02 | 103.3
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 228 | 17 | 0 | 58 | 15 | 294 | 55 | 35 | 17 | 0 | 0 | 130 | 280 | 0 | 35 | 270 | 0 | 0 | 6 | 51 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 34 | 0 | 0 | 17 | 10 | 25 | 2.5 | 222 | 54 | 0 | 1125 | 16 | 0 | 25 | 0 | 38 | 205 | 0 | 0 | 0 | 1120 | 6 | 25 | 0 | 0 | 280 | 220 | 43 | 0 | 187 | 0 | 33 | 138 | 108 | 57 | 19 | 34 | 152 | 20 | 26 | 23 | 295 | 0 | 342 | 12 | 0 | 136 | 10 | 8 | 0 | 5 | 0 | 141 | 0 | 100 | 0 | 57 | 16.62 | 114 | 0 | 2.3 | 38.35 | 12 | 7363.77 | 845 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 46.86 | 823 | 0 | 0 | 0 | 1296.34 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 23.31 | 10 | 0 | 0 | 4.6 | 134 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 0.64 | 186 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 3.7 | 109 | 0.22 | 0 | 264 | 100 | 220 | 0 | 849 | 1065 | 0 | 6271.67 | 13635.44 | 103.29
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 231 | 17 | 4 | 53 | 15 | 294 | 55 | 48 | 17 | 0 | 0 | 115 | 285 | 0 | 35 | 270 | 0 | 0 | 4 | 51 | 2.5 | 21 | 0 | 0 | 31 | 0 | 4 | 0 | 24 | 0 | 0 | 17 | 24 | 25 | 2.21 | 222 | 100 | 2 | 1125 | 15 | 0 | 25 | 0 | 96 | 213 | 0 | 0 | 0 | 1100 | 2 | 25 | 0 | 0 | 280 | 220 | 43 | 0 | 193 | 0 | 34 | 141 | 150 | 42 | 17 | 31 | 152 | 16 | 56 | 22 | 300 | 0 | 339 | 41 | 0 | 145 | 5 | 8 | 0 | 5 | 0 | 142 | 0 | 100 | 0 | 57 | 7.9 | 114 | 0 | 0 | 23.55 | 12 | 7584.16 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 35.06 | 871 | 0 | 0 | 0 | 1330.53 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 21.44 | 10 | 0 | 0 | 22.26 | 138 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 1.89 | 185 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 1.4 | 163 | 0.38 | 0 | 247 | 120 | 220 | 0 | 681 | 1072 | 0 | 6327.96 | 13912.12 | 103.29
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 222 | 17 | 18 | 53 | 15 | 294 | 55 | 35 | 17 | 0 | 0 | 115 | 280 | 0 | 35 | 270 | 0 | 0 | 5 | 51 | 5.5 | 21 | 0 | 0 | 0 | 0 | 12 | 0 | 19 | 0 | 0 | 17 | 12 | 25 | 1.53 | 222 | 92 | 2 | 1125 | 0 | 0 | 22 | 0 | 17 | 213 | 0 | 0 | 0 | 1100 | 0 | 25 | 0 | 0 | 280 | 220 | 43 | 0 | 198 | 0 | 34 | 141 | 140 | 27 | 19 | 17 | 136 | 16 | 20 | 22 | 300 | 0 | 334 | 41 | 0 | 140 | 7 | 8 | 0 | 5 | 0 | 142 | 0 | 102 | 0 | 57 | 3.2 | 114 | 0 | 1 | 9.87 | 12 | 7319.1 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21.59 | 959 | 0 | 0 | 0 | 1273.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.15 | 23 | 0 | 0 | 13.96 | 139 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 1.35 | 185 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0.7 | 60 | 0.02 | 0 | 276 | 120 | 220 | 0 | 645 | 1054 | 0 | 6160.53 | 13479.63 | 103.29
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 227 | 17 | 17 | 53 | 15 | 294 | 55 | 55 | 17 | 0 | 0 | 115 | 280 | 0 | 35 | 270 | 0 | 0 | 3 | 51 | 7 | 21 | 0 | 0 | 0 | 0 | 11 | 0 | 35 | 0 | 0 | 17 | 12 | 25 | 1.08 | 222 | 68 | 2 | 1125 | 0 | 0 | 19 | 0 | 15 | 213 | 0 | 0 | 0 | 1105 | 0 | 25 | 0 | 0 | 280 | 220 | 43 | 0 | 205 | 0 | 34 | 143 | 68 | 27 | 19 | 17 | 114 | 16 | 16 | 22 | 300 | 0 | 337 | 41 | 0 | 132 | 3 | 17 | 0 | 5 | 0 | 142 | 0 | 100 | 0 | 64 | 5.1 | 114 | 0 | 0.8 | 3.27 | 12 | 7244.25 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 5.1 | 1048 | 0 | 0 | 0 | 1180.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.61 | 26 | 0 | 0 | 10.66 | 139 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 1.29 | 185 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.2 | 48 | 0.03 | 0 | 276 | 120 | 220 | 0 | 613 | 1006 | 0 | 6046.28 | 13290.53 | 103.28
18:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 251 | 0 | 50 | 53 | 15 | 294 | 55 | 55 | 51 | 0 | 0 | 115 | 290 | 0 | 0 | 270 | 0 | 0 | 1 | 51 | 7 | 21 | 0 | 0 | 0 | 0 | 12 | 0 | 18 | 0 | 0 | 17 | 0 | 12 | 0.19 | 222 | 34 | 2 | 1000 | 0 | 0 | 6 | 0 | 0 | 213 | 0 | 0 | 0 | 1130 | 0 | 0 | 0 | 0 | 280 | 220 | 51 | 0 | 208 | 0 | 16 | 146 | 0 | 0 | 14 | 0 | 120 | 0 | 2 | 22 | 305 | 0 | 353 | 41 | 0 | 125 | 0 | 17 | 0 | 5 | 0 | 142 | 0 | 100 | 0 | 64 | 0.2 | 115 | 0 | 0.2 | 0 | 8 | 6916.59 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3.3 | 1060 | 0 | 0 | 0 | 1244.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 4 | 0 | 0 | 1.61 | 139 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0.16 | 185 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0.01 | 0 | 287 | 120 | 220 | 0 | 871 | 970 | 0 | 6266.66 | 13183.25 | 103.28
19:00 | 0 | 88 | 10 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 239 | 35 | 14 | 71 | 129 | 294 | 55 | 55 | 80 | 0 | 0 | 115 | 285 | 0 | 20 | 270 | 0 | 0 | 0 | 143 | 7 | 21 | 0 | 0 | 7 | 16 | 31 | 0 | 12 | 34 | 36 | 54.36 | 24 | 42 | 0 | 222 | 35 | 2 | 1065 | 15 | 0 | 6 | 4 | 1 | 217 | 0 | 0 | 0 | 1160 | 0 | 1 | 0 | 0 | 280 | 220 | 51 | 0 | 209 | 0 | 18 | 146 | 7 | 2 | 14 | 25 | 140 | 1 | 0 | 24 | 300 | 0 | 347 | 41 | 0 | 145 | 0 | 17 | 0 | 5 | 0 | 143 | 0 | 102 | 1 | 65 | 0 | 115 | 0 | 0 | 0 | 12 | 7646.36 | 896 | 0 | 0 | 9 | 0 | 38 | 0 | 0 | 0 | 0 | 6 | 0 | 1117 | 0 | 0 | 0 | 1311.08 | 0 | 0 | 0 | 35 | 8 | 0 | 29 | 23 | 8 | 0 | 0 | 16 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 185 | 0 | 82 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 250 | 120 | 220 | 0 | 957 | 1085 | 17 | 6818.08 | 14464.44 | 103.3
19:30 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 217 | 35 | 17 | 149 | 145 | 294 | 55 | 55 | 108 | 0 | 0 | 115 | 250 | 0 | 35 | 290 | 0 | 0 | 0 | 143 | 7 | 21 | 0 | 0 | 40 | 49 | 55 | 0 | 17 | 34 | 40 | 54.36 | 50 | 50 | 0 | 222 | 45 | 4 | 1075 | 70 | 0 | 35 | 8 | 51 | 217 | 0 | 0 | 0 | 1160 | 0 | 12 | 0 | 0 | 280 | 220 | 51 | 0 | 209 | 0 | 68 | 146 | 95 | 27 | 19 | 52 | 138 | 8 | 0 | 24 | 295 | 0 | 347 | 41 | 0 | 137 | 0 | 17 | 0 | 5 | 0 | 142 | 0 | 102 | 17 | 66 | 0 | 153 | 0 | 0 | 0 | 12 | 8308.36 | 845 | 0 | 0 | 31 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1145 | 0 | 0 | 0 | 1287.74 | 0 | 0 | 0 | 50 | 45 | 0 | 101 | 25 | 16 | 0 | 0 | 20 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 185 | 0 | 92 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 271 | 100 | 180 | 0 | 950 | 1138 | 55 | 7062.74 | 15371.1 | 103.28
20:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 212 | 35 | 17 | 149 | 146 | 295 | 55 | 55 | 108 | 0 | 0 | 115 | 270 | 0 | 55 | 270 | 0 | 0 | 0 | 143 | 8.5 | 21 | 0 | 0 | 17 | 15 | 50 | 0 | 20 | 34 | 40 | 54.36 | 50 | 50 | 0 | 220 | 60 | 2 | 1070 | 17 | 0 | 31 | 8 | 49 | 216 | 0 | 0 | 0 | 1155 | 0 | 12 | 0 | 0 | 280 | 220 | 51 | 0 | 210 | 0 | 68 | 146 | 89 | 25 | 19 | 17 | 146 | 8 | 0 | 24 | 295 | 0 | 327 | 41 | 0 | 130 | 0 | 8 | 0 | 42 | 0 | 142 | 0 | 101 | 17 | 67 | 0 | 153 | 0 | 0 | 0 | 12 | 8175.86 | 895 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1166 | 0 | 0 | 0 | 1289.54 | 0 | 36 | 0 | 35 | 59 | 0 | 101 | 27 | 8 | 0 | 0 | 18 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 239 | 0 | 0 | 185 | 0 | 95 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 209 | 100 | 180 | 0 | 950 | 1146 | 54 | 7134.54 | 15310.4 | 103.27
21:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 230 | 35 | 18 | 149 | 145 | 295 | 55 | 40 | 72 | 0 | 0 | 115 | 280 | 0 | 35 | 270 | 0 | 0 | 0 | 143.2 | 8 | 21 | 0 | 0 | 15 | 15 | 12 | 0 | 0 | 34 | 40 | 54.36 | 12 | 12 | 0 | 220 | 39 | 3 | 1125 | 15 | 0 | 19 | 8 | 30 | 200 | 0 | 0 | 0 | 1190 | 0 | 12 | 0 | 0 | 280 | 220 | 51 | 0 | 210 | 0 | 68 | 146 | 17 | 27 | 19 | 17 | 130 | 0 | 0 | 24 | 300 | 0 | 366 | 42 | 0 | 130 | 0 | 17 | 0 | 42 | 0 | 144 | 0 | 103 | 17 | 67 | 0 | 155 | 0 | 0 | 0 | 12 | 7983.56 | 896 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1196 | 0 | 0 | 0 | 1478.19 | 0 | 40 | 0 | 35 | 35 | 0 | 101 | 25 | 8 | 0 | 0 | 18 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 185 | 0 | 46 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 273 | 120 | 220 | 0 | 1000 | 1099 | 34 | 7401.19 | 15384.75 | 103.27
22:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 232 | 35 | 17 | 149 | 145 | 295 | 55 | 35 | 54 | 0 | 0 | 115 | 290 | 0 | 17 | 270 | 0 | 0 | 0 | 143 | 8 | 22 | 0 | 0 | 15 | 15 | 12 | 0 | 4 | 34 | 40 | 17 | 12 | 12 | 0 | 220 | 33 | 3 | 1125 | 17 | 0 | 19 | 8 | 17 | 186 | 0 | 0 | 0 | 1190 | 0 | 12 | 0 | 0 | 280 | 220 | 51 | 0 | 211 | 0 | 34 | 146 | 16 | 9 | 19 | 17 | 138 | 0 | 0 | 24 | 300 | 0 | 366 | 42 | 0 | 142 | 0 | 17 | 0 | 5 | 0 | 144 | 0 | 102 | 17 | 67 | 0 | 155 | 0 | 0 | 0 | 12 | 7803 | 896 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1207 | 0 | 0 | 0 | 1485.52 | 0 | 40 | 0 | 35 | 35 | 0 | 50 | 25 | 8 | 0 | 0 | 18 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 0 | 185 | 0 | 48 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 277 | 120 | 220 | 0 | 1049 | 1099 | 16 | 7401.52 | 15204.52 | 103.27
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 242 | 17 | 17 | 105 | 145 | 295 | 55 | 35 | 52 | 0 | 0 | 115 | 290 | 0 | 17 | 270 | 0 | 0 | 0 | 143 | 8 | 22 | 0 | 0 | 16 | 15 | 12 | 0 | 8 | 34 | 40 | 17 | 12 | 12 | 0 | 221 | 32 | 3 | 1125 | 17 | 0 | 19 | 8 | 16 | 186 | 0 | 0 | 0 | 1195 | 0 | 12 | 0 | 0 | 280 | 220 | 51 | 0 | 207 | 0 | 32 | 144 | 17 | 9 | 19 | 17 | 136 | 0 | 0 | 24 | 305 | 0 | 368 | 42 | 0 | 151 | 0 | 17 | 0 | 5 | 0 | 143 | 0 | 102 | 17 | 67 | 0 | 154 | 0 | 0 | 0 | 12 | 7684 | 896 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1205 | 0 | 0 | 0 | 1483.08 | 0 | 40 | 0 | 35 | 35 | 0 | 50 | 25 | 8 | 0 | 0 | 18 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 185 | 0 | 47 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 278 | 120 | 220 | 0 | 1038 | 1141 | 16 | 7393.08 | 15077.08 | 103.26
Total KWH | 0 | 846720 | 174720 | 0 | 0 | 0 | 0 | 0 | 7308000 | 0 | 5495130 | 260280 | 425160 | 1881216 | 1606080 | 5235218 | 1202916 | 605421 | 705600 | 0 | 0 | 3089193 | 6927727 | 0 | 339055 | 6322703 | 0 | 0 | 58232 | 2192400 | 176400 | 475920 | 0 | 0 | 288545 | 165600 | 298560 | 0 | 492960 | 263879 | 204355 | 381578 | 195840 | 534720 | 19801 | 5180175 | 1484545 | 239040 | 26603636.36 | 227491 | 0 | 468000 | 85356 | 841381 | 4924853 | 0 | 0 | 0 | 27534543 | 31590 | 602181 | 0 | 0 | 7268900 | 5732000 | 1174578 | 0 | 4903000 | 0 | 584640 | 3410690 | 1812480 | 319200 | 435070 | 289560 | 3226560 | 178810 | 382636 | 567392 | 7274000 | 0 | 8729000 | 858000 | 0 | 3342109.09 | 69562 | 279072 | 0 | 577920 | 282432 | 3263500 | 0 | 2156030 | 96480 | 1327200 | 102459 | 2241600 | 0 | 12600 | 253630 | 285600 | 177833430.45 | 21541091 | 0 | 0 | 113760 | 0 | 912000 | 0 | 0 | 0 | 0 | 15120 | 444960 | 23709090 | 0 | 0 | 0 | 33055561 | 0 | 171141 | 0 | 344448 | 647232 | 0 | 417656 | 133472 | 123888 | 184536 | 278170 | 83963 | 0 | 246144 | 3667936 | 0 | 1646964 | 0 | 0 | 0 | 5926472 | 0 | 23700 | 4538000 | 0 | 675053 | 208115 | 786710 | 0 | 0 | 0 | 28998.48 | 1281600 | 3252 | 753408 | 6327000 | 2786000 | 5301920 | 0 | 18196363 | 27252363.64 | 228000 | 162054087.12 | 339887517.57 | 103.26

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-07-2026 | during | 23-07-2026 | during | 23-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 300 | 300 | 412 | 412 | 300 | 300 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 130 | 115 | 335 | 335 | 130 | 130 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 270 | 270 | 335 | 335 | 270 | 270 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 110 | 145 | 149.36 | 149.36 | 48 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 40 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 7.5 | 8 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 294 | 295 | 300 | 300 | 48 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 96 | 149 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 105 | 105 | 34 | 88 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 72 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 6 | 0 | 7 | 0 | 7 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 18 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 285 | 280 | 583 | 583 | 285 | 285 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 243 | 230 | 718 | 718 | 245 | 245 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143 | 143.2 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6668.974 | 2106.5 | 2324.2 | 5782.64 | 5775.64 | 1776.42 | 2310.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 4 | 0 | 8 | 0 | 8 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 220 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 205 | 200 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 32 | 30 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 24 | 56 | 24 | 56 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 34 | 0 | 34 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 3 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.57 | 0 | 4.26 | 0 | 4.26 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 54 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 50 | 39 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 15 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 15 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1190 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 31 | 0 | 30 | 20 | 30 | 20 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1050 | 1125 | 1150 | 1150 | 1125 | 1125 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2763.57 | 3043.36 | 4114.12 | 4172.86 | 3447.26 | 3548
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 184 | 210 | 221.25 | 221.25 | 205.25 | 205.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 280 | 280 | 350.01 | 350.01 | 280 | 280 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 260 | 220 | 342.01 | 342.01 | 220 | 220 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 50 | 12 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 16 | 24 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 146 | 163 | 163 | 150 | 150 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 47 | 17 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 134 | 130 | 84 | 80 | 150 | 150 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 16 | 27 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 6 | 68 | 115 | 115 | 34 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 79 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1282 | 1221 | 2361.44 | 2297.44 | 1412.45 | 1620.45
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-07-2026 | during | 23-07-2026 | during | 23-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 155 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 67 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42.26 | 0 | 47 | 0 | 47 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 249.46 | 251 | 535.4 | 516.5 | 277.9 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 28 | 42 | 28 | 28 | 28 | 28 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 143 | 130 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 143 | 144 | 142 | 142 | 142 | 142 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 25 | 25 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 11 | 42 | 84 | 84 | 5 | 5 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 70 | 103 | 100 | 100 | 100 | 100 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 17 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 346 | 366 | 385 | 385 | 385 | 385 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1037 | 1144 | 1318 | 1318 | 1156 | 1156
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 896 | 896 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 23 | 27 | 27 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 42.99 | 0 | 92 | 0 | 92 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1002 | 1196 | 1234.2 | 1234.2 | 1194.2 | 1194.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1978.99 | 2168 | 3623.2 | 3531.2 | 2371.2 | 2279.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 900 | 1000 | 700 | 1050 | 700 | 1050 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 48 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 1095 | 1099 | 1163.05 | 1163.05 | 1163.05 | 1163.05 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 34 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 251 | 273 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.33 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2586.33 | 2794 | 2781.05 | 3130.05 | 2607.05 | 2956.05
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 11.04 | 0 | 55 | 0 | 55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 135 | 139 | 214 | 214 | 140 | 140 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 115 | 0 | 220 | 220 | 130 | 130 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 179 | 245 | 413.79 | 413.79 | 290 | 290 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 18 | 22 | 22 | 22 | 22 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 101 | 100 | 100 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 3.63 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1386.08 | 1478.19 | 1469.13 | 1469.13 | 1389.13 | 1389.13 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 43.5 | 0 | 52 | 0 | 52 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 6 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1914.25 | 2124.19 | 3253.62 | 3041.12 | 2267.83 | 2217.33
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 185 | 185 | 180 | 180 | 185 | 185 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 84 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.3 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 46 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 170 | 0 | 166 | 0 | 166 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 372.3 | 315 | 641 | 442 | 533 | 369
System Total |  |  |  |  | 28843.2 | 29169.167 | 14290.4 | 15384.75 | 24410.47 | 24224.81 | 15849.11 | 16715.45
Forecast Scenario (23-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15050 |  | 47.75 |  | 15100
|  |  |  | 1:00 | 14750 |  | 47.75 |  | 14800
|  |  |  | 2:00 | 14300 |  | 85.95 |  | 14390
|  |  |  | 3:00 | 13900 |  | 38.2 |  | 13940
|  |  |  | 4:00 | 13800 |  | 28.65 |  | 13830
|  |  |  | 5:00 | 13500 |  | 76.4 |  | 13580
|  |  |  | 6:00 | 12800 |  | 85.95 |  | 12890
|  |  |  | 7:00 | 13300 |  | 28.65 |  | 13330
|  |  |  | 8:00 | 13200 |  | 66.85 |  | 13270
|  |  |  | 9:00 | 13400 |  | 38.2 |  | 13440
|  |  |  | 10:00 | 13700 |  | 85.95 |  | 13790
|  |  |  | 11:00 | 13900 |  | 57.3 |  | 13960
|  |  |  | 12:00 | 14400 |  | 66.85 |  | 14470
|  |  |  | 13:00 | 14700 |  | 47.75 |  | 14750
|  |  |  | 14:00 | 14200 |  | 19.1 |  | 14220
|  |  |  | 15:00 | 14580 |  | 19.1 |  | 14600
|  |  |  | 16:00 | 14000 |  | 57.3 |  | 14060
|  |  |  | 17:00 | 13600 |  | 85.95 |  | 13690
|  |  |  | 18:00 | 13500 |  | 9.55 |  | 13510
|  |  |  | 18:30 | 13950 |  | 47.75 |  | 14000
|  |  |  | 19:00 | 14700 |  | 19.1 |  | 14720
|  |  |  | 19:30 | 15700 |  | 85.95 |  | 15790
|  |  |  | 20:00 | 15600 |  | 85.95 |  | 15690
|  |  |  | 21:00 | 15500 |  | 76.4 |  | 15580
|  |  |  | 22:00 | 15250 |  | 47.75 |  | 15300
|  |  |  | 23:00 | 15220 |  | 76.4 |  | 15300
Probable Maximum Temperature: |  |  | 28.00°C
Probable Maximum Demand at Day Peak: |  |  | 14470.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 76
Probable Maximum Demand at Evening Peak: |  |  | 15790.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15700.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 340.85 MKWHr. |  | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 76
*** This report is generated digitally from Operation Information System (OIS) at 10:54 hrs on 23-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14290.4 | MW | 12:00 Hr. | Energy Generated |  |  | 339.8875 |  | MKWHr.
| Day Peak Demand |  |  | 14474.4 | MW | 12:00 Hr. | Energy Unserverd |  |  | 7.735 |  | MKWHr.
| Evening Peak Generation |  |  | 15384.75 | MW | 21:00 Hr. | Energy Demand |  |  | 347.6225 |  | MKWHr.
| Evening Peak Demand |  |  | 15612.75 | MW | 21:00 Hr. | Maximum Temperature |  |  | 30.7 |  | °C
| Minimum Generation of the Day |  |  | 12626.25 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 751.1 |  | MMCFD
| Maximum Generation of the Day |  |  | 15384.75 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.7925 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 29.7951 | 0 | 15.4748 | 0 | 0 | 0.058232 | 0 | 0 | 45.3281 | Gas | 103.9746 | Gas | 361923771.2728
| Chattogram Zone |  |  | 5.1639 | 54.1382 | 5.4398 | 0 | 5.1802 | 0.051391 | 0 | 0.49296 | 70.4664 | Coal | 134.161 | Coal | 899659167.9632
| Cumilla Zone |  |  | 22.9242 | 0 | 4.3543 | 0 | 0 | 0.38264 | 3.2266 | 0 | 30.8877 | HFO | 33.7136 | HFO | 608330163.23
| Mymensingh Zone |  |  | 0 | 0 | 3.9509 | 0 | 0 | 0.36869 | 0 | 0 | 4.3196 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 26.7621 | 0 | 0 | 0 | 0 | 0.069562 | 0 | 0 | 26.8316 | Hydro | 5.1802 | Hydro | 518017.5
| Khulna Zone |  |  | 0 | 23.7091 | 0.12888 | 0 | 0 | 0.44496 | 22.4531 | 0 | 46.736 | Solar | 3.63 | Solar | 59809954.0884
| Barishal Zone |  |  | 8.0879 | 51.7757 | 0.98141 | 0 | 0 | 0.003252 | 0 | 0 | 60.8483 | Import | 58.7352 | Import | 371177333.49
| Rajshahi Zone |  |  | 11.2414 | 0 | 1.9218 | 0 | 0 | 0.73255 | 33.0556 | 0 | 46.9513 | Wind | 0.49296 | Wind | 7251441.6
| Rangpur Zone |  |  | 0 | 4.538 | 1.4618 | 0 | 0 | 1.5187 | 0 | 0 | 7.5185
| Total |  |  | 103.9746 | 134.161 | 33.7136 | 0 | 5.1802 | 3.63 | 58.7352 | 0.49296 | 339.8875
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 361923771.2728 |  | Hydro | 518017.5
|  |  |  | Coal | 899659167.9632 |  | Solar | 59809954.0884
|  |  |  | HFO | 608330163.23 |  | Import | 371177333.49
|  |  |  | HSD | 0 |  | Wind | 7251441.6
[5 empty] | Total: | 230,86,69,849 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5411 | Peak Hr Flow | 896.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 53089181.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.0556 | Peak Hr Flow | 1478.19 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2523 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.2266 | Peak Hr Flow | 130.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2888 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 57.8232 | Peak Hr Flow | 2504.19 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 63 |  | 5564
|  |  |  | Chattogram |  | 0 |  | 1400
|  |  |  | Cumilla |  | 0 |  | 1409
|  |  |  | Mymensingh |  | 155 |  | 1308
|  |  |  | Sylhet |  | 0 |  | 683
|  |  |  | Khulna |  | 0 |  | 1680
|  |  |  | Barishal |  | 0 |  | 454
|  |  |  | Rajshahi |  | 0 |  | 1504
|  |  |  | Rangpur |  | 0 |  | 996
|  |  |  | Total |  | 218 |  | 14998
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 489
|  |  |  | Total Unavailable Capacity |  |  |  | 789
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:04 | Munshiganj 132/33kV S/S Transformer-1 LT is restored.
|  | 08:04 | Munshiganj 132/33kV S/S Transformer-1 HT is restored.
| 08:08 | 09:33 | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to Red hot maintenance at 33KV | [7 empty] | 35.0MW load
|  |  | bus-01. | [7 empty] | interrup.
| 08:09 | 09:33 | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to Red hot maintenance at 33KV | [7 empty] | 35.0MW load
|  |  | bus-01. | [7 empty] | interrup.
| 09:40 | 21:21 | Korerhat 400/230/132kV S/S ATR-4(7403T) LT Project Work S/D Due to For project work
| 09:45 | 21:20 | Korerhat 400/230/132kV S/S ATR-4(7403T) HT Project Work S/D Due to For project work
| 09:47 | 21:48 | Korerhat 400/230/132kV S/S Meghnaghat-1 Project Work S/D Due to For project work
| 09:48 | 21:46 | Madunaghat-Meghnaghat 400kV Ckt-1 Project Work S/D from Meghnaghat 400/230kV end Due to
For korerhat ss project work
| 10:05 | 17:30 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Scheduled S/D from Thakurgaon 132/33kV end Due
to Work at EPVTL CRP.
| 12:19 |  | Sirajgonj 225MW CCPP Unit-2 ST Shutdown with remarks:- Shutdown due to extremely low gas
pressure as per consent of BPDB
| 12:19 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- ST
| 12:23 | 20:21 | Maijdee 132/33kV S/S TR-01 HT Scheduled S/D Due to TR-01 S/D for BREB 33 kV DS REPLACE &
Other Maintenance Work.
| 12:31 |  | Sirajgonj 225MW CCPP Unit-2 GT Shutdown with remarks:- Shutdown due to extremely low gas
pressure as per instruction of PGCL with consent of BPDB
| 12:31 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- GT
| 12:32 |  | Sirajgonj 225MW CCPP Unit-2 ST Ready with remarks:- None
| 12:32 |  | Sirajgonj 225MW CCPP Unit-2 GT Ready with remarks:- None
| 12:40 |  | BSRM 230/33kV S/S 230/33 kV Transformer-1 (125/140 MVA) HT Scheduled S/D Due to Annual
Maintenance
| 14:18 | 15:50 | Bajitpur 132/33kV S/S 132 kV Bus-1 Scheduled S/D
| 14:22 | 15:46 | Bajitpur 132/33kV S/S Tr-2(414T) LT Scheduled S/D
| 14:47 | 16:31 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to DPBS-1 Shutdown for Red hot | [7 empty] | 54.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 15:59 | 16:45 | Bajitpur 132/33kV S/S Tr-1(404T) LT Scheduled S/D
| 16:40 | 17:47 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to Dohazari PDB 33kv | [7 empty] | 56.0MW load
|  |  | bus isolator Maintenance. | [7 empty] | interrup.
| 16:40 | 17:47 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to Dohazari PDB 33kv | [7 empty] | 56.0MW load
|  |  | bus isolator Maintenance. | [7 empty] | interrup.
| 17:28 | 18:43 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Forced S/D | [7 empty] | 24.0MW load
interrup.
| 17:28 | 18:43 | Niamatpur 132/33kV S/S Transformer-1(407T) HT Forced S/D Due to 33kV PBS feeder red hot | [7 empty] | 24.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 21:18 | 01:07 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT Forced S/D Due to Red hot Repaire.
| 21:18 | 01:07 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT Forced S/D Due to Red hot Repaire.
| 06:00 |  | Minimum Generation: 12638 MW.
| 06:33 |  | Natore 132/33kV S/S TR-2 (415 T) LT Scheduled S/D | [7 empty] | 58.0MW load
interrup.
| 06:33 |  | Natore 132/33kV S/S TR-1 (405 T) LT Scheduled S/D | [7 empty] | 58.0MW load
interrup.
| 06:34 |  | Natore 132/33kV S/S TR-1 (405 T) HT Scheduled S/D | [7 empty] | 58.0MW load
interrup.
| 06:34 |  | Natore 132/33kV S/S TR-2 (415 T) HT Scheduled S/D | [7 empty] | 58.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 300 | 7308000 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 115 | 3089193 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1202916 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6322703 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 260280 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 145 | 1606080 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 40 | 605421 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 339055 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 8 | 176400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 475920 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 174720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 5235218 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1881216 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 846720 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 705600 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 58232 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 18 | 425160 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 280 | 6927727 | AGC+FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 230 | 5495130 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.2 | 2192400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6668.974 | 2324.2 | 45328091
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 85356 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 31590 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 468000 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5180175 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 200 | 4924853 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 30 | 841381 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 204355 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 263879 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 195840 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 3 | 239040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 298560 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19801 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 165600 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 381578 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 39 | 1484545 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 534720 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 288545 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 15 | 227491 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1190 | 27534543 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 492960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 26603636.36 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 3043.36 | 70466448.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 210 | 4903000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 280 | 7268900 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 220 | 5732000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1174578 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 12 | 602181 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 24 | 567392 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 146 | 3410690 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 1812480 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 130 | 3226560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 178810 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 435070 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 289560 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 319200 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 584640 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 382636 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1221 | 30887697
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 102459 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 155 | 2241600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 1327200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 253630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 285600 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 96480 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 251 | 4319569
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 69562 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 858000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | plant availability zero
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3342109.09 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 144 | 3263500 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 282432 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 42 | 577920 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 103 | 2156030 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 279072 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7274000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 8729000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1144 | 26831625.09
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 896 | 21541091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 23 | 113760 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 15120 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 444960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1196 | 23709090 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2168 | 46736021
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1000 | 18196363 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 753408 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2786000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 1099 | 27252363.64 | AGC+FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5301920 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 34 | 228000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 273 | 6327000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3252 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2794 | 60848306.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 184536 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 171141 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 133472 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 139 | 3667936 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 1646964 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 245 | 5926472 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 18 | 83963 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 123888 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 101 | 417656 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 647232 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 344448 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 23700 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1478.19 | 33055561 | AGC+FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 246144 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 278170 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2124.19 | 46951283
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 185 | 4538000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 84 | 786710 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 28998.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 46 | 675053 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 208115 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1281600 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 315 | 7518476.48
Eastern Grid Total |  |  |  |  | 17438.042 | 7983.56 | 177833430.45
Western Grid Total |  |  |  |  | 11731.125 | 7401.19 | 162054087.12
National Grid Total |  |  |  |  | 29169.167 | 15384.75 | 339887517.57
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10192.26 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4634.4 | MW
i) Dhaka area |  |  | 5501.26 |  | MW | i) Khulna area |  |  |  | 1680 | MW
ii) Chattogram area |  |  | 1446 |  | MW | ii) Barishal area |  |  |  | 454 | MW
iii) Cumilla area |  |  | 1409 |  | MW | iii) Rajshahi area |  |  |  | 1504.4 | MW
iv) Mymensingh area |  |  | 1153 |  | MW | iv) Rangpur area |  |  |  | 996 | MW
v) Sylhet area |  |  | 683 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14826.66 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 145 | 08:00 | 133 | Narshingdi | 190 | 22:00 | 199 | Uttara | 90 | 15:00
2 | AKSML | 140 | 02:00 | 68 | Hasnabad | 87 | 19:30 | 134 | Natore | 147 | 19:30 | 200 | UttaraNew | 53 | 13:00
3 | Aftabnagar | 42 | 13:00 | 69 | Hathazari | 87 | 20:00 | 135 | Nawabganj | 55.5 | 00:00 | 201 | Zigatola | 108 | 13:00
4 | Agargaon | 117 | 13:00 | 70 | Hatirjheel | 88 | 15:00 | 136 | Netrakona | 110 | 18:30
5 | Agrabad | 72 | 14:00 | 71 | Ishurdi | 79 | 19:30 | 137 | New | 86 | 15:00
6 | Amnura | 31 | 23:00 | 72 | Jaldhaka | 93 | 00:00 | 138 | Niamatpur | 74 | 00:00
7 | Ashuganj | 91 | 23:00 | 73 | Jamalpur | 128 | 21:00 | 139 | Noapara | 42 | 21:00
8 | BSRM | 185 | 06:00 | 74 | Jashore | 143 | 19:30 | 140 | PHP | 9 | 17:00
9 | Bagerhat | 94 | 20:00 | 75 | Jhenaidah | 87 | 22:00 | 141 | Pabna | 101 | 19:30
10 | Bajitpur | 86 | 22:00 | 76 | Joydebpur | 181 | 19:30 | 142 | Palashbari | 129 | 19:30
11 | Bakerganj | 14.2 | 19:30 | 77 | Joypurhat | 65 | 00:00 | 143 | Panchagarh | 63 | 00:00
12 | Bakulia | 93 | 19:00 | 78 | Juldah | 16 | 16:00 | 144 | Patiya | 10.5 | 20:00
13 | Banani | 69.4 | 14:00 | 79 | KSRM | 28 | 00:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 17 | 10:00 | 80 | Kabirpur | 275 | 18:30 | 146 | Patuakhali | 68 | 00:00
15 | Barapukuria | 71 | 19:30 | 81 | Kachua | 90 | 01:00 | 147 | Payra | 34 | 22:00
16 | Barguna | 22 | 22:00 | 82 | Kaliganj | 35 | 20:00 | 148 | Postogola | 62 | 13:00
17 | Barishal | 104 | 12:00 | 83 | Kallyanpur | 114 | 15:00 | 149 | Pubail | 42 | 20:00
18 | Barishal-230 | 98 | 00:00 | 84 | Kalurghat | 39 | 09:00 | 150 | Purbachal | 27 | 12:00
19 | Baroaulia | 44 | 09:00 | 85 | Kamrangirchar | 80 | 13:00 | 151 | Purbasadipur | 139 | 00:00
20 | Baroirhat | 64 | 19:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 39 | 23:00
21 | Bashundhara | 184 | 14:00 | 87 | Kasba | 39 | 19:30 | 153 | Rahim | 53 | 21:00
22 | BashundharaCement | 7 | 23:00 | 88 | Kazla | 122 | 13:00 | 154 | Rajbari | 87 | 19:30
23 | Beanibazar | 76 | 21:00 | 89 | Keranigonj | 83 | 19:30 | 155 | Rajendrapur | 124 | 00:00
24 | Benapole | 58 | 00:00 | 90 | Khagrachori | 30 | 19:00 | 156 | Rajshahi | 99 | 21:00
25 | Bhaluka | 173 | 20:00 | 91 | Khulna | 58 | 18:00 | 157 | Rajshahi-230 | 94 | 12:00
26 | Bhandaria | 56 | 00:00 | 92 | Khulshi | 179 | 19:00 | 158 | Ramganj | 110 | 00:00
27 | Bhangura | 34 | 00:00 | 93 | Kishoreganj | 124 | 20:00 | 159 | Rampur | 40 | 00:00
28 | Bheramara(GK) | 63 | 19:30 | 94 | Kodda | 315 | 19:30 | 160 | Rangamati | 18 | 19:30
29 | Bhulta | 255 | 18:00 | 95 | Kulaura | 56 | 20:00 | 161 | Rangpur | 144 | 19:30
30 | Bog-Sherpur | 86 | 00:00 | 96 | Kurigram | 72 | 00:00 | 162 | Ruppur | 4.4 | 10:00
31 | Bogura | 174 | 21:00 | 97 | Kushtia | 149 | 00:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 75 | 00:00 | 98 | Laksam | 36 | 00:00 | 164 | Saidpur | 103 | 00:00
33 | Brahmanbaria | 137 | 21:00 | 99 | Lakshmipur | 41 | 00:00 | 165 | Santhia | 34 | 19:00
34 | Cantonment | 124 | 14:00 | 100 | Lalbag | 83 | 12:00 | 166 | Satkhira | 127 | 21:00
35 | Chandina | 42 | 03:00 | 101 | Lalmonirhat | 70 | 20:00 | 167 | Satmasjid | 95 | 19:30
36 | Chandpur | 84 | 00:00 | 102 | MI_Cement | 12.6 | 17:00 | 168 | Savar | 216 | 12:00
37 | Chandraghona | 32 | 17:00 | 103 | Madanganj | 46 | 20:00 | 169 | SevenRings | 5.66 | 19:30
38 | Chapai | 69 | 00:00 | 104 | Madaripur | 110 | 00:00 | 170 | ShahCement | 37 | 18:00
39 | Charfasson | 32 | 00:00 | 105 | Madartek | 75 | 21:00 | 171 | Shahjadpur | 79 | 21:00
40 | Charsaidpur | 43 | 07:00 | 106 | Madunaghat | 53 | 19:00 | 172 | Shahjibazar | 145 | 21:00
41 | Chauddagram | 76 | 22:00 | 107 | Magura | 65 | 19:30 | 173 | Shahmirpur | 50 | 19:00
42 | Chhatak | 44 | 21:00 | 108 | Mahasthangarh | 82 | 23:00 | 174 | Shariatpur | 89 | 00:00
43 | Chowmuhani | 164 | 19:00 | 109 | Maijdee | 41 | 00:00 | 175 | Sherpur | 140 | 21:00
44 | Chuadanga | 109 | 20:00 | 110 | Manikganj | 138 | 00:00 | 176 | Shikalbaha | 26.5 | 00:00
45 | Coxsbazar | 142 | 22:00 | 111 | Maniknagar | 75 | 13:00 | 177 | Shitalakhya | 76.9 | 13:00
46 | Cumilla(N) | 116 | 01:00 | 112 | Matarbari | 51 | 19:00 | 178 | Sholosohor | 47 | 15:00
47 | Cumilla(S) | 152 | 14:00 | 113 | Matuail | 76 | 15:00 | 179 | Shomvuganj | 36 | 20:00
48 | Daganbhuiyan | 32 | 23:00 | 114 | Metrorail_Motijheel | 20 | 13:00 | 180 | Shyampur | 156 | 12:00
49 | Daudkandi | 139 | 20:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 131 | 12:00
50 | DhakaUniversity | 88 | 11:00 | 116 | Millgate | 115 | 12:00 | 182 | Sirajganj | 116 | 21:00
51 | Dhamrai | 104 | 19:00 | 117 | Mirpur | 148 | 14:00 | 183 | Sitakunda | 32 | 23:00
52 | Dhanmondi | 107 | 14:00 | 118 | Mirsorai | 37 | 12:00 | 184 | Sonargaon | 150 | 09:00
53 | Dohazari | 107 | 19:30 | 119 | Mirzapur | 48 | 19:00 | 185 | Sreemongol | 92 | 19:00
54 | Faridpur | 171 | 22:00 | 120 | Mithapukur | 73 | 21:00 | 186 | Sreepur | 101 | 16:00
55 | Fatullah | 104 | 15:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 46.2 | 00:00
56 | Fenchuganj | 47 | 19:00 | 122 | Mogbazar | 11.2 | 14:00 | 188 | Sunamganj | 64 | 19:00
57 | Feni | 106 | 00:00 | 123 | Mongla | 41 | 12:00 | 189 | Sylhet | 124 | 19:30
58 | GPH | 71 | 15:00 | 124 | Motijheel | 48 | 13:00 | 190 | Sylhet_(South) | 73 | 00:00
59 | Ghatail | 100 | 19:30 | 125 | Muktagacha | 41 | 19:30 | 191 | TK | 27 | 18:30
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 106 | 00:00 | 192 | Tangail | 180 | 20:00
61 | Ghorashal-230 | 106 | 05:00 | 127 | Muradnagar | 50 | 22:00 | 193 | Taraganj | 27 | 00:00
62 | Goalpara | 39 | 13:00 | 128 | Mymensingh | 153 | 01:00 | 194 | Tasnim | 46 | 01:00
63 | Gollamari | 94 | 12:00 | 129 | Nabinagar | 110 | 14:00 | 195 | Thakurgaon | 108 | 01:00
64 | Gopalganj | 104 | 19:30 | 130 | Naogaon | 138 | 00:00 | 196 | Tongi | 162 | 11:00
65 | Gulshan | 112 | 14:00 | 131 | Narail | 60 | 20:00 | 197 | Ullahpara | 36 | 00:00
66 | Halishahar | 112 | 15:00 | 132 | Narinda | 77 | 13:00 | 198 | Ullon | 71 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14891.37 | 488 |  | 15401.33
1:00 | 14510.78 | 470 |  | 15001.93
2:00 | 14194.02 | 382 |  | 14593.21
3:00 | 13808.96 | 320 |  | 14143.36
4:00 | 13592.82 | 327 |  | 13934.54
5:00 | 13298.47 | 372 |  | 13687.21
6:00 | 12626.25 | 351 |  | 12993.05
7:00 | 12949.54 | 371 |  | 13337.54
8:00 | 12881.26 | 374 |  | 13272.26
9:00 | 13199.42 | 232 |  | 13441.42
10:00 | 13759.3 | 30 |  | 13790.3
11:00 | 13947.34 | 18 |  | 13966.34
12:00 | 14290.4 | 176 |  | 14474.4
13:00 | 14392.02 | 343 |  | 14750.02
14:00 | 13635.44 | 560 |  | 14220.44
15:00 | 13912.12 | 659 |  | 14601.12
16:00 | 13479.63 | 564 |  | 14068.63
17:00 | 13290.53 | 385 |  | 13692.53
18:00 | 13183.25 | 321 |  | 13518.25
19:00 | 14464.44 | 158 |  | 14629.44
19:30 | 15371.1 | 210 |  | 15590.1
20:00 | 15310.4 | 172 |  | 15490.14
21:00 | 15384.75 | 218 |  | 15612.75
22:00 | 15204.52 | 142 |  | 15352.52
23:00 | 15077.08 | 302 |  | 15392.67
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7865 | 7026.37 | 14891.37 | DAILY GENERATION CURVE
00:30 | 7775.25 | 6925.825 | 14701.075
01:00 | 7685.5 | 6825.28 | 14510.78 | 22-07-2026
01:30 | 7579.25 | 6773.15 | 14352.4
02:00 | 7473 | 6721.02 | 14194.02
02:30 | 7358 | 6643.49 | 14001.49
03:00 | 7243 | 6565.96 | 13808.96
03:30 | 7230.5 | 6470.39 | 13700.89
04:00 | 7218 | 6374.82 | 13592.82
04:30 | 7085.5 | 6360.145 | 13445.645
05:00 | 6953 | 6345.47 | 13298.47
05:30 | 6729.715 | 6232.645 | 12962.36
06:00 | 6506.43 | 6119.82 | 12626.25
06:30 | 6506.73 | 6281.165 | 12787.895
07:00 | 6507.03 | 6442.51 | 12949.54
07:30 | 6462.105 | 6453.295 | 12915.4
08:00 | 6417.18 | 6464.08 | 12881.26
08:30 | 6463.235 | 6577.105 | 13040.34
09:00 | 6509.29 | 6690.13 | 13199.42
09:30 | 6769.21 | 6710.15 | 13479.36
10:00 | 7029.13 | 6730.17 | 13759.3
10:30 | 7201.075 | 6652.245 | 13853.32
11:00 | 7373.02 | 6574.32 | 13947.34
11:30 | 7405.775 | 6713.095 | 14118.87
12:00 | 7438.53 | 6851.87 | 14290.4
12:30 | 7546.91 | 6794.3 | 14341.21
13:00 | 7655.29 | 6736.73 | 14392.02
13:30 | 7509.53 | 6504.2 | 14013.73
14:00 | 7363.77 | 6271.67 | 13635.44
14:30 | 7473.965 | 6299.815 | 13773.78
15:00 | 7584.16 | 6327.96 | 13912.12
15:30 | 7451.63 | 6244.245 | 13695.875
16:00 | 7319.1 | 6160.53 | 13479.63
16:30 | 7281.675 | 6103.405 | 13385.08
17:00 | 7244.25 | 6046.28 | 13290.53
17:30 | 7080.42 | 6156.47 | 13236.89
18:00 | 6916.59 | 6266.66 | 13183.25
18:30 | 7281.475 | 6542.37 | 13823.845
19:00 | 7646.36 | 6818.08 | 14464.44
19:30 | 8308.36 | 7062.74 | 15371.1
20:00 | 8175.86 | 7134.54 | 15310.4
20:30 | 8079.71 | 7267.865 | 15347.575 |  | Executive Engineer
21:00 | 7983.56 | 7401.19 | 15384.75 |  | Network Operation Division
21:30 | 7893.28 | 7401.355 | 15294.635
22:00 | 7803 | 7401.52 | 15204.52
22:30 | 7743.5 | 7397.3 | 15140.8
23:00 | 7684 | 7393.08 | 15077.08

## En-Curve
QF-LDC-12
Date | 22-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2949 | 1408 | 890 | 38 | 142 | 1471.17 | 202 | 5458 | 0 | 314 | 2019.2 | 0 | 0 | 0 | 488 | DAILY ENERGY CURVE
00:30 | 2942.5 | 1436 | 890 | 38 | 140 | 1453.625 | 202.5 | 5460 | 0 | 246.5 | 1884.45 | 0 | 0 | 7.5 | 479 | 22-07-2026
01:00 | 2936 | 1464 | 890 | 38 | 138 | 1436.08 | 203 | 5462 | 0 | 179 | 1749.7 | 0 | 0 | 15 | 470
01:30 | 2953 | 1470 | 890 | 38 | 131 | 1426.55 | 203 | 5455.5 | 0 | 179 | 1589.85 | 0 | 0 | 16.5 | 426 | Energy Generated | 339.8875 |  | MKWHr
02:00 | 2970 | 1476 | 890 | 38 | 124 | 1417.02 | 203 | 5449 | 0 | 179 | 1430 | 0 | 0 | 18 | 382 | Energy not Served | 7.735 |  | MKWHr
02:30 | 2991.5 | 1466 | 890 | 38 | 127 | 1394.49 | 203 | 5428.5 | 0 | 162 | 1279.5 | 0 | 0 | 21.5 | 351 | Total Energy Requirement | 347.6225 |  | MKWHr
03:00 | 3013 | 1456 | 890 | 38 | 130 | 1371.96 | 203 | 5408 | 0 | 145 | 1129 | 0 | 0 | 25 | 320
03:30 | 3010.5 | 1464 | 890 | 38 | 128 | 1378.89 | 204 | 5305 | 0 | 130 | 1123.5 | 0 | 0 | 29 | 323.5
04:00 | 3008 | 1472 | 890 | 38 | 126 | 1385.82 | 205 | 5202 | 0 | 115 | 1118 | 0 | 0 | 33 | 327
04:30 | 2994.5 | 1472.5 | 890 | 38 | 124 | 1388.645 | 205 | 5196.5 | 0 | 115 | 985.5 | 0 | 0 | 36 | 349.5
05:00 | 2981 | 1473 | 890 | 38 | 122 | 1391.47 | 205 | 5191 | 0 | 115 | 853 | 0 | 0 | 39 | 372
05:30 | 2982 | 1445 | 890 | 38 | 121 | 1386.23 | 205 | 5189.5 | 13.63 | 107 | 558.5 | 0 | 0 | 26.5 | 361.5
06:00 | 2983 | 1417 | 890 | 38 | 120 | 1380.99 | 205 | 5188 | 27.26 | 99 | 264 | 0 | 0 | 14 | 351
06:30 | 2978 | 1448 | 890 | 38 | 119 | 1418.39 | 204 | 5267.5 | 70.505 | 99 | 238.5 | 0 | 0 | 17 | 361
07:00 | 2973 | 1479 | 890 | 38 | 118 | 1455.79 | 203 | 5347 | 113.75 | 99 | 213 | 0 | 0 | 20 | 371
07:30 | 2908.5 | 1439.75 | 890 | 38 | 118 | 1439.225 | 207.5 | 5342.5 | 167.925 | 99 | 230 | 0 | 0 | 35 | 372.5
08:00 | 2844 | 1400.5 | 890 | 38 | 118 | 1422.66 | 212 | 5338 | 222.1 | 99 | 247 | 0 | 0 | 50 | 374
08:30 | 2877.5 | 1417.5 | 889.5 | 38 | 120 | 1422.65 | 217 | 5359 | 243.19 | 133 | 283 | 0 | 0 | 40 | 303
09:00 | 2911 | 1434.5 | 889 | 38 | 122 | 1422.64 | 222 | 5380 | 264.28 | 167 | 319 | 0 | 0 | 30 | 232
09:30 | 2874.5 | 1437 | 889 | 38 | 122 | 1431.595 | 222 | 5405 | 336.765 | 272 | 426 | 0 | 0 | 25.5 | 131
10:00 | 2838 | 1439.5 | 889 | 38 | 122 | 1440.55 | 222 | 5430 | 409.25 | 377 | 533 | 0 | 0 | 21 | 30
10:30 | 2842 | 1403.5 | 893 | 38 | 130 | 1397.895 | 222 | 5439 | 398.425 | 369 | 701 | 0 | 0 | 19.5 | 24
11:00 | 2846 | 1367.5 | 897 | 38 | 138 | 1355.24 | 222 | 5448 | 387.6 | 361 | 869 | 0 | 0 | 18 | 18
11:30 | 2810.5 | 1394.5 | 896.5 | 38 | 136 | 1370.66 | 222 | 5515.5 | 421.71 | 353.5 | 935.5 | 0 | 0 | 24.5 | 97
12:00 | 2775 | 1421.5 | 896 | 38 | 134 | 1386.08 | 222 | 5583 | 455.82 | 346 | 1002 | 0 | 0 | 31 | 176
12:30 | 2722.5 | 1412 | 896 | 38 | 134 | 1354.845 | 222 | 5644 | 454.365 | 357.5 | 1075.5 | 0 | 0 | 30.5 | 259.5
13:00 | 2670 | 1402.5 | 896 | 38 | 134 | 1323.61 | 222 | 5705 | 452.91 | 369 | 1149 | 0 | 0 | 30 | 343
13:30 | 2653.5 | 1383.25 | 870.5 | 38 | 143 | 1309.975 | 222 | 5568.5 | 384.505 | 237.5 | 1171 | 0 | 0 | 32 | 451.5
14:00 | 2637 | 1364 | 845 | 38 | 152 | 1296.34 | 222 | 5432 | 316.1 | 106 | 1193 | 0 | 0 | 34 | 560
14:30 | 2674 | 1379.25 | 870 | 38 | 152 | 1313.435 | 222 | 5356.5 | 349.595 | 105.5 | 1284.5 | 0 | 0 | 29 | 609.5
15:00 | 2711 | 1394.5 | 895 | 38 | 152 | 1330.53 | 222 | 5281 | 383.09 | 105 | 1376 | 0 | 0 | 24 | 659
15:30 | 2713 | 1387.5 | 895.5 | 38 | 144 | 1302.145 | 222 | 5312.5 | 285.23 | 105 | 1269.5 | 0 | 0 | 21.5 | 611.5
16:00 | 2715 | 1380.5 | 896 | 38 | 136 | 1273.76 | 222 | 5344 | 187.37 | 105 | 1163 | 0 | 0 | 19 | 564
16:30 | 2725.5 | 1384.25 | 896 | 38 | 125 | 1227.075 | 222 | 5351 | 159.255 | 105 | 1125 | 0 | 0 | 27 | 474.5
17:00 | 2736 | 1388 | 896 | 38 | 114 | 1180.39 | 222 | 5358 | 131.14 | 105 | 1087 | 0 | 0 | 35 | 385
17:30 | 2746 | 1405.5 | 896 | 38 | 117 | 1212.355 | 222 | 5430.5 | 73.535 | 105 | 964.5 | 0 | 0 | 26.5 | 353
18:00 | 2756 | 1423 | 896 | 38 | 120 | 1244.32 | 222 | 5503 | 15.93 | 105 | 842 | 0 | 0 | 18 | 321
18:30 | 2763 | 1422 | 896 | 38 | 130 | 1277.7 | 222 | 5661 | 7.965 | 326 | 1065.18 | 0 | 0 | 15 | 239.5
19:00 | 2770 | 1421 | 896 | 38 | 140 | 1311.08 | 222 | 5819 | 0 | 547 | 1288.36 | 0 | 0 | 12 | 158
19:30 | 2769 | 1318 | 845 | 38 | 138 | 1287.74 | 222 | 5924 | 0 | 691 | 2121.36 | 0 | 0 | 17 | 210
20:00 | 2731 | 1353.5 | 895 | 38 | 146 | 1289.54 | 220 | 5881 | 0 | 725 | 2011.36 | 0 | 0 | 20 | 172
20:30 | 2758 | 1394.75 | 895.5 | 38 | 138 | 1383.865 | 220 | 5974.5 | 0 | 723.1 | 1811.86 | 0 | 0 | 10 | 195
21:00 | 2785 | 1436 | 896 | 38 | 130 | 1478.19 | 220 | 6068 | 0 | 721.2 | 1612.36 | 0 | 0 | 0 | 218
21:30 | 2780 | 1430 | 896 | 38 | 134 | 1481.855 | 220 | 6100 | 0 | 687.1 | 1525.68 | 0 | 0 | 2 | 180
22:00 | 2775 | 1424 | 896 | 38 | 138 | 1485.52 | 220 | 6132 | 0 | 653 | 1439 | 0 | 0 | 4 | 142
22:30 | 2767.5 | 1436 | 896 | 38 | 137 | 1484.3 | 220.5 | 6149.5 | 0 | 606 | 1400 | 0 | 0 | 6 | 222
23:00 | 2760 | 1448 | 896 | 38 | 136 | 1483.08 | 221 | 6167 | 0 | 559 | 1361 | 0 | 0 | 8 | 302
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 22-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 138 | 27 | 470 | 198 | 1560 | 578 | Ishurdi-Ghorashal Ckt-1 | Export | 3638181.82
1:00 | 125 | 27 | 448 | 196 | 1522 | 584
2:00 | 132 | 34 | 464 | 210 | 1552 | 606 |  | Import | 0
3:00 | 135 | 38 | 470 | 226 | 1558 | 640
4:00 | 142 | 44 | 486 | 222 | 1510 | 658 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 151 | 50 | 482 | 214 | 1552 | 674
6:00 | 157 | 52 | 502 | 204 | 1566 | 684 |  | Import | 0
7:00 | 161 | 52 | 510 | 210 | 1678 | 688
8:00 | 177 | 58 | 560 | 230 | 1248 | 740 | Sirajganj-Sreepur Ckt-1 | Export | 3212000
9:00 | 201 | 81 | 596 | 232 | 2028 | 860
10:00 | 208 | 77 | 616 | 248 | 2064 | 926 |  | Import | 0
11:00 | 178 | 61 | 554 | 238 | 1914 | 888
12:00 | 170 | 59 | 430 | 232 | 1922 | 840 | Sirajganj-Sreepur Ckt-2 | Export | 3179000
13:00 | 153 | 39 | 480 | 204 | 1918 | 810
14:00 | 136 | 49 | 420 | 236 | 1568 | 812 |  | Import | 0
15:00 | 164 | 59 | 514 | 250 | 1746 | 838
16:00 | 155 | 51 | 496 | 240 | 1816 | 812 | Gopalganj-Aminbazar Ckt-1 | Export | 21520000
17:00 | 161 | 58 | 462 | 232 | 1734 | 830
18:00 | 163 | 59 | 500 | 238 | 2056 | 798 |  | Import | 0
18:30 | 161 | 60 | 496 | 230 | 2022 | 780
19:00 | 139 | 48 | 454 | 246 | 1332 | 716 | Gopalganj-Aminbazar Ckt-2 | Export | 21540000
19:30 | 109 | 35 | 356 | 224 | 1750 | 680
20:00 | 117 | 27 | 380 | 212 | 1774 | 668 |  | Import | 0
21:00 | 131 | 24 | 438 | 202 | 1954 | 698
22:00 | 121 | 21 | 420 | 194 | 1930 | 614 |  | Total Export | 53089181.82
23:00 | 125 | 27 | 426 | 206 | 1934 | 600 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 359 | 17:00 | 351 | 21:00 | Madunaghat | 386 | 01:00 | 380 | 12:00
Amtali | 411 | 06:00 | 401 | 23:00 | Meghnaghat | 372 | 05:00 | 351 | 12:00
Ashuganj | 389 | 6:00 | 368 | 12:00 | Payra | 411 | 03:00 | 404 | 23:00
Bhulta | 394 | 00:00 | 362 | 12:00 | Rahanpur | 399 | 17:00 | 385 | 21:00
Bibiana | 374 | 01:00 | 365 | 12:00 | Rampal | 390 | 05:00 | 377 | 23:00
BIPTC | 403 | 14:00 | 396 | 11:00
Bogura | 380 | 05:00 | 364 | 22:00
Gopalganj | 385 | 05:00 | 370 | 12:00
Kaliakoir | 357 | 04:00 | 318 | 20:00
Korerhat | 383 | 04:00 | 374 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 04:00 | 208 | 12:00 | Ishurdi | 232 | 05:00 | 217 | 21:00
AKSML | 230 | 00:00 | 225 | 11:00 | Jhenaidah | 224 | 05:00 | 206 | 21:00
Aminbazar | 218 | 18:30 | 214 | 21:00 | Kachua | 219 | 05:00 | 210 | 23:00
Ashuganj | 221 | 06:00 | 212 | 21:00 | Kaliakoir | 222 | 01:00 | 207 | 12:00
Ashuganj-400 | 221 | 06:00 | 212 | 21:00 | Keranigonj | 221 | 05:00 | 206 | 12:00
Baghabari | 230 | 06:00 | 219 | 21:00 | Khulna(S) | 224 | 06:00 | 209 | 21:00
Barapukuria | 224 | 18:30 | 215 | 21:00 | Korerhat | 219 | 00:00 | 213 | 22:00
Barapukuria-230 | 224 | 18:30 | 215 | 21:00 | Madunaghat | 234 | 00:00 | 230 | 12:00
Barishal | 226 | 04:00 | 218 | 22:00 | Madunaghat-400 | 236 | 00:00 | 231 | 12:00
Bheramara | 235 | 05:00 | 214 | 21:00 | Maniknagar | 218 | 03:00 | 203 | 12:00
Bhulta | 226 | 00:00 | 206 | 12:00 | Meghnaghat | 226 | 06:00 | 213 | 11:00
Bibiana | 216 | 04:00 | 210 | 12:00 | Meghnaghat-400 | 222 | 04:00 | 209 | 12:00
BIPTC | 234 | 06:00 | 215 | 21:00 | Mirsorai | 223 | 00:00 | 218 | 22:00
Bogura | 238 | 05:00 | 228 | 21:00 | Naogaon | 223 | 05:00 | 204 | 21:00
Bogura-400 | 238 | 04:00 | 228 | 22:00 | Purbasadipur | 221 | 05:00 | 212 | 21:00
Borhanuddin | 229 | 05:00 | 223 | 23:00 | Rajshahi | 230 | 17:00 | 214 | 21:00
BSRM | 221 | 04:00 | 215 | 22:00 | Rampal | 222 | 05:00 | 211 | 21:00
Charfasson | 229 | 13:00 | 226 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 219 | 05:00 | 214 | 10:00 | Rampura | 220 | 04:00 | 205 | 12:00
Cumilla(N) | 218 | 06:00 | 208 | 12:00 | Shikalbaha | 235 | 19:00 | 229 | 07:00
Faridpur | 222 | 06:00 | 211 | 22:00 | Shyampur | 221 | 04:00 | 206 | 12:00
Fenchuganj | 219 | 06:00 | 211 | 12:00 | Siddhirganj | 220 | 05:00 | 207 | 12:00
Feni | 217 | 00:00 | 210 | 23:00 | Sirajgonj | 236 | 04:00 | 227 | 21:00
Ghorashal | 222 | 02:00 | 220 | 00:00 | Sreepur | 219 | 06:00 | 209 | 21:00
Ghorashal-230 | 209 | 01:00 | 194 | 12:00 | Tongi | 212 | 00:00 | 195 | 09:00
Gopalganj | 223 | 05:00 | 213 | 23:00
GPH | 229 | 19:30 | 223 | 23:00
Haripur | 221 | 06:00 | 207 | 11:00
Hasnabad | 220 | 04:00 | 207 | 11:00
Hathazari | 232 | 00:00 | 226 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 130 | 03:00 | 123 | 11:00 | Madunaghat | 135 | 00:00 | 132 | 22:00
Agargaon | 131 | 04:00 | 120 | 12:00 | Magura | 134 | 17:00 | 120 | 21:00
Agrabad | 134 | 19:30 | 130 | 10:00 | Mahasthangarh | 134 | 00:00 | 126 | 21:00
AKS | 132 | 01:00 | 128 | 12:00 | Maijdee | 123 | 16:00 | 118 | 22:00
Aminbazar | 124 | 17:00 | 121 | 21:00 | Manikganj | 126 | 01:00 | 119 | 09:00
Amnura | 134 | 00:00 | 125 | 12:00 | Maniknagar | 129 | 03:00 | 117 | 12:00
Ashuganj | 125 | 00:00 | 120 | 21:00 | Matarbari | 129 | 06:00 | 114 | 21:00
Ashuganj-230 | 130 | 01:00 | 126 | 12:00 | Matuail | 127 | 04:00 | 120 | 10:00
Bagerhat | 127 | 17:00 | 116 | 22:00 | Metrorail_Motijheel | 129 | 04:00 | 117 | 12:00
Bajitpur | 121 | 05:00 | 114 | 22:00 | Metrorail_Uttara | 129 | 01:00 | 115 | 12:00
Bakerganj | 131 | 08:00 | 128 | 00:00 | Millgate | 130 | 01:00 | 116 | 09:00
Bakulia | 134 | 00:00 | 129 | 22:00 | Mirpur | 126 | 01:00 | 117 | 11:00
Banani | 131 | 05:00 | 122 | 12:00 | Mirzapur | 126 | 00:00 | 120 | 21:00
Bangabhaban | 128 | 03:00 | 117 | 12:00 | Mithapukur | 134 | 19:00 | 125 | 07:00
Barapukuria | 136 | 04:00 | 127 | 21:00 | MI_Cement | 130 | 04:00 | 119 | 12:00
Barguna | 129 | 04:00 | 124 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 129 | 00:00 | 125 | 12:00 | Mogbazar | 132 | 04:00 | 125 | 10:00
Barishal-230 | 131 | 04:00 | 125 | 12:00 | Mongla | 126 | 06:00 | 116 | 21:00
Baroaulia | 134 | 00:00 | 130 | 21:00 | Motijheel | 128 | 03:00 | 117 | 12:00
Baroirhat | 127 | 00:00 | 123 | 10:00 | Muktagacha | 125 | 23:00 | 114 | 04:00
Bashundhara | 131 | 06:00 | 116 | 09:00 | Munshiganj | 126 | 04:00 | 119 | 11:00
BashundharaCement | 126 | 07:00 | 120 | 10:00 | Muradnagar | 122 | 06:00 | 116 | 21:00
Beanibazar | 122 | 06:00 | 115 | 22:00 | Mymensingh | 127 | 23:00 | 107 | 19:30
Benapole | 130 | 05:00 | 114 | 21:00 | Nabinagar | 125 | 01:00 | 114 | 12:00
Bhaluka | 121 | 11:00 | 116 | 15:00 | Naogaon | 134 | 04:00 | 123 | 21:00
Bhandaria | 127 | 06:00 | 121 | 21:00 | Narail | 135 | 06:00 | 120 | 21:00
Bhangura | 133 | 06:00 | 126 | 21:00 | Narinda | 129 | 03:00 | 117 | 12:00
Bheramara | 138 | 05:00 | 126 | 21:00 | Narshingdi | 123 | 08:00 | 112 | 10:00
Bheramara(GK) | 136 | 05:00 | 126 | 21:00 | Natore | 133 | 06:00 | 125 | 21:00
Bhulta | 121 | 07:00 | 118 | 11:00 | Nawabganj | 130 | 06:00 | 120 | 12:00
Bog-Sherpur | 135 | 05:00 | 127 | 21:00 | Netrakona | 112 | 05:00 | 103 | 19:00
Bogura | 137 | 01:00 | 130 | 21:00 | New | 129 | 00:00 | 118 | 09:00
Bogura-230 | 137 | 00:00 | 130 | 21:00 | Niamatpur | 132 | 17:00 | 125 | 00:00
Brahmanbaria | 122 | 01:00 | 118 | 21:00 | Noapara | 131 | 05:00 | 122 | 21:00
Cantonment | 132 | 05:00 | 121 | 12:00 | Pabna | 134 | 06:00 | 125 | 21:00
Chandina | 125 | 04:00 | 120 | 11:00 | Palashbari | 131 | 19:00 | 121 | 21:00
Chandpur | 127 | 00:00 | 119 | 23:00 | Panchagarh | 141 | 19:00 | 132 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 00:00 | 133 | 10:00 | Patiya | 134 | 19:30 | 128 | 22:00
Chapai | 132 | 18:00 | 124 | 23:00 | Patnitala | 131 | 06:00 | 124 | 21:00
Charsaidpur | 127 | 06:00 | 120 | 10:00 | Patuakhali | 130 | 01:00 | 124 | 22:00
Chauddagram | 125 | 05:00 | 119 | 23:00 | Payra | 134 | 05:00 | 131 | 22:00
Chhatak | 121 | 05:00 | 112 | 00:00 | PHP | 127 | 06:00 | 122 | 23:00
Chowmuhani | 123 | 16:00 | 119 | 22:00 | Postogola | 132 | 05:00 | 121 | 12:00
Chuadanga | 132 | 05:00 | 117 | 21:00 | Pubail | 123 | 00:00 | 115 | 09:00
Coxsbazar | 128 | 17:00 | 115 | 22:00 | Purbachal | 130 | 03:00 | 122 | 11:00
Cumilla(N) | 126 | 06:00 | 120 | 11:00 | Purbasadipur | 134 | 04:00 | 128 | 21:00
Cumilla(S) | 129 | 05:00 | 120 | 11:00 | Rahanpur | 134 | 17:00 | 128 | 21:00
Daganbhuiyan | 125 | 00:00 | 120 | 23:00 | Rahanpur-400 | 134 | 17:00 | 129 | 21:00
Daudkandi | 123 | 05:00 | 115 | 10:00 | Rahim | 128 | 05:00 | 120 | 10:00
DhakaUniversity | 131 | 05:00 | 122 | 12:00 | Rajbari | 125 | 04:00 | 118 | 22:00
Dhamrai | 128 | 03:00 | 115 | 12:00 | Rajendrapur | 122 | 05:00 | 116 | 12:00
Dhanmondi | 132 | 05:00 | 122 | 12:00 | Rajshahi | 132 | 17:00 | 124 | 21:00
Dohazari | 132 | 17:00 | 124 | 22:00 | Rajshahi-230 | 133 | 18:30 | 123 | 21:00
Faridpur | 127 | 04:00 | 123 | 22:00 | Ramganj | 124 | 16:00 | 116 | 23:00
Fatullah | 131 | 05:00 | 118 | 11:00 | Rampur | 134 | 00:00 | 129 | 18:00
Fenchuganj | 129 | 06:00 | 123 | 12:00 | Rampura | 130 | 04:00 | 122 | 12:00
Feni | 125 | 00:00 | 121 | 21:00 | Rangamati | 135 | 00:00 | 132 | 10:00
Feni-230 | 126 | 05:00 | 121 | 23:00 | Rangpur | 131 | 05:00 | 123 | 23:00
Ghatail | 124 | 23:00 | 111 | 21:00 | Ruppur | 136 | 17:00 | 127 | 21:00
Ghorashal | 125 | 01:00 | 119 | 09:00 | Saidpur | 135 | 18:30 | 128 | 23:00
Goalpara | 133 | 04:00 | 125 | 21:00 | Santhia | 133 | 04:00 | 126 | 21:00
Gollamari | 134 | 06:00 | 124 | 21:00 | Satkhira | 130 | 06:00 | 118 | 22:00
Gopalganj | 128 | 05:00 | 120 | 23:00 | Satmasjid | 131 | 04:00 | 121 | 12:00
Gopalganj-400 | 130 | 04:00 | 124 | 22:00 | Savar | 127 | 02:00 | 114 | 12:00
Gulshan | 130 | 05:00 | 122 | 12:00 | SevenRings | 125 | 00:00 | 118 | 09:00
Halishahar | 135 | 02:00 | 130 | 10:00 | ShahCement | 127 | 06:00 | 120 | 10:00
Haripur | 127 | 05:00 | 121 | 10:00 | Shahjadpur | 135 | 04:00 | 130 | 21:00
HaripurSBU | 128 | 05:00 | 121 | 10:00 | Shahjibazar | 123 | 06:00 | 114 | 22:00
Hasnabad | 133 | 04:00 | 121 | 11:00 | Shahmirpur | 135 | 00:00 | 130 | 19:00
Hathazari | 140 | 21:00 | 132 | 22:00 | Shariatpur | 128 | 05:00 | 122 | 21:00
Hatirjheel | 130 | 04:00 | 122 | 12:00 | Sherpur | 128 | 23:00 | 109 | 07:00
Ishurdi | 137 | 05:00 | 128 | 21:00 | Shikalbaha | 125 | 01:00 | 120 | 12:00
Jaldhaka | 131 | 05:00 | 124 | 21:00 | Shikalbaha-230 | 136 | 19:00 | 131 | 18:00
Jamalpur | 131 | 23:00 | 114 | 02:00 | Shitalakhya | 130 | 04:00 | 119 | 12:00
Jashore | 132 | 05:00 | 118 | 23:00 | Sholosohor | 135 | 20:00 | 131 | 18:00
Jhenaidah | 136 | 17:00 | 123 | 21:00 | Shomvuganj | 115 | 03:00 | 109 | 22:00
Jhenaidah-230 | 137 | 06:00 | 124 | 21:00 | Shyampur | 128 | 01:00 | 119 | 12:00
Joydebpur | 121 | 19:00 | 113 | 09:00 | Shyampur-230 | 129 | 04:00 | 121 | 10:00
Joypurhat | 132 | 03:00 | 124 | 21:00 | Siddhirganj | 128 | 04:00 | 120 | 12:00
Juldah | 135 | 00:00 | 130 | 18:00 | Sirajganj | 130 | 04:00 | 124 | 22:00
Kabirpur | 129 | 00:00 | 112 | 09:00 | Sitakunda | 135 | 01:00 | 131 | 13:00
Kachua | 125 | 16:00 | 119 | 23:00 | Sonargaon | 125 | 06:00 | 118 | 10:00
Kaliakoir | 131 | 01:00 | 120 | 12:00 | Sreemongol | 124 | 06:00 | 116 | 22:00
Kaliganj | 135 | 06:00 | 121 | 21:00 | Sreepur | 125 | 06:00 | 119 | 21:00
Kallyanpur | 127 | 02:00 | 116 | 11:00 | Srinagar | 130 | 04:00 | 120 | 12:00
Kalurghat | 134 | 00:00 | 132 | 10:00 | SSM | 140 | 01:00 | 136 | 09:00
Kamrangirchar | 132 | 04:00 | 113 | 12:00 | Sunamganj | 117 | 06:00 | 109 | 19:00
Kaptai | 137 | 9:00 | 135 | 12:00 | Sylhet | 123 | 05:00 | 118 | 13:00
Kasba | 122 | 06:00 | 115 | 21:00 | Sylhet_(South) | 123 | 06:00 | 118 | 00:00
Kazla | 129 | 06:00 | 116 | 13:00 | Tangail | 123 | 16:00 | 114 | 21:00
Keranigonj | 131 | 05:00 | 121 | 12:00 | Taraganj | 132 | 03:00 | 126 | 21:00
Khagrachori | 134 | 00:00 | 130 | 18:30 | Tasnim | 125 | 06:00 | 118 | 10:00
Khulna | 133 | 16:00 | 123 | 23:00 | Thakurgaon | 140 | 19:00 | 131 | 12:00
Khulna(S) | 134 | 05:00 | 125 | 21:00 | TK | 136 | 19:30 | 132 | 22:00
Khulshi | 133 | 01:00 | 128 | 18:30 | Tongi | 130 | 04:00 | 120 | 09:00
Kishoreganj | 118 | 03:00 | 113 | 19:00 | Ullahpara | 133 | 04:00 | 125 | 21:00
Kodda | 128 | 00:00 | 115 | 15:00 | Ullon | 130 | 04:00 | 123 | 11:00
Korerhat | 129 | 00:00 | 126 | 22:00 | Uttara | 129 | 05:00 | 115 | 09:00
KSRM | 135 | 00:00 | 129 | 12:00 | UttaraNew | 129 | 01:00 | 115 | 12:00
Kulaura | 128 | 06:00 | 122 | 12:00 | Zigatola | 131 | 05:00 | 120 | 12:00
Kurigram | 131 | 04:00 | 120 | 21:00
Kushtia | 132 | 05:00 | 123 | 12:00
Laksam | 124 | 01:00 | 118 | 23:00
Lakshmipur | 123 | 16:00 | 117 | 22:00
Lalbag | 130 | 02:00 | 120 | 12:00
Lalmonirhat | 128 | 19:00 | 118 | 23:00
Madanganj | 126 | 07:00 | 120 | 10:00
Madaripur | 129 | 05:00 | 124 | 23:00
Madartek | 130 | 04:00 | 122 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division