## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-07-2026 | during | 24-07-2026 | during | 24-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 300 | 300 | 412 | 412 | 300 | 300 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 225 | 225 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 120 | 142 | 335 | 335 | 335 | 335 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 270 | 330 | 335 | 335 | 270 | 270 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 125 | 128 | 149.36 | 149.36 | 48 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 5 | 8 | 33 | 33 | 9 | 9 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 25 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 195 | 113 | 300 | 300 | 48 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 115 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 34 | 88 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 90 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 3 | 0 | 8 | 0 | 8 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 23.297 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 285 | 330 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 232 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 123 | 143 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6637.271 | 1933 | 2028 | 5783.64 | 5775.64 | 2178.12 | 2711.12
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 1 | 0 | 8 | 0 | 8 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 222 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 172 | 194 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 28 | 90 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 44 | 40 | 72 | 40 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 34 | 0 | 34 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 20 | 50 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 3 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 82 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.63 | 0 | 1.57 | 0 | 1.57 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 70 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 54 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 40 | 102 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 50 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 10 | 60 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 27 | 90 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1195 | 1180 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 8 | 8 | 23 | 6 | 23 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 1125 | 1150 | 1150 | 720 | 720 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2971.63 | 3525.36 | 4120.43 | 4183.86 | 3048.57 | 3137
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 192 | 156 | 221.25 | 221.25 | 185 | 185 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 280 | 280 | 350.01 | 350.01 | 300 | 300 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 220 | 200 | 342.01 | 342.01 | 300 | 300 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 41 | 100 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 16 | 32 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 143 | 163 | 163 | 150 | 150 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 105 | 170 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 128 | 148 | 84 | 78 | 150 | 150 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 65 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 28 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 32 | 68 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 18 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1276 | 1494 | 2351.44 | 2295.44 | 1482.2 | 1678.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-07-2026 | during | 24-07-2026 | during | 24-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 7.1 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 124 | 152 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 47 | 66 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 10.99 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 202.19 | 235 | 534.6 | 516.5 | 277.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 41 | 41 | 41 | 41 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 139 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 143 | 0 | 142 | 142 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 25 | 25 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 33 | 86 | 86 | 5 | 5 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 100 | 100 | 100 | 100 | 100 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 8 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 327 | 292 | 385 | 385 | 357 | 357 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1106 | 914 | 1333 | 1333 | 999 | 999
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 901 | 884 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 36 | 27 | 27 | 27 | 27 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 34 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1123 | 1140 | 1234.2 | 1234.2 | 1194.2 | 1194.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2096 | 2113 | 3601.2 | 3531.2 | 2344.2 | 2274.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 644 | 1050 | 700 | 1050 | 700 | 1050 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 64 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 1116 | 1140 | 1163.05 | 1163.05 | 1163.05 | 1163.05 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 230 | 307 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.11 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2330.11 | 2955 | 2781.05 | 3130.05 | 2607.05 | 2956.05
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 27.46 | 0 | 55 | 0 | 55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 150 | 140 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 274 | 250 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 101 | 100 | 100 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 10 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 6.06 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1109.5 | 1145.94 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | Machine Problem
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.27 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 27 | 0 | 90 | 0 | 90 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1703.29 | 1802.94 | 3254.62 | 3043.12 | 2361.24 | 2311.74
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 195 | 190 | 190 | 190 | 185 | 185 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 100 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.9 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 68 | 92 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 199 | 0 | 182.5 | 0 | 182.5 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 488.9 | 382 | 667.5 | 452 | 538.5 | 358
System Total |  |  |  |  | 28843.2 | 29137.464 | 14107.12 | 15449.3 | 24427.48 | 24260.81 | 15835.98 | 16684.31
Forecast Scenario (24-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15500 |  | 0 |  | 15500
|  |  |  | 1:00 | 15180 |  | 0 |  | 15180
|  |  |  | 2:00 | 14880 |  | 0 |  | 14880
|  |  |  | 3:00 | 14470 |  | 0 |  | 14470
|  |  |  | 4:00 | 13960 |  | 0 |  | 13960
|  |  |  | 5:00 | 13570 |  | 0 |  | 13570
|  |  |  | 6:00 | 12850 |  | 0 |  | 12850
|  |  |  | 7:00 | 12650 |  | 0 |  | 12650
|  |  |  | 8:00 | 12520 |  | 0 |  | 12520
|  |  |  | 9:00 | 12490 |  | 0 |  | 12490
|  |  |  | 10:00 | 12400 |  | 0 |  | 12400
|  |  |  | 11:00 | 12560 |  | 0 |  | 12560
|  |  |  | 12:00 | 13080 |  | 0 |  | 13080
|  |  |  | 13:00 | 13800 |  | 0 |  | 13800
|  |  |  | 14:00 | 13360 |  | 0 |  | 13360
|  |  |  | 15:00 | 13230 |  | 0 |  | 13230
|  |  |  | 16:00 | 12660 |  | 0 |  | 12660
|  |  |  | 17:00 | 12200 |  | 0 |  | 12200
|  |  |  | 18:00 | 11960 |  | 0 |  | 11960
|  |  |  | 18:30 | 12500 |  | 0 |  | 12500
|  |  |  | 19:00 | 13280 |  | 0 |  | 13280
|  |  |  | 19:30 | 14450 |  | 0 |  | 14450
|  |  |  | 20:00 | 14600 |  | 0 |  | 14600
|  |  |  | 21:00 | 15100 |  | 0 |  | 15100
|  |  |  | 22:00 | 15190 |  | 0 |  | 15190
|  |  |  | 23:00 | 15300 |  | 0 |  | 15300
Probable Maximum Temperature: |  |  | 31.90°C
Probable Maximum Demand at Day Peak: |  |  | 13080.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 326.79 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:22 hrs on 24-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-07-2026 | [28 empty] | Date: | 23-07-2026 | [28 empty] | Date: | 23-07-2026 | [28 empty] | Date: | 23-07-2026 | [28 empty] | Date: | 23-07-2026 | [18 empty] | Date: | 23-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [18 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 23.297 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 226 | 0 | 17 | 37 | 145 | 295 | 55 | 35 | 50 | 0 | 0 | 115 | 285 | 0 | 0 | 270 | 0 | 0 | 0 | 105 | 8 | 22 | 0 | 0 | 15 | 15 | 13 | 0 | 7 | 34 | 40 | 34 | 12 | 25 | 0 | 221 | 49 | 2 | 1125 | 16 | 0 | 19 | 8 | 15 | 161 | 0 | 0 | 0 | 1190 | 0 | 12 | 0 | 0 | 280 | 220 | 51 | 0 | 216 | 0 | 53 | 144 | 49 | 0 | 19 | 17 | 142 | 0 | 0 | 24 | 295 | 0 | 360 | 42 | 0 | 140 | 0 | 17 | 0 | 5 | 0 | 142 | 0 | 102 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 7421 | 897 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1205 | 0 | 0 | 0 | 1478.23 | 0 | 40 | 0 | 35 | 35 | 0 | 50 | 25 | 8 | 0 | 0 | 18 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 185 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 274 | 120 | 180 | 0 | 1003 | 1130 | 16 | 7305.23 | 14726.23 | 103.26
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 230 | 0 | 17 | 35 | 76 | 65 | 55 | 35 | 51 | 0 | 0 | 115 | 287 | 0 | 0 | 270 | 0 | 0 | 0 | 68 | 9 | 22 | 0 | 0 | 16 | 15 | 12 | 0 | 2 | 34 | 31 | 54.36 | 12 | 25 | 0 | 221 | 105 | 10 | 1125 | 17 | 0 | 19 | 8 | 14 | 161 | 0 | 0 | 0 | 1190 | 0 | 12 | 0 | 0 | 280 | 220 | 51 | 0 | 215 | 0 | 69 | 144 | 77 | 0 | 19 | 16 | 138 | 0 | 0 | 24 | 295 | 0 | 350 | 42 | 0 | 142 | 0 | 17 | 0 | 5 | 0 | 143 | 0 | 102 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 7192.36 | 896 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1194 | 0 | 0 | 0 | 1469.57 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 25 | 8 | 0 | 0 | 18 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 184 | 0 | 47 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 276 | 120 | 220 | 0 | 800 | 1100 | 16 | 7002.57 | 14194.93 | 103.25
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 226 | 0 | 17 | 35 | 76 | 65 | 55 | 35 | 49 | 0 | 0 | 115 | 280 | 0 | 0 | 270 | 0 | 0 | 0 | 68 | 9 | 22 | 0 | 0 | 0 | 0 | 10 | 0 | 8 | 0 | 0 | 0 | 0 | 25 | 0 | 221 | 104 | 22 | 1125 | 0 | 0 | 19 | 0 | 14 | 161 | 0 | 0 | 0 | 1190 | 0 | 12 | 0 | 0 | 280 | 220 | 51 | 0 | 216 | 0 | 0 | 144 | 81 | 0 | 19 | 0 | 134 | 0 | 0 | 24 | 300 | 0 | 368 | 42 | 0 | 131 | 0 | 17 | 0 | 5 | 0 | 143 | 0 | 102 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 6935 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1207 | 0 | 0 | 0 | 1466.65 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 185 | 0 | 32 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 277 | 120 | 220 | 0 | 800 | 1100 | 16 | 6905.65 | 13840.65 | 103.25
03:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 223 | 0 | 17 | 35 | 76 | 65 | 55 | 0 | 34 | 0 | 0 | 115 | 280 | 0 | 0 | 270 | 0 | 0 | 0 | 68 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 25 | 0 | 222 | 105 | 34 | 1125 | 0 | 0 | 6 | 0 | 14 | 161 | 0 | 0 | 0 | 1190 | 0 | 12 | 0 | 0 | 280 | 220 | 51 | 0 | 216 | 0 | 0 | 144 | 74 | 0 | 19 | 0 | 132 | 0 | 0 | 24 | 295 | 0 | 368 | 42 | 0 | 128 | 0 | 17 | 0 | 5 | 0 | 143 | 0 | 102 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 6857 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1205 | 0 | 0 | 0 | 1481.8 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 185 | 0 | 33 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 276 | 120 | 220 | 0 | 621 | 1086 | 16 | 6735.8 | 13592.8 | 103.24
04:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 227 | 0 | 17 | 35 | 76 | 65 | 30 | 0 | 0 | 0 | 0 | 115 | 285 | 0 | 0 | 270 | 0 | 0 | 0 | 68 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 25 | 0 | 222 | 85 | 34 | 1125 | 0 | 0 | 1 | 0 | 15 | 161 | 0 | 0 | 0 | 1190 | 0 | 12 | 0 | 0 | 280 | 220 | 51 | 0 | 215 | 0 | 0 | 144 | 17 | 0 | 19 | 0 | 126 | 0 | 0 | 24 | 295 | 0 | 368 | 42 | 0 | 137 | 0 | 17 | 0 | 5 | 0 | 142 | 0 | 102 | 0 | 47 | 0 | 48 | 0 | 0 | 0 | 12 | 6723 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1207 | 0 | 0 | 0 | 1429.02 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 185 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 276 | 120 | 220 | 0 | 500 | 1090 | 5 | 6514.02 | 13237.02 | 103.24
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 225 | 0 | 17 | 35 | 76 | 30 | 15 | 0 | 0 | 0 | 0 | 115 | 285 | 0 | 0 | 270 | 0 | 0 | 0 | 68 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 32 | 1125 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1190 | 0 | 0 | 0 | 0 | 280 | 220 | 51 | 0 | 215 | 0 | 0 | 144 | 0 | 0 | 19 | 0 | 118 | 0 | 0 | 24 | 295 | 0 | 368 | 42 | 0 | 141 | 0 | 17 | 0 | 5 | 0 | 143 | 0 | 102 | 0 | 47 | 0 | 48 | 0 | 0 | 0 | 12 | 6506 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 0 | 0 | 0 | 1432.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 120 | 220 | 0 | 500 | 1100 | 0 | 6433.6 | 12939.6 | 103.23
06:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 230 | 0 | 17 | 35 | 76 | 15 | 15 | 0 | 0 | 0 | 0 | 115 | 280 | 0 | 0 | 270 | 0 | 0 | 0 | 68 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0.1 | 222 | 0 | 30 | 1050 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1100 | 1 | 0 | 0 | 0 | 280 | 220 | 51 | 0 | 198 | 0 | 0 | 144 | 0 | 0 | 19 | 0 | 112 | 0 | 4 | 24 | 290 | 0 | 384 | 42 | 0 | 132 | 1 | 17 | 0 | 5 | 0 | 141 | 0 | 102 | 0 | 47 | 0.4 | 48 | 0 | 0 | 2.54 | 12 | 6318.04 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 1130 | 0 | 0 | 0 | 1373.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 154 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 185 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.2 | 7 | 0.05 | 0 | 278 | 120 | 220 | 0 | 500 | 1100 | 0 | 6320.6 | 12638.64 | 103.2
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 233 | 0 | 17 | 35 | 76 | 15 | 15 | 0 | 0 | 0 | 0 | 115 | 295 | 0 | 0 | 270 | 0 | 0 | 1 | 68 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0.12 | 221 | 0 | 24 | 1050 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1110 | 1 | 0 | 0 | 0 | 280 | 220 | 51 | 0 | 203 | 0 | 0 | 143 | 0 | 0 | 19 | 0 | 106 | 0 | 5 | 16 | 305 | 0 | 371 | 42 | 0 | 150 | 3 | 17 | 0 | 5 | 0 | 141 | 0 | 102 | 0 | 47 | 2.09 | 48 | 0 | 0.1 | 3.6 | 12 | 6359.91 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 1105 | 0 | 0 | 0 | 1424.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.71 | 1 | 0 | 0 | 0.81 | 156 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0.01 | 185 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0.9 | 34 | 0.11 | 0 | 276 | 120 | 220 | 0 | 500 | 1120 | 0 | 6415.14 | 12775.05 | 103.22
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 248 | 0 | 17 | 35 | 76 | 15 | 15 | 0 | 0 | 0 | 0 | 115 | 290 | 0 | 0 | 270 | 0 | 0 | 2 | 68 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 1.19 | 172 | 0 | 4 | 1050 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1110 | 2 | 0 | 0 | 0 | 280 | 220 | 51 | 0 | 210 | 0 | 0 | 143 | 0 | 0 | 19 | 0 | 122 | 0 | 14 | 16 | 300 | 0 | 366 | 42 | 0 | 148 | 0 | 17 | 0 | 5 | 0 | 143 | 0 | 102 | 0 | 47 | 5.7 | 48 | 0 | 0.2 | 12.78 | 12 | 6301.87 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 47 | 1106 | 0 | 0 | 0 | 1467.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.39 | 8 | 0 | 0 | 9.25 | 161 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 1.01 | 186 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 3.2 | 49 | 0.17 | 0 | 280 | 120 | 220 | 0 | 500 | 1140 | 0 | 6568.47 | 12870.34 | 103.22
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 266 | 0 | 233 | 0 | 17 | 35 | 76 | 95 | 16 | 0 | 17 | 0 | 0 | 115 | 280 | 0 | 0 | 270 | 0 | 0 | 4 | 86 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 1.86 | 222 | 0 | 0 | 1125 | 0 | 0 | 36 | 0 | 0 | 162 | 0 | 0 | 0 | 1110 | 3 | 1 | 0 | 0 | 280 | 220 | 51 | 0 | 203 | 0 | 0 | 142 | 0 | 0 | 19 | 0 | 120 | 0 | 12 | 16 | 295 | 0 | 355 | 42 | 0 | 139 | 5 | 17 | 0 | 5 | 0 | 142 | 0 | 102 | 0 | 46 | 7.5 | 48 | 0 | 0.4 | 12.7 | 12 | 6523.46 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 76 | 1084 | 0 | 0 | 0 | 1413.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.03 | 37 | 0 | 0 | 24.01 | 161 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 2.82 | 185 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 2.8 | 120 | 0.2 | 0 | 218 | 120 | 220 | 0 | 645 | 1125 | 0 | 6714.47 | 13237.93 | 103.24
10:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 231 | 0 | 17 | 35 | 125 | 105 | 28 | 0 | 17 | 0 | 0 | 115 | 285 | 0 | 0 | 270 | 0 | 0 | 12 | 123 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 7 | 0 | 0 | 5 | 222 | 5 | 0 | 1125 | 0 | 0 | 50 | 0 | 0 | 173 | 0 | 0 | 0 | 1150 | 0 | 13 | 0 | 0 | 280 | 220 | 51 | 0 | 198 | 0 | 0 | 142 | 12 | 0 | 19 | 0 | 122 | 0 | 9 | 16 | 300 | 0 | 355 | 42 | 0 | 143 | 4 | 17 | 0 | 5 | 0 | 141 | 0 | 102 | 0 | 55 | 10.63 | 112 | 0 | 1.4 | 27.56 | 12 | 6869.59 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 1058 | 0 | 0 | 0 | 1303.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.1 | 85 | 0 | 0 | 36.91 | 158 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 4.18 | 195 | 0 | 17 | 27 | 0 | 0 | 0 | 0 | 5 | 106 | 0.3 | 0 | 216 | 120 | 220 | 0 | 692 | 1110 | 0 | 6644 | 13513.59 | 103.2
11:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 241 | 0 | 17 | 63 | 125 | 145 | 41 | 0 | 17 | 0 | 0 | 120 | 280 | 0 | 0 | 270 | 0 | 0 | 5 | 123 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 0 | 25 | 5.11 | 222 | 33 | 0 | 1125 | 15 | 0 | 50 | 0 | 16 | 173 | 0 | 0 | 0 | 1156 | 1 | 36 | 0 | 0 | 280 | 220 | 43 | 0 | 198 | 0 | 2 | 142 | 62 | 0 | 19 | 0 | 122 | 0 | 50 | 16 | 295 | 0 | 348 | 42 | 0 | 141 | 3 | 17 | 0 | 5 | 0 | 145 | 0 | 102 | 0 | 47 | 20 | 124 | 0 | 0.6 | 15.03 | 12 | 7164.74 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36 | 1067 | 0 | 0 | 0 | 1108.1 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 54.21 | 65 | 0 | 0 | 59.93 | 155 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 4.71 | 198 | 0 | 35 | 31 | 0 | 0 | 0 | 0 | 7.9 | 88 | 0.4 | 0 | 220 | 120 | 220 | 0 | 643 | 1092 | 0 | 6454.25 | 13618.99 | 103.2
12:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 232 | 0 | 17 | 70 | 125 | 195 | 55 | 17 | 17 | 0 | 0 | 120 | 285 | 0 | 35 | 270 | 0 | 0 | 3 | 123 | 5 | 22 | 0 | 0 | 10 | 30 | 0 | 0 | 8 | 0 | 0 | 17 | 20 | 25 | 1.63 | 222 | 40 | 0 | 1125 | 27 | 0 | 50 | 0 | 28 | 172 | 0 | 0 | 0 | 1195 | 1 | 41 | 0 | 0 | 280 | 220 | 51 | 0 | 192 | 0 | 32 | 140 | 105 | 0 | 19 | 34 | 128 | 0 | 18 | 16 | 310 | 0 | 327 | 42 | 0 | 152 | 8 | 17 | 0 | 5 | 0 | 143 | 0 | 102 | 0 | 47 | 7.1 | 124 | 0 | 1.1 | 10.99 | 12 | 7488.82 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34 | 1123 | 0 | 0 | 0 | 1109.5 | 0 | 0 | 0 | 10 | 35 | 0 | 0 | 0 | 8 | 27.46 | 27 | 0 | 0 | 56.27 | 150 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 6.06 | 195 | 0 | 68 | 19 | 0 | 0 | 0 | 0 | 7.9 | 199 | 0.11 | 0 | 230 | 120 | 220 | 0 | 644 | 1116 | 0 | 6618.3 | 14107.12 | 103.2
13:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 241 | 17 | 11 | 70 | 95 | 195 | 55 | 35 | 17 | 0 | 0 | 120 | 280 | 0 | 35 | 270 | 0 | 0 | 8 | 105 | 8 | 22 | 0 | 0 | 15 | 30 | 17 | 0 | 15 | 0 | 0 | 17 | 25 | 25 | 1.63 | 222 | 67 | 0 | 1125 | 52 | 0 | 50 | 0 | 50 | 172 | 0 | 0 | 0 | 1195 | 2 | 60 | 0 | 0 | 280 | 220 | 51 | 0 | 195 | 0 | 34 | 140 | 112 | 0 | 19 | 30 | 142 | 0 | 61 | 24 | 305 | 0 | 327 | 42 | 0 | 136 | 11 | 17 | 0 | 5 | 0 | 143 | 0 | 102 | 0 | 47 | 16.56 | 124 | 0 | 0.2 | 37.94 | 12 | 7702.33 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 54 | 1133 | 0 | 0 | 0 | 1103.91 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 8 | 16.4 | 72 | 0 | 0 | 52.76 | 149 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 4.33 | 195 | 0 | 69 | 34 | 2 | 0 | 0 | 0 | 3.7 | 134 | 0.16 | 0 | 247 | 120 | 220 | 0 | 646 | 1101 | 0 | 6644.26 | 14346.59 | 103.2
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 231 | 17 | 17 | 70 | 60 | 160 | 55 | 35 | 17 | 0 | 0 | 120 | 280 | 0 | 35 | 270 | 0 | 0 | 2 | 105 | 8 | 22 | 0 | 0 | 23 | 48 | 24 | 0 | 14 | 0 | 0 | 17 | 25 | 25 | 0.9 | 222 | 75 | 0 | 1090 | 30 | 0 | 50 | 0 | 49 | 173 | 0 | 0 | 0 | 1168 | 3 | 40 | 0 | 0 | 280 | 220 | 51 | 0 | 178 | 0 | 34 | 140 | 110 | 0 | 19 | 43 | 144 | 0 | 16 | 32 | 305 | 0 | 348 | 42 | 0 | 137 | 2 | 17 | 0 | 5 | 0 | 143 | 0 | 104 | 0 | 47 | 7.3 | 124 | 0 | 0.1 | 16.43 | 12 | 7484.73 | 873 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 1162 | 0 | 0 | 0 | 1106.46 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 1.6 | 13 | 0 | 0 | 35.85 | 146 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 5.3 | 195 | 0 | 50 | 23 | 0 | 0 | 0 | 0 | 7.9 | 202 | 0.43 | 0 | 257 | 100 | 180 | 0 | 634 | 1096 | 0 | 6486.54 | 13971.27 | 103.2
15:00 | 0 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 231 | 17 | 17 | 70 | 45 | 145 | 55 | 35 | 17 | 0 | 0 | 120 | 290 | 0 | 35 | 270 | 0 | 0 | 1 | 105 | 8 | 22 | 0 | 0 | 15 | 65 | 24 | 0 | 6 | 0 | 0 | 17 | 25 | 25 | 1.16 | 222 | 82 | 2 | 1125 | 32 | 0 | 50 | 0 | 50 | 173 | 0 | 0 | 0 | 1190 | 1 | 40 | 0 | 0 | 280 | 220 | 51 | 0 | 170 | 0 | 34 | 142 | 116 | 0 | 19 | 17 | 140 | 0 | 35 | 32 | 310 | 0 | 324 | 41 | 0 | 146 | 1 | 17 | 0 | 11 | 0 | 143 | 0 | 102 | 0 | 47 | 5.56 | 124 | 0 | 0.4 | 26.17 | 12 | 7554.29 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 33 | 1172 | 0 | 0 | 0 | 1104.87 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 4.27 | 23 | 0 | 0 | 27.26 | 145 | 0 | 0 | 0 | 0 | 0 | 258 | 0 | 2.66 | 195 | 0 | 49 | 17 | 0 | 0 | 0 | 0 | 7.2 | 75 | 0.24 | 0 | 276 | 120 | 220 | 0 | 680 | 1120 | 0 | 6528.5 | 14082.79 | 103.2
16:00 | 0 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 230 | 0 | 17 | 70 | 45 | 145 | 40 | 35 | 37 | 0 | 0 | 120 | 275 | 0 | 35 | 270 | 0 | 0 | 1 | 105 | 8 | 22 | 0 | 0 | 15 | 15 | 24 | 0 | 4 | 0 | 0 | 17 | 25 | 25 | 1.53 | 222 | 33 | 2 | 1125 | 17 | 0 | 50 | 0 | 17 | 179 | 0 | 0 | 0 | 1190 | 2 | 40 | 0 | 0 | 280 | 220 | 51 | 0 | 148 | 0 | 41 | 142 | 111 | 0 | 19 | 17 | 134 | 12 | 16 | 32 | 300 | 0 | 292 | 41 | 0 | 130 | 2 | 17 | 0 | 11 | 0 | 140 | 0 | 102 | 0 | 47 | 11.31 | 124 | 0 | 0.6 | 15.54 | 12 | 7273.98 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 32 | 1207 | 0 | 0 | 0 | 995.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 5.36 | 4 | 0 | 0 | 31.21 | 145 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 3.23 | 195 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 5 | 102 | 0.16 | 0 | 275 | 120 | 220 | 0 | 634 | 1100 | 0 | 6312.79 | 13586.77 | 103.21
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 70 | 60 | 145 | 55 | 35 | 54 | 0 | 0 | 144 | 295 | 0 | 35 | 270 | 0 | 0 | 0 | 105 | 8 | 22 | 0 | 0 | 16 | 15 | 24 | 0 | 11 | 0 | 0 | 17 | 25 | 25 | 1.9 | 222 | 32 | 2 | 1125 | 16 | 0 | 50 | 0 | 16 | 194 | 0 | 0 | 0 | 1175 | 1 | 40 | 0 | 0 | 280 | 220 | 51 | 0 | 150 | 0 | 51 | 143 | 111 | 5 | 19 | 17 | 128 | 25 | 20 | 32 | 300 | 0 | 315 | 42 | 0 | 136 | 1 | 0 | 0 | 11 | 0 | 125 | 0 | 100 | 0 | 47 | 5.67 | 124 | 0 | 0.6 | 9.44 | 12 | 7120.61 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24 | 1125 | 0 | 0 | 0 | 963.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6.96 | 3 | 0 | 0 | 2.65 | 141 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 0.23 | 195 | 0 | 0 | 4 | 67 | 0 | 0 | 0 | 3.4 | 81 | 0.27 | 0 | 274 | 100 | 180 | 0 | 649 | 1080 | 0 | 6115.98 | 13236.59 | 103.21
18:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 35 | 17 | 111 | 60 | 145 | 55 | 35 | 90 | 0 | 0 | 147 | 320 | 0 | 35 | 270 | 0 | 0 | 0 | 105 | 8 | 22 | 0 | 0 | 17 | 15 | 24 | 0 | 10 | 0 | 0 | 17 | 50 | 50 | 0.24 | 222 | 33 | 2 | 1050 | 15 | 0 | 50 | 0 | 15 | 194 | 0 | 0 | 0 | 1100 | 0 | 40 | 0 | 0 | 280 | 220 | 51 | 0 | 150 | 0 | 51 | 144 | 114 | 27 | 19 | 17 | 128 | 25 | 1 | 32 | 305 | 0 | 315 | 42 | 0 | 148 | 1 | 6 | 0 | 25 | 0 | 0 | 0 | 100 | 0 | 47 | 1 | 124 | 0 | 0 | 4.34 | 12 | 7065.58 | 884 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3.88 | 1070 | 0 | 0 | 0 | 1006.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1.23 | 0 | 0 | 0 | 1.51 | 141 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0.16 | 195 | 0 | 0 | 3 | 74 | 0 | 0 | 0 | 0.3 | 12 | 0.01 | 16 | 276 | 100 | 180 | 0 | 878 | 1080 | 0 | 6236.04 | 13301.62 | 103.21
19:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 35 | 17 | 115 | 128 | 113 | 55 | 35 | 90 | 0 | 0 | 150 | 300 | 0 | 35 | 300 | 0 | 0 | 0 | 143 | 8 | 22 | 0 | 0 | 15 | 45 | 48 | 0 | 7 | 34 | 36 | 49 | 50 | 50 | 0 | 222 | 44 | 2 | 1125 | 40 | 0 | 50 | 6 | 33 | 194 | 0 | 0 | 0 | 1196 | 0 | 50 | 0 | 0 | 280 | 200 | 51 | 0 | 153 | 0 | 51 | 143 | 113 | 27 | 19 | 52 | 146 | 25 | 0 | 32 | 280 | 0 | 336 | 42 | 0 | 137 | 0 | 8 | 0 | 33 | 0 | 0 | 0 | 100 | 0.72 | 47 | 0 | 124 | 0 | 0 | 0 | 0 | 7654.72 | 884 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1093 | 0 | 0 | 0 | 1148.51 | 0 | 0 | 0 | 25 | 14 | 3 | 104 | 18 | 25 | 0 | 0 | 20 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 191 | 0 | 48 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 271 | 120 | 220 | 0 | 1050 | 1094 | 35 | 6949.51 | 14604.23 | 103.22
19:30 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 35 | 17 | 115 | 128 | 113 | 55 | 35 | 90 | 0 | 0 | 142 | 330 | 0 | 35 | 330 | 0 | 0 | 0 | 143 | 8 | 22 | 0 | 0 | 60 | 70 | 82 | 0 | 8 | 34 | 44 | 54.36 | 50 | 50 | 0 | 222 | 102 | 3 | 1125 | 90 | 0 | 50 | 17 | 90 | 194 | 0 | 0 | 0 | 1180 | 0 | 100 | 0 | 0 | 280 | 200 | 51 | 0 | 156 | 0 | 68 | 143 | 170 | 28 | 19 | 65 | 148 | 34 | 0 | 32 | 300 | 0 | 292 | 42 | 0 | 139 | 0 | 8 | 0 | 33 | 0 | 0 | 0 | 100 | 17 | 66 | 0 | 152 | 0 | 0 | 0 | 0 | 8196.36 | 884 | 0 | 0 | 36 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1140 | 0 | 0 | 0 | 1145.94 | 0 | 0 | 0 | 35 | 50 | 5 | 101 | 22 | 34 | 0 | 0 | 20 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 190 | 0 | 92 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 307 | 120 | 220 | 0 | 1050 | 1140 | 54 | 7252.94 | 15449.3
20:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 35 | 17 | 115 | 143 | 113 | 55 | 35 | 90 | 0 | 0 | 142 | 320 | 0 | 35 | 330 | 0 | 0 | 0 | 143 | 8 | 22 | 0 | 0 | 38 | 45 | 81 | 0 | 10 | 34 | 46 | 54.36 | 50 | 50 | 0 | 222 | 106 | 2 | 1125 | 52 | 0 | 50 | 17 | 94 | 194 | 0 | 0 | 0 | 1180 | 0 | 80 | 0 | 0 | 280 | 200 | 51 | 0 | 159 | 0 | 60 | 143 | 172 | 26 | 19 | 52 | 144 | 34 | 0 | 32 | 305 | 0 | 296 | 42 | 0 | 133 | 0 | 8 | 0 | 33 | 0 | 0 | 0 | 100 | 17 | 66 | 0 | 152 | 0 | 0 | 0 | 0 | 8087.36 | 884 | 0 | 0 | 33 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1185 | 0 | 0 | 0 | 1109.78 | 0 | 25 | 0 | 55 | 60 | 5 | 101 | 27 | 25 | 0 | 0 | 20 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 191 | 0 | 95 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 307 | 120 | 220 | 0 | 1050 | 1134 | 54 | 7305.78 | 15393.14 | 103.22
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 35 | 17 | 115 | 143 | 113 | 55 | 35 | 90 | 0 | 0 | 144 | 295 | 0 | 35 | 330 | 0 | 0 | 0 | 143 | 8 | 22 | 0 | 0 | 15 | 45 | 55 | 0 | 9 | 34 | 14 | 54.36 | 50 | 50 | 0 | 222 | 105 | 3 | 1125 | 17 | 0 | 50 | 17 | 96 | 196 | 0 | 0 | 0 | 1190 | 0 | 100 | 0 | 0 | 280 | 200 | 51 | 0 | 170 | 0 | 69 | 143 | 176 | 29 | 19 | 17 | 138 | 34 | 0 | 32 | 300 | 0 | 315 | 42 | 0 | 135 | 0 | 15 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 66 | 0 | 154 | 0 | 0 | 0 | 0 | 8012.36 | 884 | 0 | 0 | 33 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1205 | 0 | 0 | 0 | 1135.19 | 0 | 33 | 0 | 55 | 70 | 5 | 102 | 27 | 8 | 0 | 0 | 20 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 191 | 0 | 95 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 307 | 120 | 220 | 0 | 1050 | 1140 | 54 | 7399.19 | 15411.55 | 103.23
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 35 | 17 | 115 | 143 | 113 | 55 | 35 | 54 | 0 | 0 | 144 | 290 | 0 | 0 | 309 | 0 | 0 | 0 | 143 | 8 | 22 | 0 | 0 | 14 | 45 | 44 | 0 | 14 | 34 | 14 | 17 | 50 | 50 | 0 | 222 | 104 | 2 | 1125 | 16 | 0 | 50 | 20 | 94 | 195 | 0 | 0 | 0 | 1190 | 0 | 100 | 0 | 0 | 280 | 200 | 51 | 0 | 173 | 0 | 69 | 143 | 173 | 28 | 19 | 17 | 134 | 34 | 0 | 32 | 300 | 0 | 322 | 42 | 0 | 125 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 67 | 0 | 154 | 0 | 0 | 0 | 0 | 7762 | 884 | 0 | 0 | 33 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1207 | 0 | 0 | 0 | 1112.51 | 0 | 33 | 0 | 55 | 70 | 0 | 102 | 27 | 8 | 0 | 0 | 20 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 191 | 0 | 93 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 307 | 110 | 180 | 0 | 1050 | 1163 | 54 | 7328.51 | 15090.51 | 103.2
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 35 | 17 | 84 | 143 | 113 | 55 | 35 | 17 | 0 | 0 | 147 | 305 | 0 | 0 | 307 | 0 | 0 | 0 | 143 | 8 | 22 | 0 | 0 | 16 | 51 | 16 | 0 | 15 | 34 | 14 | 17 | 50 | 50 | 0 | 221 | 106 | 2 | 1125 | 17 | 0 | 50 | 17 | 101 | 196 | 0 | 0 | 0 | 1190 | 0 | 100 | 0 | 0 | 280 | 200 | 51 | 0 | 178 | 0 | 49 | 142 | 175 | 28 | 19 | 16 | 144 | 16 | 0 | 32 | 315 | 0 | 345 | 42 | 0 | 144 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 67 | 0 | 154 | 0 | 0 | 0 | 0 | 7724 | 888 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1207 | 0 | 0 | 0 | 996.29 | 0 | 33 | 0 | 55 | 70 | 0 | 102 | 27 | 8 | 0 | 0 | 20 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 259 | 0 | 0 | 191 | 0 | 95 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 120 | 220 | 0 | 1050 | 1163 | 54 | 7261.29 | 14985.29 | 103.2
Total KWH | 0 | 718080 | 161760 | 0 | 0 | 0 | 0 | 0 | 7203600 | 0 | 3966280 | 261360 | 426600 | 1543968 | 2303520 | 2587375 | 1064106 | 518998 | 802080 | 0 | 0 | 3096553 | 7110909 | 0 | 338221 | 6756776 | 0 | 0 | 41568 | 2565600 | 184800 | 518760 | 0 | 0 | 345000 | 607200 | 439680 | 0 | 238080 | 250910 | 195250 | 423150 | 1135680 | 593280 | 16559 | 5294787 | 1557300 | 214560 | 26698181.82 | 488436 | 0 | 852480 | 112057.2 | 874836 | 4234930 | 0 | 0 | 0 | 28041815 | 20790 | 1012000 | 0 | 0 | 7169800 | 5336000 | 1233153 | 0 | 4613000 | 0 | 706560 | 3429827 | 2124960 | 178080 | 468740 | 430920 | 3132480 | 238920 | 270564 | 610560 | 7310000 | 0 | 8392000 | 985000 | 0 | 3345872.73 | 51641 | 346896 | 0 | 384960 | 0 | 2347200 | 0 | 2435960 | 74880 | 1206000 | 90313 | 2280000 | 0 | 6800 | 217880 | 231840 | 175468682.75 | 21577455 | 0 | 0 | 193440 | 0 | 912000 | 0 | 0 | 0 | 0 | 47520 | 426240 | 27629090 | 0 | 0 | 0 | 29578644 | 0 | 138855 | 0 | 405696 | 760992 | 12134 | 571296 | 153400 | 244906 | 159040 | 313080 | 127000 | 0 | 336080 | 3548273 | 0 | 0 | 0 | 0 | 0 | 6660800 | 0 | 32940 | 4705000 | 0 | 970279 | 203381 | 810595 | 0 | 0 | 0 | 44005.56 | 1141200 | 3109 | 721632 | 6502000 | 2801000 | 5335660 | 0 | 17767272 | 27314909.09 | 356400 | 162505323.65 | 337974006.4

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14107.12 | MW | 12:00 Hr. | Energy Generated |  |  | 337.974 |  | MKWHr.
| Day Peak Demand |  |  | 14483.12 | MW | 12:00 Hr. | Energy Unserverd |  |  | 7.208 |  | MKWHr.
| Evening Peak Generation |  |  | 15449.3 | MW | 19:30 Hr. | Energy Demand |  |  | 345.182 |  | MKWHr.
| Evening Peak Demand |  |  | 15672.3 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.2 |  | °C
| Minimum Generation of the Day |  |  | 12638.64 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 711.44 |  | MMCFD
| Maximum Generation of the Day |  |  | 15449.3 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.8933 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 28.8377 | 0 | 13.2917 | 0 | 0 | 0.041568 | 0 | 0 | 42.1709 | Gas | 99.4313 | Gas | 343574909.4516
| Chattogram Zone |  |  | 4.4495 | 54.74 | 7.8753 | 0 | 5.2948 | 0.037349 | 0 | 0.23808 | 72.635 | Coal | 138.6583 | Coal | 933861412.519
| Cumilla Zone |  |  | 22.2505 | 0 | 5.302 | 0 | 0 | 0.27056 | 3.1325 | 0 | 30.9556 | HFO | 35.7758 | HFO | 648916553.008
| Mymensingh Zone |  |  | 0 | 0 | 3.7927 | 0 | 0 | 0.31499 | 0 | 0 | 4.1077 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 25.5479 | 0 | 0 | 0 | 0 | 0.051641 | 0 | 0 | 25.5995 | Hydro | 5.2948 | Hydro | 529478.7
| Khulna Zone |  |  | 0 | 27.6291 | 0.24096 | 0 | 0 | 0.42624 | 22.4895 | 0 | 50.7857 | Solar | 3.3752 | Solar | 55496973.6148
| Barishal Zone |  |  | 8.1367 | 51.5842 | 1.078 | 0 | 0 | 0.003109 | 0 | 0 | 60.802 | Import | 55.2006 | Import | 343891593
| Rajshahi Zone |  |  | 10.2091 | 0 | 2.4143 | 0 | 0 | 0.84114 | 29.5786 | 0 | 43.0431 | Wind | 0.23808 | Wind | 3502156.8
| Rangpur Zone |  |  | 0 | 4.705 | 1.7809 | 0 | 0 | 1.3886 | 0 | 0 | 7.8745
| Total |  |  | 99.4313 | 138.6583 | 35.7758 | 0 | 5.2948 | 3.3752 | 55.2006 | 0.23808 | 337.974
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 343574909.4516 |  | Hydro | 529478.7
|  |  |  | Coal | 933861412.519 |  | Solar | 55496973.6148
|  |  |  | HFO | 648916553.008 |  | Import | 343891593
|  |  |  | HSD | 0 |  | Wind | 3502156.8
[5 empty] | Total: | 232,97,73,077 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5775 | Peak Hr Flow | 884.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 54286290.91 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.5786 | Peak Hr Flow | 1145.94 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2422 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.1325 | Peak Hr Flow | 148.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2825 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.2886 | Peak Hr Flow | 2177.94 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 64 |  | 5647
|  |  |  | Chattogram |  | 0 |  | 1496
|  |  |  | Cumilla |  | 22 |  | 1424
|  |  |  | Mymensingh |  | 89 |  | 1247
|  |  |  | Sylhet |  | 38 |  | 657
|  |  |  | Khulna |  | 0 |  | 1723
|  |  |  | Barishal |  | 0 |  | 460
|  |  |  | Rajshahi |  | 0 |  | 1412
|  |  |  | Rangpur |  | 0 |  | 1081
|  |  |  | Total |  | 213 |  | 15147
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Karnaphuli Hydro PP Unit-3 |  |  | 50
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 139
|  |  |  | Total Unavailable Capacity |  |  |  | 439
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 17:46 | Halishahar-Julda 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to To removing
building near transmission line.
|  | 08:31 | Natore 132/33kV S/S TR-2 (415 T) HT is restored.
|  | 08:31 | Natore 132/33kV S/S TR-1 (405 T) HT is restored.
|  | 08:32 | Natore 132/33kV S/S TR-1 (405 T) LT is restored.
|  | 08:32 | Natore 132/33kV S/S TR-2 (415 T) LT is restored.
| 08:35 |  | Mirpur-Uttara 3PH 132kV Ckt-1 Project Work S/D from Mirpur 132/33kV end Due to LILO
Work on Tower no. 48 by EEGBPS
| 09:39 | 17:32 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Scheduled S/D from Thakurgaon 132/33kV end Due
to EMA Power Plant Work in RTU Control Pannel.
| 10:18 | 21:02 | Korerhat 400/230/132kV S/S ATR-2(7203T)-Three Ph LT Project Work S/D Due to Project work
(DFDR)
| 10:21 | 21:00 | Korerhat 400/230/132kV S/S ATR-2(7203T)-Three Ph HT Project Work S/D Due to Project work
(DFDR)
| 11:41 | 12:11 | BIPTC S/S 20DF22 Scheduled S/D
| 12:00 |  | Day Peak Generation: 14107 MW.
| 14:21 | 16:13 | Mymensingh RPCL -Mymensingh 132kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due
to NLDC AE.
| 14:22 | 15:19 | Bajitpur 132/33kV S/S Tr-2(414T) LT Forced S/D Due to High temperature maintenance | [7 empty] | 20.0MW load
interrup.
| 14:47 | 15:34 | BIPTC S/S 20DF11 Forced S/D Due to Shutdow is taken for cleaning grass and weeds inside
the filter bank
| 15:21 | 15:57 | Korerhat 400/230/132kV S/S Meghnaghat-1 Tripped showing 6MD85 relays Due to Shunt Reactor
Work
| 15:21 | 15:57 | Madunaghat-Meghnaghat 400kV Ckt-1 Tripped from Meghnaghat 400/230kV end showing 86.1,
86.2, 96 relays Due to 400kV Korerhat ckt-1 Tripped by Line Differential and DTT.
| 16:34 |  | JERA Meghnaghat Power Limited 718 MW CCPP was shutdown due to gas shortage.
| 16:40 | 17:58 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to | [7 empty] | 25.0MW load
|  |  | 132/33kV GT-3 X-Former LT Side Y-Phase Bushing Clamp Redhot Remove. | [7 empty] | interrup.
| 16:40 | 17:52 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to | [7 empty] | 25.0MW load
|  |  | 132/33kV GT-3 X-Former LT Side Y-Phase Bushing Clamp Redhot Remove. | [7 empty] | interrup.
| 01:47 | 06:49 | Ghorashal 230kV S/S TARFO-2 LT Tripped showing Over current, Earth fualt relays Due to | [7 empty] | 80.0MW load
|  |  | Post Insulator flasing and bus Ds. | [7 empty] | interrup.
| 04:22 | 06:49 | Ghorashal 230kV S/S TARFO-2 HT Scheduled S/D Due to Emergency Maintenance. | [7 empty] | 80.0MW load
interrup.
| 06:10 |  | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end Due to | [7 empty] | 70.0MW load
|  |  | PGNS (G2G) project works. | [7 empty] | interrup.
Mymensingh 132/33kV
end
| 06:12 |  | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to 33kv Doara bazar feeder DS Maintanance | [7 empty] | 12.0MW load
interrup.
| 06:12 |  | Chhatak 132/33kV S/S T-1 LT Scheduled S/D Due to 33kv Doara bazar feeder DS Maintanance | [7 empty] | 12.0MW load
interrup.
| 06:40 |  | Munshiganj 132/33kV S/S Transformer-2 LT Scheduled S/D | [7 empty] | 25.0MW load
interrup.
| 06:40 |  | Munshiganj 132/33kV S/S Transformer-2 LT Scheduled S/D | [7 empty] | 25.0MW load
interrup.
| 06:43 |  | Saidpur 132/33kV S/S TR-3 (424T) LT Scheduled S/D Due to 33 kV loop change of golahat | [7 empty] | 12.0MW load
|  |  | 33kV feeder. | [7 empty] | interrup.
| 06:44 |  | Saidpur 132/33kV S/S TR-3 (424T) HT Scheduled S/D Due to 33 kV loop change of golahat | [7 empty] | 12.0MW load
|  |  | 33kV feeder. | [7 empty] | interrup.
| 06:55 |  | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Shomvuganj 400/132kV end Due to
G2G Project work
| 07:00 |  | Minimum generation is 11834 MW.
| 07:14 |  | Nawabganj 132/33kV S/S TR-2 LT Scheduled S/D Due to 33kv Bus-02 shutdown for PT changing | [7 empty] | 20.0MW load
|  |  | of kushumhati feeder. | [7 empty] | interrup.
| 07:30 |  | Narail 132/33kV S/S TR1 (403-T) LT Scheduled S/D Due to Red hot maintenance | [7 empty] | 24.0MW load
interrup.
| 07:32 |  | Narail 132/33kV S/S TR1 (403-T) HT Scheduled S/D Due to Red hot maintenance | [7 empty] | 24.0MW load
interrup.
| 07:59 |  | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Tripped showing . relays Due to Trip for PRD
| 07:59 |  | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Tripped showing . relays Due to PRD Trip | [7 empty] | 34.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 300 | 7203600 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 142 | 3096553 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1064106 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 6756776 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 261360 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 128 | 2303520 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 518998 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 338221 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 8 | 184800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 518760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 161760 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 113 | 2587375 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 1543968 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 718080 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 802080 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 41568 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 23.297 | 17 | 426600 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 330 | 7110909 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 3966280 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143 | 2565600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6637.271 | 2028 | 42170914
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 112057.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 20790 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 852480 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5294787 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 194 | 4234930 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 90 | 874836 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 44 | 195250 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 250910 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 1135680 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 3 | 214560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 82 | 439680 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 16559 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 70 | 607200 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 423150 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 102 | 1557300 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 593280 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 60 | 345000 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 90 | 488436 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1180 | 28041815 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 238080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 26698181.82 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 3525.36 | 72634962.02
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 156 | 4613000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 280 | 7169800 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 200 | 5336000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1233153 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 1012000 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 32 | 610560 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 143 | 3429827 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 2124960 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 148 | 3132480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 238920 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 468740 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 65 | 430920 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 178080 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 706560 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 270564 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1494 | 30955564
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 90313 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 152 | 2280000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 66 | 1206000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 217880 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 231840 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 74880 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 235 | 4107713
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 51641 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 985000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 139 | 3345872.73 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 2347200 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 33 | 384960 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2435960 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 346896 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7310000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 292 | 8392000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 914 | 25599529.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 884 | 21577455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 36 | 193440 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 47520 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 426240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1140 | 27629090 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2113 | 50785745
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1050 | 17767272 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 64 | 721632 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2801000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 1140 | 27314909.09 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5335660 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 356400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6502000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3109 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2955 | 60801982.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 159040 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 138855 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 12134 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 153400 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 3548273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 250 | 6660800 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 127000 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 34 | 244906 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 101 | 571296 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 760992 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 405696 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 32940 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1145.94 | 29578644 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 336080 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 313080 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1802.94 | 43043136
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 190 | 4705000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 100 | 810595 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44005.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 92 | 970279 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 203381 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1141200 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 382 | 7874460.56
Eastern Grid Total |  |  |  |  | 17406.339 | 8196.36 | 175468682.75
Western Grid Total |  |  |  |  | 11731.125 | 7252.94 | 162505323.65
National Grid Total |  |  |  |  | 29137.464 | 15449.3 | 337974006.4
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-07-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10311.58 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4676.4 | MW
i) Dhaka area |  |  | 5583.28 |  | MW | i) Khulna area |  |  |  | 1723 | MW
ii) Chattogram area |  |  | 1549.3 |  | MW | ii) Barishal area |  |  |  | 460 | MW
iii) Cumilla area |  |  | 1402 |  | MW | iii) Rajshahi area |  |  |  | 1412.4 | MW
iv) Mymensingh area |  |  | 1158 |  | MW | iv) Rangpur area |  |  |  | 1081 | MW
v) Sylhet area |  |  | 619 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14987.98 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 140 | 19:30 | 133 | Narshingdi | 187 | 00:00 | 199 | Uttara | 85 | 13:00
2 | AKSML | 138.8 | 13:00 | 68 | Hasnabad | 86 | 16:00 | 134 | Natore | 143 | 19:30 | 200 | UttaraNew | 50 | 13:00
3 | Aftabnagar | 40 | 20:00 | 69 | Hathazari | 83 | 21:00 | 135 | Nawabganj | 54.2 | 21:00 | 201 | Zigatola | 106 | 13:00
4 | Agargaon | 116 | 13:00 | 70 | Hatirjheel | 87 | 15:00 | 136 | Netrakona | 130 | 18:30
5 | Agrabad | 68 | 13:00 | 71 | Ishurdi | 75 | 13:00 | 137 | New | 86 | 12:00
6 | Amnura | 31 | 00:00 | 72 | Jaldhaka | 90 | 22:00 | 138 | Niamatpur | 72 | 22:00
7 | Ashuganj | 98 | 00:00 | 73 | Jamalpur | 110 | 19:30 | 139 | Noapara | 40 | 19:30
8 | BSRM | 196 | 07:00 | 74 | Jashore | 136 | 13:00 | 140 | PHP | 11 | 18:00
9 | Bagerhat | 89 | 00:00 | 75 | Jhenaidah | 90 | 19:00 | 141 | Pabna | 92 | 19:30
10 | Bajitpur | 88 | 19:00 | 76 | Joydebpur | 173 | 19:00 | 142 | Palashbari | 126 | 21:00
11 | Bakerganj | 14.6 | 21:00 | 77 | Joypurhat | 64 | 00:00 | 143 | Panchagarh | 63 | 20:00
12 | Bakulia | 89 | 19:00 | 78 | Juldah | 16 | 12:00 | 144 | Patiya | 10 | 21:00
13 | Banani | 68 | 15:00 | 79 | KSRM | 16 | 02:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 15 | 10:00 | 80 | Kabirpur | 272 | 19:30 | 146 | Patuakhali | 65 | 22:00
15 | Barapukuria | 71 | 19:30 | 81 | Kachua | 90 | 22:00 | 147 | Payra | 32 | 00:00
16 | Barguna | 20 | 00:00 | 82 | Kaliganj | 34 | 00:00 | 148 | Postogola | 59 | 13:00
17 | Barishal | 106 | 12:00 | 83 | Kallyanpur | 111 | 14:00 | 149 | Pubail | 40 | 11:00
18 | Barishal-230 | 94 | 19:00 | 84 | Kalurghat | 42 | 12:00 | 150 | Purbachal | 27 | 12:00
19 | Baroaulia | 42 | 12:00 | 85 | Kamrangirchar | 79 | 13:00 | 151 | Purbasadipur | 142 | 21:00
20 | Baroirhat | 61 | 19:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 39 | 22:00
21 | Bashundhara | 187 | 13:00 | 87 | Kasba | 36 | 19:30 | 153 | Rahim | 54 | 10:00
22 | BashundharaCement | 7 | 05:00 | 88 | Kazla | 117 | 13:00 | 154 | Rajbari | 80 | 19:30
23 | Beanibazar | 76 | 01:00 | 89 | Keranigonj | 80 | 20:00 | 155 | Rajendrapur | 130 | 02:00
24 | Benapole | 53 | 00:00 | 90 | Khagrachori | 34 | 19:00 | 156 | Rajshahi | 107 | 22:00
25 | Bhaluka | 156 | 12:00 | 91 | Khulna | 55 | 13:00 | 157 | Rajshahi-230 | 94 | 15:00
26 | Bhandaria | 54 | 22:00 | 92 | Khulshi | 184 | 19:00 | 158 | Ramganj | 110 | 23:00
27 | Bhangura | 36 | 19:30 | 93 | Kishoreganj | 120 | 07:00 | 159 | Rampur | 40 | 19:00
28 | Bheramara(GK) | 63 | 19:30 | 94 | Kodda | 306 | 15:00 | 160 | Rangamati | 16 | 19:00
29 | Bhulta | 235 | 10:00 | 95 | Kulaura | 56 | 20:00 | 161 | Rangpur | 150 | 20:00
30 | Bog-Sherpur | 76 | 00:00 | 96 | Kurigram | 78 | 19:30 | 162 | Ruppur | 4.2 | 11:00
31 | Bogura | 169 | 23:00 | 97 | Kushtia | 150 | 13:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 72 | 00:00 | 98 | Laksam | 33 | 19:00 | 164 | Saidpur | 106 | 19:30
33 | Brahmanbaria | 125 | 12:00 | 99 | Lakshmipur | 43 | 19:00 | 165 | Santhia | 32 | 19:30
34 | Cantonment | 120 | 13:00 | 100 | Lalbag | 84 | 13:00 | 166 | Satkhira | 124 | 21:00
35 | Chandina | 35 | 20:00 | 101 | Lalmonirhat | 70 | 19:30 | 167 | Satmasjid | 97 | 13:00
36 | Chandpur | 82 | 22:00 | 102 | MI_Cement | 11.8 | 03:00 | 168 | Savar | 198 | 12:00
37 | Chandraghona | 32 | 19:30 | 103 | Madanganj | 47 | 19:30 | 169 | SevenRings | 6.84 | 23:00
38 | Chapai | 68 | 23:00 | 104 | Madaripur | 109 | 21:00 | 170 | ShahCement | 36 | 01:00
39 | Charfasson | 31 | 00:00 | 105 | Madartek | 74 | 21:00 | 171 | Shahjadpur | 75 | 20:00
40 | Charsaidpur | 23 | 00:00 | 106 | Madunaghat | 51 | 19:00 | 172 | Shahjibazar | 130 | 21:00
41 | Chauddagram | 74 | 00:00 | 107 | Magura | 61 | 19:30 | 173 | Shahmirpur | 48 | 18:30
42 | Chhatak | 38 | 01:00 | 108 | Mahasthangarh | 82 | 00:00 | 174 | Shariatpur | 88 | 23:00
43 | Chowmuhani | 151 | 19:30 | 109 | Maijdee | 37 | 22:00 | 175 | Sherpur | 146 | 22:00
44 | Chuadanga | 105 | 19:30 | 110 | Manikganj | 133 | 19:30 | 176 | Shikalbaha | 32 | 21:00
45 | Coxsbazar | 135 | 19:30 | 111 | Maniknagar | 74 | 13:00 | 177 | Shitalakhya | 75.4 | 12:00
46 | Cumilla(N) | 120 | 19:00 | 112 | Matarbari | 53 | 19:30 | 178 | Sholosohor | 49 | 15:00
47 | Cumilla(S) | 147 | 19:00 | 113 | Matuail | 76 | 11:00 | 179 | Shomvuganj | 44 | 20:00
48 | Daganbhuiyan | 33 | 22:00 | 114 | Metrorail_Motijheel | 23 | 18:30 | 180 | Shyampur | 154 | 10:00
49 | Daudkandi | 140 | 21:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 129 | 12:00
50 | DhakaUniversity | 84 | 12:00 | 116 | Millgate | 105 | 12:00 | 182 | Sirajganj | 110 | 21:00
51 | Dhamrai | 100 | 19:00 | 117 | Mirpur | 145 | 13:00 | 183 | Sitakunda | 31 | 20:00
52 | Dhanmondi | 107.4 | 13:00 | 118 | Mirsorai | 41 | 03:00 | 184 | Sonargaon | 150 | 00:00
53 | Dohazari | 109 | 19:30 | 119 | Mirzapur | 45 | 19:00 | 185 | Sreemongol | 85 | 00:00
54 | Faridpur | 171 | 19:30 | 120 | Mithapukur | 74 | 19:30 | 186 | Sreepur | 101 | 06:00
55 | Fatullah | 109 | 10:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 45.8 | 22:00
56 | Fenchuganj | 45 | 00:00 | 122 | Mogbazar | 21 | 15:00 | 188 | Sunamganj | 60 | 22:00
57 | Feni | 95 | 19:30 | 123 | Mongla | 40 | 10:00 | 189 | Sylhet | 110 | 14:00
58 | GPH | 72 | 16:00 | 124 | Motijheel | 47 | 13:00 | 190 | Sylhet_(South) | 69 | 00:00
59 | Ghatail | 93 | 23:00 | 125 | Muktagacha | 39 | 19:00 | 191 | TK | 26 | 19:30
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 102 | 00:00 | 192 | Tangail | 176 | 19:30
61 | Ghorashal-230 | 107 | 04:00 | 127 | Muradnagar | 47 | 22:00 | 193 | Taraganj | 27 | 19:30
62 | Goalpara | 36 | 00:00 | 128 | Mymensingh | 163 | 19:30 | 194 | Tasnim | 44 | 09:00
63 | Gollamari | 98 | 13:00 | 129 | Nabinagar | 106 | 10:00 | 195 | Thakurgaon | 115 | 20:00
64 | Gopalganj | 105 | 20:00 | 130 | Naogaon | 133 | 00:00 | 196 | Tongi | 155 | 15:00
65 | Gulshan | 110 | 15:00 | 131 | Narail | 56 | 19:00 | 197 | Ullahpara | 37 | 21:00
66 | Halishahar | 107 | 18:30 | 132 | Narinda | 72 | 13:00 | 198 | Ullon | 65 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14726.23 | 553 |  | 15304.12
1:00 | 14194.93 | 480 |  | 14696.93
2:00 | 13840.65 | 457 |  | 14318.65
3:00 | 13592.8 | 418 |  | 14029.8
4:00 | 13237.02 | 368 |  | 13622.02
5:00 | 12939.6 | 321 |  | 13274.6
6:00 | 12638.64 | 309 |  | 12961.64
7:00 | 12775.05 | 318 |  | 13107.05
8:00 | 12870.34 | 295 |  | 13178.34
9:00 | 13237.93 | 323 |  | 13575.93
10:00 | 13513.59 | 83 |  | 13600.59
11:00 | 13618.99 | 98 |  | 13720.99
12:00 | 14107.12 | 360 |  | 14483.12
13:00 | 14346.59 | 301 |  | 14661.59
14:00 | 13971.27 | 322 |  | 14307.27
15:00 | 14082.79 | 382 |  | 14481.79
16:00 | 13586.77 | 392 |  | 13996.77
17:00 | 13236.59 | 246 |  | 13493.59
18:00 | 13301.62 | 135 |  | 13442.62
19:00 | 14604.23 | 131 |  | 14741.23
19:30 | 15449.3 | 213 |  | 15672.3
20:00 | 15393.14 | 201 |  | 15603.14
21:00 | 15411.55 | 212 |  | 15633.55
22:00 | 15090.51 | 232 |  | 15332.51
23:00 | 14985.29 | 271 |  | 15268.29
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7421 | 7305.23 | 14726.23 | DAILY GENERATION CURVE
00:30 | 7306.68 | 7153.9 | 14460.58
01:00 | 7192.36 | 7002.57 | 14194.93 | 23-07-2026
01:30 | 7063.68 | 6954.11 | 14017.79
02:00 | 6935 | 6905.65 | 13840.65
02:30 | 6896 | 6820.725 | 13716.725
03:00 | 6857 | 6735.8 | 13592.8
03:30 | 6790 | 6624.91 | 13414.91
04:00 | 6723 | 6514.02 | 13237.02
04:30 | 6614.5 | 6473.81 | 13088.31
05:00 | 6506 | 6433.6 | 12939.6
05:30 | 6412.02 | 6377.1 | 12789.12
06:00 | 6318.04 | 6320.6 | 12638.64
06:30 | 6338.975 | 6367.87 | 12706.845
07:00 | 6359.91 | 6415.14 | 12775.05
07:30 | 6330.89 | 6491.805 | 12822.695
08:00 | 6301.87 | 6568.47 | 12870.34
08:30 | 6412.665 | 6641.47 | 13054.135
09:00 | 6523.46 | 6714.47 | 13237.93
09:30 | 6696.525 | 6679.235 | 13375.76
10:00 | 6869.59 | 6644 | 13513.59
10:30 | 7017.165 | 6549.125 | 13566.29
11:00 | 7164.74 | 6454.25 | 13618.99
11:30 | 7326.78 | 6536.275 | 13863.055
12:00 | 7488.82 | 6618.3 | 14107.12
12:30 | 7595.575 | 6631.28 | 14226.855
13:00 | 7702.33 | 6644.26 | 14346.59
13:30 | 7593.53 | 6565.4 | 14158.93
14:00 | 7484.73 | 6486.54 | 13971.27
14:30 | 7519.51 | 6507.52 | 14027.03
15:00 | 7554.29 | 6528.5 | 14082.79
15:30 | 7414.135 | 6420.645 | 13834.78
16:00 | 7273.98 | 6312.79 | 13586.77
16:30 | 7197.295 | 6214.385 | 13411.68
17:00 | 7120.61 | 6115.98 | 13236.59
17:30 | 7093.095 | 6176.01 | 13269.105
18:00 | 7065.58 | 6236.04 | 13301.62
18:30 | 7360.15 | 6592.775 | 13952.925
19:00 | 7654.72 | 6949.51 | 14604.23
19:30 | 8196.36 | 7252.94 | 15449.3
20:00 | 8087.36 | 7305.78 | 15393.14
20:30 | 8049.86 | 7352.485 | 15402.345 |  | Executive Engineer
21:00 | 8012.36 | 7399.19 | 15411.55 |  | Network Operation Division
21:30 | 7887.18 | 7363.85 | 15251.03
22:00 | 7762 | 7328.51 | 15090.51
22:30 | 7743 | 7294.9 | 15037.9
23:00 | 7724 | 7261.29 | 14985.29

## En-Curve
QF-LDC-12
Date | 23-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2749 | 1365 | 897 | 38 | 142 | 1478.23 | 221 | 6112 | 0 | 521 | 1196 | 0 | 0 | 7 | 553 | DAILY ENERGY CURVE
00:30 | 2750.5 | 1393.5 | 896.5 | 38 | 140 | 1473.9 | 221 | 5990.5 | 0 | 418.5 | 1133.68 | 0 | 0 | 4.5 | 516.5 | 23-07-2026
01:00 | 2752 | 1422 | 896 | 38 | 138 | 1469.57 | 221 | 5869 | 0 | 316 | 1071.36 | 0 | 0 | 2 | 480
01:30 | 2770 | 1419.5 | 896 | 38 | 136 | 1468.11 | 221 | 5876.5 | 0 | 250.5 | 937.18 | 0 | 0 | 5 | 468.5 | Energy Generated | 337.974 |  | MKWHr
02:00 | 2788 | 1417 | 896 | 38 | 134 | 1466.65 | 221 | 5884 | 0 | 185 | 803 | 0 | 0 | 8 | 457 | Energy not Served | 7.208 |  | MKWHr
02:30 | 2793 | 1417.5 | 896 | 38 | 133 | 1474.225 | 221.5 | 5786 | 0 | 185 | 764 | 0 | 0 | 8.5 | 437.5 | Total Energy Requirement | 345.182 |  | MKWHr
03:00 | 2798 | 1418 | 896 | 38 | 132 | 1481.8 | 222 | 5688 | 0 | 185 | 725 | 0 | 0 | 9 | 418
03:30 | 2802 | 1427 | 896 | 38 | 129 | 1455.41 | 222 | 5630.5 | 0 | 185 | 622.5 | 0 | 0 | 7.5 | 393
04:00 | 2806 | 1436 | 896 | 38 | 126 | 1429.02 | 222 | 5573 | 0 | 185 | 520 | 0 | 0 | 6 | 368
04:30 | 2813.5 | 1436 | 896.5 | 38 | 122 | 1430.81 | 222 | 5579 | 0 | 185 | 362 | 0 | 0 | 3.5 | 344.5
05:00 | 2821 | 1436 | 897 | 38 | 118 | 1432.6 | 222 | 5585 | 0 | 185 | 204 | 0 | 0 | 1 | 321
05:30 | 2826.5 | 1428 | 896.5 | 38 | 115 | 1402.92 | 222 | 5464 | 9.7 | 185 | 196.5 | 0 | 0 | 5 | 315
06:00 | 2832 | 1420 | 896 | 38 | 112 | 1373.24 | 222 | 5343 | 19.4 | 185 | 189 | 0 | 0 | 9 | 309
06:30 | 2829 | 1442 | 896 | 38 | 109 | 1398.92 | 221.5 | 5344.5 | 46.925 | 181 | 189 | 0 | 0 | 11 | 313.5
07:00 | 2826 | 1464 | 896 | 38 | 106 | 1424.6 | 221 | 5346 | 74.45 | 177 | 189 | 0 | 0 | 13 | 318
07:30 | 2812 | 1455.5 | 895.5 | 38 | 114 | 1446.025 | 196.5 | 5359 | 128.67 | 177 | 189 | 0 | 0 | 11.5 | 306.5
08:00 | 2798 | 1447 | 895 | 38 | 122 | 1467.45 | 172 | 5372 | 182.89 | 177 | 189 | 0 | 0 | 10 | 295
08:30 | 2780.5 | 1425.5 | 895.5 | 38 | 121 | 1440.53 | 197 | 5432 | 270.105 | 186 | 256 | 0 | 0 | 12 | 309
09:00 | 2763 | 1404 | 896 | 38 | 120 | 1413.61 | 222 | 5492 | 357.32 | 195 | 323 | 0 | 0 | 14 | 323
09:30 | 2768.5 | 1410 | 896.5 | 38 | 121 | 1358.56 | 222 | 5519 | 375.7 | 246.5 | 404 | 0 | 0 | 16 | 203
10:00 | 2774 | 1416 | 897 | 38 | 122 | 1303.51 | 222 | 5546 | 394.08 | 298 | 485 | 0 | 0 | 18 | 83
10:30 | 2772 | 1413.5 | 896.5 | 38 | 122 | 1205.805 | 222 | 5523.5 | 420.485 | 302 | 633.5 | 0 | 0 | 17 | 90.5
11:00 | 2770 | 1411 | 896 | 38 | 122 | 1108.1 | 222 | 5501 | 446.89 | 306 | 782 | 0 | 0 | 16 | 98
11:30 | 2751 | 1424.5 | 898.5 | 38 | 125 | 1108.8 | 222 | 5564.5 | 437.255 | 306 | 975.5 | 0 | 0 | 12 | 229
12:00 | 2732 | 1438 | 901 | 38 | 128 | 1109.5 | 222 | 5628 | 427.62 | 306 | 1169 | 0 | 0 | 8 | 360
12:30 | 2732 | 1431 | 901 | 38 | 135 | 1106.705 | 222 | 5635 | 468.65 | 286 | 1260 | 0 | 0 | 11.5 | 330.5
13:00 | 2732 | 1424 | 901 | 38 | 142 | 1103.91 | 222 | 5642 | 509.68 | 266 | 1351 | 0 | 0 | 15 | 301
13:30 | 2719 | 1399.5 | 887 | 38 | 143 | 1105.185 | 222 | 5622 | 443.245 | 244 | 1321.5 | 0 | 0 | 14.5 | 311.5
14:00 | 2706 | 1375 | 873 | 38 | 144 | 1106.46 | 222 | 5602 | 376.81 | 222 | 1292 | 0 | 0 | 14 | 322
14:30 | 2697 | 1411 | 887 | 38 | 142 | 1105.665 | 222 | 5680 | 318.865 | 232 | 1283.5 | 0 | 0 | 10 | 352
15:00 | 2688 | 1447 | 901 | 38 | 140 | 1104.87 | 222 | 5758 | 260.92 | 242 | 1275 | 0 | 0 | 6 | 382
15:30 | 2660.5 | 1426 | 901 | 38 | 137 | 1050.35 | 222 | 5742 | 256.93 | 235.5 | 1160.5 | 0 | 0 | 5 | 387
16:00 | 2633 | 1405 | 901 | 38 | 134 | 995.83 | 222 | 5726 | 252.94 | 229 | 1046 | 0 | 0 | 4 | 392
16:30 | 2632.5 | 1286.5 | 901 | 38 | 131 | 979.65 | 222 | 5674.5 | 209.03 | 221.5 | 1108.5 | 0 | 0 | 7.5 | 319
17:00 | 2632 | 1168 | 901 | 38 | 128 | 963.47 | 222 | 5623 | 165.12 | 214 | 1171 | 0 | 0 | 11 | 246
17:30 | 2569 | 1200.5 | 892.5 | 38 | 128 | 985.21 | 222 | 5636 | 97.395 | 214 | 1276 | 0 | 0 | 10.5 | 190.5
18:00 | 2506 | 1233 | 884 | 38 | 128 | 1006.95 | 222 | 5649 | 29.67 | 214 | 1381 | 0 | 0 | 10 | 135
18:30 | 2532.5 | 1231.5 | 884 | 38 | 137 | 1077.73 | 222 | 5834.5 | 14.835 | 444.5 | 1527.86 | 0 | 0 | 8.5 | 133
19:00 | 2559 | 1230 | 884 | 38 | 146 | 1148.51 | 222 | 6020 | 0 | 675 | 1674.72 | 0 | 0 | 7 | 131
19:30 | 2547 | 1275 | 884 | 38 | 148 | 1145.94 | 222 | 6132 | 0 | 710 | 2339.36 | 0 | 0 | 8 | 213
20:00 | 2554 | 1263 | 884 | 38 | 144 | 1109.78 | 222 | 6172 | 0 | 754 | 2242.36 | 0 | 0 | 10 | 201
20:30 | 2571 | 1264 | 884 | 38 | 141 | 1122.485 | 222 | 6190 | 0 | 742.5 | 2217.86 | 0 | 0 | 9.5 | 206.5
21:00 | 2588 | 1265 | 884 | 38 | 138 | 1135.19 | 222 | 6208 | 0 | 731 | 2193.36 | 0 | 0 | 9 | 212
21:30 | 2583.5 | 1238 | 884 | 38 | 136 | 1123.85 | 222 | 6220.5 | 0 | 668.5 | 2125.18 | 0 | 0 | 11.5 | 222
22:00 | 2579 | 1211 | 884 | 38 | 134 | 1112.51 | 222 | 6233 | 0 | 606 | 2057 | 0 | 0 | 14 | 232
22:30 | 2597 | 1257 | 886 | 38 | 139 | 1054.4 | 221.5 | 6233 | 0 | 599.5 | 1998 | 0 | 0 | 14.5 | 251.5
23:00 | 2615 | 1303 | 888 | 38 | 144 | 996.29 | 221 | 6233 | 0 | 593 | 1939 | 0 | 0 | 15 | 271
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 23-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 127 | 26 | 426 | 194 | 1862 | 636 | Ishurdi-Ghorashal Ckt-1 | Export | 3944290.91
1:00 | 139 | 36 | 426 | 202 | 1804 | 662
2:00 | 144 | 40 | 460 | 214 | 1810 | 660 |  | Import | 0
3:00 | 153 | 46 | 464 | 214 | 1760 | 692
4:00 | 157 | 52 | 470 | 212 | 1710 | 688 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 168 | 56 | 492 | 212 | 1794 | 690
6:00 | 174 | 64 | 490 | 206 | 1738 | 702 |  | Import | 0
7:00 | 174 | 62 | 496 | 204 | 1778 | 704
8:00 | 195 | 72 | 530 | 210 | 1944 | 738 | Sirajganj-Sreepur Ckt-1 | Export | 2810000
9:00 | 207 | 79 | 560 | 214 | 2058 | 828
10:00 | 210 | 85 | 582 | 238 | 1958 | 816 |  | Import | 0
11:00 | 198 | 85 | 512 | 224 | 1820 | 840
12:00 | 174 | 54 | 500 | 220 | 1806 | 806 | Sirajganj-Sreepur Ckt-2 | Export | 2822000
13:00 | 164 | 58 | 440 | 216 | 1692 | 742
14:00 | 162 | 59 | 480 | 210 | 1774 | 772 |  | Import | 0
15:00 | 174 | 60 | 480 | 220 | 1936 | 832
16:00 | 176 | 76 | 460 | 224 | 1842 | 818 | Gopalganj-Aminbazar Ckt-1 | Export | 22320000
17:00 | 165 | 66 | 440 | 184 | 1742 | 760
18:00 | 168 | 69 | 430 | 180 | 1872 | 710 |  | Import | 0
18:30 | 169 | 69 | 450 | 186 | 2048 | 718
19:00 | 168 | 57 | 460 | 220 | 1942 | 736 | Gopalganj-Aminbazar Ckt-2 | Export | 22390000
19:30 | 138 | 45 | 390 | 200 | 1894 | 690
20:00 | 132 | 39 | 360 | 180 | 1898 | 666 |  | Import | 0
21:00 | 141 | 43 | 380 | 192 | 1960 | 704
22:00 | 143 | 46 | 370 | 184 | 1904 | 674 |  | Total Export | 54286290.91
23:00 | 136 | 46 | 340 | 176 | 1876 | 676 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 364 | 06:00 | 352 | 15:00 | Madunaghat | 386 | 18:00 | 380 | 00:00
Amtali | 408 | 14:00 | 401 | 21:00 | Meghnaghat | 369 | 06:00 | 358 | 15:00
Ashuganj | 385 | 6:00 | 374 | 10:00 | Payra | 411 | 04:00 | 405 | 00:00
Bhulta | 380 | 06:00 | 367 | 15:00 | Rahanpur | 403 | 17:00 | 387 | 01:00
Bibiana | 372 | 06:00 | 364 | 15:00 | Rampal | 392 | 06:00 | 379 | 00:00
BIPTC | 404 | 18:30 | 397 | 00:00
Bogura | 384 | 18:30 | 364 | 00:00
Gopalganj | 383 | 06:00 | 370 | 19:30
Kaliakoir | 352 | 07:00 | 339 | 15:00
Korerhat | 384 | 18:00 | 375 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 221 | 05:00 | 212 | 15:00 | Ishurdi | 236 | 18:30 | 219 | 00:00
AKSML | 233 | 18:00 | 225 | 01:00 | Jhenaidah | 227 | 17:00 | 209 | 00:00
Aminbazar | 223 | 06:00 | 212 | 15:00 | Kachua | 221 | 18:00 | 212 | 00:00
Ashuganj | 221 | 18:00 | 213 | 13:00 | Kaliakoir | 217 | 04:00 | 209 | 15:00
Ashuganj-400 | 221 | 18:00 | 213 | 13:00 | Keranigonj | 219 | 05:00 | 210 | 15:00
Baghabari | 231 | 17:00 | 220 | 00:00 | Khulna(S) | 224 | 06:00 | 212 | 00:00
Barapukuria | 225 | 18:30 | 214 | 00:00 | Korerhat | 220 | 18:00 | 213 | 00:00
Barapukuria-230 | 225 | 18:30 | 214 | 00:00 | Madunaghat | 235 | 18:00 | 230 | 09:00
Barishal | 225 | 17:00 | 219 | 00:00 | Madunaghat-400 | 236 | 19:00 | 231 | 00:00
Bheramara | 235 | 18:30 | 217 | 00:00 | Maniknagar | 217 | 04:00 | 209 | 12:00
Bhulta | 219 | 06:00 | 210 | 12:00 | Meghnaghat | 224 | 06:00 | 217 | 16:00
Bibiana | 216 | 18:00 | 210 | 00:00 | Meghnaghat-400 | 221 | 06:00 | 211 | 10:00
BIPTC | 237 | 18:30 | 218 | 00:00 | Mirsorai | 223 | 18:00 | 218 | 00:00
Bogura | 241 | 18:30 | 228 | 00:00 | Naogaon | 228 | 18:30 | 207 | 00:00
Bogura-400 | 240 | 17:00 | 228 | 00:00 | Purbasadipur | 223 | 18:30 | 210 | 00:00
Borhanuddin | 229 | 17:00 | 224 | 00:00 | Rajshahi | 235 | 18:00 | 217 | 01:00
BSRM | 221 | 18:00 | 215 | 00:00 | Rampal | 223 | 06:00 | 212 | 00:00
Charfasson | 229 | 06:00 | 225 | 02:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 221 | 18:00 | 214 | 00:00 | Rampura | 219 | 06:00 | 209 | 12:00
Cumilla(N) | 217 | 18:00 | 210 | 00:00 | Shikalbaha | 235 | 19:00 | 229 | 11:00
Faridpur | 220 | 05:00 | 212 | 00:00 | Shyampur | 219 | 06:00 | 211 | 11:00
Fenchuganj | 217 | 07:00 | 211 | 00:00 | Siddhirganj | 221 | 14:00 | 211 | 14:00
Feni | 218 | 18:00 | 211 | 00:00 | Sirajgonj | 236 | 17:00 | 227 | 00:00
Ghorashal | 220 | 00:00 | 220 | 00:00 | Sreepur | 220 | 18:00 | 209 | 01:00
Ghorashal-230 | 205 | 17:00 | 194 | 15:00 | Tongi | 208 | 04:00 | 200 | 09:00
Gopalganj | 222 | 06:00 | 215 | 00:00
GPH | 229 | 18:00 | 224 | 00:00
Haripur | 219 | 06:00 | 211 | 00:00
Hasnabad | 218 | 07:00 | 211 | 11:00
Hathazari | 231 | 18:30 | 227 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 06:00 | 125 | 12:00 | Madunaghat | 136 | 18:00 | 132 | 09:00
Agargaon | 131 | 06:00 | 123 | 15:00 | Magura | 136 | 06:00 | 123 | 00:00
Agrabad | 135 | 20:00 | 130 | 08:00 | Mahasthangarh | 136 | 18:30 | 126 | 00:00
AKS | 131 | 14:00 | 128 | 05:00 | Maijdee | 123 | 17:00 | 118 | 00:00
Aminbazar | 125 | 06:00 | 120 | 10:00 | Manikganj | 125 | 17:00 | 116 | 15:00
Amnura | 138 | 18:30 | 126 | 01:00 | Maniknagar | 128 | 05:00 | 120 | 00:00
Ashuganj | 126 | 18:00 | 121 | 00:00 | Matarbari | 126 | 13:00 | 115 | 00:00
Ashuganj-230 | 130 | 18:00 | 126 | 00:00 | Matuail | 126 | 03:00 | 122 | 00:00
Bagerhat | 127 | 06:00 | 117 | 00:00 | Metrorail_Motijheel | 128 | 05:00 | 120 | 00:00
Bajitpur | 122 | 06:00 | 115 | 00:00 | Metrorail_Uttara | 126 | 05:00 | 116 | 15:00
Bakerganj | 130 | 08:00 | 126 | 00:00 | Millgate | 125 | 03:00 | 117 | 15:00
Bakulia | 135 | 18:00 | 130 | 00:00 | Mirpur | 125 | 07:00 | 118 | 11:00
Banani | 133 | 05:00 | 125 | 11:00 | Mirzapur | 125 | 13:00 | 118 | 19:00
Bangabhaban | 128 | 04:00 | 119 | 00:00 | Mithapukur | 134 | 18:00 | 122 | 00:00
Barapukuria | 137 | 17:00 | 126 | 00:00 | MI_Cement | 129 | 05:00 | 122 | 11:00
Barguna | 130 | 06:00 | 125 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 130 | 06:00 | 126 | 00:00 | Mogbazar | 134 | 04:00 | 127 | 12:00
Barishal-230 | 130 | 04:00 | 126 | 00:00 | Mongla | 127 | 07:00 | 117 | 00:00
Baroaulia | 134 | 18:00 | 131 | 00:00 | Motijheel | 128 | 04:00 | 119 | 00:00
Baroirhat | 127 | 14:00 | 123 | 00:00 | Muktagacha | 125 | 11:00 | 111 | 19:00
Bashundhara | 133 | 04:00 | 117 | 10:00 | Munshiganj | 126 | 18:00 | 121 | 00:00
BashundharaCement | 128 | 18:00 | 122 | 00:00 | Muradnagar | 123 | 18:00 | 117 | 01:00
Beanibazar | 121 | 18:00 | 115 | 00:00 | Mymensingh | 127 | 11:00 | 107 | 08:00
Benapole | 136 | 17:00 | 118 | 22:00 | Nabinagar | 122 | 04:00 | 115 | 15:00
Bhaluka | 123 | 18:00 | 114 | 02:00 | Naogaon | 137 | 18:30 | 124 | 00:00
Bhandaria | 129 | 18:00 | 120 | 00:00 | Narail | 137 | 08:00 | 123 | 23:00
Bhangura | 134 | 18:30 | 125 | 01:00 | Narinda | 128 | 05:00 | 120 | 00:00
Bheramara | 138 | 18:30 | 127 | 00:00 | Narshingdi | 124 | 18:00 | 112 | 00:00
Bheramara(GK) | 138 | 18:30 | 128 | 00:00 | Natore | 136 | 18:30 | 126 | 00:00
Bhulta | 122 | 17:00 | 119 | 01:00 | Nawabganj | 129 | 06:00 | 123 | 10:00
Bog-Sherpur | 136 | 17:00 | 127 | 00:00 | Netrakona | 115 | 17:00 | 107 | 00:00
Bogura | 139 | 18:30 | 130 | 00:00 | New | 126 | 04:00 | 119 | 11:00
Bogura-230 | 139 | 18:30 | 130 | 00:00 | Niamatpur | 134 | 17:00 | 126 | 00:00
Brahmanbaria | 124 | 18:30 | 118 | 00:00 | Noapara | 132 | 05:00 | 123 | 00:00
Cantonment | 130 | 04:00 | 122 | 15:00 | Pabna | 135 | 18:00 | 126 | 00:00
Chandina | 126 | 18:00 | 120 | 00:00 | Palashbari | 133 | 18:00 | 121 | 00:00
Chandpur | 127 | 17:00 | 119 | 04:00 | Panchagarh | 139 | 13:00 | 131 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 20:00 | 133 | 00:00 | Patiya | 138 | 02:00 | 130 | 00:00
Chapai | 135 | 17:00 | 124 | 00:00 | Patnitala | 134 | 18:30 | 124 | 00:00
Charsaidpur | 127 | 18:00 | 121 | 00:00 | Patuakhali | 130 | 08:00 | 125 | 00:00
Chauddagram | 125 | 18:00 | 120 | 00:00 | Payra | 134 | 04:00 | 132 | 00:00
Chhatak | 120 | 06:00 | 113 | 00:00 | PHP | 127 | 18:00 | 123 | 00:00
Chowmuhani | 124 | 18:00 | 119 | 00:00 | Postogola | 131 | 07:00 | 124 | 11:00
Chuadanga | 135 | 09:00 | 119 | 23:00 | Pubail | 125 | 18:30 | 116 | 11:00
Coxsbazar | 127 | 12:00 | 118 | 00:00 | Purbachal | 133 | 06:00 | 125 | 11:00
Cumilla(N) | 125 | 18:00 | 120 | 00:00 | Purbasadipur | 135 | 18:30 | 127 | 00:00
Cumilla(S) | 131 | 05:00 | 120 | 00:00 | Rahanpur | 135 | 17:00 | 128 | 00:00
Daganbhuiyan | 126 | 18:00 | 120 | 00:00 | Rahanpur-400 | 135 | 17:00 | 129 | 01:00
Daudkandi | 122 | 18:00 | 115 | 00:00 | Rahim | 127 | 06:00 | 122 | 10:00
DhakaUniversity | 133 | 06:00 | 125 | 15:00 | Rajbari | 125 | 06:00 | 119 | 00:00
Dhamrai | 124 | 03:00 | 117 | 15:00 | Rajendrapur | 122 | 18:00 | 115 | 01:00
Dhanmondi | 133 | 05:00 | 120 | 01:00 | Rajshahi | 135 | 18:30 | 125 | 00:00
Dohazari | 131 | 13:00 | 126 | 00:00 | Rajshahi-230 | 135 | 18:00 | 125 | 00:00
Faridpur | 127 | 07:00 | 123 | 00:00 | Ramganj | 124 | 18:00 | 117 | 00:00
Fatullah | 129 | 04:00 | 121 | 10:00 | Rampur | 134 | 19:30 | 130 | 09:00
Fenchuganj | 128 | 18:00 | 124 | 00:00 | Rampura | 133 | 06:00 | 125 | 12:00
Feni | 126 | 13:00 | 122 | 00:00 | Rangamati | 135 | 13:00 | 132 | 00:00
Feni-230 | 126 | 17:00 | 122 | 00:00 | Rangpur | 132 | 18:30 | 121 | 00:00
Ghatail | 123 | 13:00 | 111 | 00:00 | Ruppur | 138 | 18:30 | 128 | 00:00
Ghorashal | 125 | 20:00 | 117 | 15:00 | Saidpur | 134 | 11:00 | 127 | 19:30
Goalpara | 134 | 06:00 | 125 | 00:00 | Santhia | 135 | 18:30 | 126 | 00:00
Gollamari | 134 | 06:00 | 126 | 00:00 | Satkhira | 130 | 09:00 | 120 | 00:00
Gopalganj | 128 | 06:00 | 121 | 23:00 | Satmasjid | 130 | 05:00 | 123 | 12:00
Gopalganj-400 | 129 | 05:00 | 124 | 23:00 | Savar | 125 | 18:00 | 117 | 11:00
Gulshan | 132 | 06:00 | 125 | 11:00 | SevenRings | 127 | 18:30 | 117 | 11:00
Halishahar | 135 | 18:00 | 130 | 10:00 | ShahCement | 127 | 18:00 | 121 | 00:00
Haripur | 127 | 06:00 | 123 | 00:00 | Shahjadpur | 135 | 07:00 | 130 | 00:00
HaripurSBU | 126 | 05:00 | 123 | 01:00 | Shahjibazar | 122 | 18:00 | 115 | 00:00
Hasnabad | 132 | 06:00 | 123 | 15:00 | Shahmirpur | 136 | 13:00 | 130 | 00:00
Hathazari | 135 | 18:30 | 132 | 00:00 | Shariatpur | 128 | 06:00 | 122 | 00:00
Hatirjheel | 133 | 06:00 | 125 | 12:00 | Sherpur | 126 | 11:00 | 109 | 06:00
Ishurdi | 139 | 17:00 | 130 | 00:00 | Shikalbaha | 126 | 18:30 | 121 | 00:00
Jaldhaka | 132 | 13:00 | 123 | 00:00 | Shikalbaha-230 | 136 | 18:00 | 133 | 00:00
Jamalpur | 133 | 14:00 | 114 | 03:00 | Shitalakhya | 129 | 05:00 | 122 | 11:00
Jashore | 138 | 17:00 | 120 | 00:00 | Sholosohor | 135 | 18:00 | 130 | 11:00
Jhenaidah | 138 | 06:00 | 126 | 23:00 | Shomvuganj | 117 | 18:30 | 109 | 01:00
Jhenaidah-230 | 140 | 17:00 | 126 | 00:00 | Shyampur | 130 | 19:00 | 121 | 10:00
Joydebpur | 125 | 20:00 | 112 | 11:00 | Shyampur-230 | 128 | 05:00 | 117 | 11:00
Joypurhat | 135 | 18:30 | 124 | 00:00 | Siddhirganj | 127 | 05:00 | 123 | 00:00
Juldah | 136 | 14:00 | 131 | 00:00 | Sirajganj | 132 | 17:00 | 126 | 00:00
Kabirpur | 127 | 13:00 | 113 | 15:00 | Sitakunda | 134 | 18:00 | 131 | 00:00
Kachua | 126 | 17:00 | 120 | 00:00 | Sonargaon | 124 | 18:00 | 120 | 00:00
Kaliakoir | 129 | 17:00 | 121 | 15:00 | Sreemongol | 122 | 18:00 | 116 | 00:00
Kaliganj | 139 | 17:00 | 124 | 23:00 | Sreepur | 126 | 17:00 | 119 | 01:00
Kallyanpur | 127 | 05:00 | 118 | 15:00 | Srinagar | 129 | 06:00 | 123 | 11:00
Kalurghat | 136 | 18:30 | 133 | 00:00 | SSM | 140 | 19:30 | 134 | 11:00
Kamrangirchar | 129 | 05:00 | 117 | 10:00 | Sunamganj | 117 | 09:00 | 111 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 122 | 07:00 | 119 | 00:00
Kasba | 123 | 18:00 | 115 | 00:00 | Sylhet_(South) | 122 | 06:00 | 118 | 00:00
Kazla | 126 | 05:00 | 120 | 00:00 | Tangail | 124 | 13:00 | 114 | 19:00
Keranigonj | 129 | 04:00 | 124 | 10:00 | Taraganj | 132 | 17:00 | 124 | 10:00
Khagrachori | 134 | 13:00 | 131 | 01:00 | Tasnim | 124 | 18:00 | 120 | 00:00
Khulna | 133 | 05:00 | 125 | 00:00 | Thakurgaon | 138 | 18:30 | 130 | 00:00
Khulna(S) | 134 | 06:00 | 126 | 00:00 | TK | 136 | 19:30 | 132 | 00:00
Khulshi | 133 | 18:00 | 129 | 10:00 | Tongi | 128 | 04:00 | 122 | 15:00
Kishoreganj | 121 | 18:00 | 113 | 00:00 | Ullahpara | 134 | 18:30 | 125 | 00:00
Kodda | 127 | 19:00 | 114 | 23:00 | Ullon | 132 | 05:00 | 125 | 12:00
Korerhat | 130 | 18:00 | 126 | 00:00 | Uttara | 126 | 04:00 | 117 | 19:00
KSRM | 134 | 18:00 | 131 | 09:00 | UttaraNew | 126 | 03:00 | 116 | 15:00
Kulaura | 126 | 05:00 | 122 | 00:00 | Zigatola | 130 | 06:00 | 122 | 16:00
Kurigram | 130 | 18:00 | 118 | 00:00
Kushtia | 134 | 18:30 | 124 | 00:00
Laksam | 125 | 17:00 | 118 | 00:00
Lakshmipur | 123 | 18:00 | 117 | 00:00
Lalbag | 129 | 06:00 | 122 | 11:00
Lalmonirhat | 130 | 18:30 | 118 | 00:00
Madanganj | 128 | 18:00 | 122 | 00:00
Madaripur | 129 | 05:00 | 125 | 00:00
Madartek | 132 | 05:00 | 125 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division