## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 25-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-07-2026 | during | 25-07-2026 | during | 25-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 273 | 286 | 412 | 412 | 300 | 300 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 225 | 225 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 145 | 148 | 335 | 335 | 335 | 335 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 10 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 307 | 335 | 335 | 270 | 270 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 60 | 125 | 149.36 | 149.36 | 48 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 10 | 11 | 33 | 33 | 9 | 9 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 145 | 300 | 300 | 48 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 133 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 105 | 105 | 34 | 88 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 14 | 72 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 9 | 0 | 14 | 0 | 14 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 23.297 | 0 | 0 | 23.29 | 23.29 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 380 | 320 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 105 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6637.271 | 1395 | 1977.42 | 5757.93 | 5743.93 | 2184.12 | 2711.12
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 10 | 0 | 12 | 0 | 12 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 222 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 189 | 190 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 40 | 72 | 40 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 34 | 0 | 34 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 22 | 35 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.7 | 0 | 1.62 | 0 | 1.62 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 54.36 | 54.36 | 54.36 | 54 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 104 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 24 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 17 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1058 | 1224 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 12 | 20 | 15 | 12 | 15 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 1125 | 1150 | 1150 | 720 | 720 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2651.7 | 3049.36 | 4116.48 | 4189.86 | 3044.62 | 3143
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 187 | 188 | 221.25 | 221.25 | 185 | 185 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 280 | 280 | 350.01 | 350.01 | 300 | 300 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 200 | 200 | 342.01 | 342.01 | 300 | 300 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 39 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 32 | 40 | 40 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 141 | 142 | 163 | 163 | 150 | 150 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 97 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 116 | 124 | 84 | 78 | 150 | 150 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 5 | 89 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1054 | 1222 | 2369.44 | 2303.44 | 1492.2 | 1678.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-07-2026 | during | 25-07-2026 | during | 25-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 20.35 | 0 | 15 | 0 | 15 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.9 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 154 | 160 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 57 | 75 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 2.03 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 209.28 | 258 | 562.6 | 516.5 | 265.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 40 | 0 | 0 | 41 | 41 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 136 | 140 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 25 | 25 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 53 | 86 | 86 | 5 | 5 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 102 | 100 | 100 | 100 | 100 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 330 | 322 | 350 | 350 | 357 | 357 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1026 | 984 | 1095 | 1095 | 999 | 999
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 898 | 884 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 32 | 32 | 27 | 27 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 74 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 938 | 1201 | 1234.2 | 1234.2 | 1194.2 | 1194.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1948 | 2152 | 3556.2 | 3486.2 | 2344.2 | 2274.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 681 | 1050 | 700 | 1050 | 700 | 1050 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 1048 | 1163 | 1163.05 | 1163.05 | 1163.05 | 1163.05 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 257 | 307 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.23 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2326.23 | 2860 | 2781.05 | 3130.05 | 2607.05 | 2956.05
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 20.57 | 0 | 55 | 0 | 55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 159 | 152 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 316 | 326 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 12 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 101 | 101 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 107 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 6.35 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 917.14 | 998.94 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 47.98 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 85 | 0 | 85 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1577.04 | 1622.94 | 3250.62 | 3044.12 | 2356.24 | 2311.74
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 191 | 185 | 190 | 190 | 185 | 185 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.7 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 124 | 0 | 183.72 | 0 | 183.72 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 354.7 | 325 | 648.72 | 432 | 519.72 | 338
System Total |  |  |  |  | 28843.2 | 29137.464 | 12541.95 | 14450.72 | 24138.04 | 23941.1 | 15812.25 | 16670.31
Forecast Scenario (25-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15300 |  | 0 |  | 15300
|  |  |  | 1:00 | 14690 |  | 0 |  | 14690
|  |  |  | 2:00 | 14280 |  | 0 |  | 14280
|  |  |  | 3:00 | 13890 |  | 0 |  | 13890
|  |  |  | 4:00 | 13630 |  | 0 |  | 13630
|  |  |  | 5:00 | 13400 |  | 0 |  | 13400
|  |  |  | 6:00 | 13080 |  | 0 |  | 13080
|  |  |  | 7:00 | 12980 |  | 0 |  | 12980
|  |  |  | 8:00 | 13000 |  | 0 |  | 13000
|  |  |  | 9:00 | 13530 |  | 0 |  | 13530
|  |  |  | 10:00 | 13630 |  | 0 |  | 13630
|  |  |  | 11:00 | 13780 |  | 0 |  | 13780
|  |  |  | 12:00 | 14400 |  | 0 |  | 14400
|  |  |  | 13:00 | 14860 |  | 0 |  | 14860
|  |  |  | 14:00 | 14720 |  | 0 |  | 14720
|  |  |  | 15:00 | 14690 |  | 0 |  | 14690
|  |  |  | 16:00 | 14630 |  | 0 |  | 14630
|  |  |  | 17:00 | 14040 |  | 0 |  | 14040
|  |  |  | 18:00 | 13950 |  | 0 |  | 13950
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15340 |  | 0 |  | 15340
|  |  |  | 19:30 | 16190 |  | 0 |  | 16190
|  |  |  | 20:00 | 16110 |  | 0 |  | 16110
|  |  |  | 21:00 | 16350 |  | 0 |  | 16350
|  |  |  | 22:00 | 16210 |  | 0 |  | 16210
|  |  |  | 23:00 | 16210 |  | 0 |  | 16210
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 14400.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16350.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15891.75 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 344.98873 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:11 hrs on 25-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 24-07-2026 | [28 empty] | Date: | 24-07-2026 | [28 empty] | Date: | 24-07-2026 | [28 empty] | Date: | 24-07-2026 | [28 empty] | Date: | 24-07-2026 | [18 empty] | Date: | 24-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 23.297 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 17 | 17 | 36 | 94 | 113 | 55 | 35 | 17 | 0 | 0 | 141 | 305 | 0 | 0 | 312 | 0 | 0 | 0 | 143 | 8 | 22 | 0 | 0 | 61 | 51 | 33 | 0 | 18 | 34 | 19 | 17 | 25 | 25 | 0 | 222 | 106 | 2 | 1125 | 34 | 0 | 50 | 25.5 | 101 | 160 | 0 | 0 | 0 | 1190 | 0 | 100 | 0 | 0 | 280 | 200 | 43 | 0 | 186 | 0 | 34 | 142 | 174 | 0 | 19 | 98 | 138 | 30 | 0 | 32 | 310 | 0 | 353 | 42 | 0 | 146 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7531.5 | 902 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1207 | 0 | 0 | 0 | 1007.41 | 0 | 33 | 0 | 55 | 70 | 0 | 102 | 25 | 52 | 0 | 0 | 20 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 191 | 0 | 94 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 307 | 120 | 220 | 0 | 700 | 1120 | 54 | 6931.41 | 14462.91 | 103.23
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 17 | 0 | 35 | 60 | 113 | 55 | 35 | 17 | 0 | 0 | 138 | 295 | 0 | 0 | 293 | 0 | 0 | 0 | 68 | 9 | 0 | 0 | 0 | 90 | 51 | 83 | 0 | 13 | 34 | 52 | 0 | 25 | 25 | 0 | 220 | 107 | 2 | 1080 | 50 | 0 | 50 | 25.5 | 96 | 160 | 0 | 0 | 0 | 1140 | 0 | 100 | 0 | 0 | 280 | 200 | 43 | 0 | 190 | 0 | 34 | 142 | 170 | 0 | 8 | 96 | 134 | 52.2 | 0 | 32 | 305 | 0 | 339 | 42 | 0 | 131 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 0 | 47 | 0 | 48 | 0 | 0 | 0 | 1 | 7311.7 | 901 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1182 | 0 | 0 | 0 | 995.33 | 0 | 33 | 0 | 35 | 35 | 0 | 0 | 27 | 52.2 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 191 | 0 | 93 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 272 | 120 | 180 | 0 | 500 | 1095 | 35 | 6403.53 | 13715.23 | 103.24
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 17 | 0 | 35 | 60 | 113 | 55 | 35 | 17 | 0 | 0 | 139 | 295 | 0 | 0 | 260 | 0 | 0 | 0 | 68 | 9 | 0 | 0 | 0 | 87 | 51 | 89 | 0 | 19 | 0 | 52 | 0 | 25 | 25 | 0 | 222 | 106 | 20 | 1050 | 51 | 0 | 50 | 25.5 | 95 | 159 | 0 | 0 | 0 | 1100 | 0 | 100 | 0 | 0 | 280 | 200 | 51 | 0 | 192 | 0 | 34 | 142 | 168 | 0 | 19 | 96 | 134 | 52.2 | 0 | 32 | 300 | 0 | 339 | 40 | 0 | 131 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 0 | 47 | 0 | 48 | 0 | 0 | 0 | 12 | 7225.7 | 898 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 0 | 0 | 0 | 999.94 | 0 | 33 | 0 | 35 | 35 | 0 | 0 | 27 | 52.2 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 191 | 0 | 90 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 246 | 120 | 180 | 0 | 500 | 1055 | 35 | 6251.14 | 13476.84 | 103.24
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 20 | 60 | 113 | 55 | 35 | 17 | 0 | 0 | 140 | 305 | 0 | 0 | 298 | 0 | 0 | 0 | 68 | 9 | 0 | 0 | 0 | 0 | 51 | 49 | 0 | 15 | 0 | 0 | 0 | 25 | 25 | 0 | 222 | 107 | 25 | 1100 | 0 | 0 | 50 | 0 | 98 | 158 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 197 | 0 | 0 | 143 | 180 | 0 | 19 | 65 | 122 | 16 | 0 | 32 | 315 | 0 | 339 | 40 | 0 | 145 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 0 | 47 | 0 | 48 | 0 | 0 | 0 | 12 | 6875 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 994.83 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 191 | 0 | 85 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 277 | 120 | 220 | 0 | 500 | 1060 | 17 | 6170.83 | 13045.83 | 103.25
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 11 | 17 | 60 | 45 | 55 | 35 | 17 | 0 | 0 | 141 | 320 | 0 | 0 | 309 | 0 | 0 | 0 | 68 | 9 | 15 | 0 | 0 | 0 | 0 | 26 | 0 | 18 | 0 | 0 | 0 | 25 | 25 | 0 | 216 | 106 | 29 | 1100 | 0 | 0 | 33 | 0 | 17 | 159 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 199 | 0 | 0 | 143 | 155 | 0 | 19 | 0 | 120 | 0 | 0 | 32 | 315 | 0 | 347 | 40 | 0 | 150 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 0 | 47 | 0 | 48 | 0 | 0 | 0 | 12 | 6585 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1121 | 0 | 0 | 0 | 1001.77 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 191 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 277 | 120 | 220 | 0 | 500 | 1120 | 17 | 6166.77 | 12751.77 | 103.25
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 17 | 17 | 60 | 0 | 15 | 35 | 0 | 0 | 0 | 147 | 335 | 0 | 0 | 305 | 0 | 0 | 0 | 68 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 25 | 0 | 216 | 107 | 31 | 1125 | 0 | 0 | 19 | 0 | 16 | 159 | 0 | 0 | 0 | 1140 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 201 | 0 | 0 | 144 | 100 | 0 | 19 | 0 | 122 | 0 | 0 | 32 | 305 | 0 | 356 | 40 | 0 | 140 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 0 | 47 | 0 | 48 | 0 | 0 | 0 | 12 | 6423 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1132 | 0 | 0 | 0 | 998.21 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 191 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 278 | 120 | 220 | 0 | 500 | 1118 | 17 | 6128.21 | 12551.21 | 103.25
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 0 | 0 | 0 | 0 | 34 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 345 | 0 | 0 | 310 | 0 | 0 | 0 | 68 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0.09 | 216 | 33 | 31 | 1125 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 1115 | 1 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 201 | 0 | 0 | 144 | 0 | 0 | 19 | 0 | 118 | 0 | 1 | 16 | 305 | 0 | 330 | 40 | 0 | 130 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 101 | 0 | 47 | 0.44 | 48 | 0 | 0.2 | 0.49 | 12 | 6034.22 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 1150 | 0 | 0 | 0 | 993.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | 0 | 0 | 1.23 | 157 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0.1 | 191 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.4 | 8 | 0.01 | 0 | 249 | 120 | 220 | 0 | 500 | 1070 | 0 | 5918.67 | 11952.89 | 103.25
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 350 | 0 | 0 | 317 | 0 | 0 | 2 | 68 | 8 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0.51 | 222 | 0 | 27 | 1125 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 200 | 0 | 0 | 144 | 0 | 0 | 19 | 0 | 104 | 0 | 8 | 16 | 310 | 0 | 341 | 40 | 0 | 134 | 3 | 17 | 0 | 52 | 0 | 0 | 0 | 101 | 0 | 47 | 1.1 | 48 | 0 | 0.4 | 8.92 | 12 | 5972.93 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7.75 | 1080 | 0 | 0 | 0 | 995.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.88 | 9 | 0 | 0 | 5.66 | 159 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0.45 | 191 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0.9 | 19 | 0.08 | 0 | 246 | 120 | 220 | 0 | 500 | 1038 | 0 | 5860.81 | 11833.74 | 103.27
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 345 | 0 | 0 | 290 | 0 | 0 | 1 | 68 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 3.3 | 172 | 0 | 13 | 1050 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 1000 | 4 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 195 | 0 | 0 | 145 | 0 | 0 | 19 | 0 | 94 | 0 | 31 | 0 | 310 | 0 | 310 | 40 | 0 | 135 | 5 | 0 | 0 | 53 | 0 | 0 | 0 | 101 | 0 | 47 | 5.6 | 48 | 0 | 0.4 | 7.82 | 12 | 5733.12 | 888 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25.72 | 1025 | 0 | 0 | 0 | 1006.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.53 | 5 | 0 | 0 | 8.72 | 159 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0.46 | 191 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 2.9 | 49 | 0.18 | 0 | 241 | 120 | 220 | 0 | 500 | 1075 | 0 | 5900.93 | 11634.05 | 103.27
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 345 | 0 | 0 | 280 | 0 | 0 | 4 | 68 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 3.72 | 217 | 0 | 13 | 990 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 945 | 6 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 187 | 0 | 0 | 145 | 0 | 0 | 19 | 0 | 108 | 0 | 26 | 0 | 305 | 0 | 339 | 40 | 0 | 134 | 5 | 0 | 0 | 53 | 0 | 0 | 0 | 102 | 0 | 47 | 5.2 | 48 | 0 | 0.8 | 5 | 12 | 5698.72 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 35.61 | 927 | 0 | 0 | 0 | 1012.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.82 | 1 | 0 | 0 | 13.69 | 159 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 1.5 | 191 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 4.2 | 144 | 0.25 | 0 | 212 | 120 | 180 | 0 | 625 | 1076 | 0 | 5989.34 | 11688.06 | 103.28
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 345 | 0 | 0 | 305 | 0 | 0 | 4 | 68 | 9 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 4.61 | 222 | 0 | 21 | 950 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 850 | 2 | 0 | 0 | 0 | 280 | 200 | 20 | 0 | 187 | 0 | 0 | 145 | 0 | 0 | 19 | 0 | 104 | 0 | 16 | 0 | 305 | 0 | 340 | 40 | 0 | 135 | 7 | 17 | 0 | 53 | 0 | 0 | 0 | 100 | 0 | 47 | 12.36 | 121 | 0 | 1.4 | 13 | 12 | 5706.37 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 51 | 832 | 0 | 0 | 0 | 992.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.79 | 41 | 0 | 0 | 25.93 | 159 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 2.85 | 190 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 4.5 | 120 | 0.33 | 0 | 180 | 100 | 180 | 0 | 691 | 1048 | 0 | 5851.65 | 11558.02 | 103.28
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 360 | 0 | 0 | 295 | 0 | 0 | 18 | 68 | 9.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 4.62 | 222 | 0 | 21 | 950 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 908 | 7 | 0 | 0 | 0 | 280 | 200 | 26 | 0 | 187 | 0 | 0 | 143 | 0 | 0 | 14 | 0 | 108 | 0 | 23 | 0 | 315 | 0 | 339 | 40 | 0 | 146 | 12 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 0 | 47 | 20.3 | 124 | 0 | 0.3 | 55.09 | 12 | 5855.81 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 810 | 0 | 0 | 0 | 995.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.75 | 46 | 0 | 0 | 35.19 | 159 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 5.53 | 191 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 3.3 | 45 | 0.15 | 0 | 206 | 120 | 220 | 0 | 683 | 1072 | 0 | 5947.02 | 11802.83 | 103.28
12:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 0 | 0 | 0 | 35 | 60 | 15 | 10 | 0 | 14 | 0 | 0 | 145 | 380 | 0 | 0 | 300 | 0 | 0 | 9 | 105 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 1.7 | 222 | 0 | 22 | 1125 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 1058 | 10 | 0 | 0 | 0 | 280 | 200 | 39 | 0 | 187 | 0 | 5 | 141 | 0 | 0 | 19 | 0 | 116 | 0 | 67 | 0 | 305 | 0 | 330 | 42 | 0 | 136 | 12 | 17 | 0 | 83 | 0 | 0 | 0 | 101 | 0 | 57 | 20.35 | 116 | 0 | 1.9 | 2.03 | 12 | 6335.98 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 74 | 938 | 0 | 0 | 0 | 917.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.57 | 110 | 0 | 0 | 47.98 | 159 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 6.35 | 191 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 4.7 | 124 | 0.23 | 0 | 257 | 120 | 220 | 0 | 681 | 1048 | 0 | 6205.97 | 12541.95 | 103.28
13:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 17 | 0 | 68 | 45 | 60 | 21 | 17 | 41 | 0 | 0 | 150 | 345 | 0 | 17 | 297 | 0 | 0 | 9 | 123 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 0 | 25 | 1.8 | 222 | 13 | 24 | 1080 | 0 | 0 | 6 | 0 | 0 | 189 | 0 | 0 | 0 | 1190 | 6 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 187 | 0 | 24 | 142 | 25 | 0 | 19 | 0 | 116 | 0 | 79 | 0 | 310 | 0 | 329 | 41 | 0 | 141 | 12 | 17 | 0 | 81 | 0 | 0 | 0 | 101 | 0 | 57 | 17.92 | 116 | 0 | 0.8 | 53.04 | 12 | 6763.56 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 49 | 1130 | 0 | 0 | 0 | 1013.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.43 | 35 | 0 | 0 | 18.97 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 2.06 | 191 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 3.9 | 156 | 0.24 | 0 | 307 | 120 | 180 | 0 | 652 | 1085 | 0 | 6303.42 | 13066.98 | 103.28
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 17 | 0 | 51 | 30 | 30 | 30 | 17 | 0 | 0 | 0 | 147 | 315 | 0 | 0 | 319 | 0 | 0 | 17 | 105 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0.56 | 222 | 0 | 25 | 1050 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 1110 | 1 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 187 | 0 | 32 | 140 | 0 | 0 | 19 | 0 | 122 | 0 | 15 | 0 | 305 | 0 | 359 | 40 | 0 | 137 | 4 | 17 | 0 | 52 | 0 | 0 | 0 | 101 | 0 | 57 | 16.53 | 116 | 0 | 2.2 | 18.42 | 12 | 6316.71 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6 | 1135 | 0 | 0 | 0 | 978.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.46 | 111 | 0 | 0 | 14.28 | 145 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 1.43 | 191 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 6.6 | 37 | 0.32 | 0 | 244 | 100 | 180 | 0 | 684 | 1150 | 0 | 6286.14 | 12602.85 | 103.28
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 17 | 0 | 52 | 30 | 30 | 30 | 17 | 0 | 0 | 0 | 150 | 320 | 0 | 0 | 295 | 0 | 0 | 12 | 105 | 10 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 1.34 | 222 | 0 | 23 | 1050 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 1100 | 5 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 188 | 0 | 16 | 142 | 0 | 0 | 19 | 0 | 116 | 0 | 54 | 0 | 310 | 0 | 339 | 40 | 0 | 144 | 8 | 17 | 0 | 52 | 0 | 0 | 0 | 101 | 0 | 57 | 20.5 | 116 | 0 | 1.9 | 16.29 | 12 | 6270.03 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34 | 1079 | 0 | 0 | 0 | 987.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.86 | 43 | 0 | 0 | 18.28 | 153 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 1.57 | 191 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 5.8 | 58 | 0.24 | 0 | 238 | 120 | 220 | 0 | 695 | 1085 | 0 | 6217.79 | 12487.82 | 103.28
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 44 | 30 | 0 | 15 | 17 | 0 | 0 | 0 | 149 | 320 | 0 | 0 | 295 | 0 | 0 | 5 | 105 | 10 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.57 | 222 | 0 | 16 | 1000 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 1045 | 7 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 191 | 0 | 0 | 142 | 0 | 0 | 19 | 0 | 110 | 0 | 31 | 0 | 310 | 0 | 315 | 40 | 0 | 140 | 8 | 17 | 0 | 52 | 0 | 0 | 0 | 101 | 0 | 57 | 13.5 | 115 | 0 | 1.3 | 29.56 | 8 | 6005.93 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 37 | 1041 | 0 | 0 | 0 | 981.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.57 | 32 | 0 | 0 | 37.83 | 153 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 3.49 | 191 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 3 | 94 | 0.4 | 0 | 238 | 120 | 220 | 0 | 661 | 1000 | 0 | 6084.99 | 12090.92 | 103.27
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 35 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 148 | 315 | 0 | 0 | 300 | 0 | 0 | 5 | 143.42 | 10 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.89 | 222 | 0 | 18 | 1000 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 1000 | 4 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 195 | 0 | 0 | 142 | 0 | 0 | 19 | 0 | 106 | 0 | 14 | 0 | 310 | 0 | 312 | 40 | 0 | 134 | 3 | 8 | 0 | 52 | 0 | 0 | 0 | 101 | 0 | 60 | 6.66 | 115 | 0 | 0.7 | 8.78 | 12 | 5892.45 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 1013 | 0 | 0 | 0 | 925.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 33 | 0 | 0 | 9.82 | 153 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0.73 | 191 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0.7 | 63 | 0.05 | 0 | 199 | 120 | 220 | 0 | 639 | 990 | 0 | 5844.16 | 11736.61 | 103.27
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 35 | 15 | 0 | 15 | 0 | 0 | 0 | 0 | 148 | 320 | 0 | 0 | 300 | 0 | 0 | 1 | 143.42 | 10 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0.31 | 222 | 0 | 18 | 1000 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 1000 | 1 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 193 | 0 | 0 | 142 | 0 | 0 | 19 | 0 | 96 | 0 | 2 | 0 | 310 | 0 | 317 | 40 | 0 | 137 | 1 | 8 | 0 | 52 | 0 | 0 | 0 | 101 | 0 | 60 | 1.06 | 115 | 0 | 0.3 | 2.9 | 12 | 5858.99 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 1008 | 0 | 0 | 0 | 921.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.13 | 2 | 0 | 0 | 2.33 | 153 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0.17 | 191 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.8 | 17 | 0.03 | 0 | 199 | 120 | 220 | 0 | 667 | 990 | 0 | 5752.99 | 11611.98 | 103.27
19:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 17 | 0 | 57 | 143 | 60 | 18 | 17 | 35 | 0 | 0 | 147 | 320 | 0 | 0 | 322 | 0 | 0 | 0 | 143.42 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 0 | 5 | 0 | 24 | 0 | 222 | 3 | 27 | 1120 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 1070 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 196 | 0 | 12 | 142 | 7 | 0 | 19 | 0 | 126 | 0 | 0 | 18 | 305 | 0 | 350 | 40 | 0 | 137 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 102 | 1 | 58 | 0 | 140 | 0 | 0 | 0 | 12 | 6562.42 | 898 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 0 | 0 | 0 | 1024.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 20 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 190 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 120 | 220 | 0 | 1050 | 990 | 0 | 6370.26 | 12932.68 | 103.27
19:30 | 0 | 100 | 16 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 54 | 0 | 133 | 142 | 74 | 30 | 55 | 72 | 0 | 0 | 138 | 315 | 0 | 0 | 300 | 0 | 0 | 0 | 143.42 | 4.3 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 34 | 0 | 54.36 | 0 | 24 | 0 | 222 | 64 | 27 | 1125 | 17 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 1175 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 196 | 0 | 90 | 142 | 90 | 0 | 19 | 0 | 120 | 0 | 0 | 28 | 310 | 0 | 315 | 40 | 0 | 150 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 102 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 12 | 7257.08 | 898 | 0 | 0 | 38 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 0 | 0 | 0 | 1012.2 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 19 | 0 | 0 | 0 | 22 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 191 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 1050 | 1100 | 0 | 6660.2 | 13917.28 | 103.27
20:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 45.5 | 0 | 129 | 139 | 145 | 31 | 55 | 108 | 0 | 0 | 146 | 325 | 0 | 0 | 297 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 34 | 0 | 47 | 0 | 24 | 0 | 222 | 77 | 30 | 1125 | 16 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 196 | 0 | 70 | 142 | 64 | 0 | 19 | 0 | 124 | 0 | 0 | 32 | 310 | 0 | 315 | 40 | 0 | 145 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 17 | 70 | 0 | 153 | 0 | 0 | 0 | 12 | 7419.92 | 898 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1136 | 0 | 0 | 0 | 1003.12 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 27 | 0 | 0 | 0 | 12 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 184 | 0 | 70 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 1050 | 1126 | 0 | 6807.12 | 14227.04 | 103.26
21:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 54 | 0 | 133 | 125 | 145 | 55 | 35 | 72 | 0 | 0 | 148 | 320 | 0 | 0 | 307 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 0 | 54.36 | 0 | 24 | 0 | 222 | 104 | 35 | 1125 | 17 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 188 | 0 | 89 | 142 | 97 | 0 | 19 | 0 | 124 | 0 | 0 | 32 | 310 | 0 | 322 | 40 | 0 | 140 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 17 | 75 | 0 | 154 | 0 | 0 | 0 | 12 | 7490.78 | 884 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1201 | 0 | 0 | 0 | 998.94 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 27 | 0 | 0 | 0 | 12 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 185 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 120 | 220 | 0 | 1050 | 1163 | 0 | 6959.94 | 14450.72 | 103.26
22:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 17 | 0 | 133 | 125 | 145 | 55 | 35 | 100 | 0 | 0 | 138 | 330 | 0 | 10 | 295 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 34 | 0 | 54.36 | 0 | 62 | 0 | 222 | 106 | 40 | 1125 | 38 | 0 | 0 | 0 | 1 | 190 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 183 | 0 | 71 | 143 | 112 | 0 | 19 | 0 | 124 | 0 | 0 | 32 | 315 | 0 | 306 | 42 | 0 | 149 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 102 | 17 | 67 | 0 | 153 | 0 | 0 | 0 | 12 | 7491.78 | 883 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1202 | 0 | 0 | 0 | 1009.72 | 0 | 0 | 0 | 20 | 113 | 0 | 0 | 27 | 0 | 0 | 0 | 12 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 185 | 0 | 70 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 307 | 120 | 220 | 0 | 1050 | 1163 | 0 | 6992.72 | 14484.5
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 2 | 133 | 125 | 220 | 55 | 45 | 155 | 0 | 0 | 146 | 315 | 0 | 35 | 308 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 1 | 16 | 0 | 0 | 12 | 34 | 0 | 54.36 | 0 | 62 | 0 | 222 | 107 | 35 | 1125 | 52 | 0 | 0 | 0 | 68 | 189 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 180 | 0 | 70 | 143 | 158 | 15 | 19 | 5 | 136 | 0 | 0 | 32 | 305 | 0 | 317 | 42 | 0 | 126 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 102 | 17 | 67 | 0 | 154 | 0 | 0 | 0 | 12 | 7707.78 | 884 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 1014.5 | 0 | 0 | 0 | 100 | 113 | 0 | 0 | 25 | 0 | 0 | 0 | 12 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 185 | 0 | 91 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 120 | 220 | 0 | 700 | 1163 | 36 | 6797.5 | 14505.28
Total KWH | 0 | 494400 | 50880 | 0 | 0 | 0 | 0 | 0 | 6717600 | 0 | 0 | 259200 | 79560 | 1399248 | 1705920 | 1365196 | 706377 | 486769 | 676800 | 0 | 0 | 3460538 | 7959050 | 0 | 96734 | 7201930 | 0 | 0 | 79257 | 2520000 | 221400 | 417960 | 0 | 0 | 260945 | 208255 | 258240 | 0 | 301920 | 233818 | 92208 | 322523 | 120000 | 383040 | 23641 | 5260518 | 1242800 | 562560 | 25745454.55 | 304436 | 0 | 277440 | 51451.2 | 542799 | 4160876 | 0 | 0 | 0 | 26061810 | 48735 | 292727 | 0 | 0 | 7169800 | 5020000 | 1165717 | 0 | 4701000 | 0 | 555840 | 3410828 | 1514400 | 42840 | 463930 | 349980 | 2810880 | 134755 | 333082 | 361680 | 7476000 | 0 | 8092000 | 965000 | 0 | 3319527.27 | 79100 | 317760 | 0 | 1307520 | 0 | 0 | 0 | 2431510 | 75600 | 1305600 | 98197 | 2282400 | 0 | 10850 | 211440 | 281040 | 158943292.02 | 21647273 | 0 | 0 | 172800 | 0 | 912000 | 0 | 0 | 0 | 0 | 0 | 392400 | 25832730 | 0 | 0 | 0 | 23862662 | 0 | 62267 | 0 | 369888 | 641376 | 0 | 28880 | 157757 | 115368 | 204424 | 464310 | 71249 | 0 | 240592 | 3713455 | 0 | 0 | 0 | 0 | 0 | 7211127 | 0 | 22380 | 4670000 | 0 | 767919 | 193060 | 698448 | 0 | 0 | 0 | 42790.08 | 1019520 | 2292 | 663648 | 6196000 | 2825000 | 5308820 | 0 | 16421818 | 26343272.73 | 236400 | 151511925.81 | 310455217.83

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 24-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 12541.95 | MW | 12:00 Hr. | Energy Generated |  |  | 310.4552 |  | MKWHr.
| Day Peak Demand |  |  | 12735.95 | MW | 12:00 Hr. | Energy Unserverd |  |  | 8.868 |  | MKWHr.
| Evening Peak Generation |  |  | 14450.72 | MW | 21:00 Hr. | Energy Demand |  |  | 319.3232 |  | MKWHr.
| Evening Peak Demand |  |  | 14682.72 | MW | 21:00 Hr. | Maximum Temperature |  |  | 31.4 |  | °C
| Minimum Generation of the Day |  |  | 11558.02 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 689.21 |  | MMCFD
| Maximum Generation of the Day |  |  | 14505.28 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 6.5454 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.9785 | 0 | 9.8411 | 0 | 0 | 0.079257 | 0 | 0 | 35.8988 | Gas | 95.6009 | Gas | 333357540.1484
| Chattogram Zone |  |  | 4.7234 | 51.8073 | 4.298 | 0 | 5.2605 | 0.072376 | 0 | 0.30192 | 66.4635 | Coal | 131.2711 | Coal | 883717859.5883
| Cumilla Zone |  |  | 21.9313 | 0 | 3.2522 | 0 | 0 | 0.33308 | 2.8109 | 0 | 28.3275 | HFO | 25.3219 | HFO | 456183663.958
| Mymensingh Zone |  |  | 0 | 0 | 3.9446 | 0 | 0 | 0.32049 | 0 | 0 | 4.2651 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.9093 | 0 | 0 | 0 | 0 | 0.0791 | 0 | 0 | 23.9884 | Hydro | 5.2605 | Hydro | 526051.8
| Khulna Zone |  |  | 0 | 25.8327 | 0.1728 | 0 | 0 | 0.3924 | 22.5593 | 0 | 48.9572 | Solar | 3.4661 | Solar | 56218649.9964
| Barishal Zone |  |  | 8.1338 | 48.9611 | 0.90005 | 0 | 0 | 0.002292 | 0 | 0 | 57.9973 | Import | 49.2328 | Import | 297605567.82
| Rajshahi Zone |  |  | 10.9246 | 0 | 1.4468 | 0 | 0 | 0.93171 | 23.8627 | 0 | 37.1657 | Wind | 0.30192 | Wind | 4441243.2
| Rangpur Zone |  |  | 0 | 4.67 | 1.4664 | 0 | 0 | 1.2554 | 0 | 0 | 7.3917
| Total |  |  | 95.6009 | 131.2711 | 25.3219 | 0 | 5.2605 | 3.4661 | 49.2328 | 0.30192 | 310.4552
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 333357540.1484 |  | Hydro | 526051.8
|  |  |  | Coal | 883717859.5883 |  | Solar | 56218649.9964
|  |  |  | HFO | 456183663.958 |  | Import | 297605567.82
|  |  |  | HSD | 0 |  | Wind | 4441243.2
[5 empty] | Total: | 203,20,50,576 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6473 | Peak Hr Flow | 884.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47936636.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.8627 | Peak Hr Flow | 998.94 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2175 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.8109 | Peak Hr Flow | 124.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2516 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.3208 | Peak Hr Flow | 2006.94 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4891
|  |  |  | Chattogram |  | 0 |  | 1309
|  |  |  | Cumilla |  | 0 |  | 1327
|  |  |  | Mymensingh |  | 142 |  | 1311
|  |  |  | Sylhet |  | 80 |  | 705
|  |  |  | Khulna |  | 0 |  | 1656
|  |  |  | Barishal |  | 0 |  | 451
|  |  |  | Rajshahi |  | 0 |  | 1458
|  |  |  | Rangpur |  | 0 |  | 952
|  |  |  | Total |  | 222 |  | 14060
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 89
|  |  |  | Total Unavailable Capacity |  |  |  | 389
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:20 | Munshiganj 132/33kV S/S Transformer-2 LT is restored.
| 08:34 | 13:11 | Ghorasal- Ishwardi 230 kV Ckt-1 Project Work S/D from Ishurdi 230/132kV end.
| 08:46 | 11:36 | Kushtia 132/33kV S/S T-2 LT Scheduled S/D Due to Wzpdcl 33kv mozompur feeder bus isolator | [7 empty] | 15.0MW load
|  |  | clamp change | [7 empty] | interrup.
| 08:47 | 11:35 | Kushtia 132/33kV S/S T-2 HT Scheduled S/D Due to Wzpdcl 33kv mozompur feeder bus isolator | [7 empty] | 15.0MW load
|  |  | clamp change | [7 empty] | interrup.
|  | 09:26 | Narail 132/33kV S/S TR1 (403-T) HT is restored.
|  | 09:28 | Narail 132/33kV S/S TR1 (403-T) LT is restored.
| 10:10 | 16:29 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Scheduled S/D Due to
132/33kV X-Former GT-4 33kV Side Redhot Remove.
| 10:10 | 16:30 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to
132/33kV X-Former GT-4 33kV Side Redhot Remove.
| 11:25 | 14:19 | Haripur-Haripur (360MW) 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to
Multifuntional Meter Changing work
|  | 11:26 | Chhatak 132/33kV S/S T-1 LT is restored.
|  | 11:26 | Chhatak 132/33kV S/S T-1 HT is restored.
| 12:00 |  | Day Peak Generation: 12542 MW.
| 12:01 | 16:21 | Kushtia 132/33kV S/S T-3 LT Project Work S/D Due to DWZTGE project work for newly
meherpur bay
| 12:02 | 16:20 | Kushtia 132/33kV S/S T-3 HT Project Work S/D Due to DWZTGE project work for newly
meherpur bay
| 12:20 |  | Kushtia 132/33kV S/S 132 KV Bus-A Project Work S/D Due to DWZTGE project work for newly
meherpur bay
|  | 12:40 | Saidpur 132/33kV S/S TR-3 (424T) HT is restored.
|  | 12:41 | Saidpur 132/33kV S/S TR-3 (424T) LT is restored.
|  | 12:55 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT is restored.
|  | 12:56 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT is restored.
|  | 13:07 | Nawabganj 132/33kV S/S TR-2 LT is restored.
|  | 14:56 | Kishoreganj-Mymensingh 132kV Ckt-2 is restored.
|  | 15:33 | Kishoreganj-Mymensingh 132kV Ckt-1 is restored.
| 21:00 |  | Evening Peak Generation: 14451 MW
| 21:00 |  | Evening Peak Generation: 14451 MW
| 21:29 | 21:41 | Dohazari 132/33kV S/S Power Transformer -T-1 LT Tripped showing Lockout Relay | [7 empty] | 35.0MW load
|  |  | K861, Lockout Relay K862 relays Due to Due to Banshkhali 33 KV feeder O/C & E/F | [7 empty] | interrup.
| 00:30 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown with remarks:- ST
| 00:50 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown with remarks:- GT
| 00:51 | 01:36 | Dohazari 132/33kV S/S Power Transformer -T-1 HT Scheduled S/D Due to Due to Banshkhali 33 | [7 empty] | 25.0MW load
|  |  | KV feeder BUS DS maintenance . | [7 empty] | interrup.
| 00:51 | 01:36 | Dohazari 132/33kV S/S Power Transformer -T-1 LT Scheduled S/D Due to Due to Banshkhali 33 | [7 empty] | 25.0MW load
|  |  | KV feeder BUS DS maintenance . | [7 empty] | interrup.
| 06:00 |  | Minimum generation is 12274 MW.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 24-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 286 | 6717600 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 148 | 3460538 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 706377 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 307 | 7201930 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 259200 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 1705920 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 486769 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 96734 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11 | 221400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 417960 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 50880 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 1365196 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 1399248 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 494400 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 676800 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 79257 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 23.297 | 0 | 79560 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 320 | 7959050 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 2520000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6637.271 | 1977.42 | 35898819
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 51451.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 48735 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 277440 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5260518 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 190 | 4160876 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 542799 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 92208 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 233818 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 120000 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 35 | 562560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 258240 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23641 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 208255 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 322523 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 104 | 1242800 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 383040 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 260945 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 17 | 304436 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 26061810 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 20 | 301920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 25745454.55 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 3049.36 | 66463469.75
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 188 | 4701000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 280 | 7169800 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 200 | 5020000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1165717 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 292727 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 32 | 361680 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 142 | 3410828 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 97 | 1514400 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 124 | 2810880 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 134755 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 463930 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 349980 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 42840 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 555840 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 333082 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1222 | 28327459
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 98197 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 154 | 2282400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 75 | 1305600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 211440 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 281040 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 75600 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 258 | 4265127
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 79100 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 965000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 140 | 3319527.27 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 53 | 1307520 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 2431510 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 317760 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7476000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 322 | 8092000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 984 | 23988417.27
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 884 | 21647273 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 172800 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 392400 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1201 | 25832730 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2152 | 48957203
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1050 | 16421818 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 663648 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2825000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 1163 | 26343272.73 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5308820 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 236400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6196000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2292 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2860 | 57997250.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 204424 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 62267 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 157757 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 152 | 3713455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 326 | 7211127 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 12 | 71249 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 115368 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 28880 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 107 | 641376 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 369888 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 22380 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 998.94 | 23862662 | Machine Problem
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 240592 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 464310 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1622.94 | 37165735
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 185 | 4670000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 698448 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42790.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 767919 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 193060 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1019520 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 325 | 7391737.08
Eastern Grid Total |  |  |  |  | 17406.339 | 7490.78 | 158943292.02
Western Grid Total |  |  |  |  | 11731.125 | 6959.94 | 151511925.81
National Grid Total |  |  |  |  | 29137.464 | 14450.72 | 310455217.83
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9357.9 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4517.4 | MW
i) Dhaka area |  |  | 4891.1 |  | MW | i) Khulna area |  |  |  | 1656 | MW
ii) Chattogram area |  |  | 1345.8 |  | MW | ii) Barishal area |  |  |  | 451 | MW
iii) Cumilla area |  |  | 1327 |  | MW | iii) Rajshahi area |  |  |  | 1458.4 | MW
iv) Mymensingh area |  |  | 1169 |  | MW | iv) Rangpur area |  |  |  | 952 | MW
v) Sylhet area |  |  | 625 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13875.3 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 138 | 00:00 | 133 | Narshingdi | 190 | 00:00 | 199 | Uttara | 80 | 19:30
2 | AKSML | 151.5 | 07:00 | 68 | Hasnabad | 80 | 00:00 | 134 | Natore | 146 | 20:00 | 200 | UttaraNew | 52 | 13:00
3 | Aftabnagar | 40 | 12:00 | 69 | Hathazari | 80 | 22:00 | 135 | Nawabganj | 60.2 | 23:00 | 201 | Zigatola | 98 | 13:00
4 | Agargaon | 102 | 13:00 | 70 | Hatirjheel | 61 | 15:00 | 136 | Netrakona | 129 | 18:30
5 | Agrabad | 54 | 21:00 | 71 | Ishurdi | 73 | 20:00 | 137 | New | 68 | 00:00
6 | Amnura | 30 | 00:00 | 72 | Jaldhaka | 90 | 20:00 | 138 | Niamatpur | 83 | 23:00
7 | Ashuganj | 84 | 00:00 | 73 | Jamalpur | 130 | 19:30 | 139 | Noapara | 36 | 01:00
8 | BSRM | 187 | 00:00 | 74 | Jashore | 128 | 00:00 | 140 | PHP | 9 | 00:00
9 | Bagerhat | 86.5 | 20:00 | 75 | Jhenaidah | 89 | 19:30 | 141 | Pabna | 92 | 19:30
10 | Bajitpur | 98 | 20:00 | 76 | Joydebpur | 139 | 20:00 | 142 | Palashbari | 130 | 00:00
11 | Bakerganj | 14.2 | 23:00 | 77 | Joypurhat | 68 | 23:00 | 143 | Panchagarh | 63 | 00:00
12 | Bakulia | 77 | 00:00 | 78 | Juldah | 14 | 00:00 | 144 | Patiya | 10 | 00:00
13 | Banani | 46 | 19:00 | 79 | KSRM | 17 | 03:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 4 | 20:00 | 80 | Kabirpur | 203 | 06:00 | 146 | Patuakhali | 64 | 22:00
15 | Barapukuria | 65 | 20:00 | 81 | Kachua | 92 | 19:30 | 147 | Payra | 34 | 22:00
16 | Barguna | 20 | 02:00 | 82 | Kaliganj | 34 | 19:30 | 148 | Postogola | 52 | 13:00
17 | Barishal | 91 | 00:00 | 83 | Kallyanpur | 117 | 13:00 | 149 | Pubail | 46 | 20:00
18 | Barishal-230 | 96 | 23:00 | 84 | Kalurghat | 32 | 00:00 | 150 | Purbachal | 27 | 13:00
19 | Baroaulia | 41 | 09:00 | 85 | Kamrangirchar | 69 | 00:00 | 151 | Purbasadipur | 139 | 23:00
20 | Baroirhat | 60 | 00:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 42 | 22:00
21 | Bashundhara | 177 | 13:00 | 87 | Kasba | 40 | 23:00 | 153 | Rahim | 47 | 01:00
22 | BashundharaCement | 1 | 00:00 | 88 | Kazla | 107 | 13:00 | 154 | Rajbari | 83 | 19:30
23 | Beanibazar | 82 | 20:00 | 89 | Keranigonj | 74 | 00:00 | 155 | Rajendrapur | 123 | 22:00
24 | Benapole | 54 | 22:00 | 90 | Khagrachori | 32 | 19:30 | 156 | Rajshahi | 102 | 21:00
25 | Bhaluka | 151 | 00:00 | 91 | Khulna | 51 | 19:30 | 157 | Rajshahi-230 | 93 | 13:00
26 | Bhandaria | 58 | 23:00 | 92 | Khulshi | 165 | 12:00 | 158 | Ramganj | 110 | 19:30
27 | Bhangura | 38 | 19:30 | 93 | Kishoreganj | 122 | 21:00 | 159 | Rampur | 38 | 00:00
28 | Bheramara(GK) | 64 | 20:00 | 94 | Kodda | 261 | 19:00 | 160 | Rangamati | 16 | 19:30
29 | Bhulta | 189 | 05:00 | 95 | Kulaura | 58 | 19:30 | 161 | Rangpur | 136 | 20:00
30 | Bog-Sherpur | 72 | 00:00 | 96 | Kurigram | 74 | 20:00 | 162 | Ruppur | 17 | 13:00
31 | Bogura | 175 | 22:00 | 97 | Kushtia | 130 | 20:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 74 | 22:00 | 98 | Laksam | 34 | 01:00 | 164 | Saidpur | 97 | 01:00
33 | Brahmanbaria | 121 | 00:00 | 99 | Lakshmipur | 44 | 19:00 | 165 | Santhia | 34 | 19:00
34 | Cantonment | 112 | 13:00 | 100 | Lalbag | 69 | 00:00 | 166 | Satkhira | 128 | 19:30
35 | Chandina | 45 | 01:00 | 101 | Lalmonirhat | 76 | 19:30 | 167 | Satmasjid | 91 | 13:00
36 | Chandpur | 86 | 23:00 | 102 | MI_Cement | 16 | 23:00 | 168 | Savar | 174 | 00:00
37 | Chandraghona | 33 | 12:00 | 103 | Madanganj | 43 | 00:00 | 169 | SevenRings | 16.28 | 01:00
38 | Chapai | 72 | 23:00 | 104 | Madaripur | 112 | 23:00 | 170 | ShahCement | 34 | 01:00
39 | Charfasson | 30 | 00:00 | 105 | Madartek | 77 | 13:00 | 171 | Shahjadpur | 69 | 19:30
40 | Charsaidpur | 45 | 21:00 | 106 | Madunaghat | 47 | 20:00 | 172 | Shahjibazar | 110 | 00:00
41 | Chauddagram | 77 | 00:00 | 107 | Magura | 68 | 21:00 | 173 | Shahmirpur | 46 | 00:00
42 | Chhatak | 41 | 21:00 | 108 | Mahasthangarh | 80 | 21:00 | 174 | Shariatpur | 95 | 22:00
43 | Chowmuhani | 147 | 23:00 | 109 | Maijdee | 38 | 22:00 | 175 | Sherpur | 152 | 19:30
44 | Chuadanga | 108 | 22:00 | 110 | Manikganj | 132 | 22:00 | 176 | Shikalbaha | 32 | 00:00
45 | Coxsbazar | 134 | 20:00 | 111 | Maniknagar | 70 | 13:00 | 177 | Shitalakhya | 53.4 | 13:00
46 | Cumilla(N) | 119 | 00:00 | 112 | Matarbari | 52 | 19:30 | 178 | Sholosohor | 40 | 01:00
47 | Cumilla(S) | 137 | 00:00 | 113 | Matuail | 70 | 00:00 | 179 | Shomvuganj | 37 | 18:30
48 | Daganbhuiyan | 36 | 05:00 | 114 | Metrorail_Motijheel | 25 | 17:00 | 180 | Shyampur | 152 | 00:00
49 | Daudkandi | 141 | 20:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 103 | 21:00
50 | DhakaUniversity | 42 | 13:00 | 116 | Millgate | 80 | 00:00 | 182 | Sirajganj | 102 | 00:00
51 | Dhamrai | 100 | 00:00 | 117 | Mirpur | 136 | 13:00 | 183 | Sitakunda | 30 | 01:00
52 | Dhanmondi | 84 | 13:00 | 118 | Mirsorai | 44 | 07:00 | 184 | Sonargaon | 143 | 00:00
53 | Dohazari | 108 | 21:00 | 119 | Mirzapur | 45 | 19:30 | 185 | Sreemongol | 81 | 00:00
54 | Faridpur | 170 | 23:00 | 120 | Mithapukur | 78 | 19:30 | 186 | Sreepur | 100 | 20:00
55 | Fatullah | 90 | 00:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 47.77 | 22:00
56 | Fenchuganj | 46 | 19:30 | 122 | Mogbazar | 17.3 | 21:00 | 188 | Sunamganj | 65 | 19:00
57 | Feni | 94 | 00:00 | 123 | Mongla | 35 | 02:00 | 189 | Sylhet | 112 | 21:00
58 | GPH | 71 | 17:00 | 124 | Motijheel | 36 | 13:00 | 190 | Sylhet_(South) | 69 | 21:00
59 | Ghatail | 100 | 22:00 | 125 | Muktagacha | 42 | 19:30 | 191 | TK | 24 | 00:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 108 | 23:00 | 192 | Tangail | 176 | 19:30
61 | Ghorashal-230 | 108 | 01:00 | 127 | Muradnagar | 50 | 23:00 | 193 | Taraganj | 26 | 08:00
62 | Goalpara | 36 | 13:00 | 128 | Mymensingh | 163 | 21:00 | 194 | Tasnim | 34 | 08:00
63 | Gollamari | 90 | 13:00 | 129 | Nabinagar | 94 | 00:00 | 195 | Thakurgaon | 112 | 20:00
64 | Gopalganj | 107 | 19:30 | 130 | Naogaon | 138 | 23:00 | 196 | Tongi | 150 | 00:00
65 | Gulshan | 76 | 15:00 | 131 | Narail | 54 | 20:00 | 197 | Ullahpara | 37 | 19:30
66 | Halishahar | 67.5 | 00:00 | 132 | Narinda | 48 | 13:00 | 198 | Ullon | 53 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 24-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14462.91 | 683 |  | 15176.91
1:00 | 13715.23 | 924 |  | 14681.23
2:00 | 13476.84 | 514 |  | 14013.84
3:00 | 13045.83 | 486 |  | 13553.83
4:00 | 12751.77 | 557 |  | 13333.77
5:00 | 12551.21 | 511 |  | 13085.21
6:00 | 11952.89 | 439 |  | 12411.89
7:00 | 11833.74 | 486 |  | 12341.74
8:00 | 11634.05 | 410 |  | 12062.05
9:00 | 11688.06 | 402 |  | 12108.15
10:00 | 11558.02 | 254 |  | 11823.02
11:00 | 11802.83 | 238 |  | 12051.83
12:00 | 12541.95 | 186 |  | 12735.95
13:00 | 13066.98 | 248 |  | 13325.98
14:00 | 12602.85 | 245 |  | 12858.85
15:00 | 12487.82 | 166 |  | 12660.82
16:00 | 12090.92 | 176 |  | 12274.92
17:00 | 11736.61 | 173 |  | 11917.61
18:00 | 11611.98 | 171 |  | 11790.98
19:00 | 12932.68 | 320 |  | 13267.08
19:30 | 13917.28 | 340 |  | 14272.28
20:00 | 14227.04 | 310 |  | 14551.04
21:00 | 14450.72 | 222 |  | 14682.72
22:00 | 14484.5 | 323 |  | 14822.5
23:00 | 14505.28 | 424 |  | 14948.36
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 24-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7531.5 | 6931.41 | 14462.91 | DAILY GENERATION CURVE
00:30 | 7421.6 | 6667.47 | 14089.07
01:00 | 7311.7 | 6403.53 | 13715.23 | 24-07-2026
01:30 | 7268.7 | 6327.335 | 13596.035
02:00 | 7225.7 | 6251.14 | 13476.84
02:30 | 7050.35 | 6210.985 | 13261.335
03:00 | 6875 | 6170.83 | 13045.83
03:30 | 6730 | 6168.8 | 12898.8
04:00 | 6585 | 6166.77 | 12751.77
04:30 | 6504 | 6147.49 | 12651.49
05:00 | 6423 | 6128.21 | 12551.21
05:30 | 6228.61 | 6023.44 | 12252.05
06:00 | 6034.22 | 5918.67 | 11952.89
06:30 | 6003.575 | 5889.74 | 11893.315
07:00 | 5972.93 | 5860.81 | 11833.74
07:30 | 5853.025 | 5880.87 | 11733.895
08:00 | 5733.12 | 5900.93 | 11634.05
08:30 | 5715.92 | 5945.135 | 11661.055
09:00 | 5698.72 | 5989.34 | 11688.06
09:30 | 5702.545 | 5920.495 | 11623.04
10:00 | 5706.37 | 5851.65 | 11558.02
10:30 | 5781.09 | 5899.335 | 11680.425
11:00 | 5855.81 | 5947.02 | 11802.83
11:30 | 6095.895 | 6076.495 | 12172.39
12:00 | 6335.98 | 6205.97 | 12541.95
12:30 | 6549.77 | 6254.695 | 12804.465
13:00 | 6763.56 | 6303.42 | 13066.98
13:30 | 6540.135 | 6294.78 | 12834.915
14:00 | 6316.71 | 6286.14 | 12602.85
14:30 | 6293.37 | 6251.965 | 12545.335
15:00 | 6270.03 | 6217.79 | 12487.82
15:30 | 6137.98 | 6151.39 | 12289.37
16:00 | 6005.93 | 6084.99 | 12090.92
16:30 | 5949.19 | 5964.575 | 11913.765
17:00 | 5892.45 | 5844.16 | 11736.61
17:30 | 5875.72 | 5798.575 | 11674.295
18:00 | 5858.99 | 5752.99 | 11611.98
18:30 | 6210.705 | 6061.625 | 12272.33
19:00 | 6562.42 | 6370.26 | 12932.68
19:30 | 7257.08 | 6660.2 | 13917.28
20:00 | 7419.92 | 6807.12 | 14227.04
20:30 | 7455.35 | 6883.53 | 14338.88 |  | Executive Engineer
21:00 | 7490.78 | 6959.94 | 14450.72 |  | Network Operation Division
21:30 | 7491.28 | 6976.33 | 14467.61
22:00 | 7491.78 | 6992.72 | 14484.5
22:30 | 7599.78 | 6895.11 | 14494.89
23:00 | 7707.78 | 6797.5 | 14505.28

## En-Curve
QF-LDC-12
Date | 24-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2612 | 1286 | 902 | 38 | 138 | 1007.41 | 222 | 5840 | 0 | 547 | 1852.5 | 0 | 0 | 18 | 683 | DAILY ENERGY CURVE
00:30 | 2597 | 1233.5 | 901.5 | 38 | 136 | 1001.37 | 221 | 5650 | 0 | 441 | 1854.2 | 0 | 0 | 15.5 | 803.5 | 24-07-2026
01:00 | 2582 | 1181 | 901 | 38 | 134 | 995.33 | 220 | 5460 | 0 | 335 | 1855.9 | 0 | 0 | 13 | 924
01:30 | 2576.5 | 1197.5 | 899.5 | 38 | 134 | 997.635 | 221 | 5366 | 0 | 316 | 1833.9 | 0 | 0 | 16 | 719 | Energy Generated | 310.4552 |  | MKWHr
02:00 | 2571 | 1214 | 898 | 38 | 134 | 999.94 | 222 | 5272 | 0 | 297 | 1811.9 | 0 | 0 | 19 | 514 | Energy not Served | 8.868 |  | MKWHr
02:30 | 2600.5 | 1256.5 | 898 | 38 | 128 | 997.385 | 222 | 5310 | 0 | 228.5 | 1565.45 | 0 | 0 | 17 | 500 | Total Energy Requirement | 319.3232 |  | MKWHr
03:00 | 2630 | 1299 | 898 | 38 | 122 | 994.83 | 222 | 5348 | 0 | 160 | 1319 | 0 | 0 | 15 | 486
03:30 | 2641.5 | 1319 | 898 | 38 | 121 | 998.3 | 219 | 5378.5 | 0 | 160 | 1109 | 0 | 0 | 16.5 | 521.5
04:00 | 2653 | 1339 | 898 | 38 | 120 | 1001.77 | 216 | 5409 | 0 | 160 | 899 | 0 | 0 | 18 | 557
04:30 | 2649 | 1343.5 | 898 | 38 | 121 | 999.99 | 216 | 5446.5 | 0 | 160 | 761.5 | 0 | 0 | 18 | 534
05:00 | 2645 | 1348 | 898 | 38 | 122 | 998.21 | 216 | 5484 | 0 | 160 | 624 | 0 | 0 | 18 | 511
05:30 | 2625.5 | 1343.5 | 898 | 38 | 120 | 995.85 | 216 | 5442 | 7.7 | 152 | 399 | 0 | 0 | 14.5 | 475
06:00 | 2606 | 1339 | 898 | 38 | 118 | 993.49 | 216 | 5400 | 15.4 | 144 | 174 | 0 | 0 | 11 | 439
06:30 | 2613.5 | 1347 | 898 | 38 | 111 | 994.29 | 219 | 5315 | 45.525 | 144 | 158 | 0 | 0 | 10 | 462.5
07:00 | 2621 | 1355 | 898 | 38 | 104 | 995.09 | 222 | 5230 | 75.65 | 144 | 142 | 0 | 0 | 9 | 486
07:30 | 2605.5 | 1335 | 893 | 38 | 99 | 1000.755 | 197 | 5156 | 123.64 | 136 | 142 | 0 | 0 | 8 | 448
08:00 | 2590 | 1315 | 888 | 38 | 94 | 1006.42 | 172 | 5082 | 171.63 | 128 | 142 | 0 | 0 | 7 | 410
08:30 | 2594.5 | 1291.5 | 893 | 38 | 101 | 1009.345 | 194.5 | 5024 | 228.71 | 136.5 | 142 | 0 | 0 | 8 | 406
09:00 | 2599 | 1268 | 898 | 38 | 108 | 1012.27 | 217 | 4966 | 285.79 | 145 | 142 | 0 | 0 | 9 | 402
09:30 | 2581.5 | 1269 | 897.5 | 38 | 106 | 1002.26 | 219.5 | 4853.5 | 310.28 | 145 | 178.5 | 0 | 0 | 22 | 328
10:00 | 2564 | 1270 | 897 | 38 | 104 | 992.25 | 222 | 4741 | 334.77 | 145 | 215 | 0 | 0 | 35 | 254
10:30 | 2592.5 | 1310.25 | 897.5 | 38 | 106 | 993.675 | 222 | 4780.5 | 354 | 145 | 216.5 | 0 | 0 | 24.5 | 246
11:00 | 2621 | 1350.5 | 898 | 38 | 108 | 995.1 | 222 | 4820 | 373.23 | 145 | 218 | 0 | 0 | 14 | 238
11:30 | 2629.5 | 1374.25 | 898 | 38 | 112 | 956.12 | 222 | 5059 | 460.02 | 163.5 | 247 | 0 | 0 | 13 | 212
12:00 | 2638 | 1398 | 898 | 38 | 116 | 917.14 | 222 | 5298 | 546.81 | 182 | 276 | 0 | 0 | 12 | 186
12:30 | 2617 | 1374 | 898 | 38 | 116 | 965.48 | 222 | 5466.5 | 502.485 | 183.5 | 407 | 0 | 0 | 14.5 | 217
13:00 | 2596 | 1350 | 898 | 38 | 116 | 1013.82 | 222 | 5635 | 458.16 | 185 | 538 | 0 | 0 | 17 | 248
13:30 | 2628.5 | 1315 | 898 | 38 | 119 | 995.935 | 222 | 5599.5 | 384.98 | 168.5 | 450 | 0 | 0 | 15.5 | 246.5
14:00 | 2661 | 1280 | 898 | 38 | 122 | 978.05 | 222 | 5564 | 311.8 | 152 | 362 | 0 | 0 | 14 | 245
14:30 | 2648.5 | 1308.5 | 898 | 38 | 119 | 982.545 | 222 | 5501 | 318.29 | 143.5 | 354.5 | 0 | 0 | 11.5 | 205.5
15:00 | 2636 | 1337 | 898 | 38 | 116 | 987.04 | 222 | 5438 | 324.78 | 135 | 347 | 0 | 0 | 9 | 166
15:30 | 2626 | 1331 | 898 | 38 | 113 | 984.37 | 222 | 5307 | 329 | 135 | 301.5 | 0 | 0 | 4.5 | 171
16:00 | 2616 | 1325 | 898 | 38 | 110 | 981.7 | 222 | 5176 | 333.22 | 135 | 256 | 0 | 0 | 0 | 176
16:30 | 2621.5 | 1315.5 | 897.5 | 38 | 108 | 953.78 | 222 | 5104 | 260.275 | 146.71 | 246.5 | 0 | 0 | 0 | 174.5
17:00 | 2627 | 1306 | 897 | 38 | 106 | 925.86 | 222 | 5032 | 187.33 | 158.42 | 237 | 0 | 0 | 0 | 173
17:30 | 2630 | 1308.5 | 897.5 | 38 | 101 | 923.695 | 222 | 5043.5 | 114.18 | 158.42 | 237 | 0 | 0 | 0.5 | 172
18:00 | 2633 | 1311 | 898 | 38 | 96 | 921.53 | 222 | 5055 | 41.03 | 158.42 | 237 | 0 | 0 | 1 | 171
18:30 | 2662 | 1301 | 898 | 38 | 111 | 972.895 | 222 | 5363 | 20.515 | 293.42 | 386 | 0 | 0 | 4.5 | 245.5
19:00 | 2691 | 1291 | 898 | 38 | 126 | 1024.26 | 222 | 5671 | 0 | 428.42 | 535 | 0 | 0 | 8 | 320
19:30 | 2638 | 1303.3 | 898 | 38 | 120 | 1012.2 | 222 | 6003 | 0 | 542.42 | 1126.36 | 0 | 0 | 14 | 340
20:00 | 2636 | 1349 | 898 | 38 | 124 | 1003.12 | 222 | 6152 | 0 | 537.42 | 1248.5 | 0 | 0 | 19 | 310
20:30 | 2645.5 | 1347.5 | 891 | 38 | 124 | 1001.03 | 222 | 6203.5 | 0 | 530.42 | 1316.43 | 0 | 0 | 19.5 | 266
21:00 | 2655 | 1346 | 884 | 38 | 124 | 998.94 | 222 | 6255 | 0 | 523.42 | 1384.36 | 0 | 0 | 20 | 222
21:30 | 2612 | 1347 | 883.5 | 38 | 124 | 1004.33 | 222 | 6255.5 | 0 | 516.92 | 1448.86 | 0 | 0 | 15.5 | 272.5
22:00 | 2569 | 1348 | 883 | 38 | 124 | 1009.72 | 222 | 6256 | 0 | 510.42 | 1513.36 | 0 | 0 | 11 | 323
22:30 | 2552 | 1329.5 | 883.5 | 38 | 130 | 1012.11 | 222 | 6080 | 0 | 461.42 | 1774.86 | 0 | 0 | 11.5 | 373.5
23:00 | 2535 | 1311 | 884 | 38 | 136 | 1014.5 | 222 | 5904 | 0 | 412.42 | 2036.36 | 0 | 0 | 12 | 424
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 24-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 149 | 53 | 320 | 192 | 1708 | 628 | Ishurdi-Ghorashal Ckt-1 | Export | 2199636.36
1:00 | 132 | 50 | 324 | 170 | 1492 | 610
2:00 | 90 | 28 | 310 | 140 | 1324 | 542 |  | Import | 0
3:00 | 91 | 26 | 320 | 140 | 1438 | 544
4:00 | 102 | 31 | 354 | 180 | 1534 | 574 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 114 | 34 | 380 | 180 | 1590 | 590
6:00 | 127 | 33 | 400 | 162 | 1588 | 590 |  | Import | 0
7:00 | 128 | 35 | 390 | 148 | 1572 | 590
8:00 | 141 | 39 | 410 | 150 | 1650 | 584 | Sirajganj-Sreepur Ckt-1 | Export | 2350000
9:00 | 0 | 0 | 530 | 154 | 1808 | 630
10:00 | 0 | 0 | 530 | 160 | 1880 | 616 |  | Import | 0
11:00 | 0 | 0 | 560 | 162 | 1916 | 652
12:00 | 0 | 0 | 540 | 180 | 1962 | 720 | Sirajganj-Sreepur Ckt-2 | Export | 2357000
13:00 | 0 | 0 | 460 | 192 | 1920 | 660
14:00 | 0 | -29 | 490 | 162 | 1934 | 662 |  | Import | 0
15:00 | 151 | 30 | 490 | 164 | 1808 | 610
16:00 | 164 | 33 | 480 | 156 | 1872 | 626 | Gopalganj-Aminbazar Ckt-1 | Export | 20490000
17:00 | 173 | 43 | 460 | 140 | 1808 | 610
18:00 | 165 | 40 | 430 | 136 | 1750 | 572 |  | Import | 0
18:30 | 167 | 38 | 460 | 144 | 1864 | 546
19:00 | 149 | 27 | 450 | 150 | 1855 | 504 | Gopalganj-Aminbazar Ckt-2 | Export | 20540000
19:30 | 91 | 9 | 280 | 120 | 1684 | 404
20:00 | 81 | 4 | 270 | 120 | 1722 | 376 |  | Import | 0
21:00 | 91 | 10 | 340 | 170 | 1744 | 448
22:00 | 77 | 4 | 290 | 166 | 1620 | 426 |  | Total Export | 47936636.36
23:00 | 83 | 11 | 270 | 166 | 1488 | 446 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 24-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 375 | 08:00 | 359 | 00:00 | Madunaghat | 392 | 02:00 | 376 | 03:00
Amtali | 412 | 06:00 | 403 | 21:00 | Meghnaghat | 381 | 08:00 | 364 | 00:00
Ashuganj | 407 | 6:00 | 388 | 12:00 | Payra | 414 | 02:00 | 406 | 22:00
Bhulta | 395 | 18:00 | 381 | 12:00 | Rahanpur | 407 | 17:00 | 397 | 20:00
Bibiana | 379 | 06:00 | 372 | 12:00 | Rampal | 397 | 17:00 | 383 | 21:00
BIPTC | 403 | 03:00 | 394 | 11:00
Bogura | 389 | 18:00 | 376 | 20:00
Gopalganj | 391 | 08:00 | 378 | 21:00
Kaliakoir | 363 | 08:00 | 349 | 12:00
Korerhat | 391 | 08:00 | 381 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 08:00 | 218 | 00:00 | Ishurdi | 236 | 06:00 | 225 | 22:00
AKSML | 237 | 02:00 | 225 | 13:00 | Jhenaidah | 229 | 06:00 | 212 | 22:00
Aminbazar | 230 | 02:00 | 227 | 01:00 | Kachua | 224 | 09:00 | 218 | 00:00
Ashuganj | 226 | 08:00 | 216 | 00:00 | Kaliakoir | 227 | 02:00 | 217 | 12:00
Ashuganj-400 | 226 | 8:00 | 216 | 23:00 | Keranigonj | 228 | 18:00 | 215 | 00:00
Baghabari | 234 | 16:00 | 225 | 22:00 | Khulna(S) | 228 | 07:00 | 215 | 21:00
Barapukuria | 226 | 18:30 | 216 | 20:00 | Korerhat | 224 | 01:00 | 218 | 00:00
Barapukuria-230 | 226 | 18:00 | 215 | 21:00 | Madunaghat | 239 | 01:00 | 232 | 12:00
Barishal | 228 | 17:00 | 220 | 22:00 | Madunaghat-400 | 241 | 02:00 | 233 | 13:00
Bheramara | 234 | 08:00 | 218 | 00:00 | Maniknagar | 226 | 07:00 | 218 | 12:00
Bhulta | 228 | 18:00 | 220 | 12:00 | Meghnaghat | 235 | 18:00 | 224 | 00:00
Bibiana | 220 | 07:00 | 214 | 22:00 | Meghnaghat-400 | 229 | 08:00 | 218 | 00:00
BIPTC | 237 | 06:00 | 223 | 22:00 | Mirsorai | 228 | 02:00 | 221 | 13:00
Bogura | 243 | 17:00 | 235 | 20:00 | Naogaon | 229 | 17:00 | 210 | 22:00
Bogura-400 | 244 | 18:00 | 235 | 20:00 | Purbasadipur | 225 | 19:00 | 211 | 20:00
Borhanuddin | 231 | 05:00 | 225 | 22:00 | Rajshahi | 233 | 05:00 | 220 | 22:00
BSRM | 225 | 02:00 | 219 | 00:00 | Rampal | 227 | 17:00 | 214 | 22:00
Charfasson | 233 | 10:00 | 226 | 21:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 224 | 02:00 | 217 | 00:00 | Rampura | 227 | 08:00 | 216 | 00:00
Cumilla(N) | 224 | 18:00 | 214 | 00:00 | Shikalbaha | 239 | 01:00 | 230 | 12:00
Faridpur | 225 | 08:00 | 216 | 22:00 | Shyampur | 228 | 08:00 | 212 | 00:00
Fenchuganj | 222 | 10:00 | 214 | 00:00 | Siddhirganj | 230 | 07:00 | 221 | 12:00
Feni | 223 | 02:00 | 216 | 00:00 | Sirajgonj | 239 | 18:00 | 233 | 22:00
Ghorashal | 230 | 03:00 | 220 | 00:00 | Sreepur | 226 | 18:00 | 216 | 00:00
Ghorashal-230 | 217 | 02:00 | 201 | 12:00 | Tongi | 220 | 18:30 | 202 | 00:00
Gopalganj | 228 | 09:00 | 218 | 21:00
GPH | 234 | 02:00 | 227 | 12:00
Haripur | 228 | 18:00 | 216 | 00:00
Hasnabad | 228 | 08:00 | 216 | 00:00
Hathazari | 233 | 09:00 | 228 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 07:00 | 130 | 12:00 | Madunaghat | 138 | 01:00 | 134 | 12:00
Agargaon | 136 | 08:00 | 128 | 00:00 | Magura | 138 | 06:00 | 122 | 22:00
Agrabad | 136 | 00:00 | 132 | 12:00 | Mahasthangarh | 137 | 17:00 | 129 | 19:30
AKS | 135 | 01:00 | 130 | 12:00 | Maijdee | 126 | 10:00 | 121 | 00:00
Aminbazar | 132 | 23:00 | 124 | 00:00 | Manikganj | 130 | 20:00 | 121 | 00:00
Amnura | 135 | 00:00 | 128 | 13:00 | Maniknagar | 134 | 18:00 | 127 | 13:00
Ashuganj | 130 | 07:00 | 125 | 00:00 | Matarbari | 126 | 09:00 | 119 | 20:00
Ashuganj-230 | 132 | 08:00 | 128 | 00:00 | Matuail | 134 | 18:00 | 124 | 00:00
Bagerhat | 131 | 09:00 | 120 | 22:00 | Metrorail_Motijheel | 134 | 18:00 | 127 | 13:00
Bajitpur | 127 | 09:00 | 119 | 00:00 | Metrorail_Uttara | 132 | 02:00 | 123 | 00:00
Bakerganj | 132 | 08:00 | 126 | 19:30 | Millgate | 132 | 02:00 | 124 | 00:00
Bakulia | 135 | 00:00 | 132 | 12:00 | Mirpur | 131 | 23:00 | 123 | 00:00
Banani | 136 | 01:00 | 130 | 13:00 | Mirzapur | 129 | 10:00 | 123 | 00:00
Bangabhaban | 133 | 08:00 | 127 | 13:00 | Mithapukur | 134 | 19:00 | 125 | 20:00
Barapukuria | 137 | 17:00 | 127 | 20:00 | MI_Cement | 135 | 17:00 | 126 | 00:00
Barguna | 132 | 02:00 | 125 | 19:30 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 00:00 | 126 | 21:00 | Mogbazar | 139 | 08:00 | 132 | 00:00
Barishal-230 | 133 | 01:00 | 126 | 13:00 | Mongla | 130 | 09:00 | 120 | 19:30
Baroaulia | 136 | 01:00 | 134 | 00:00 | Motijheel | 134 | 18:00 | 127 | 13:00
Baroirhat | 130 | 18:00 | 126 | 03:00 | Muktagacha | 129 | 10:00 | 116 | 00:00
Bashundhara | 137 | 08:00 | 124 | 00:00 | Munshiganj | 132 | 18:00 | 124 | 00:00
BashundharaCement | 133 | 08:00 | 125 | 00:00 | Muradnagar | 127 | 18:00 | 119 | 00:00
Beanibazar | 123 | 07:00 | 116 | 22:00 | Mymensingh | 129 | 10:00 | 111 | 12:00
Benapole | 133 | 05:00 | 118 | 22:00 | Nabinagar | 131 | 18:00 | 120 | 00:00
Bhaluka | 127 | 14:00 | 121 | 00:00 | Naogaon | 138 | 17:00 | 126 | 22:00
Bhandaria | 130 | 07:00 | 120 | 22:00 | Narail | 139 | 06:00 | 121 | 22:00
Bhangura | 135 | 17:00 | 130 | 19:30 | Narinda | 134 | 18:00 | 127 | 13:00
Bheramara | 138 | 06:00 | 129 | 00:00 | Narshingdi | 125 | 01:00 | 115 | 12:00
Bheramara(GK) | 138 | 06:00 | 130 | 22:00 | Natore | 135 | 01:00 | 128 | 20:00
Bhulta | 122 | 08:00 | 120 | 00:00 | Nawabganj | 134 | 08:00 | 126 | 00:00
Bog-Sherpur | 138 | 18:00 | 132 | 20:00 | Netrakona | 119 | 14:00 | 111 | 00:00
Bogura | 139 | 18:00 | 135 | 13:00 | New | 134 | 18:30 | 121 | 00:00
Bogura-230 | 140 | 17:00 | 134 | 20:00 | Niamatpur | 135 | 18:30 | 129 | 22:00
Brahmanbaria | 125 | 01:00 | 121 | 21:00 | Noapara | 135 | 08:00 | 125 | 22:00
Cantonment | 135 | 02:00 | 129 | 12:00 | Pabna | 137 | 18:00 | 128 | 22:00
Chandina | 129 | 10:00 | 123 | 00:00 | Palashbari | 132 | 17:00 | 123 | 20:00
Chandpur | 128 | 22:00 | 124 | 12:00 | Panchagarh | 139 | 19:00 | 130 | 20:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 138 | 02:00 | 134 | 12:00 | Patiya | 134 | 09:00 | 131 | 07:00
Chapai | 133 | 00:00 | 131 | 05:00 | Patnitala | 134 | 07:00 | 127 | 19:30
Charsaidpur | 133 | 18:00 | 128 | 12:00 | Patuakhali | 132 | 01:00 | 125 | 21:00
Chauddagram | 128 | 08:00 | 124 | 12:00 | Payra | 135 | 01:00 | 132 | 19:30
Chhatak | 125 | 06:00 | 113 | 22:00 | PHP | 130 | 02:00 | 125 | 13:00
Chowmuhani | 126 | 10:00 | 121 | 00:00 | Postogola | 137 | 18:00 | 130 | 00:00
Chuadanga | 136 | 17:00 | 121 | 22:00 | Pubail | 131 | 19:30 | 119 | 00:00
Coxsbazar | 127 | 06:00 | 122 | 19:00 | Purbachal | 136 | 01:00 | 130 | 13:00
Cumilla(N) | 129 | 07:00 | 124 | 00:00 | Purbasadipur | 136 | 19:00 | 127 | 20:00
Cumilla(S) | 131 | 07:00 | 124 | 00:00 | Rahanpur | 136 | 17:00 | 132 | 00:00
Daganbhuiyan | 128 | 02:00 | 124 | 00:00 | Rahanpur-400 | 136 | 17:00 | 132 | 22:00
Daudkandi | 125 | 07:00 | 118 | 00:00 | Rahim | 134 | 18:30 | 125 | 00:00
DhakaUniversity | 137 | 01:00 | 131 | 00:00 | Rajbari | 128 | 07:00 | 121 | 00:00
Dhamrai | 132 | 18:00 | 124 | 00:00 | Rajendrapur | 127 | 17:00 | 120 | 00:00
Dhanmondi | 137.6 | 01:00 | 130 | 13:00 | Rajshahi | 135 | 18:00 | 127 | 23:00
Dohazari | 132 | 01:00 | 128 | 14:00 | Rajshahi-230 | 134 | 01:00 | 127 | 22:00
Faridpur | 130 | 06:00 | 125 | 20:00 | Ramganj | 125 | 01:00 | 120 | 00:00
Fatullah | 136 | 18:00 | 124 | 00:00 | Rampur | 137 | 01:00 | 131 | 12:00
Fenchuganj | 131 | 07:00 | 126 | 00:00 | Rampura | 137 | 01:00 | 130 | 13:00
Feni | 128 | 01:00 | 124 | 12:00 | Rangamati | 137 | 02:00 | 133 | 12:00
Feni-230 | 129 | 02:00 | 125 | 00:00 | Rangpur | 132 | 17:00 | 123 | 20:00
Ghatail | 127 | 11:00 | 117 | 00:00 | Ruppur | 139 | 17:00 | 132 | 20:00
Ghorashal | 130 | 20:00 | 120 | 00:00 | Saidpur | 136 | 19:00 | 129 | 20:00
Goalpara | 138 | 08:00 | 128 | 20:00 | Santhia | 136 | 08:00 | 130 | 19:00
Gollamari | 137 | 07:00 | 128 | 19:30 | Satkhira | 135 | 08:00 | 121 | 19:30
Gopalganj | 131 | 07:00 | 123 | 21:00 | Satmasjid | 142 | 00:00 | 128 | 13:00
Gopalganj-400 | 132 | 06:00 | 127 | 19:30 | Savar | 131 | 23:00 | 122 | 00:00
Gulshan | 136 | 07:00 | 130 | 12:00 | SevenRings | 130 | 19:30 | 121 | 00:00
Halishahar | 138 | 01:00 | 132 | 12:00 | ShahCement | 133 | 18:00 | 128 | 12:00
Haripur | 134 | 18:30 | 126 | 00:00 | Shahjadpur | 137 | 18:30 | 132 | 00:00
HaripurSBU | 134 | 18:30 | 126 | 00:00 | Shahjibazar | 126 | 08:00 | 120 | 00:00
Hasnabad | 135 | 05:00 | 127 | 00:00 | Shahmirpur | 138 | 01:00 | 132 | 12:00
Hathazari | 136 | 04:00 | 133 | 12:00 | Shariatpur | 131 | 07:00 | 123 | 22:00
Hatirjheel | 137 | 01:00 | 130 | 13:00 | Sherpur | 128 | 11:00 | 114 | 03:00
Ishurdi | 140 | 18:00 | 132 | 22:00 | Shikalbaha | 128 | 03:00 | 121 | 13:00
Jaldhaka | 134 | 19:00 | 123 | 20:00 | Shikalbaha-230 | 139 | 01:00 | 132 | 12:00
Jamalpur | 131 | 10:00 | 119 | 00:00 | Shitalakhya | 135 | 17:00 | 126 | 00:00
Jashore | 135 | 06:00 | 121 | 22:00 | Sholosohor | 138 | 02:00 | 132 | 12:00
Jhenaidah | 139 | 03:00 | 126 | 22:00 | Shomvuganj | 122 | 16:00 | 114 | 00:00
Jhenaidah-230 | 140 | 06:00 | 127 | 22:00 | Shyampur | 132 | 08:00 | 126 | 01:00
Joydebpur | 130 | 19:30 | 117 | 00:00 | Shyampur-230 | 136 | 08:00 | 124 | 00:00
Joypurhat | 135 | 18:00 | 128 | 20:00 | Siddhirganj | 134 | 18:00 | 126 | 00:00
Juldah | 135 | 01:00 | 132 | 12:00 | Sirajganj | 135 | 18:00 | 128 | 19:30
Kabirpur | 133 | 19:00 | 120 | 01:00 | Sitakunda | 135 | 08:00 | 132 | 04:00
Kachua | 127 | 02:00 | 124 | 00:00 | Sonargaon | 130 | 10:00 | 126 | 00:00
Kaliakoir | 135 | 18:30 | 128 | 00:00 | Sreemongol | 126 | 07:00 | 121 | 00:00
Kaliganj | 137 | 05:00 | 121 | 19:30 | Sreepur | 130 | 17:00 | 123 | 12:00
Kallyanpur | 131 | 18:00 | 120 | 00:00 | Srinagar | 134 | 06:00 | 126 | 00:00
Kalurghat | 138 | 02:00 | 133 | 12:00 | SSM | 140 | 01:00 | 138 | 00:00
Kamrangirchar | 135 | 08:00 | 122 | 12:00 | Sunamganj | 118 | 07:00 | 111 | 22:00
Kaptai | 137 | 7:00 | 134 | 16:00 | Sylhet | 124 | 08:00 | 120 | 00:00
Kasba | 127 | 18:00 | 119 | 00:00 | Sylhet_(South) | 125 | 07:00 | 120 | 00:00
Kazla | 133 | 08:00 | 124 | 00:00 | Tangail | 128 | 09:00 | 118 | 22:00
Keranigonj | 135 | 08:00 | 126 | 00:00 | Taraganj | 134 | 19:00 | 122 | 19:30
Khagrachori | 136 | 01:00 | 132 | 12:00 | Tasnim | 130 | 10:00 | 126 | 00:00
Khulna | 137 | 08:00 | 127 | 19:30 | Thakurgaon | 138 | 19:00 | 129 | 20:00
Khulna(S) | 137 | 07:00 | 128 | 19:30 | TK | 136 | 00:00 | 133 | 12:00
Khulshi | 136 | 01:00 | 130 | 12:00 | Tongi | 135 | 17:00 | 125 | 01:00
Kishoreganj | 126 | 09:00 | 118 | 00:00 | Ullahpara | 135 | 10:00 | 129 | 19:30
Kodda | 133 | 20:00 | 118 | 00:00 | Ullon | 137 | 01:00 | 130 | 12:00
Korerhat | 132 | 01:00 | 129 | 00:00 | Uttara | 132 | 02:00 | 122 | 00:00
KSRM | 136 | 08:00 | 129 | 02:00 | UttaraNew | 134 | 18:30 | 129 | 16:00
Kulaura | 129 | 07:00 | 124 | 00:00 | Zigatola | 135 | 18:00 | 127 | 00:00
Kurigram | 132 | 23:00 | 119 | 20:00
Kushtia | 136 | 09:00 | 127 | 19:30
Laksam | 126 | 01:00 | 123 | 00:00
Lakshmipur | 125 | 10:00 | 120 | 00:00
Lalbag | 134 | 07:00 | 124 | 00:00
Lalmonirhat | 130 | 18:30 | 120 | 00:00
Madanganj | 133 | 08:00 | 125 | 00:00
Madaripur | 131 | 05:00 | 125 | 13:00
Madartek | 136 | 01:00 | 130 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division