## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 26-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-07-2026 | during | 26-07-2026 | during | 26-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 281 | 340 | 412 | 412 | 350 | 350 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 138 | 139 | 335 | 335 | 150 | 150 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 50 | 55 | 55 | 55 | 55 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 290 | 290 | 335 | 335 | 320 | 320 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 78 | 142 | 149.36 | 149.36 | 48 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 11 | 33 | 33 | 9 | 9 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 8 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 48 | 95 | 300 | 300 | 48 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 133 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 88 | 105 | 105 | 34 | 88 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 90 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 8 | 0 | 14 | 0 | 14 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 23.297 | 17 | 17 | 23.29 | 23.29 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 315 | 275 | 583 | 583 | 340 | 340 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 123 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6637.271 | 1519 | 1972.42 | 5757.93 | 5743.93 | 1689.42 | 2216.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 8 | 0 | 8 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 222 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 210 | 0 | 0 | 215 | 215 | plant availability zero
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 66 | 79 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 39 | 40 | 72 | 40 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 34 | 0 | 34 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 50 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 6 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 10 | 60 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.17 | 0 | 1.69 | 0 | 1.69 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 120 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 54 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 105 | 107 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 50 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 35 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 16 | 115 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1192 | 1186 | 1224 | 1224 | 1204 | 1204 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 26 | 16 | 30 | 40 | 30 | 40 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 1125 | 725 | 725 | 720 | 720 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 3107.17 | 3583.86 | 3487.55 | 3568.86 | 3055.69 | 3179
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 190 | 182 | 221.25 | 221.25 | 185 | 185 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 280 | 280 | 350.01 | 350.01 | 280 | 280 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 200 | 200 | 342.01 | 342.01 | 200 | 200 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 11 | 24 | 150 | 150 | 30 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 29 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 141 | 141 | 163 | 163 | 145 | 145 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 173 | 172 | 200 | 200 | 17 | 100 | Liquid fuel shortage
| Import (Tripura) | Import | Import |  | 160 | 160 | 134 | 150 | 84 | 80 | 150 | 150 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 16 | 65 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 27 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 31 | 91 | 115 | 115 | 34 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 74 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1320 | 1456 | 2361.44 | 2297.44 | 1367.2 | 1575.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-07-2026 | during | 26-07-2026 | during | 26-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 16.02 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.7 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 153 | 152 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 18 | 67 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 48.87 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 250.59 | 248 | 527.6 | 516.5 | 270.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 41 | 42 | 42 | 41 | 41 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 148 | 136 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 86 | 86 | 86 | 53 | 53 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 101 | 100 | 100 | 100 | 100 | 100 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 10 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 341 | 341 | 307 | 307 | Machine Problem
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 306 | 298 | 350 | 350 | 357 | 357 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 977 | 976 | 1157 | 1157 | 1022 | 1022
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 883 | 896 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 32 | 32 | 27 | 27 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 67 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 58 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1145 | 1139 | 1234.2 | 1234.2 | 1194.2 | 1194.2 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2124 | 2169 | 3561.2 | 3486.2 | 2349.2 | 2274.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 700 | 883 | 700 | 1050 | 700 | 1050 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 15 | 60 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 1155 | 1163 | 1163.05 | 1163.05 | 1163.05 | 1163.05 | AGC
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 27 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 275 | 273 | 307 | 307 | 287 | 287 | FGMO
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.41 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2502.41 | 2746 | 2781.05 | 3130.05 | 2607.05 | 2956.05
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 58.22 | 0 | 55 | 0 | 55 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 30 | 32 | 32 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 205 | 174 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 0 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 93 | 100 | 100 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 18 | 50 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 35 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 1.88 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1278.25 | 1405.23 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | AGC
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 38.87 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 112 | 0 | 90 | 0 | 90 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1747.22 | 2299.43 | 3246.62 | 3035.12 | 2422.62 | 2373.12
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 180 | 190 | 190 | 190 | 185 | 185 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 95 | 115 | 115 | 104 | 104 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 209 | 0 | 112.88 | 0 | 112.88 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 460 | 334 | 577.88 | 432 | 448.88 | 338
System Total |  |  |  |  | 28843.2 | 29137.464 | 14007.39 | 15784.71 | 23458.27 | 23367.1 | 15232.16 | 16192.99
Forecast Scenario (26-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15200 |  | 1350 |  | 16550
|  |  |  | 1:00 | 14900 |  | 1530 |  | 16430
|  |  |  | 2:00 | 14500 |  | 1220 |  | 15720
|  |  |  | 3:00 | 14200 |  | 950 |  | 15150
|  |  |  | 4:00 | 14100 |  | 890 |  | 14990
|  |  |  | 5:00 | 13930 |  | 790 |  | 14720
|  |  |  | 6:00 | 13830 |  | 720 |  | 14550
|  |  |  | 7:00 | 13910 |  | 670 |  | 14580
|  |  |  | 8:00 | 13970 |  | 650 |  | 14620
|  |  |  | 9:00 | 14100 |  | 95.5 |  | 14200
|  |  |  | 10:00 | 14160 |  | 95.5 |  | 14260
|  |  |  | 11:00 | 14200 |  | 382 |  | 14600
|  |  |  | 12:00 | 14250 |  | 716.25 |  | 15000
|  |  |  | 13:00 | 14450 |  | 735.35 |  | 15220
|  |  |  | 14:00 | 14400 |  | 849.95 |  | 15290
|  |  |  | 15:00 | 14400 |  | 945.45 |  | 15390
|  |  |  | 16:00 | 14400 |  | 744.9 |  | 15180
|  |  |  | 17:00 | 14400 |  | 305.6 |  | 14720
|  |  |  | 18:00 | 13950 |  | 429.75 |  | 14400
|  |  |  | 18:30 | 14500 |  | 573 |  | 15100
|  |  |  | 19:00 | 15000 |  | 849.95 |  | 15890
|  |  |  | 19:30 | 15740 |  | 1012.3 |  | 16800
|  |  |  | 20:00 | 15790 |  | 955 |  | 16790
|  |  |  | 21:00 | 15690 |  | 1040.95 |  | 16780
|  |  |  | 22:00 | 15650 |  | 993.2 |  | 16690
|  |  |  | 23:00 | 15300 |  | 1146 |  | 16500
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 15000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 16800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15790.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 348.68 MKWHr. |  | 187 | 0 | 60 | 410 | 195 | 120 | 0 | 0 | 40 | 1012
*** This report is generated digitally from Operation Information System (OIS) at 08:01 hrs on 26-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 25-07-2026 | [28 empty] | Date: | 25-07-2026 | [28 empty] | Date: | 25-07-2026 | [28 empty] | Date: | 25-07-2026 | [28 empty] | Date: | 25-07-2026 | [18 empty] | Date: | 25-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [18 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 23.297 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 23.29 | 133 | 125 | 225 | 55 | 55 | 153 | 0 | 0 | 139 | 315 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 41 | 35 | 0 | 0 | 14 | 34 | 0 | 54.36 | 10 | 25 | 0 | 222 | 105 | 35 | 1125 | 54 | 0 | 25 | 0 | 83 | 189 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 184 | 0 | 70 | 142 | 187 | 26 | 19 | 29 | 122 | 0 | 0 | 32 | 310 | 0 | 292 | 42 | 0 | 132 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 7702.07 | 884 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 1004.8 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 26 | 3 | 0 | 0 | 12 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 185 | 0 | 93 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 307 | 120 | 220 | 0 | 700 | 1163 | 54 | 6779.8 | 14481.87 | 103.25
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 23.29 | 71 | 125 | 225 | 55 | 35 | 108 | 0 | 0 | 140 | 320 | 0 | 35 | 285 | 0 | 0 | 0 | 143.42 | 10 | 22 | 0 | 0 | 48 | 75 | 9 | 0 | 28 | 34 | 0 | 0 | 25 | 25 | 0 | 220 | 107 | 35 | 1125 | 50 | 0 | 33 | 0 | 85 | 190 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 188 | 0 | 59 | 142 | 186 | 27 | 19 | 45 | 126 | 0 | 0 | 25 | 300 | 0 | 326 | 40 | 0 | 141 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 7630.71 | 884 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1202 | 0 | 0 | 0 | 1004.81 | 0 | 0 | 0 | 113 | 113 | 0 | 0 | 25 | 52.2 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 120 | 220 | 0 | 500 | 1163 | 35 | 6444.01 | 14074.72 | 103.25
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 17 | 34 | 125 | 195 | 55 | 35 | 17 | 0 | 0 | 144 | 310 | 0 | 35 | 305 | 0 | 0 | 0 | 123 | 10 | 22 | 0 | 0 | 45 | 45 | 50 | 0 | 13 | 0 | 0 | 0 | 25 | 25 | 0 | 220 | 105 | 35 | 1125 | 17 | 0 | 38 | 0 | 98 | 190 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 194 | 0 | 0 | 144 | 186 | 27 | 19 | 68 | 126 | 0 | 0 | 8 | 305 | 0 | 348 | 40 | 0 | 128 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 7371 | 884 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1202 | 0 | 0 | 0 | 1008.4 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 70 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 275 | 120 | 220 | 0 | 500 | 1163 | 35 | 6280.6 | 13651.6 | 103.25
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 17 | 34 | 110 | 145 | 55 | 0 | 0 | 0 | 0 | 147 | 315 | 0 | 35 | 290 | 0 | 0 | 0 | 105 | 10 | 22 | 0 | 0 | 0 | 45 | 30 | 0 | 18 | 0 | 0 | 0 | 25 | 25 | 0 | 220 | 105 | 42 | 1125 | 0 | 0 | 39 | 0 | 68 | 190 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 194 | 0 | 0 | 143 | 187 | 28 | 19 | 0 | 120 | 0 | 0 | 0 | 305 | 0 | 350 | 40 | 0 | 127 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 7050 | 884 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1204 | 0 | 0 | 0 | 999.55 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 66 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 276 | 120 | 220 | 0 | 500 | 1163 | 35 | 6121.55 | 13171.55 | 103.24
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 17 | 34 | 110 | 95 | 40 | 0 | 0 | 0 | 0 | 144 | 315 | 0 | 35 | 302 | 0 | 0 | 0 | 105 | 10 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 25 | 0 | 222 | 106 | 42 | 1125 | 0 | 0 | 19 | 0 | 34 | 189 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 196 | 0 | 0 | 143 | 100 | 26 | 19 | 0 | 122 | 0 | 0 | 0 | 310 | 0 | 364 | 40 | 0 | 135 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 0 | 47 | 0 | 48 | 0 | 0 | 0 | 12 | 6800 | 884 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1205 | 0 | 0 | 0 | 1022.8 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 32 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 276 | 120 | 220 | 0 | 500 | 1163 | 35 | 6064.8 | 12864.8 | 103.24
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 34 | 110 | 45 | 40 | 0 | 0 | 0 | 0 | 147 | 325 | 0 | 0 | 302 | 0 | 0 | 0 | 86 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 222 | 109 | 42 | 1125 | 0 | 0 | 19 | 0 | 33 | 191 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 196 | 0 | 0 | 143 | 100 | 0 | 19 | 0 | 116 | 0 | 0 | 0 | 315 | 0 | 364 | 40 | 0 | 147 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 6731 | 883 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1204 | 0 | 0 | 0 | 1014.02 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 34 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 277 | 120 | 220 | 0 | 500 | 1163 | 35 | 6006.02 | 12737.02 | 103.23
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 34 | 110 | 0 | 15 | 0 | 0 | 0 | 0 | 149 | 320 | 0 | 0 | 313 | 0 | 0 | 0 | 86 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 25 | 0.11 | 222 | 33 | 42 | 1125 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 1196 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 200 | 0 | 0 | 143 | 0 | 0 | 19 | 0 | 112 | 0 | 3 | 0 | 305 | 0 | 364 | 40 | 0 | 137 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 102 | 0 | 48 | 0.4 | 48 | 0 | 0 | 2.22 | 12 | 6363.73 | 884 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 1206 | 0 | 0 | 0 | 1033.72 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 5.49 | 7 | 0 | 0 | 1.84 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 185 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.1 | 6 | 0.01 | 16 | 278 | 120 | 220 | 0 | 500 | 1163 | 0 | 5910.33 | 12274.06 | 103.23
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 34 | 110 | 0 | 15 | 0 | 0 | 0 | 0 | 140 | 335 | 0 | 0 | 307 | 0 | 0 | 3 | 86 | 11.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 17 | 0 | 25 | 1.12 | 222 | 32 | 40 | 1125 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 1180 | 5 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 195 | 0 | 0 | 143 | 0 | 0 | 19 | 0 | 106 | 0 | 15 | 0 | 315 | 0 | 339 | 40 | 0 | 155 | 1 | 8 | 0 | 53 | 0 | 0 | 0 | 102 | 0 | 48 | 4 | 48 | 0 | 0.3 | 9.87 | 12 | 6432.79 | 884 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 1210 | 0 | 0 | 0 | 1028.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.73 | 5 | 0 | 0 | 8.13 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 185 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1.5 | 45 | 0.06 | 15 | 307 | 120 | 220 | 0 | 500 | 1140 | 0 | 5958.62 | 12391.41 | 103.22
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 34 | 110 | 45 | 24 | 0 | 0 | 0 | 0 | 143 | 335 | 0 | 0 | 300 | 0 | 0 | 5 | 86 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 17 | 0 | 25 | 2.28 | 222 | 33 | 5 | 1125 | 0 | 0 | 8 | 0 | 18 | 192 | 0 | 0 | 0 | 1185 | 11 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 187 | 0 | 0 | 143 | 21 | 0 | 19 | 0 | 112 | 0 | 34 | 0 | 310 | 0 | 339 | 40 | 0 | 139 | 3 | 8 | 0 | 53 | 0 | 0 | 0 | 102 | 0 | 45 | 6 | 48 | 0 | 0.4 | 10.92 | 12 | 6509.1 | 883 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 1212 | 0 | 0 | 0 | 1014.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.17 | 50 | 0 | 0 | 22.32 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.45 | 185 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 3.6 | 100 | 0.29 | 0 | 307 | 120 | 220 | 0 | 500 | 1156 | 0 | 6084.89 | 12593.99 | 103.22
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 35 | 78 | 45 | 40 | 0 | 12 | 0 | 0 | 150 | 315 | 0 | 0 | 300 | 0 | 0 | 12 | 86 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 17 | 0 | 25 | 2.32 | 222 | 34 | 8 | 1125 | 0 | 0 | 25 | 0 | 33 | 191 | 0 | 0 | 0 | 1185 | 16 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 185 | 0 | 0 | 142 | 33 | 0 | 19 | 0 | 114 | 0 | 39 | 0 | 310 | 0 | 316 | 40 | 0 | 132 | 4 | 8 | 0 | 53 | 0 | 0 | 0 | 101 | 0 | 9 | 10.47 | 87 | 0 | 1 | 21.13 | 12 | 6527.92 | 883 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 21 | 1206 | 0 | 0 | 0 | 1032.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.43 | 72 | 0 | 0 | 43.19 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.69 | 185 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 3.7 | 145 | 0.58 | 0 | 307 | 120 | 220 | 0 | 700 | 1163 | 0 | 6389.83 | 12917.75 | 103.22
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 35 | 78 | 45 | 40 | 17 | 17 | 0 | 0 | 141 | 320 | 0 | 0 | 307 | 0 | 0 | 9 | 86 | 10 | 22 | 0 | 0 | 0 | 30 | 0 | 0 | 15 | 0 | 0 | 17 | 0 | 25 | 1.78 | 222 | 40 | 9 | 1125 | 0 | 0 | 25 | 0 | 32 | 202 | 0 | 0 | 0 | 1200 | 0 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 188 | 0 | 0 | 140 | 47 | 0 | 17 | 0 | 122 | 0 | 50 | 0 | 310 | 0 | 316 | 40 | 0 | 137 | 8 | 8 | 0 | 53 | 0 | 0 | 0 | 100 | 0 | 38 | 17.14 | 123 | 0 | 1.9 | 53.99 | 12 | 6697.81 | 883 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 82 | 1200 | 0 | 0 | 0 | 1036.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.98 | 77 | 0 | 0 | 50.24 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.44 | 190 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 2.7 | 139 | 0.47 | 0 | 307 | 120 | 220 | 0 | 700 | 1163 | 0 | 6463.99 | 13161.8 | 103.22
11:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 34 | 78 | 48 | 40 | 17 | 17 | 0 | 0 | 145 | 320 | 0 | 0 | 290 | 0 | 0 | 14 | 86 | 10 | 22 | 0 | 0 | 6 | 30 | 0 | 0 | 20 | 0 | 0 | 17 | 12 | 25 | 1.36 | 222 | 106 | 4 | 1125 | 8 | 0 | 25 | 0 | 47 | 200 | 0 | 0 | 0 | 1180 | 11 | 0 | 0 | 0 | 280 | 200 | 51 | 0 | 190 | 0 | 1 | 140 | 123 | 0 | 19 | 17 | 124 | 0 | 72 | 0 | 305 | 0 | 298 | 40 | 0 | 152 | 12 | 8 | 0 | 52 | 0 | 0 | 0 | 101 | 0 | 45 | 21.14 | 135 | 0 | 2.2 | 23.88 | 12 | 6915.58 | 884 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 1195 | 0 | 0 | 0 | 1023.9 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 51.47 | 43 | 0 | 0 | 47.98 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.73 | 185 | 0 | 35 | 38 | 0 | 0 | 0 | 0 | 5.5 | 199 | 0.68 | 15 | 307 | 120 | 220 | 0 | 700 | 1163 | 3 | 6520.26 | 13435.84 | 103.22
12:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 17 | 17 | 35 | 78 | 48 | 50 | 35 | 17 | 0 | 0 | 138 | 315 | 0 | 0 | 290 | 0 | 0 | 8 | 123 | 12 | 21 | 0 | 0 | 17 | 30 | 10 | 0 | 26 | 0 | 0 | 17 | 12 | 12 | 2.17 | 222 | 105 | 2 | 1125 | 16 | 0 | 25 | 0 | 66 | 211 | 0 | 0 | 0 | 1192 | 17 | 11 | 0 | 0 | 280 | 200 | 51 | 0 | 190 | 0 | 31 | 141 | 173 | 0 | 19 | 16 | 134 | 0 | 74 | 0 | 310 | 0 | 306 | 40 | 0 | 148 | 12 | 8 | 0 | 52 | 0 | 0 | 0 | 101 | 0 | 18 | 16.02 | 153 | 0 | 2.7 | 48.87 | 12 | 7173.76 | 883 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 58 | 1145 | 0 | 0 | 0 | 1278.25 | 0 | 0 | 0 | 35 | 18 | 0 | 0 | 0 | 0 | 58.22 | 112 | 0 | 0 | 38.87 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.88 | 180 | 0 | 35 | 36 | 0 | 0 | 0 | 0 | 0 | 209 | 0.41 | 15 | 275 | 120 | 220 | 0 | 700 | 1155 | 17 | 6833.63 | 14007.39 | 103.22
13:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 17 | 17 | 42 | 78 | 48 | 55 | 55 | 17 | 0 | 0 | 146 | 310 | 0 | 0 | 305 | 0 | 0 | 8 | 123 | 12 | 21 | 0 | 0 | 17 | 30 | 12 | 0 | 27 | 0 | 0 | 17 | 12 | 25 | 3.2 | 222 | 105 | 2 | 1125 | 16 | 0 | 25 | 0 | 62 | 213 | 0 | 0 | 0 | 1192 | 9 | 12 | 0 | 0 | 280 | 200 | 51 | 0 | 190 | 0 | 35 | 139 | 177 | 0 | 19 | 17 | 130 | 0 | 68 | 0 | 300 | 0 | 315 | 40 | 0 | 129 | 9 | 8 | 0 | 51 | 0 | 0 | 0 | 101 | 0 | 18 | 20.84 | 153 | 0 | 1.7 | 49.56 | 12 | 7209.3 | 884 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 100 | 1150 | 0 | 0 | 0 | 1432.48 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 50.4 | 113 | 0 | 0 | 22.59 | 203 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 1.93 | 190 | 0 | 35 | 38 | 0 | 0 | 0 | 0 | 3 | 160 | 0.36 | 14 | 275 | 120 | 180 | 0 | 700 | 1083 | 17 | 6898.76 | 14108.06 | 103.2
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 17 | 17 | 53 | 78 | 48 | 55 | 35 | 17 | 0 | 0 | 145 | 315 | 0 | 0 | 300 | 0 | 0 | 14 | 123 | 12 | 21 | 0 | 0 | 15 | 30 | 12 | 0 | 40 | 0 | 0 | 17 | 12 | 25 | 1.2 | 222 | 104 | 2 | 1125 | 16 | 0 | 25 | 0 | 63 | 214 | 0 | 0 | 0 | 1192 | 20 | 12 | 0 | 0 | 280 | 200 | 51 | 0 | 185 | 0 | 33 | 140 | 175 | 0 | 19 | 17 | 146 | 0 | 24 | 0 | 305 | 0 | 334 | 40 | 0 | 133 | 10 | 8 | 0 | 51 | 0 | 0 | 0 | 101 | 0 | 21 | 21.27 | 153 | 0 | 2.1 | 47.83 | 12 | 7187.4 | 884 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 86 | 1146 | 0 | 0 | 0 | 1382.18 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 52.23 | 108 | 0 | 0 | 13.55 | 186 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 5.47 | 190 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 7 | 186 | 0.29 | 14 | 274 | 120 | 180 | 0 | 700 | 1084 | 17 | 7002.72 | 14190.12 | 103.21
15:00 | 0 | 4 | 25 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 17 | 53 | 78 | 48 | 55 | 35 | 35 | 0 | 0 | 147 | 320 | 0 | 0 | 292 | 0 | 0 | 9 | 123 | 11 | 21 | 0 | 0 | 15 | 30 | 12 | 0 | 44 | 0 | 0 | 17 | 12 | 25 | 3.46 | 222 | 105 | 2 | 1125 | 26 | 0 | 25 | 0 | 65 | 210 | 0 | 0 | 0 | 1192 | 12 | 18 | 0 | 0 | 280 | 200 | 51 | 0 | 184 | 0 | 34 | 140 | 177 | 0 | 19 | 50 | 142 | 0 | 38 | 5 | 310 | 0 | 295 | 41 | 0 | 137 | 9 | 8 | 0 | 51 | 0 | 0 | 0 | 101 | 7 | 28 | 17.95 | 152 | 0 | 1 | 40.77 | 12 | 7272.18 | 895 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 76 | 1149 | 0 | 0 | 0 | 1351.97 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 0 | 41.92 | 86 | 0 | 0 | 29.28 | 182 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 3.37 | 190 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 6.2 | 61 | 0.5 | 15 | 257 | 100 | 220 | 0 | 623 | 1090 | 0 | 6926.24 | 14198.42 | 103.21
16:00 | 0 | 17 | 52 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 53 | 78 | 48 | 55 | 35 | 54 | 0 | 0 | 144 | 300 | 0 | 17 | 290 | 0 | 0 | 9 | 143.42 | 11 | 21 | 0 | 0 | 15 | 50 | 12 | 0 | 52 | 0 | 0 | 17 | 12 | 25 | 2.57 | 222 | 104 | 2 | 1125 | 50 | 0 | 25 | 0 | 34 | 210 | 0 | 0 | 0 | 1193 | 8 | 45 | 0 | 0 | 280 | 200 | 51 | 0 | 188 | 0 | 34 | 139 | 172 | 0 | 19 | 50 | 136 | 0 | 25 | 22 | 300 | 0 | 312 | 41 | 0 | 131 | 6 | 8 | 0 | 51 | 0 | 0 | 0 | 100 | 17 | 55 | 12.1 | 113 | 0 | 1.2 | 29.81 | 12 | 7373.1 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 27 | 1149 | 0 | 0 | 0 | 1309.3 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35.32 | 64 | 0 | 0 | 29.66 | 181 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 3.03 | 190 | 0 | 35 | 18 | 0 | 0 | 0 | 0 | 3.9 | 91 | 0.37 | 0 | 243 | 100 | 220 | 0 | 624 | 1076 | 0 | 6773.58 | 14146.68 | 103.21
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 17 | 17 | 71 | 78 | 48 | 55 | 35 | 90 | 0 | 0 | 145 | 300 | 0 | 35 | 306 | 0 | 0 | 2 | 143.42 | 11 | 21 | 0 | 0 | 0 | 50 | 12 | 0 | 25 | 0 | 0 | 17 | 12 | 25 | 1.89 | 222 | 66 | 2 | 1125 | 34 | 0 | 25 | 0 | 31 | 210 | 0 | 0 | 0 | 1194 | 3 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 187 | 0 | 34 | 139 | 120 | 5 | 19 | 17 | 144 | 0 | 19 | 22 | 305 | 0 | 316 | 41 | 0 | 134 | 3 | 8 | 0 | 51 | 0 | 0 | 0 | 101 | 17 | 55 | 6.06 | 113 | 0 | 0.6 | 14.07 | 18 | 7218.04 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 16 | 1148 | 0 | 0 | 0 | 1313.24 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 14.32 | 17 | 5 | 0 | 13.66 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.44 | 190 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 2.5 | 59 | 0.09 | 0 | 248 | 100 | 220 | 0 | 654 | 1080 | 0 | 6685.25 | 13903.29 | 103.21
18:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 35 | 17 | 77 | 95 | 95 | 55 | 32 | 90 | 0 | 0 | 146 | 305 | 0 | 35 | 303 | 0 | 0 | 1 | 143.42 | 11 | 21 | 0 | 0 | 0 | 50 | 12 | 0 | 25 | 0 | 0 | 17 | 12 | 25 | 0.16 | 222 | 67 | 2 | 1075 | 32 | 0 | 25 | 0 | 31 | 210 | 0 | 0 | 0 | 1100 | 1 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 183 | 0 | 34 | 139 | 110 | 27 | 8 | 17 | 126 | 0 | 3 | 29 | 310 | 0 | 302 | 41 | 0 | 137 | 0 | 8 | 0 | 52 | 0 | 0 | 0 | 100 | 17 | 54 | 0.66 | 113 | 0 | 0.1 | 1.85 | 12 | 7072.19 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4 | 1111 | 0 | 0 | 0 | 1325.82 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 2.58 | 5 | 10 | 0 | 1.96 | 167 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.24 | 190 | 0 | 35 | 2 | 34 | 0 | 0 | 0 | 0.8 | 25 | 0.04 | 0 | 199 | 100 | 180 | 0 | 814 | 1078 | 0 | 6604.44 | 13676.63 | 103.21
19:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 35 | 17 | 128 | 127 | 95 | 55 | 35 | 90 | 0 | 0 | 146 | 290 | 0 | 35 | 315 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 5 | 100 | 24 | 0 | 21 | 34 | 43 | 26 | 50 | 50 | 0 | 222 | 77 | 2 | 1125 | 50 | 0 | 30 | 12 | 39 | 210 | 0 | 0 | 0 | 1133 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 189 | 0 | 48 | 142 | 125 | 26 | 19 | 67 | 156 | 8 | 0 | 29 | 305 | 0 | 319 | 41 | 0 | 125 | 0 | 8 | 0 | 52 | 0 | 0 | 0 | 100 | 17 | 54 | 0 | 144 | 0 | 0 | 0 | 12 | 7764.42 | 897 | 0 | 0 | 19 | 0 | 38 | 0 | 0 | 0 | 0 | 42 | 0 | 1055 | 0 | 0 | 0 | 1452.17 | 0 | 0 | 0 | 30 | 45 | 0 | 40 | 24 | 16 | 0 | 0 | 26 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 190 | 0 | 90 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 218 | 120 | 220 | 0 | 886 | 1093 | 4 | 7093.17 | 14857.59 | 103.2
19:30 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 35 | 17 | 133 | 141 | 95 | 55 | 55 | 90 | 0 | 0 | 142 | 285 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 25 | 115 | 60 | 0 | 16 | 34 | 45 | 54.36 | 50 | 50 | 0 | 222 | 102 | 3 | 1125 | 107 | 0 | 50 | 25.5 | 75 | 210 | 0 | 0 | 0 | 1192 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 187 | 0 | 89 | 142 | 173 | 28 | 19 | 67 | 152 | 25 | 0 | 29 | 310 | 0 | 296 | 41 | 0 | 131 | 0 | 10 | 0 | 84 | 0 | 0 | 0 | 100 | 17 | 66 | 0 | 152 | 0 | 0 | 0 | 12 | 8238.28 | 885 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1095 | 0 | 0 | 0 | 1416.09 | 0 | 0 | 0 | 35 | 50 | 0 | 60 | 25 | 34 | 0 | 0 | 20 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 190 | 0 | 95 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 278 | 120 | 220 | 0 | 984 | 1163 | 27 | 7494.09 | 15732.37 | 103.2
20:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 35 | 17 | 133 | 142 | 95 | 55 | 55 | 90 | 0 | 0 | 139 | 275 | 0 | 35 | 290 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 35 | 120 | 60 | 0 | 16 | 34 | 39 | 54.36 | 50 | 50 | 0 | 222 | 107 | 6 | 1125 | 115 | 0 | 50 | 25.5 | 79 | 210 | 0 | 0 | 0 | 1186 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 182 | 0 | 91 | 141 | 172 | 27 | 19 | 65 | 150 | 25 | 0 | 29 | 305 | 0 | 298 | 41 | 0 | 136 | 0 | 10 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 67 | 0 | 152 | 0 | 0 | 0 | 12 | 8236.28 | 896 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 1139 | 0 | 0 | 0 | 1405.23 | 0 | 30 | 0 | 35 | 50 | 0 | 93 | 26 | 52.2 | 0 | 0 | 20 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 190 | 0 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 273 | 120 | 220 | 0 | 883 | 1163 | 27 | 7548.43 | 15784.71 | 103.2
21:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 35 | 17 | 133 | 142 | 95 | 55 | 35 | 17 | 0 | 0 | 140 | 270 | 0 | 35 | 284 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 16 | 100 | 56 | 0 | 14 | 31 | 39 | 54.36 | 24 | 50 | 0 | 222 | 104 | 9 | 1125 | 50 | 0 | 50 | 25.5 | 68 | 211 | 0 | 0 | 0 | 1190 | 0 | 35 | 0 | 0 | 280 | 200 | 51 | 0 | 180 | 0 | 88 | 141 | 136 | 27 | 19 | 17 | 148 | 25 | 0 | 28 | 290 | 0 | 289 | 41 | 0 | 131 | 0 | 10 | 0 | 86 | 0 | 0 | 0 | 100 | 17 | 67 | 0 | 153 | 0 | 0 | 0 | 12 | 7879.28 | 897 | 0 | 0 | 37 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 1172 | 0 | 0 | 0 | 1481.65 | 0 | 32 | 0 | 35 | 50 | 0 | 93 | 26 | 52.2 | 0 | 0 | 26 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 190 | 0 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 268 | 120 | 220 | 0 | 1050 | 1163 | 27 | 7806.85 | 15686.13 | 103.2
22:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 35 | 17 | 133 | 145 | 97 | 55 | 35 | 17 | 0 | 0 | 144 | 285 | 0 | 0 | 302 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 15 | 100 | 40 | 0 | 4 | 17 | 39 | 17 | 24 | 50 | 0 | 222 | 106 | 0 | 975 | 47 | 0 | 50 | 25.5 | 64 | 211 | 0 | 0 | 0 | 1225 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 180 | 0 | 68 | 143 | 122 | 27 | 19 | 22 | 146 | 25 | 0 | 28 | 300 | 0 | 317 | 40 | 0 | 133 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 67 | 0 | 154 | 0 | 0 | 0 | 12 | 7561.92 | 897 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 1194 | 0 | 0 | 0 | 1475.06 | 0 | 32 | 0 | 35 | 50 | 0 | 85 | 26 | 52.2 | 0 | 0 | 26 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 190 | 0 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 278 | 120 | 220 | 0 | 1050 | 1163 | 17 | 7764.26 | 15326.18 | 103.2
23:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 17 | 17 | 96 | 145 | 97 | 55 | 35 | 0 | 0 | 0 | 149 | 315 | 0 | 0 | 320 | 0 | 0 | 0 | 140 | 11 | 22 | 0 | 0 | 43 | 190 | 44 | 0 | 14 | 17 | 39 | 17 | 25 | 50 | 0 | 222 | 107 | 2 | 835 | 50 | 0 | 50 | 25.5 | 78 | 211 | 0 | 0 | 0 | 1224 | 0 | 24 | 0 | 0 | 280 | 200 | 51 | 0 | 186 | 0 | 51 | 142 | 143 | 26 | 19 | 96 | 156 | 25 | 0 | 31 | 315 | 0 | 350 | 41 | 0 | 148 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 67 | 0 | 154 | 0 | 0 | 0 | 12 | 7712.5 | 897 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 1186 | 0 | 0 | 0 | 1478.04 | 0 | 32 | 0 | 35 | 50 | 0 | 85 | 26 | 52.2 | 0 | 0 | 26 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 190 | 0 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 307 | 120 | 220 | 0 | 850 | 1163 | 17 | 7610.24 | 15322.74 | 103.19
Total KWH | 0 | 484800 | 120480 | 0 | 0 | 0 | 0 | 0 | 7524000 | 0 | 0 | 259200 | 449640 | 1507248 | 2572800 | 1914938 | 1150149 | 598712 | 802080 | 0 | 0 | 3488640 | 7566982 | 0 | 337840 | 7228485 | 0 | 0 | 103474 | 2929200 | 261600 | 501840 | 0 | 0 | 469200 | 1359927 | 465600 | 0 | 531360 | 190405 | 211969 | 430154 | 369600 | 699840 | 28441 | 5359370 | 2209700 | 364320 | 26407272.73 | 796218 | 0 | 716640 | 139971.6 | 1388364 | 4942101 | 0 | 0 | 0 | 28587270 | 120150 | 354618 | 0 | 0 | 7183200 | 5008000 | 1283850 | 0 | 4645000 | 0 | 714240 | 3395421 | 3106560 | 283080 | 468680 | 670320 | 3119040 | 155626 | 456445 | 288832 | 7449000 | 0 | 7965000 | 958000 | 0 | 3313881.82 | 76526 | 269080 | 0 | 1335360 | 0 | 0 | 0 | 2419280 | 168120 | 1078800 | 143575 | 2476800 | 0 | 15550 | 363500 | 294720 | 175050086.15 | 21470545 | 0 | 0 | 146400 | 0 | 912000 | 0 | 0 | 0 | 0 | 360288 | 514080 | 28138180 | 0 | 0 | 0 | 29147771 | 0 | 136756 | 0 | 585504 | 1036032 | 0 | 415504 | 152111 | 359827 | 393344 | 759590 | 131805 | 0 | 351280 | 4526818 | 0 | 0 | 0 | 0 | 0 | 3756946 | 0 | 36600 | 4637000 | 0 | 1165220 | 213942 | 728707 | 0 | 0 | 0 | 43604.88 | 1458720 | 3765 | 980160 | 6677000 | 2800000 | 5328460 | 0 | 16589090 | 27601454.55 | 381600 | 161940104.43 | 336990190.58 | 103.19

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 25-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14007.39 | MW | 12:00 Hr. | Energy Generated |  |  | 336.9902 |  | MKWHr.
| Day Peak Demand |  |  | 14512.39 | MW | 12:00 Hr. | Energy Unserverd |  |  | 13.724 |  | MKWHr.
| Evening Peak Generation |  |  | 15784.71 | MW | 20:00 Hr. | Energy Demand |  |  | 350.7142 |  | MKWHr.
| Evening Peak Demand |  |  | 16692.71 | MW | 20:00 Hr. | Maximum Temperature |  |  | 34.5 |  | °C
| Minimum Generation of the Day |  |  | 12274.06 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 698.92 |  | MMCFD
| Maximum Generation of the Day |  |  | 15784.71 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 7.0857 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.5715 | 0 | 13.1271 | 0 | 0 | 0.10347 | 0 | 0 | 39.8021 | Gas | 93.9839 | Gas | 327707390.2044
| Chattogram Zone |  |  | 5.3064 | 54.9945 | 9.4476 | 0 | 5.3594 | 0.14859 | 0 | 0.53136 | 75.7879 | Coal | 138.6373 | Coal | 934451097.4549
| Cumilla Zone |  |  | 21.9842 | 0 | 5.5733 | 0 | 0 | 0.45644 | 3.119 | 0 | 31.1329 | HFO | 38.7463 | HFO | 694987396.304
| Mymensingh Zone |  |  | 0 | 0 | 4.0184 | 0 | 0 | 0.52263 | 0 | 0 | 4.5411 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.7096 | 0 | 0 | 0 | 0 | 0.076526 | 0 | 0 | 23.7861 | Hydro | 5.3594 | Hydro | 535937
| Khulna Zone |  |  | 0 | 28.1382 | 0.50669 | 0 | 0 | 0.51408 | 22.3825 | 0 | 51.5415 | Solar | 5.0826 | Solar | 82233818.1104
| Barishal Zone |  |  | 8.1285 | 50.8675 | 1.3618 | 0 | 0 | 0.003765 | 0 | 0 | 60.3615 | Import | 54.6494 | Import | 340066742.55
| Rajshahi Zone |  |  | 8.2838 | 0 | 2.8175 | 0 | 0 | 1.5408 | 29.1478 | 0 | 41.7899 | Wind | 0.53136 | Wind | 7816305.6
| Rangpur Zone |  |  | 0 | 4.637 | 1.8939 | 0 | 0 | 1.7163 | 0 | 0 | 8.2472
| Total |  |  | 93.9839 | 138.6373 | 38.7463 | 0 | 5.3594 | 5.0826 | 54.6494 | 0.53136 | 336.9902
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 327707390.2044 |  | Hydro | 535937
|  |  |  | Coal | 934451097.4549 |  | Solar | 82233818.1104
|  |  |  | HFO | 694987396.304 |  | Import | 340066742.55
|  |  |  | HSD | 0 |  | Wind | 7816305.6
[5 empty] | Total: | 238,77,98,687 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4705 | Peak Hr Flow | 896.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 50669436.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.1478 | Peak Hr Flow | 1405.23 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2346 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.119 | Peak Hr Flow | 150.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2667 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.7374 | Peak Hr Flow | 2451.23 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 161 |  | 5705
|  |  |  | Chattogram |  | 0 |  | 1595
|  |  |  | Cumilla |  | 8 |  | 1428
|  |  |  | Mymensingh |  | 353 |  | 1483
|  |  |  | Sylhet |  | 207 |  | 768
|  |  |  | Khulna |  | 101 |  | 1869
|  |  |  | Barishal |  | 2 |  | 464
|  |  |  | Rajshahi |  | 0 |  | 1617
|  |  |  | Rangpur |  | 37 |  | 1144
|  |  |  | Total |  | 869 |  | 16073
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 489
|  |  |  | Total Unavailable Capacity |  |  |  | 789
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:24 | 10:51 | Kasba 132/33kV S/S TR-2 HT Scheduled S/D Due to Kasba-2 feeder 33kV side DS isolator
maintenace by PBS
| 09:24 | 10:51 | Kasba 132/33kV S/S TR-2 LT Scheduled S/D Due to Kasba-2 feeder 33kV side DS isolator
maintenace by PBS
| 10:00 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Project Work S/D Due to CCC PROJECT WORK ( ds
clamp and loop measurements)
| 10:01 | 19:47 | Korerhat 400/230/132kV S/S ATR-3(7103T) LT Project Work S/D Due to DFDR work
| 10:04 | 19:46 | Korerhat 400/230/132kV S/S ATR-3(7103T) HT Project Work S/D Due to DFDR work
| 10:58 | 21:46 | Joydebpur 132/33kV S/S GT-4 HT Forced S/D Due to Oil Leakage Maintenance | [7 empty] | 20.0MW load
interrup.
| 11:35 | 15:43 | KSRM 132/33kV S/S Transformer-01 HT Scheduled S/D Due to for 33 KV Incoming CT Oil
Leakage maintenance
| 12:00 |  | Day Peak Generation: 14007 MW.
| 12:01 | 13:43 | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 Tripped showing Lock out relay
Differential relay relays Due to Transient fault
| 12:27 | 13:13 | Kabirpur 132/33kV S/S XFR, T-I HT Tripped showing Micom relays Due to 33kV Boroibari
feeder earth fault.
| 12:27 | 13:13 | Kabirpur 132/33kV S/S XFR, T-I LT Tripped showing Micom relays Due to 33kV Boroibari
Feeder Earth Fault.
| 12:49 |  | Sirajgonj 400 MW CCPP Unit-4 Synchronized with remarks:- GT
| 13:48 | 16:35 | Mithapukur 132/33kV S/S TR-2 (414T) LT Scheduled S/D Due to incomer -2 DS maintenance | [7 empty] | 16.0MW load
interrup.
| 13:48 | 16:34 | Mithapukur 132/33kV S/S TR-2 (414T) HT Scheduled S/D Due to incomer -2 DS maintenance | [7 empty] | 16.0MW load
interrup.
| 14:39 | 21:44 | Madanganj 132/33kV S/S GT-1 LT Forced S/D Due to 33kv busbar faulty sound occuring
| 14:40 | 21:42 | Madanganj 132/33kV S/S GT-1 HT Forced S/D Due to 33kv busbar faulty sound occuring
| 15:23 | 18:00 | Barishal 230/132kV S/S ATR-1 LT Scheduled S/D Due to Maintenance of tap changer motor
| 15:24 | 18:04 | Barishal 230/132kV S/S ATR-1 HT Scheduled S/D Due to Maintenance of tap changer motor
| 18:01 | 01:21 | Bibiyana-Fenchuganj 230 kV Ckt-2 Forced S/D from Bibiana 400/230kV end Due to
Disconnected Switch Flashing and from Fenchuganj 230/132/33kV end Due to Bibiyana SS end
work.
| 20:00 |  | Evening Peak Generation: 15785 MW.
| 20:20 | 22:26 | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to Red hot maintenance at Tr-02 LT side | [7 empty] | 15.0MW load
|  |  | Y-phase. | [7 empty] | interrup.
| 20:27 | 22:24 | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to Red hot maintenance at Tr-02 LT side | [7 empty] | 15.0MW load
|  |  | Y-phase. | [7 empty] | interrup.
| 22:45 | 23:39 | Srinagar 132/33kV S/S Tr-01 LT Scheduled S/D Due to Red hot maintenance by Pbs. | [7 empty] | 20.0MW load
interrup.
| 22:46 | 23:37 | Srinagar 132/33kV S/S Tr-01 HT Scheduled S/D Due to Red hot maintenance by Pbs. | [7 empty] | 20.0MW load
interrup.
| 06:15 |  | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to Maint. Work of South ckt-2 main bus DS
| 06:15 |  | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to Maint. Work of south ckt-2 main bus DS.
| 06:20 |  | Khulna(C )-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end. and from Khulna
(C) end Due to S/D for south ckt-02 bus DS maintenance work.
| 06:21 |  | Khulna(C )-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end. and from Khulna
(C) end Due to S/D for south ckt-02 bus DS maintenance work.
| 06:23 |  | Khulna (C) S/S North-WestCkt-1 Scheduled S/D Due to S/D for south ckt-02 bus DS
maintenance work.
| 06:23 |  | Khulna (C) S/S North- West Ckt-2 Scheduled S/D Due to S/D for south ckt-02 bus DS
maintenance work.
| 06:24 |  | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to Maint. Work
of South ckt-2 main bus DS and from Khulna(S) 230/132kV end Due to Project Work at
Central SS end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 25-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 7524000 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 139 | 3488640 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1150149 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 290 | 7228485 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 259200 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 142 | 2572800 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 598712 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 337840 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11 | 261600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 501840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 120480 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 1914938 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 1507248 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 484800 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 802080 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 103474 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 23.297 | 17 | 449640 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 275 | 7566982 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 2929200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6637.271 | 1972.42 | 39802108
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 139971.6 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 120150 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 716640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5359370 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 210 | 4942101 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 79 | 1388364 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 39 | 211969 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 190405 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 369600 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 6 | 364320 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 60 | 465600 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 28441 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 120 | 1359927 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 430154 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 107 | 2209700 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 699840 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 469200 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 115 | 796218 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1186 | 28587270 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 16 | 531360 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 26407272.73 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 3583.86 | 75787873.33
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 182 | 4645000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 280 | 7183200 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 200 | 5008000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1283850 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 24 | 354618 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 288832 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 141 | 3395421 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 172 | 3106560 | Liquid fuel shortage
| Import (Tripura) |  | Import | 0 | 160 | 150 | 3119040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 155626 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 468680 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 65 | 670320 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 283080 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 91 | 714240 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 456445 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1456 | 31132912
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 143575 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 152 | 2476800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 1078800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 363500 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 294720 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 168120 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 248 | 4541065
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 76526 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 958000 | Under Maintenance
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 136 | 3313881.82 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1335360 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2419280 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 10 | 269080 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7449000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 298 | 7965000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 976 | 23786127.82
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 896 | 21470545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 146400 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 360288 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 514080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1139 | 28138180 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2169 | 51541493
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 883 | 16589090 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 60 | 980160 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2800000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 1163 | 27601454.55 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5328460 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 27 | 381600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 273 | 6677000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3765 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2746 | 60361529.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 393344 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 30 | 136756 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 152111 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 174 | 4526818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 3756946 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 131805 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 359827 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 415504 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 1036032 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 35 | 585504 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 36600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1405.23 | 29147771 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 351280 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 759590 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2299.43 | 41789888
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 190 | 4637000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 728707 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 43604.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 1165220 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 213942 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1458720 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 334 | 8247193.88
Eastern Grid Total |  |  |  |  | 17406.339 | 8236.28 | 175050086.15
Western Grid Total |  |  |  |  | 11731.125 | 7548.43 | 161940104.43
National Grid Total |  |  |  |  | 29137.464 | 15784.71 | 336990190.58
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 25-07-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10304.47 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4954.3 | MW
i) Dhaka area |  |  | 5543.57 |  | MW | i) Khulna area |  |  |  | 1768.5 | MW
ii) Chattogram area |  |  | 1649.9 |  | MW | ii) Barishal area |  |  |  | 461.8 | MW
iii) Cumilla area |  |  | 1420 |  | MW | iii) Rajshahi area |  |  |  | 1617 | MW
iv) Mymensingh area |  |  | 1130 |  | MW | iv) Rangpur area |  |  |  | 1107 | MW
v) Sylhet area |  |  | 561 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15258.77 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 95 | 02:00 | 133 | Narshingdi | 109 | 13:00 | 199 | Uttara | 91 | 13:00
2 | AKSML | 140 | 00:00 | 68 | Hasnabad | 92 | 19:30 | 134 | Natore | 161 | 23:00 | 200 | UttaraNew | 53 | 13:00
3 | Aftabnagar | 42 | 13:00 | 69 | Hathazari | 92 | 19:00 | 135 | Nawabganj | 63.6 | 22:00 | 201 | Zigatola | 108 | 12:00
4 | Agargaon | 110 | 13:00 | 70 | Hatirjheel | 79 | 15:00 | 136 | Netrakona | 126 | 08:00
5 | Agrabad | 64 | 14:00 | 71 | Ishurdi | 80 | 19:30 | 137 | New | 86 | 12:00
6 | Amnura | 31 | 00:00 | 72 | Jaldhaka | 96 | 20:00 | 138 | Niamatpur | 86 | 22:00
7 | Ashuganj | 78 | 12:00 | 73 | Jamalpur | 112 | 21:00 | 139 | Noapara | 44 | 19:30
8 | BSRM | 188 | 23:00 | 74 | Jashore | 146 | 20:00 | 140 | PHP | 12 | 18:30
9 | Bagerhat | 87 | 19:30 | 75 | Jhenaidah | 98 | 19:30 | 141 | Pabna | 103 | 19:30
10 | Bajitpur | 95 | 02:00 | 76 | Joydebpur | 145 | 19:30 | 142 | Palashbari | 132 | 22:00
11 | Bakerganj | 14.6 | 19:30 | 77 | Joypurhat | 70 | 23:00 | 143 | Panchagarh | 71 | 20:00
12 | Bakulia | 96 | 19:00 | 78 | Juldah | 16 | 23:00 | 144 | Patiya | 11 | 19:00
13 | Banani | 60 | 13:00 | 79 | KSRM | 13 | 07:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 6 | 11:00 | 80 | Kabirpur | 254 | 19:00 | 146 | Patuakhali | 67.5 | 22:00
15 | Barapukuria | 74 | 19:30 | 81 | Kachua | 96 | 22:00 | 147 | Payra | 34 | 00:00
16 | Barguna | 22 | 23:00 | 82 | Kaliganj | 38 | 19:30 | 148 | Postogola | 62 | 13:00
17 | Barishal | 99 | 12:00 | 83 | Kallyanpur | 120 | 13:00 | 149 | Pubail | 46 | 20:00
18 | Barishal-230 | 104 | 19:30 | 84 | Kalurghat | 41 | 16:00 | 150 | Purbachal | 30 | 13:00
19 | Baroaulia | 44 | 16:00 | 85 | Kamrangirchar | 80 | 13:00 | 151 | Purbasadipur | 146 | 23:00
20 | Baroirhat | 66 | 19:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 45 | 23:00
21 | Bashundhara | 198 | 13:00 | 87 | Kasba | 46 | 19:00 | 153 | Rahim | 55 | 14:00
22 | BashundharaCement | 1 | 15:00 | 88 | Kazla | 122 | 13:00 | 154 | Rajbari | 90 | 20:00
23 | Beanibazar | 82 | 00:00 | 89 | Keranigonj | 89 | 19:30 | 155 | Rajendrapur | 124 | 18:30
24 | Benapole | 57 | 19:30 | 90 | Khagrachori | 34 | 19:00 | 156 | Rajshahi | 112 | 23:00
25 | Bhaluka | 151 | 20:00 | 91 | Khulna | 60 | 21:00 | 157 | Rajshahi-230 | 100 | 21:00
26 | Bhandaria | 56 | 00:00 | 92 | Khulshi | 196 | 20:00 | 158 | Ramganj | 114 | 23:00
27 | Bhangura | 40 | 20:00 | 93 | Kishoreganj | 120 | 00:00 | 159 | Rampur | 42 | 19:30
28 | Bheramara(GK) | 63 | 23:00 | 94 | Kodda | 286 | 19:00 | 160 | Rangamati | 17 | 20:00
29 | Bhulta | 220 | 21:00 | 95 | Kulaura | 56 | 00:00 | 161 | Rangpur | 148 | 19:00
30 | Bog-Sherpur | 72 | 19:30 | 96 | Kurigram | 69 | 01:00 | 162 | Ruppur | 2.8 | 10:00
31 | Bogura | 199 | 22:00 | 97 | Kushtia | 147 | 20:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 76 | 22:00 | 98 | Laksam | 34 | 00:00 | 164 | Saidpur | 116 | 19:30
33 | Brahmanbaria | 95 | 05:00 | 99 | Lakshmipur | 45 | 19:00 | 165 | Santhia | 38 | 19:30
34 | Cantonment | 122 | 12:00 | 100 | Lalbag | 80 | 13:00 | 166 | Satkhira | 120 | 00:00
35 | Chandina | 43 | 22:00 | 101 | Lalmonirhat | 66 | 00:00 | 167 | Satmasjid | 101 | 14:00
36 | Chandpur | 88 | 22:00 | 102 | MI_Cement | 16.2 | 20:00 | 168 | Savar | 216 | 16:00
37 | Chandraghona | 33 | 19:30 | 103 | Madanganj | 46 | 23:00 | 169 | SevenRings | 15.97 | 16:00
38 | Chapai | 76 | 22:00 | 104 | Madaripur | 119 | 23:00 | 170 | ShahCement | 34 | 15:00
39 | Charfasson | 31 | 23:00 | 105 | Madartek | 81 | 23:00 | 171 | Shahjadpur | 84 | 19:00
40 | Charsaidpur | 47 | 13:00 | 106 | Madunaghat | 54 | 19:00 | 172 | Shahjibazar | 93 | 20:00
41 | Chauddagram | 75 | 22:00 | 107 | Magura | 64 | 19:30 | 173 | Shahmirpur | 51 | 19:00
42 | Chhatak | 41 | 00:00 | 108 | Mahasthangarh | 85 | 23:00 | 174 | Shariatpur | 96 | 22:00
43 | Chowmuhani | 155 | 22:00 | 109 | Maijdee | 39 | 22:00 | 175 | Sherpur | 148 | 20:00
44 | Chuadanga | 116 | 22:00 | 110 | Manikganj | 140 | 21:00 | 176 | Shikalbaha | 23.5 | 19:00
45 | Coxsbazar | 139 | 19:30 | 111 | Maniknagar | 74 | 13:00 | 177 | Shitalakhya | 75.8 | 13:00
46 | Cumilla(N) | 126 | 19:30 | 112 | Matarbari | 55 | 20:00 | 178 | Sholosohor | 49 | 15:00
47 | Cumilla(S) | 156 | 19:00 | 113 | Matuail | 76 | 15:00 | 179 | Shomvuganj | 44 | 18:30
48 | Daganbhuiyan | 35 | 23:00 | 114 | Metrorail_Motijheel | 20 | 13:00 | 180 | Shyampur | 158 | 11:00
49 | Daudkandi | 136 | 21:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 132 | 11:00
50 | DhakaUniversity | 80 | 13:00 | 116 | Millgate | 109 | 16:00 | 182 | Sirajganj | 120 | 20:00
51 | Dhamrai | 102 | 19:00 | 117 | Mirpur | 152 | 19:30 | 183 | Sitakunda | 35 | 19:30
52 | Dhanmondi | 98 | 13:00 | 118 | Mirsorai | 45 | 12:00 | 184 | Sonargaon | 133 | 21:00
53 | Dohazari | 112 | 19:00 | 119 | Mirzapur | 38 | 19:00 | 185 | Sreemongol | 78 | 19:00
54 | Faridpur | 179 | 21:00 | 120 | Mithapukur | 75 | 00:00 | 186 | Sreepur | 100 | 18:30
55 | Fatullah | 104 | 12:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 48.75 | 20:00
56 | Fenchuganj | 51 | 00:00 | 122 | Mogbazar | 40 | 14:00 | 188 | Sunamganj | 63 | 01:00
57 | Feni | 106 | 19:30 | 123 | Mongla | 38 | 12:00 | 189 | Sylhet | 129 | 19:00
58 | GPH | 72 | 05:00 | 124 | Motijheel | 46 | 13:00 | 190 | Sylhet_(South) | 77 | 00:00
59 | Ghatail | 86 | 22:00 | 125 | Muktagacha | 41 | 13:00 | 191 | TK | 24 | 23:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 107 | 21:00 | 192 | Tangail | 182 | 20:00
61 | Ghorashal-230 | 94 | 01:00 | 127 | Muradnagar | 54 | 23:00 | 193 | Taraganj | 28 | 20:00
62 | Goalpara | 36 | 13:00 | 128 | Mymensingh | 165 | 21:00 | 194 | Tasnim | 44 | 16:00
63 | Gollamari | 102 | 13:00 | 129 | Nabinagar | 106 | 11:00 | 195 | Thakurgaon | 123 | 20:00
64 | Gopalganj | 119 | 20:00 | 130 | Naogaon | 144 | 23:00 | 196 | Tongi | 151 | 23:00
65 | Gulshan | 98 | 13:00 | 131 | Narail | 58.5 | 21:00 | 197 | Ullahpara | 40 | 22:00
66 | Halishahar | 118 | 15:00 | 132 | Narinda | 74 | 13:00 | 198 | Ullon | 56 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 25-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14481.87 | 454 |  | 14956.3
1:00 | 14074.72 | 471 |  | 14566.92
2:00 | 13651.6 | 462 |  | 14134.6
3:00 | 13171.55 | 452 |  | 13643.55
4:00 | 12864.8 | 443 |  | 13327.8
5:00 | 12737.02 | 406 |  | 13161.02
6:00 | 12274.06 | 417 |  | 12710.06
7:00 | 12391.41 | 396 |  | 12805.41
8:00 | 12593.99 | 400 |  | 13011.99
9:00 | 12917.75 | 448 |  | 13385.75
10:00 | 13161.8 | 347 |  | 13524.8
11:00 | 13435.84 | 367 |  | 13819.84
12:00 | 14007.39 | 483 |  | 14512.39
13:00 | 14108.06 | 479 |  | 14609.06
14:00 | 14190.12 | 623 |  | 14841.12
15:00 | 14198.42 | 796 |  | 15030.42
16:00 | 14146.68 | 821 |  | 15004.68
17:00 | 13903.29 | 668 |  | 14601.29
18:00 | 13676.63 | 550 |  | 14251.63
19:00 | 14857.59 | 605 |  | 15489.59
19:30 | 15732.37 | 793 |  | 16561.37
20:00 | 15784.71 | 869 |  | 16692.71
21:00 | 15686.13 | 847 |  | 16571.13
22:00 | 15326.18 | 958 |  | 16327.18
23:00 | 15322.74 | 962 |  | 16327.74
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 25-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7702.07 | 6779.8 | 14481.87 | DAILY GENERATION CURVE
00:30 | 7666.39 | 6611.905 | 14278.295
01:00 | 7630.71 | 6444.01 | 14074.72 | 25-07-2026
01:30 | 7500.855 | 6362.305 | 13863.16
02:00 | 7371 | 6280.6 | 13651.6
02:30 | 7210.5 | 6201.075 | 13411.575
03:00 | 7050 | 6121.55 | 13171.55
03:30 | 6925 | 6093.175 | 13018.175
04:00 | 6800 | 6064.8 | 12864.8
04:30 | 6765.5 | 6035.41 | 12800.91
05:00 | 6731 | 6006.02 | 12737.02
05:30 | 6547.365 | 5958.175 | 12505.54
06:00 | 6363.73 | 5910.33 | 12274.06
06:30 | 6398.26 | 5934.475 | 12332.735
07:00 | 6432.79 | 5958.62 | 12391.41
07:30 | 6470.945 | 6021.755 | 12492.7
08:00 | 6509.1 | 6084.89 | 12593.99
08:30 | 6518.51 | 6237.36 | 12755.87
09:00 | 6527.92 | 6389.83 | 12917.75
09:30 | 6612.865 | 6426.91 | 13039.775
10:00 | 6697.81 | 6463.99 | 13161.8
10:30 | 6806.695 | 6492.125 | 13298.82
11:00 | 6915.58 | 6520.26 | 13435.84
11:30 | 7044.67 | 6676.945 | 13721.615
12:00 | 7173.76 | 6833.63 | 14007.39
12:30 | 7191.53 | 6866.195 | 14057.725
13:00 | 7209.3 | 6898.76 | 14108.06
13:30 | 7198.35 | 6950.74 | 14149.09
14:00 | 7187.4 | 7002.72 | 14190.12
14:30 | 7229.79 | 6964.48 | 14194.27
15:00 | 7272.18 | 6926.24 | 14198.42
15:30 | 7322.64 | 6849.91 | 14172.55
16:00 | 7373.1 | 6773.58 | 14146.68
16:30 | 7295.57 | 6729.415 | 14024.985
17:00 | 7218.04 | 6685.25 | 13903.29
17:30 | 7145.115 | 6644.845 | 13789.96
18:00 | 7072.19 | 6604.44 | 13676.63
18:30 | 7418.305 | 6848.805 | 14267.11
19:00 | 7764.42 | 7093.17 | 14857.59
19:30 | 8238.28 | 7494.09 | 15732.37
20:00 | 8236.28 | 7548.43 | 15784.71
20:30 | 8057.78 | 7677.64 | 15735.42 |  | Executive Engineer
21:00 | 7879.28 | 7806.85 | 15686.13 |  | Network Operation Division
21:30 | 7720.6 | 7785.555 | 15506.155
22:00 | 7561.92 | 7764.26 | 15326.18
22:30 | 7637.21 | 7687.25 | 15324.46
23:00 | 7712.5 | 7610.24 | 15322.74

## En-Curve
QF-LDC-12
Date | 25-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2427 | 1324 | 884 | 38 | 122 | 1004.8 | 222 | 5904 | 0 | 413.42 | 2128.65 | 0 | 0 | 14 | 454 | DAILY ENERGY CURVE
00:30 | 2374.5 | 1326 | 884 | 38 | 124 | 1004.805 | 221 | 5805 | 0 | 382.92 | 2097.07 | 0 | 0 | 21 | 462.5 | 25-07-2026
01:00 | 2322 | 1328 | 884 | 38 | 126 | 1004.81 | 220 | 5706 | 0 | 352.42 | 2065.49 | 0 | 0 | 28 | 471
01:30 | 2354 | 1321 | 884 | 38 | 126 | 1006.605 | 220 | 5690 | 0 | 304.21 | 1898.845 | 0 | 0 | 20.5 | 466.5 | Energy Generated | 336.9902 |  | MKWHr
02:00 | 2386 | 1314 | 884 | 38 | 126 | 1008.4 | 220 | 5674 | 0 | 256 | 1732.2 | 0 | 0 | 13 | 462 | Energy not Served | 13.724 |  | MKWHr
02:30 | 2385.5 | 1321 | 884 | 38 | 123 | 1003.975 | 220 | 5675.5 | 0 | 235.5 | 1509.6 | 0 | 0 | 15.5 | 457 | Total Energy Requirement | 350.7142 |  | MKWHr
03:00 | 2385 | 1328 | 884 | 38 | 120 | 999.55 | 220 | 5677 | 0 | 215 | 1287 | 0 | 0 | 18 | 452
03:30 | 2402.5 | 1333 | 884 | 38 | 121 | 1011.175 | 221 | 5677.5 | 0 | 215 | 1096 | 0 | 0 | 19 | 447.5
04:00 | 2420 | 1338 | 884 | 38 | 122 | 1022.8 | 222 | 5678 | 0 | 215 | 905 | 0 | 0 | 20 | 443
04:30 | 2440.5 | 1353 | 883.5 | 38 | 119 | 1018.41 | 222 | 5678 | 0 | 205.5 | 817 | 0 | 0 | 26 | 424.5
05:00 | 2461 | 1368 | 883 | 38 | 116 | 1014.02 | 222 | 5678 | 0 | 196 | 729 | 0 | 0 | 32 | 406
05:30 | 2471 | 1347 | 883.5 | 38 | 114 | 1023.87 | 222 | 5665.5 | 15.17 | 196 | 506 | 0 | 0 | 23.5 | 411.5
06:00 | 2481 | 1326 | 884 | 38 | 112 | 1033.72 | 222 | 5653 | 30.34 | 196 | 283 | 0 | 0 | 15 | 417
06:30 | 2478.5 | 1347.75 | 884 | 38 | 109 | 1030.98 | 222 | 5650 | 87.005 | 196 | 273 | 0 | 0 | 16.5 | 406.5
07:00 | 2476 | 1369.5 | 884 | 38 | 106 | 1028.24 | 222 | 5647 | 143.67 | 196 | 263 | 0 | 0 | 18 | 396
07:30 | 2468 | 1342.5 | 883.5 | 38 | 109 | 1021.15 | 222 | 5658.5 | 229.55 | 196 | 305 | 0 | 0 | 19.5 | 398
08:00 | 2460 | 1315.5 | 883 | 38 | 112 | 1014.06 | 222 | 5670 | 315.43 | 196 | 347 | 0 | 0 | 21 | 400
08:30 | 2431 | 1306.75 | 883 | 38 | 113 | 1023.15 | 222 | 5770.5 | 374.97 | 188.5 | 385.5 | 0 | 0 | 19.5 | 424
09:00 | 2402 | 1298 | 883 | 38 | 114 | 1032.24 | 222 | 5871 | 434.51 | 181 | 424 | 0 | 0 | 18 | 448
09:30 | 2391 | 1298 | 883 | 38 | 118 | 1034.2 | 222 | 5878 | 488.075 | 181 | 492 | 0 | 0 | 16.5 | 397.5
10:00 | 2380 | 1298 | 883 | 38 | 122 | 1036.16 | 222 | 5885 | 541.64 | 181 | 560 | 0 | 0 | 15 | 347
10:30 | 2362.5 | 1303 | 883.5 | 38 | 123 | 1030.03 | 222 | 5870 | 557.29 | 189.5 | 702.5 | 0 | 0 | 17.5 | 357
11:00 | 2345 | 1308 | 884 | 38 | 124 | 1023.9 | 222 | 5855 | 572.94 | 198 | 845 | 0 | 0 | 20 | 367
11:30 | 2355 | 1302 | 883.5 | 38 | 129 | 1151.075 | 222 | 5813.5 | 634.04 | 216.5 | 954 | 0 | 0 | 23 | 425
12:00 | 2365 | 1296 | 883 | 38 | 134 | 1278.25 | 222 | 5772 | 695.14 | 235 | 1063 | 0 | 0 | 26 | 483
12:30 | 2385 | 1262.5 | 883.5 | 38 | 132 | 1355.365 | 222 | 5743.5 | 676.86 | 235 | 1097.5 | 0 | 0 | 26.5 | 481
13:00 | 2405 | 1229 | 884 | 38 | 130 | 1432.48 | 222 | 5715 | 658.58 | 235 | 1132 | 0 | 0 | 27 | 479
13:30 | 2489 | 1235.5 | 884 | 38 | 138 | 1407.33 | 222 | 5713 | 644.76 | 218 | 1126 | 0 | 0 | 33.5 | 551
14:00 | 2573 | 1242 | 884 | 38 | 146 | 1382.18 | 222 | 5711 | 630.94 | 201 | 1120 | 0 | 0 | 40 | 623
14:30 | 2643.5 | 1269.5 | 889.5 | 38 | 144 | 1367.075 | 222 | 5668.5 | 545.695 | 218 | 1146.5 | 0 | 0 | 42 | 709.5
15:00 | 2714 | 1297 | 895 | 38 | 142 | 1351.97 | 222 | 5626 | 460.45 | 235 | 1173 | 0 | 0 | 44 | 796
15:30 | 2739.5 | 1277.5 | 896 | 38 | 139 | 1330.635 | 222 | 5613 | 413.205 | 273.71 | 1182 | 0 | 0 | 48 | 808.5
16:00 | 2765 | 1258 | 897 | 38 | 136 | 1309.3 | 222 | 5600 | 365.96 | 312.42 | 1191 | 0 | 0 | 52 | 821
16:30 | 2777.5 | 1262.5 | 897 | 38 | 140 | 1311.27 | 222 | 5619.5 | 273.795 | 292.92 | 1152 | 0 | 0 | 38.5 | 744.5
17:00 | 2790 | 1267 | 897 | 38 | 144 | 1313.24 | 222 | 5639 | 181.63 | 273.42 | 1113 | 0 | 0 | 25 | 668
17:30 | 2732.5 | 1249 | 896.5 | 38 | 135 | 1319.53 | 222 | 5603 | 115.51 | 287.92 | 1166 | 0 | 0 | 25 | 609
18:00 | 2675 | 1231 | 896 | 38 | 126 | 1325.82 | 222 | 5567 | 49.39 | 302.42 | 1219 | 0 | 0 | 25 | 550
18:30 | 2721.5 | 1240.5 | 896.5 | 38 | 141 | 1388.995 | 222 | 5633.5 | 24.695 | 462.92 | 1474.5 | 0 | 0 | 23 | 577.5
19:00 | 2768 | 1250 | 897 | 38 | 156 | 1452.17 | 222 | 5700 | 0 | 623.42 | 1730 | 0 | 0 | 21 | 605
19:30 | 2807 | 1287 | 885 | 38 | 152 | 1416.09 | 222 | 6027 | 0 | 667.42 | 2214.86 | 0 | 0 | 16 | 793
20:00 | 2790 | 1279 | 896 | 38 | 150 | 1405.23 | 222 | 5959 | 0 | 748.42 | 2281.06 | 0 | 0 | 16 | 869
20:30 | 2763 | 1268.5 | 896.5 | 38 | 149 | 1443.44 | 222 | 6058.5 | 0 | 754.42 | 2127.06 | 0 | 0 | 15 | 858
21:00 | 2736 | 1258 | 897 | 38 | 148 | 1481.65 | 222 | 6158 | 0 | 760.42 | 1973.06 | 0 | 0 | 14 | 847
21:30 | 2728.5 | 1256 | 897 | 38 | 147 | 1478.355 | 222 | 6116.5 | 0 | 711.42 | 1902.38 | 0 | 0 | 9 | 902.5
22:00 | 2721 | 1254 | 897 | 38 | 146 | 1475.06 | 222 | 6075 | 0 | 662.42 | 1831.7 | 0 | 0 | 4 | 958
22:30 | 2754 | 1287.5 | 897 | 38 | 151 | 1476.55 | 222 | 5915 | 0 | 662.21 | 1912.2 | 0 | 0 | 9 | 960
23:00 | 2787 | 1321 | 897 | 38 | 156 | 1478.04 | 222 | 5755 | 0 | 662 | 1992.7 | 0 | 0 | 14 | 962
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 25-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 77 | 9 | 250 | 158 | 1516 | 440 | Ishurdi-Ghorashal Ckt-1 | Export | 3340436.36
1:00 | 74 | 19 | 196 | 160 | 1344 | 458
2:00 | 80 | 23 | 214 | 164 | 1372 | 486 |  | Import | 0
3:00 | 81 | 23 | 216 | 164 | 1432 | 524
4:00 | 91 | 25 | 230 | 160 | 1490 | 518 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 102 | 30 | 250 | 166 | 1542 | 546
6:00 | 117 | 38 | 280 | 168 | 1574 | 522 |  | Import | 0
7:00 | 107 | 33 | 270 | 166 | 1520 | 548
8:00 | 130 | 40 | 320 | 180 | 1828 | 644 | Sirajganj-Sreepur Ckt-1 | Export | 2286000
9:00 | 157 | 52 | 390 | 186 | 1938 | 696
10:00 | 176 | 65 | 400 | 190 | 1980 | 786 |  | Import | 0
11:00 | 170 | 62 | 420 | 190 | 1970 | 846
12:00 | 181 | 55 | 460 | 180 | 1994 | 860 | Sirajganj-Sreepur Ckt-2 | Export | 2293000
13:00 | 172 | 41 | 450 | 172 | 1958 | 854
14:00 | 179 | 49 | 500 | 180 | 1962 | 848 |  | Import | 0
15:00 | 182 | 47 | 540 | 182 | 1882 | 858
16:00 | 182 | 51 | 520 | 170 | 1850 | 844 | Gopalganj-Aminbazar Ckt-1 | Export | 21350000
17:00 | 183 | 56 | 540 | 200 | 1944 | 844
18:00 | 176 | 52 | 520 | 184 | 1896 | 740 |  | Import | 0
18:30 | 174 | 47 | 530 | 200 | 1916 | 738
19:00 | 169 | 48 | 530 | 214 | 1864 | 730 | Gopalganj-Aminbazar Ckt-2 | Export | 21400000
19:30 | 129 | 22 | 400 | 164 | 1798 | 660
20:00 | 130 | 20 | 410 | 166 | 1806 | 694 |  | Import | 0
21:00 | 140 | 24 | 420 | 162 | 1966 | 696
22:00 | 135 | 22 | 410 | 140 | 1954 | 642 |  | Total Export | 50669436.36
23:00 | 135 | 24 | 400 | 128 | 1830 | 692 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 25-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 372 | 05:00 | 346 | 13:00 | Madunaghat | 390 | 02:00 | 380 | 15:00
Amtali | 410 | 01:00 | 400 | 22:00 | Meghnaghat | 378 | 01:00 | 350 | 13:00
Ashuganj | 397 | 5:00 | 364 | 13:00 | Payra | 414 | 03:00 | 403 | 21:00
Bhulta | 392 | 01:00 | 359 | 13:00 | Rahanpur | 402 | 06:00 | 381 | 23:00
Bibiana | 377 | 00:00 | 364 | 12:00 | Rampal | 393 | 03:00 | 375 | 22:00
BIPTC | 401 | 04:00 | 393 | 19:30
Bogura | 384 | 02:00 | 358 | 19:30
Gopalganj | 387 | 02:00 | 367 | 21:00
Kaliakoir | 363 | 00:00 | 336 | 14:00
Korerhat | 389 | 01:00 | 373 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 01:00 | 207 | 13:00 | Ishurdi | 234 | 06:00 | 210 | 23:00
AKSML | 238 | 02:00 | 225.9 | 17:00 | Jhenaidah | 224 | 06:00 | 200 | 23:00
Aminbazar | 229 | 00:00 | 209 | 14:00 | Kachua | 222 | 00:00 | 214 | 21:00
Ashuganj | 222 | 01:00 | 210 | 13:00 | Kaliakoir | 229 | 01:00 | 205 | 14:00
Ashuganj-400 | 222 | 01:00 | 210 | 13:00 | Keranigonj | 227 | 01:00 | 205 | 13:00
Baghabari | 231 | 05:00 | 213 | 19:00 | Khulna(S) | 224 | 06:00 | 207 | 22:00
Barapukuria | 223 | 18:30 | 208 | 21:00 | Korerhat | 222 | 00:00 | 215 | 13:00
Barapukuria-230 | 223 | 18:30 | 208 | 21:00 | Madunaghat | 238 | 02:00 | 229 | 16:00
Barishal | 228 | 03:00 | 216 | 19:30 | Madunaghat-400 | 239 | 02:00 | 232 | 15:00
Bheramara | 231 | 06:00 | 207 | 23:00 | Maniknagar | 225 | 01:00 | 204 | 12:00
Bhulta | 227 | 05:00 | 205 | 13:00 | Meghnaghat | 234 | 05:00 | 214 | 12:00
Bibiana | 218 | 03:00 | 209 | 12:00 | Meghnaghat-400 | 228 | 01:00 | 208 | 13:00
BIPTC | 234 | 06:00 | 208 | 23:00 | Mirsorai | 227 | 01:00 | 216 | 13:00
Bogura | 240 | 01:00 | 223 | 19:30 | Naogaon | 223 | 06:00 | 199 | 23:00
Bogura-400 | 240 | 02:00 | 224 | 19:30 | Purbasadipur | 220 | 04:00 | 204 | 19:30
Borhanuddin | 230 | 06:00 | 223 | 19:30 | Rajshahi | 229 | 02:00 | 208 | 19:30
BSRM | 223 | 00:00 | 215 | 14:00 | Rampal | 224 | 06:00 | 208 | 19:30
Charfasson | 232 | 11:00 | 223 | 19:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 221 | 00:00 | 214 | 21:00 | Rampura | 226 | 01:00 | 203 | 13:00
Cumilla(N) | 221 | 05:00 | 207 | 13:00 | Shikalbaha | 238 | 02:00 | 230 | 15:00
Faridpur | 223 | 03:00 | 207 | 19:30 | Shyampur | 226 | 01:00 | 205 | 13:00
Fenchuganj | 219 | 04:00 | 209 | 19:00 | Siddhirganj | 229 | 06:00 | 205 | 13:00
Feni | 220 | 00:00 | 211 | 13:00 | Sirajgonj | 235 | 00:00 | 224 | 14:00
Ghorashal | 230 | 01:00 | 210 | 00:00 | Sreepur | 222 | 02:00 | 207 | 19:00
Ghorashal-230 | 216 | 02:00 | 191 | 15:00 | Tongi | 224 | 04:00 | 195 | 13:00
Gopalganj | 224 | 03:00 | 209 | 19:00
GPH | 232 | 01:00 | 225 | 13:00
Haripur | 226 | 01:00 | 206 | 13:00
Hasnabad | 227 | 01:00 | 206 | 12:00
Hathazari | 232 | 00:00 | 227 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 122 | 12:00 | Madunaghat | 137 | 01:00 | 132 | 15:00
Agargaon | 135 | 00:00 | 120 | 13:00 | Magura | 133 | 06:00 | 116 | 23:00
Agrabad | 136 | 01:00 | 129 | 14:00 | Mahasthangarh | 134 | 01:00 | 122 | 19:30
AKS | 132 | 02:00 | 129 | 08:00 | Maijdee | 124 | 01:00 | 119 | 21:00
Aminbazar | 132 | 00:00 | 117 | 14:00 | Manikganj | 128 | 00:00 | 118 | 12:00
Amnura | 133 | 02:00 | 122 | 13:00 | Maniknagar | 133 | 01:00 | 118 | 13:00
Ashuganj | 126 | 00:00 | 120 | 13:00 | Matarbari | 126 | 07:00 | 114 | 22:00
Ashuganj-230 | 130 | 00:00 | 125 | 13:00 | Matuail | 133 | 05:00 | 120 | 13:00
Bagerhat | 128 | 05:00 | 116 | 19:30 | Metrorail_Motijheel | 133 | 01:00 | 118 | 13:00
Bajitpur | 122 | 04:00 | 115 | 14:00 | Metrorail_Uttara | 133 | 01:00 | 110 | 16:00
Bakerganj | 131 | 02:00 | 124 | 21:00 | Millgate | 134 | 01:00 | 116 | 12:00
Bakulia | 136 | 01:00 | 131 | 14:00 | Mirpur | 132 | 00:00 | 117 | 13:00
Banani | 136 | 02:00 | 121 | 12:00 | Mirzapur | 128 | 00:00 | 117 | 23:00
Bangabhaban | 133 | 01:00 | 117 | 13:00 | Mithapukur | 131 | 01:00 | 115 | 23:00
Barapukuria | 135 | 18:30 | 121 | 19:30 | MI_Cement | 134 | 01:00 | 117 | 13:00
Barguna | 131 | 01:00 | 123 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 00:00 | 124 | 22:00 | Mogbazar | 139 | 03:00 | 123 | 13:00
Barishal-230 | 133 | 03:00 | 124 | 19:30 | Mongla | 127 | 06:00 | 116 | 19:30
Baroaulia | 135 | 00:00 | 130 | 14:00 | Motijheel | 133 | 01:00 | 117 | 13:00
Baroirhat | 128 | 00:00 | 124 | 12:00 | Muktagacha | 124 | 10:00 | 114 | 01:00
Bashundhara | 136 | 01:00 | 115 | 15:00 | Munshiganj | 131 | 00:00 | 120 | 13:00
BashundharaCement | 133 | 04:00 | 120 | 13:00 | Muradnagar | 125 | 06:00 | 115 | 13:00
Beanibazar | 121 | 06:00 | 116 | 12:00 | Mymensingh | 127 | 11:00 | 107 | 19:30
Benapole | 129 | 03:00 | 114 | 13:00 | Nabinagar | 130 | 01:00 | 114 | 12:00
Bhaluka | 123 | 00:00 | 116 | 21:00 | Naogaon | 134 | 06:00 | 120 | 23:00
Bhandaria | 129 | 07:00 | 120 | 19:30 | Narail | 132 | 05:00 | 116 | 23:00
Bhangura | 133 | 06:00 | 122 | 19:30 | Narinda | 133 | 01:00 | 118 | 13:00
Bheramara | 136 | 06:00 | 122 | 23:00 | Narshingdi | 119 | 00:00 | 111 | 13:00
Bheramara(GK) | 136 | 06:00 | 122 | 23:00 | Natore | 133 | 01:00 | 121 | 23:00
Bhulta | 122 | 00:00 | 122 | 00:00 | Nawabganj | 133 | 01:00 | 121 | 12:00
Bog-Sherpur | 135 | 01:00 | 124 | 19:30 | Netrakona | 114 | 00:00 | 107 | 19:00
Bogura | 137 | 01:00 | 127 | 21:00 | New | 135 | 01:00 | 118 | 14:00
Bogura-230 | 138 | 01:00 | 127 | 19:30 | Niamatpur | 133 | 06:00 | 123 | 19:30
Brahmanbaria | 123 | 00:00 | 116 | 14:00 | Noapara | 131 | 04:00 | 120 | 19:30
Cantonment | 136 | 01:00 | 120 | 13:00 | Pabna | 134 | 06:00 | 121 | 19:30
Chandina | 127 | 06:00 | 119 | 13:00 | Palashbari | 129 | 18:00 | 115 | 23:00
Chandpur | 130 | 00:00 | 124 | 07:00 | Panchagarh | 140 | 18:30 | 128 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandraghona | 136 | 00:00 | 134 | 11:00 | Patiya | 136 | 01:00 | 130 | 17:00
Chapai | 133 | 05:00 | 123 | 19:00 | Patnitala | 131 | 08:00 | 117 | 23:00
Charsaidpur | 132 | 01:00 | 119 | 13:00 | Patuakhali | 129 | 07:00 | 125 | 21:00
Chauddagram | 126 | 05:00 | 120 | 14:00 | Payra | 135 | 02:00 | 130 | 21:00
Chhatak | 120 | 05:00 | 113 | 13:00 | PHP | 128 | 00:00 | 123 | 13:00
Chowmuhani | 124 | 00:00 | 120 | 21:00 | Postogola | 135 | 00:00 | 120 | 13:00
Chuadanga | 133 | 05:00 | 113 | 22:00 | Pubail | 133 | 06:00 | 114 | 17:00
Coxsbazar | 126 | 08:00 | 118 | 21:00 | Purbachal | 136 | 01:00 | 121 | 12:00
Cumilla(N) | 127 | 05:00 | 119 | 13:00 | Purbasadipur | 134 | 18:30 | 123 | 19:30
Cumilla(S) | 131 | 05:00 | 120 | 12:00 | Rahanpur | 135 | 05:00 | 127 | 21:00
Daganbhuiyan | 127 | 01:00 | 121 | 13:00 | Rahanpur-400 | 134 | 00:00 | 127 | 19:30
Daudkandi | 125 | 04:00 | 114 | 14:00 | Rahim | 133 | 01:00 | 120 | 13:00
DhakaUniversity | 136 | 01:00 | 122 | 12:00 | Rajbari | 126 | 03:00 | 116 | 19:30
Dhamrai | 138 | 04:00 | 116 | 11:00 | Rajendrapur | 123 | 00:00 | 115 | 19:30
Dhanmondi | 137 | 05:00 | 122 | 12:00 | Rajshahi | 133 | 06:00 | 120 | 19:30
Dohazari | 132 | 01:00 | 127 | 15:00 | Rajshahi-230 | 132 | 02:00 | 120 | 19:30
Faridpur | 128 | 04:00 | 120 | 22:00 | Ramganj | 124 | 00:00 | 119 | 22:00
Fatullah | 135 | 02:00 | 117 | 13:00 | Rampur | 135 | 00:00 | 130 | 14:00
Fenchuganj | 129 | 06:00 | 123 | 13:00 | Rampura | 136 | 01:00 | 122 | 12:00
Feni | 127 | 01:00 | 122 | 15:00 | Rangamati | 135 | 00:00 | 132 | 13:00
Feni-230 | 128 | 01:00 | 122 | 13:00 | Rangpur | 131 | 4:00 | 115 | 19:30
Ghatail | 133 | 23:00 | 113 | 23:00 | Ruppur | 136 | 02:00 | 123 | 19:30
Ghorashal | 128 | 01:00 | 115 | 14:00 | Saidpur | 133 | 11:00 | 120 | 19:30
Goalpara | 134 | 05:00 | 123 | 23:00 | Santhia | 134 | 08:00 | 122 | 23:00
Gollamari | 133 | 05:00 | 123 | 21:00 | Satkhira | 129 | 03:00 | 115 | 23:00
Gopalganj | 129 | 05:00 | 121 | 21:00 | Satmasjid | 135 | 01:00 | 119 | 13:00
Gopalganj-400 | 130 | 01:00 | 123 | 22:00 | Savar | 132 | 00:00 | 116 | 13:00
Gulshan | 135 | 01:00 | 122 | 12:00 | SevenRings | 129 | 03:00 | 115 | 15:00
Halishahar | 137 | 01:00 | 131 | 13:00 | ShahCement | 132 | 01:00 | 119 | 13:00
Haripur | 133 | 02:00 | 121 | 12:00 | Shahjadpur | 136 | 03:00 | 126 | 19:00
HaripurSBU | 133 | 04:00 | 122 | 12:00 | Shahjibazar | 124 | 01:00 | 118 | 13:00
Hasnabad | 135 | 01:00 | 121 | 12:00 | Shahmirpur | 136 | 02:00 | 131 | 15:00
Hathazari | 136 | 00:00 | 133 | 12:00 | Shariatpur | 129 | 03:00 | 119 | 22:00
Hatirjheel | 136 | 02:00 | 122 | 12:00 | Sherpur | 126 | 11:00 | 108 | 02:00
Ishurdi | 138 | 06:00 | 124 | 19:30 | Shikalbaha | 127 | 02:00 | 120 | 15:00
Jaldhaka | 130 | 18:00 | 117 | 19:30 | Shikalbaha-230 | 138 | 02:00 | 131 | 16:00
Jamalpur | 131 | 11:00 | 114 | 02:00 | Shitalakhya | 134 | 01:00 | 117 | 13:00
Jashore | 131 | 06:00 | 115 | 23:00 | Sholosohor | 136 | 01:00 | 130 | 17:00
Jhenaidah | 135 | 05:00 | 119 | 23:00 | Shomvuganj | 118 | 00:00 | 112 | 15:00
Jhenaidah-230 | 136 | 06:00 | 120 | 19:30 | Shyampur | 131 | 01:00 | 120 | 11:00
Joydebpur | 126 | 01:00 | 112 | 15:00 | Shyampur-230 | 133 | 01:00 | 121 | 12:00
Joypurhat | 132 | 04:00 | 119 | 23:00 | Siddhirganj | 133 | 01:00 | 120 | 13:00
Juldah | 136 | 23:00 | 131 | 14:00 | Sirajganj | 133 | 02:00 | 120 | 19:30
Kabirpur | 133 | 00:00 | 113 | 19:30 | Sitakunda | 135 | 00:00 | 130 | 16:00
Kachua | 127 | 01:00 | 122 | 21:00 | Sonargaon | 129 | 00:00 | 118 | 13:00
Kaliakoir | 134 | 00:00 | 120 | 14:00 | Sreemongol | 125 | 06:00 | 118 | 13:00
Kaliganj | 132 | 04:00 | 119 | 19:30 | Sreepur | 127 | 01:00 | 118 | 19:00
Kallyanpur | 132 | 00:00 | 116 | 13:00 | Srinagar | 133 | 00:00 | 120 | 13:00
Kalurghat | 137 | 01:00 | 133 | 13:00 | SSM | 140 | 00:00 | 134 | 17:00
Kamrangirchar | 134 | 01:00 | 114 | 12:00 | Sunamganj | 116 | 06:00 | 111 | 13:00
Kaptai | 139 | 3:00 | 135 | 15:00 | Sylhet | 122 | 05:00 | 118 | 14:00
Kasba | 125 | 06:00 | 114 | 13:00 | Sylhet_(South) | 123 | 06:00 | 118 | 13:00
Kazla | 133 | 03:00 | 117 | 13:00 | Tangail | 122 | 00:00 | 113 | 23:00
Keranigonj | 134 | 01:00 | 120 | 13:00 | Taraganj | 130 | 18:00 | 119 | 19:30
Khagrachori | 136 | 02:00 | 131 | 12:00 | Tasnim | 132 | 08:00 | 118 | 14:00
Khulna | 132 | 01:00 | 122 | 21:00 | Thakurgaon | 139 | 18:30 | 126 | 19:30
Khulna(S) | 134 | 05:00 | 123 | 23:00 | TK | 136 | 00:00 | 132 | 14:00
Khulshi | 133 | 00:00 | 129 | 17:00 | Tongi | 137 | 04:00 | 120 | 13:00
Kishoreganj | 120 | 00:00 | 114 | 15:00 | Ullahpara | 133 | 01:00 | 121 | 19:00
Kodda | 131 | 00:00 | 112 | 14:00 | Ullon | 136 | 03:00 | 121 | 12:00
Korerhat | 131 | 00:00 | 126 | 13:00 | Uttara | 134 | 01:00 | 114 | 15:00
KSRM | 136 | 00:00 | 131 | 14:00 | UttaraNew | 133 | 01:00 | 115 | 16:00
Kulaura | 127 | 05:00 | 122 | 13:00 | Zigatola | 134 | 00:00 | 121 | 12:00
Kurigram | 126 | 03:00 | 112 | 19:30
Kushtia | 132 | 05:00 | 116 | 23:00
Laksam | 126 | 00:00 | 121 | 14:00
Lakshmipur | 123 | 00:00 | 119 | 13:00
Lalbag | 134 | 01:00 | 120 | 12:00
Lalmonirhat | 127 | 11:00 | 112 | 23:00
Madanganj | 133 | 04:00 | 120 | 13:00
Madaripur | 130 | 03:00 | 123 | 19:00
Madartek | 136 | 04:00 | 122 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division