## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 29-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-07-2026 | during | 29-07-2026 | during | 29-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 351 | 351 | 412 | 412 | 320 | 330 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 146 | 146 | 335 | 335 | 140 | 150 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 260 | 335 | 335 | 240 | 250 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 37 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 78 | 127 | 149.36 | 149.36 | 125 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 11 | 11 | 33 | 33 | 11 | 11 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 18 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 8 | 17 | 52.19 | 52.19 | 0 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 80 | 81 | 300 | 300 | 48 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 40 | 133 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 51 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 23 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 55 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 305 | 275 | 583 | 583 | 300 | 300 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1610 | 1878.42 | 5570.64 | 5545.64 | 1581.42 | 2050.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 19 | 25.5 | 25.5 | 25.5 | 8 | 25 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 1 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 222 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 212 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 87 | 92 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 13 | 74 | 40 | 72 | 40 | 72 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 34 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 9 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 40 | 95 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.37 | 0 | 2.65 | 0 | 2.65 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 54 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 103 | 105 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 86 | 89 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 115 | 104 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 910 | 1000 | 1224 | 1224 | 900 | 900 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 10 | 27 | 40 | 40 | 40 | 40 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1135 | 1140 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 3089.37 | 3364.86 | 4136.51 | 4234.86 | 3216.65 | 3340
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 209 | 195 | 221.25 | 221.25 | 221.25 | 221.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 352 | 358 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 0 | 342.01 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 30 | 37 | 41.65 | 41.65 | 30 | 30 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 20 | 20 | 52.82 | 52.82 | 20 | 20 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 62 | 150 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 139 | 142 | 163 | 163 | 145 | 145 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 50 | 187 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 140 | 138 | 84 | 76 | 150 | 150 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 29 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 96 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 28 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 2 | 88 | 115 | 115 | 34 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 55 | 0 | 35 | 0 | 35 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1270 | 1561.2 | 2697.44 | 2654.44 | 1549.46 | 1579.46
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-07-2026 | during | 29-07-2026 | during | 29-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 14 | 0 | 10 | 0 | 10 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 125 | 153 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 31.07 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 237.27 | 250 | 524.6 | 516.5 | 267.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 39 | 40 | 40 | 41 | 41 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 126 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 83 | 86 | 86 | 53 | 53 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 100 | 100 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 16 | 25 | 25 | 16 | 16 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 300 | 341 | 341 | 307 | 307 | Machine Problem
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 306 | 307 | 350 | 350 | 322 | 322 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 964 | 971 | 1155 | 1155 | 986 | 986
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 873 | 872 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 23 | 32 | 32 | 36 | 36 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 105 | 105 | 50 | 50 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 181 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1080 | 1080 | 1080 | 1080 | 1080 | 1080 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2089 | 2244 | 3402 | 3332 | 2274 | 2204
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1027 | 1050 | 1050 | 1050 | 1050 | 1050 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 30 | 16 | 110 | 110 | 99 | 99 | FGMO
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 1020 | 894 | 1163.05 | 1163.05 | 900 | 900 | Coal shortage
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 277 | 307 | 307 | 307 | 307 | 307 | Line Overload
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.44 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2711.44 | 2624 | 3131.05 | 3130.05 | 2714 | 2713
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 14.08 | 0 | 43.25 | 0 | 43.25 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 157 | 156 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 273 | 292 | 413.79 | 413.79 | 315 | 315 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 26 | 26 | 26 | 26 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 113 | 113 | 113 | 0 | 35 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 90 | 113 | 113 | 0 | 35 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 3.67 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 966.38 | 1307.6 | 1469.13 | 1469.13 | 1220 | 1220 | Wet Coal
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 20.71 | 0 | 59 | 0 | 59 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 115 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1652.04 | 2203.8 | 3252.87 | 3045.12 | 2052.95 | 2007.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 182 | 180 | 190 | 190 | 185 | 185 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 99 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.8 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 95 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 24 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 69 | 0 | 154.16 | 0 | 154.16 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 373.8 | 539 | 608.16 | 418 | 470.16 | 315
System Total |  |  |  |  | 28843.2 | 29171.687 | 13996.92 | 15636.28 | 24478.27 | 24031.61 | 15111.74 | 15454.08
Forecast Scenario (29-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15430 |  | 1680.8 |  | 17190
|  |  |  | 1:00 | 15050 |  | 1222.4 |  | 16330
|  |  |  | 2:00 | 14900 |  | 1012.3 |  | 15960
|  |  |  | 3:00 | 14620 |  | 706.7 |  | 15360
|  |  |  | 4:00 | 14460 |  | 668.5 |  | 15160
|  |  |  | 5:00 | 14140 |  | 553.9 |  | 14720
|  |  |  | 6:00 | 13900 |  | 534.8 |  | 14460
|  |  |  | 7:00 | 13890 |  | 582.55 |  | 14500
|  |  |  | 8:00 | 13760 |  | 525.25 |  | 14310
|  |  |  | 9:00 | 13620 |  | 506.15 |  | 14150
|  |  |  | 10:00 | 13740 |  | 687.6 |  | 14460
|  |  |  | 11:00 | 13760 |  | 821.3 |  | 14620
|  |  |  | 12:00 | 14200 |  | 1375.2 |  | 15640
|  |  |  | 13:00 | 14370 |  | 1212.85 |  | 15640
|  |  |  | 14:00 | 14550 |  | 1346.55 |  | 15960
|  |  |  | 15:00 | 14580 |  | 1308.35 |  | 15950
|  |  |  | 16:00 | 14490 |  | 1031.4 |  | 15570
|  |  |  | 17:00 | 14320 |  | 935.9 |  | 15300
|  |  |  | 18:00 | 14140 |  | 420.2 |  | 14580
|  |  |  | 18:30 | 14640 |  | 630.3 |  | 15300
|  |  |  | 19:00 | 15150 |  | 1079.15 |  | 16280
|  |  |  | 19:30 | 15250 |  | 1728.55 |  | 17060
|  |  |  | 20:00 | 15400 |  | 1623.5 |  | 17100
|  |  |  | 21:00 | 15450 |  | 1671.25 |  | 17200
|  |  |  | 22:00 | 15770 |  | 1270.15 |  | 17100
|  |  |  | 23:00 | 15700 |  | 1384.75 |  | 17150
Probable Maximum Temperature: |  |  | 34.30°C
Probable Maximum Demand at Day Peak: |  |  | 15640.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1671
Probable Maximum Demand at Evening Peak: |  |  | 17200.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15450.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 349.92 MKWHr. |  | 500 | 150 | 170 | 350 | 60 | 190 | 81 | 170 | 160 | 1671
*** This report is generated digitally from Operation Information System (OIS) at 08:55 hrs on 29-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-07-2026 | [28 empty] | Date: | 28-07-2026 | [28 empty] | Date: | 28-07-2026 | [28 empty] | Date: | 28-07-2026 | [28 empty] | Date: | 28-07-2026 | [18 empty] | Date: | 28-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [18 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 17 | 53 | 142 | 80 | 15 | 35 | 17 | 0 | 0 | 143 | 280 | 0 | 0 | 280 | 0 | 0 | 0 | 143.42 | 11.2 | 22 | 0 | 0 | 92 | 16 | 74 | 0 | 37 | 41 | 74 | 17 | 25 | 25 | 0 | 222 | 106 | 2 | 1130 | 150 | 0 | 50 | 17 | 90 | 212 | 0 | 0 | 0 | 1190 | 0 | 50 | 0 | 0 | 359 | 0 | 51 | 20 | 212 | 30 | 34 | 142 | 180 | 0 | 19 | 103 | 152 | 52.2 | 0 | 0 | 310 | 0 | 306 | 39 | 0 | 144 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7788.82 | 876 | 0 | 0 | 15 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1090 | 0 | 0 | 0 | 1414.77 | 0 | 33 | 0 | 35 | 90 | 0 | 92 | 22 | 52.2 | 0 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 182 | 0 | 95 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 276 | 120 | 220 | 0 | 1002 | 1116 | 17 | 7438.97 | 15227.79 | 102.88
01:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 17 | 17 | 125 | 48 | 15 | 35 | 0 | 0 | 0 | 144 | 280 | 0 | 0 | 280 | 0 | 0 | 0 | 143.42 | 11.2 | 21 | 0 | 0 | 92 | 16 | 71 | 0 | 50 | 50 | 74 | 0 | 25 | 25 | 0 | 222 | 109 | 6 | 1130 | 141 | 0 | 50 | 17 | 103 | 212 | 0 | 0 | 0 | 1180 | 0 | 50 | 0 | 0 | 359 | 0 | 51 | 20 | 212 | 30 | 34 | 141 | 172 | 0 | 19 | 104 | 144 | 52.2 | 0 | 0 | 305 | 0 | 306 | 40 | 0 | 143 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7668.82 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1413.82 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 22 | 52.2 | 0 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 182 | 0 | 95 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 274 | 120 | 220 | 0 | 1016 | 1110 | 17 | 7179.02 | 14847.84 | 102.87
02:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 17 | 17 | 125 | 48 | 15 | 35 | 0 | 0 | 0 | 146 | 280 | 0 | 0 | 280 | 0 | 0 | 0 | 143.42 | 11.5 | 21 | 0 | 0 | 90 | 16 | 65 | 0 | 30 | 0 | 74 | 0 | 25 | 25 | 0 | 222 | 107 | 10 | 1130 | 145 | 0 | 50 | 17 | 96 | 214 | 0 | 0 | 0 | 1187 | 0 | 50 | 0 | 0 | 361 | 0 | 51 | 20 | 212 | 30 | 0 | 142 | 171 | 0 | 19 | 100 | 132 | 52.2 | 0 | 0 | 305 | 0 | 306 | 40 | 0 | 138 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7549.12 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1425.71 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 22 | 52.2 | 0 | 0 | 25 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 182 | 0 | 95 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 277 | 120 | 220 | 0 | 1007 | 1100 | 17 | 7144.91 | 14694.03 | 102.86
03:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 17 | 17 | 125 | 48 | 15 | 0 | 0 | 0 | 0 | 142 | 275 | 0 | 0 | 280 | 0 | 0 | 0 | 143.42 | 11.5 | 21 | 0 | 0 | 60 | 16 | 65 | 0 | 55 | 0 | 32 | 0 | 25 | 25 | 0 | 222 | 106 | 16 | 1130 | 145 | 0 | 50 | 8 | 95 | 214 | 0 | 0 | 0 | 1180 | 0 | 50 | 0 | 0 | 359 | 0 | 51 | 20 | 212 | 29 | 0 | 142 | 171 | 0 | 19 | 70 | 136 | 8 | 0 | 0 | 300 | 0 | 306 | 40 | 0 | 130 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7361.92 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1427.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 182 | 0 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 273 | 120 | 220 | 0 | 1019 | 1075 | 17 | 7048.71 | 14410.63 | 102.85
04:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 17 | 17 | 125 | 48 | 15 | 0 | 0 | 0 | 0 | 145 | 280 | 0 | 0 | 280 | 0 | 0 | 0 | 143.42 | 11.5 | 21 | 0 | 0 | 30 | 16 | 48 | 0 | 24 | 0 | 0 | 0 | 25 | 25 | 0 | 222 | 105 | 36 | 1130 | 96 | 0 | 50 | 0 | 96 | 214 | 0 | 0 | 0 | 1188 | 0 | 50 | 0 | 0 | 360 | 0 | 51 | 20 | 212 | 30 | 0 | 142 | 172 | 0 | 19 | 31 | 138 | 0 | 0 | 0 | 305 | 0 | 317 | 40 | 0 | 137 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7211.92 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1444.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 182 | 0 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 278 | 120 | 220 | 0 | 1019 | 1085 | 17 | 7047.29 | 14259.21 | 102.84
05:00 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 17 | 17 | 142 | 48 | 15 | 0 | 0 | 0 | 0 | 149 | 280 | 0 | 0 | 280 | 0 | 0 | 0 | 143.42 | 11.5 | 21 | 0 | 0 | 30 | 16 | 44 | 0 | 33 | 0 | 0 | 0 | 25 | 25 | 0 | 222 | 106 | 38 | 1130 | 46 | 0 | 27 | 0 | 51 | 214 | 0 | 0 | 0 | 1188 | 0 | 50 | 0 | 0 | 359 | 0 | 51 | 20 | 212 | 30 | 0 | 143 | 85 | 0 | 19 | 0 | 134 | 0 | 0 | 0 | 305 | 0 | 317 | 40 | 0 | 142 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 6964.92 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1391.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 182 | 0 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 278 | 120 | 180 | 0 | 1050 | 1090 | 17 | 6972.82 | 13937.74 | 102.83
06:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 13 | 17 | 142 | 48 | 15 | 0 | 0 | 0 | 0 | 145 | 280 | 0 | 0 | 280 | 0 | 0 | 0 | 143.42 | 11.5 | 21 | 0 | 0 | 30 | 16 | 44 | 0 | 27 | 0 | 0 | 0 | 25 | 25 | 0.24 | 222 | 105 | 37 | 1130 | 48 | 0 | 26 | 0 | 50 | 214 | 0 | 0 | 0 | 1190 | 0 | 50 | 0 | 0 | 360 | 0 | 51 | 20 | 212 | 30 | 0 | 142 | 80 | 0 | 19 | 0 | 120 | 0 | 3 | 0 | 300 | 0 | 313 | 40 | 0 | 139 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 48 | 0.43 | 48 | 0 | 0 | 0.95 | 0 | 6898.54 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.15 | 1080 | 0 | 0 | 0 | 1238.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0 | 0 | 0 | 0.96 | 156 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0.08 | 182 | 0 | 95 | 1 | 35 | 0 | 0 | 0 | 0.3 | 7 | 0.07 | 58 | 277 | 120 | 180 | 0 | 1004 | 1115 | 17 | 6797.92 | 13696.46 | 102.82
07:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 48 | 17 | 142 | 48 | 15 | 0 | 0 | 0 | 0 | 149 | 280 | 0 | 0 | 280 | 0 | 0 | 1 | 51 | 9 | 21 | 0 | 0 | 28 | 16 | 44 | 0 | 32 | 0 | 0 | 0 | 25 | 25 | 0.87 | 222 | 106 | 37 | 1130 | 48 | 0 | 26 | 0 | 48 | 214 | 0 | 0 | 0 | 1200 | 1 | 50 | 0 | 0 | 359 | 0 | 51 | 20 | 212 | 30 | 0 | 141 | 81 | 0 | 19 | 0 | 112 | 0 | 3 | 0 | 310 | 0 | 313 | 40 | 0 | 136 | 1 | 16 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 48 | 1.2 | 48 | 0 | 0.2 | 6.95 | 0 | 6864.22 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 1065 | 0 | 0 | 0 | 1220.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.65 | 1 | 0 | 0 | 8.43 | 159 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0.86 | 182 | 0 | 95 | 6 | 0 | 0 | 0 | 0 | 1.8 | 30 | 0.07 | 58 | 278 | 120 | 220 | 0 | 1047 | 1080 | 17 | 6825.14 | 13689.36 | 102.81
08:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 55 | 17 | 128 | 48 | 15 | 0 | 0 | 0 | 0 | 143 | 270 | 0 | 0 | 260 | 0 | 0 | 11 | 51 | 9 | 21 | 0 | 0 | 30 | 16 | 44 | 0 | 10 | 0 | 0 | 0 | 25 | 25 | 0.98 | 222 | 104 | 12 | 1130 | 46 | 0 | 26 | 0 | 46 | 214 | 0 | 0 | 0 | 1130 | 0 | 50 | 0 | 0 | 360 | 0 | 51 | 20 | 213 | 30 | 0 | 142 | 78 | 0 | 19 | 0 | 122 | 0 | 7 | 0 | 300 | 0 | 315 | 40 | 0 | 132 | 3 | 16 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 49 | 7.5 | 48 | 0 | 0.4 | 15.89 | 0 | 6761.77 | 875 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12 | 985 | 0 | 0 | 0 | 1221.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.24 | 38 | 0 | 0 | 10.41 | 160 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0.78 | 182 | 0 | 95 | 15 | 0 | 0 | 0 | 0 | 2.7 | 107 | 0.07 | 57 | 275 | 120 | 180 | 0 | 1001 | 1090 | 17 | 6793.56 | 13555.33 | 102.8
09:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 55 | 17 | 128 | 48 | 15 | 0 | 0 | 0 | 0 | 143 | 270 | 0 | 0 | 250 | 0 | 0 | 4 | 51 | 11 | 21 | 0 | 0 | 0 | 16 | 45 | 0 | 16 | 0 | 0 | 0 | 25 | 25 | 1.41 | 222 | 103 | 6 | 1130 | 34 | 0 | 26 | 0 | 47 | 214 | 0 | 0 | 0 | 1055 | 0 | 50 | 0 | 0 | 357 | 0 | 51 | 20 | 211 | 30 | 0 | 142 | 78 | 0 | 19 | 0 | 124 | 0 | 27 | 0 | 300 | 0 | 314 | 40 | 0 | 129 | 7 | 16 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 49 | 7.1 | 65 | 0 | 0.6 | 22.46 | 0 | 6630.57 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 74 | 950 | 0 | 0 | 0 | 1213.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.47 | 20 | 0 | 0 | 39.99 | 160 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 2.62 | 182 | 0 | 95 | 23 | 0 | 0 | 0 | 0 | 5.8 | 60 | 0.22 | 56 | 275 | 120 | 180 | 0 | 1001 | 1070 | 17 | 6784.32 | 13414.89 | 102.79
10:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 55 | 19 | 62 | 80 | 15 | 17 | 17 | 0 | 0 | 147 | 295 | 0 | 0 | 300 | 0 | 0 | 13 | 51 | 9 | 21 | 0 | 0 | 0 | 16 | 40 | 0 | 27 | 0 | 0 | 0 | 25 | 25 | 1.05 | 222 | 105 | 2 | 1135 | 0 | 0 | 26 | 0 | 17 | 214 | 0 | 0 | 0 | 1115 | 1 | 24 | 0 | 0 | 352 | 0 | 51 | 20 | 210 | 30 | 0 | 141 | 51 | 0 | 19 | 0 | 122 | 0 | 39 | 0 | 310 | 0 | 314 | 40 | 0 | 137 | 10 | 0 | 0 | 52 | 0 | 0 | 0 | 101 | 20 | 49 | 16.88 | 122 | 0 | 1 | 40.12 | 0 | 6764.05 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36 | 966 | 0 | 0 | 0 | 1115.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.13 | 103 | 0 | 0 | 11.88 | 159 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 1.27 | 182 | 0 | 50 | 29 | 6 | 0 | 0 | 0 | 6.7 | 147 | 0.2 | 32 | 249 | 120 | 220 | 0 | 1043 | 1050 | 17 | 6766.7 | 13530.75 | 102.78
11:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 55 | 34 | 78 | 80 | 15 | 17 | 17 | 0 | 0 | 147 | 303 | 0 | 0 | 320 | 0 | 0 | 25 | 51 | 11 | 21 | 0 | 0 | 2 | 16 | 37 | 0 | 27 | 0 | 0 | 17 | 25 | 25 | 3.69 | 222 | 107 | 0 | 1135 | 11 | 0 | 32 | 1 | 50 | 213 | 0 | 0 | 0 | 1125 | 2 | 37 | 0 | 0 | 348 | 0 | 51 | 20 | 206 | 30 | 0 | 139 | 51 | 0 | 17 | 34 | 138 | 1 | 44 | 0 | 310 | 0 | 314 | 40 | 0 | 151 | 8 | 0 | 0 | 52 | 0 | 0 | 0 | 100 | 17 | 49 | 22.22 | 125 | 0 | 2.2 | 19.49 | 0 | 6988.6 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 1032 | 0 | 0 | 0 | 945.59 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 22.83 | 21 | 0 | 0 | 23.84 | 157 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 2.13 | 182 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 2.4 | 105 | 0.37 | 30 | 283 | 120 | 220 | 0 | 1034 | 1020 | 17 | 6565.16 | 13553.76 | 102.77
12:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 55 | 40 | 78 | 80 | 15 | 35 | 17 | 0 | 0 | 146 | 305 | 0 | 0 | 300 | 0 | 0 | 23 | 70 | 11 | 7 | 0 | 0 | 86 | 16 | 40 | 0 | 10 | 0 | 13 | 17 | 25 | 25 | 2.37 | 222 | 103 | 0 | 1135 | 115 | 0 | 50 | 19 | 87 | 213 | 0 | 0 | 0 | 910 | 1 | 62 | 0 | 0 | 352 | 0 | 51 | 20 | 209 | 30 | 2 | 139 | 50 | 0 | 17 | 114 | 140 | 29 | 55 | 0 | 315 | 0 | 306 | 40 | 0 | 147 | 4 | 0 | 0 | 52 | 0 | 0 | 0 | 100 | 17 | 49 | 14 | 125 | 0 | 1.2 | 31.07 | 0 | 7170.64 | 873 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 98 | 1080 | 0 | 0 | 0 | 966.38 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 52.2 | 14.08 | 115 | 0 | 0 | 20.71 | 157 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 3.67 | 182 | 0 | 95 | 24 | 0 | 0 | 0 | 0 | 3.8 | 69 | 0.44 | 30 | 277 | 120 | 220 | 0 | 1027 | 1020 | 17 | 6826.28 | 13996.92 | 102.76
13:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 55 | 52 | 78 | 80 | 15 | 35 | 17 | 0 | 0 | 146 | 302 | 0 | 17 | 300 | 0 | 0 | 25 | 143.42 | 11 | 7 | 0 | 0 | 95 | 16 | 55 | 0 | 13 | 0 | 13 | 17 | 25 | 25 | 2.76 | 222 | 98 | 0 | 1135 | 140 | 0 | 50 | 25.5 | 103 | 211 | 0 | 0 | 0 | 905 | 5 | 127 | 0 | 0 | 351 | 0 | 51 | 20 | 208 | 30 | 32 | 140 | 50 | 0 | 17 | 104 | 146 | 52.2 | 47 | 0 | 310 | 0 | 307 | 39 | 0 | 143 | 4 | 8 | 0 | 52 | 0 | 0 | 0 | 100 | 17 | 57 | 12.42 | 117 | 0 | 2 | 14.21 | 5 | 7378.51 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 33 | 1080 | 0 | 0 | 0 | 950.81 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 52.2 | 8.36 | 80 | 0 | 0 | 43.97 | 157 | 0 | 0 | 0 | 0 | 0 | 272 | 0 | 3.88 | 181 | 0 | 95 | 7 | 0 | 0 | 0 | 0 | 8 | 97 | 0.07 | 30 | 279 | 120 | 220 | 0 | 1050 | 1035 | 17 | 6782.29 | 14160.8 | 102.8
14:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 35 | 52 | 78 | 80 | 15 | 35 | 17 | 0 | 0 | 143 | 295 | 0 | 35 | 300 | 0 | 0 | 22 | 143.42 | 11 | 12 | 0 | 0 | 90 | 16 | 61 | 0 | 17 | 0 | 30 | 17 | 25 | 25 | 1.86 | 220 | 105 | 0 | 1135 | 138 | 0 | 50 | 25.5 | 99 | 211 | 0 | 0 | 0 | 900 | 6 | 142 | 0 | 0 | 340 | 0 | 51 | 20 | 209 | 30 | 34 | 140 | 51 | 0 | 19 | 98 | 154 | 52.2 | 55 | 0 | 300 | 0 | 307 | 39 | 0 | 133 | 9 | 8 | 0 | 52 | 0 | 0 | 0 | 100 | 17 | 58 | 22.26 | 116 | 0 | 1.5 | 15.69 | 12 | 7390.43 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 61 | 1080 | 0 | 0 | 0 | 1109.05 | 0 | 0 | 0 | 35 | 55 | 0 | 0 | 0 | 52.2 | 51.75 | 86 | 0 | 0 | 42.59 | 157 | 0 | 0 | 0 | 0 | 0 | 267 | 0 | 3.53 | 182 | 0 | 95 | 23 | 0 | 0 | 0 | 0 | 4.4 | 100 | 0.27 | 29 | 271 | 120 | 180 | 0 | 1004 | 1020 | 17 | 6957.79 | 14348.22 | 102.74
15:00 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 35 | 52 | 78 | 80 | 15 | 35 | 17 | 0 | 0 | 143 | 300 | 0 | 35 | 322 | 0 | 0 | 16 | 143.42 | 11 | 14 | 0 | 0 | 91 | 16 | 71 | 0 | 13 | 0 | 46 | 17 | 25 | 25 | 2.31 | 219 | 106 | 0 | 1135 | 88 | 0 | 50 | 25.5 | 96 | 212 | 0 | 0 | 0 | 905 | 6 | 147 | 0 | 0 | 350 | 0 | 51 | 20 | 207 | 30 | 34 | 141 | 51 | 0 | 19 | 102 | 158 | 52.2 | 24 | 0 | 305 | 0 | 307 | 39 | 0 | 139 | 3 | 8 | 0 | 51 | 0 | 0 | 0 | 100 | 17 | 58 | 16.55 | 115 | 0 | 2.1 | 42.05 | 12 | 7441.13 | 872 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30 | 1080 | 0 | 0 | 0 | 1104.43 | 0 | 0 | 0 | 35 | 105 | 0 | 0 | 0 | 52.2 | 25.59 | 88 | 0 | 0 | 28.16 | 157 | 0 | 0 | 0 | 0 | 0 | 262 | 0 | 3.39 | 182 | 0 | 93 | 16 | 0 | 0 | 0 | 0 | 1.6 | 81 | 0.45 | 16 | 239 | 120 | 220 | 0 | 1050 | 1015 | 17 | 6931.82 | 14372.95 | 102.73
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 35 | 65 | 78 | 80 | 15 | 35 | 17 | 0 | 0 | 146 | 300 | 0 | 35 | 324 | 0 | 0 | 2 | 105 | 11 | 14 | 0 | 0 | 45 | 16 | 72 | 0 | 18 | 0 | 72 | 17 | 25 | 25 | 2.89 | 220 | 105 | 0 | 1135 | 32 | 0 | 50 | 25.5 | 99 | 212 | 0 | 0 | 0 | 900 | 4 | 150 | 0 | 0 | 350 | 0 | 51 | 20 | 207 | 30 | 34 | 140 | 51 | 0 | 19 | 108 | 160 | 52.2 | 13 | 0 | 310 | 0 | 307 | 39 | 0 | 144 | 2 | 16 | 0 | 52 | 0 | 0 | 0 | 100 | 17 | 58 | 8.11 | 115 | 0 | 0.6 | 16.72 | 12 | 7351.02 | 871 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 10 | 1080 | 0 | 0 | 0 | 1103.05 | 0 | 0 | 0 | 35 | 113 | 0 | 0 | 0 | 52.2 | 13.44 | 15 | 0 | 0 | 13.34 | 157 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 1.36 | 182 | 0 | 93 | 20 | 81 | 0 | 0 | 0 | 4.5 | 113 | 0.45 | 16 | 280 | 120 | 220 | 0 | 1038 | 995 | 17 | 6936.34 | 14287.36 | 102.73
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 35 | 70 | 78 | 80 | 15 | 35 | 72 | 0 | 0 | 137 | 295 | 0 | 35 | 310 | 0 | 0 | 6 | 105 | 11 | 14 | 0 | 0 | 47 | 16 | 90 | 0 | 17 | 0 | 72 | 17 | 25 | 25 | 0.33 | 221 | 106 | 0 | 1135 | 30 | 0 | 0 | 25.5 | 97 | 210 | 0 | 0 | 0 | 900 | 1 | 150 | 0 | 0 | 356 | 0 | 51 | 20 | 204 | 30 | 34 | 139 | 54 | 5 | 19 | 85 | 148 | 52.2 | 12 | 0 | 310 | 0 | 307 | 39 | 0 | 137 | 3 | 16 | 0 | 52 | 0 | 0 | 0 | 100 | 17 | 58 | 4.45 | 115 | 0 | 0.3 | 8.39 | 12 | 7303.17 | 872 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.35 | 1080 | 0 | 0 | 0 | 1098.68 | 0 | 0 | 0 | 50 | 113 | 0 | 0 | 0 | 52.2 | 7.44 | 19 | 0 | 0 | 12.37 | 157 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 1.41 | 180 | 0 | 93 | 13 | 95 | 0 | 0 | 0 | 2.3 | 34 | 0.04 | 16 | 264 | 120 | 220 | 0 | 1009 | 972 | 17 | 6807.79 | 14110.96 | 102.72
18:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 17 | 35 | 116 | 115 | 81 | 15 | 35 | 90 | 0 | 0 | 143 | 290 | 0 | 35 | 300 | 0 | 0 | 2 | 124 | 11 | 14 | 0 | 0 | 47 | 16 | 93 | 0 | 16 | 0 | 72 | 17 | 25 | 25 | 0.21 | 221 | 105 | 0 | 1000 | 32 | 0 | 0 | 25.5 | 95 | 210 | 0 | 0 | 0 | 900 | 0 | 150 | 0 | 0 | 300 | 0 | 51 | 20 | 204 | 30 | 53 | 141 | 139 | 26 | 19 | 32 | 142 | 52.2 | 5 | 0 | 275 | 0 | 307 | 39 | 0 | 136 | 0 | 16 | 0 | 52 | 0 | 0 | 0 | 100 | 17 | 59 | 1.8 | 115 | 0 | 0 | 3.46 | 12 | 7246.17 | 871 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 4 | 1080 | 0 | 0 | 0 | 1099.22 | 0 | 0 | 0 | 50 | 113 | 0 | 0 | 0 | 52.2 | 3.53 | 4 | 0 | 0 | 1.27 | 157 | 0 | 0 | 0 | 0 | 0 | 241 | 0 | 0.13 | 180 | 0 | 94 | 2 | 99 | 0 | 0 | 0 | 0.9 | 12 | 0.02 | 16 | 219 | 100 | 220 | 0 | 1039 | 923 | 17 | 6686.27 | 13932.44 | 102.72
19:00 | 0 | 26 | 17 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 35 | 133 | 143 | 81 | 15 | 55 | 146 | 0 | 0 | 145 | 285 | 0 | 35 | 280 | 0 | 0 | 0 | 143.42 | 11 | 20 | 0 | 0 | 52 | 16 | 94 | 0 | 28 | 50 | 74 | 27 | 25 | 25 | 0 | 222 | 109 | 2 | 1135 | 100 | 0 | 0 | 25.5 | 100 | 210 | 0 | 0 | 0 | 900 | 0 | 150 | 0 | 0 | 349 | 0 | 51 | 20 | 204 | 30 | 72 | 142 | 188 | 28 | 19 | 95 | 156 | 52.2 | 0 | 0 | 310 | 0 | 307 | 39 | 0 | 141 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 66 | 0 | 115 | 0 | 0 | 0 | 12 | 7955.12 | 872 | 0 | 0 | 20 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1080 | 0 | 0 | 0 | 1133.23 | 0 | 13 | 0 | 90 | 107 | 0 | 100 | 22 | 52.2 | 0 | 0 | 20 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 180 | 0 | 95 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 267 | 120 | 220 | 0 | 1050 | 900 | 17 | 6988.43 | 14943.55 | 102.71
19:30 | 0 | 51 | 17 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 54 | 35 | 133 | 143 | 81 | 15 | 55 | 146 | 0 | 0 | 148 | 290 | 0 | 35 | 280 | 0 | 0 | 0 | 143.42 | 11 | 20 | 0 | 0 | 92 | 16 | 94 | 0 | 30 | 50 | 74 | 27 | 25 | 25 | 0 | 222 | 105 | 5 | 1135 | 138 | 0 | 0 | 25.5 | 97 | 210 | 0 | 0 | 0 | 900 | 0 | 150 | 0 | 0 | 358 | 0 | 51 | 20 | 198 | 40 | 89 | 142 | 187 | 29 | 19 | 108 | 136 | 52.2 | 0 | 0 | 315 | 0 | 307 | 39 | 0 | 154 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 68 | 0 | 151 | 0 | 0 | 0 | 12 | 8146.12 | 871 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1080 | 0 | 0 | 0 | 1160.48 | 0 | 40 | 0 | 90 | 113 | 0 | 100 | 27 | 52.2 | 0 | 0 | 25 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 180 | 0 | 95 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1050 | 895 | 17 | 7098.68 | 15244.8
20:00 | 0 | 51 | 17 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 54 | 35 | 133 | 142 | 81 | 15 | 55 | 144 | 0 | 0 | 144 | 280 | 0 | 35 | 280 | 0 | 0 | 0 | 143.42 | 11 | 14 | 0 | 0 | 95 | 16 | 95 | 0 | 27 | 50 | 74 | 54.36 | 25 | 25 | 0 | 222 | 106 | 8 | 1140 | 136 | 0 | 0 | 25.5 | 97 | 212 | 0 | 0 | 0 | 960 | 0 | 150 | 0 | 0 | 358 | 0 | 51 | 20 | 195 | 40 | 89 | 141 | 188 | 27 | 19 | 100 | 130 | 52.2 | 0 | 0 | 310 | 0 | 307 | 39 | 0 | 142 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 12 | 8175.48 | 871 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1080 | 0 | 0 | 0 | 1207.25 | 0 | 40 | 0 | 90 | 113 | 0 | 100 | 28 | 52.2 | 0 | 0 | 25 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 180 | 0 | 95 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1050 | 895 | 17 | 7157.45 | 15332.93 | 102.71
21:00 | 0 | 51 | 17 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 37 | 35 | 133 | 127 | 81 | 15 | 35 | 108 | 0 | 0 | 146 | 275 | 0 | 35 | 260 | 0 | 0 | 0 | 143.42 | 11 | 18 | 0 | 0 | 89 | 16 | 95 | 0 | 27 | 50 | 74 | 54.36 | 25 | 25 | 0 | 222 | 105 | 9 | 1140 | 104 | 0 | 0 | 25.5 | 92 | 212 | 0 | 0 | 0 | 1000 | 0 | 150 | 0 | 0 | 358 | 0 | 51 | 20 | 195 | 37 | 88 | 142 | 187 | 28 | 19 | 96 | 138 | 52.2 | 0 | 0 | 300 | 0 | 307 | 39 | 0 | 126 | 0 | 16 | 0 | 83 | 0 | 0 | 0 | 100 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 12 | 8025.48 | 872 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 181 | 0 | 50 | 0 | 1080 | 0 | 0 | 0 | 1307.6 | 0 | 40 | 0 | 90 | 113 | 0 | 100 | 28 | 52.2 | 0 | 0 | 25 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 180 | 0 | 95 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1050 | 894 | 17 | 7610.8 | 15636.28 | 102.7
22:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 35 | 35 | 133 | 127 | 81 | 15 | 35 | 108 | 0 | 0 | 145 | 280 | 0 | 35 | 260 | 0 | 0 | 0 | 143.42 | 11 | 14 | 0 | 0 | 94 | 16 | 95 | 0 | 15 | 50 | 75 | 54.36 | 25 | 25 | 0 | 222 | 106 | 6 | 1140 | 106 | 0 | 0 | 8 | 97 | 185 | 0 | 0 | 0 | 1000 | 0 | 150 | 0 | 0 | 358 | 0 | 51 | 20 | 196 | 40 | 70 | 142 | 188 | 28 | 19 | 100 | 138 | 52.2 | 0 | 0 | 305 | 0 | 307 | 39 | 0 | 136 | 0 | 16 | 0 | 84 | 0 | 0 | 0 | 100 | 17 | 69 | 0 | 154 | 0 | 0 | 0 | 12 | 7948.98 | 871 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 181 | 0 | 50 | 0 | 1080 | 0 | 0 | 0 | 1305.74 | 0 | 40 | 0 | 90 | 113 | 0 | 100 | 28 | 52.2 | 0 | 0 | 25 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 180 | 0 | 95 | 0 | 100 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1050 | 886 | 17 | 7599.94 | 15548.92 | 102.7
23:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 35 | 35 | 133 | 143 | 81 | 15 | 35 | 54 | 0 | 0 | 148 | 290 | 0 | 0 | 240 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 97 | 16 | 96 | 0 | 22 | 50 | 75 | 17 | 25 | 25 | 0 | 222 | 107 | 6 | 1140 | 120 | 0 | 0 | 8 | 100 | 185 | 0 | 0 | 0 | 895 | 0 | 150 | 0 | 0 | 360 | 0 | 51 | 20 | 196 | 40 | 67 | 142 | 188 | 28 | 19 | 100 | 146 | 52.2 | 0 | 0 | 320 | 0 | 307 | 39 | 0 | 148 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 58 | 0 | 154 | 0 | 0 | 0 | 12 | 7743.62 | 872 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 180 | 0 | 50 | 0 | 1080 | 0 | 0 | 0 | 1308.87 | 0 | 40 | 0 | 90 | 113 | 0 | 100 | 28 | 52.2 | 0 | 0 | 25 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 180 | 0 | 95 | 0 | 100 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 277 | 120 | 220 | 0 | 1035 | 880 | 17 | 7553.07 | 15296.69 | 102.69
Total KWH | 0 | 1441920 | 119040 | 0 | 0 | 0 | 0 | 0 | 8938800 | 0 | 0 | 259200 | 903240 | 1443600 | 2704800 | 1658258 | 393595 | 601709 | 802080 | 0 | 0 | 3483287 | 6981068 | 0 | 338321 | 6864667 | 0 | 0 | 126780 | 2935200 | 258600 | 429840 | 0 | 0 | 1555636 | 408982 | 1604160 | 0 | 602400 | 320763 | 920832 | 404728 | 586560 | 599040 | 20883 | 5315544 | 2581018 | 251040 | 27120000 | 2199636 | 0 | 708000 | 316918.8 | 2032363 | 4907644 | 0 | 0 | 0 | 24850907 | 19845 | 2418763 | 0 | 0 | 8807000 | 0 | 1253086 | 955360 | 5070000 | 778320 | 697920 | 3377293 | 2757600 | 179760 | 465690 | 1597140 | 3336000 | 784090 | 400618 | 0 | 7447000 | 0 | 7592000 | 940000 | 0 | 3345872.72 | 55749 | 296832 | 0 | 1295040 | 0 | 0 | 0 | 2412250 | 446400 | 1300800 | 109202 | 2251200 | 0 | 10950 | 235000 | 126480 | 178754320.52 | 21119273 | 0 | 0 | 130560 | 0 | 912000 | 0 | 0 | 545644 | 0 | 319680 | 426240 | 25592730 | 0 | 0 | 0 | 27840000 | 0 | 294408 | 0 | 758496 | 1331136 | 0 | 610848 | 184239 | 806462 | 239504 | 530990 | 190460 | 0 | 260736 | 3763636 | 0 | 0 | 0 | 0 | 0 | 6843127 | 0 | 24360 | 4522000 | 0 | 2220928 | 209785 | 1107648 | 0 | 509670 | 0 | 44832.24 | 1086480 | 2735 | 1036992 | 6698000 | 2836000 | 5285220 | 0 | 24792727 | 24618181.82 | 429600 | 168125328.06 | 346879648.58

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13996.92 | MW | 12:00 Hr. | Energy Generated |  |  | 346.8796 |  | MKWHr.
| Day Peak Demand |  |  | 15442.92 | MW | 12:00 Hr. | Energy Unserverd |  |  | 24.238 |  | MKWHr.
| Evening Peak Generation |  |  | 15636.28 | MW | 21:00 Hr. | Energy Demand |  |  | 371.1176 |  | MKWHr.
| Evening Peak Demand |  |  | 17138.28 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.2 |  | °C
| Minimum Generation of the Day |  |  | 13414.89 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 678.84 |  | MMCFD
| Maximum Generation of the Day |  |  | 15636.28 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.5048 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.9563 | 0 | 13.601 | 0 | 0 | 0.12678 | 0 | 0 | 40.684 | Gas | 94.8787 | Gas | 333258119.6624
| Chattogram Zone |  |  | 5.1587 | 51.9709 | 14.2386 | 0 | 5.3155 | 0.040728 | 0 | 0.6024 | 77.3269 | Coal | 138.1945 | Coal | 927670101.6012
| Cumilla Zone |  |  | 20.7067 | 0 | 8.4353 | 0 | 0 | 0.40062 | 3.336 | 0 | 32.8786 | HFO | 49.8212 | HFO | 914119223.792
| Mymensingh Zone |  |  | 0 | 0 | 4.1249 | 0 | 0 | 0.35515 | 0 | 0 | 4.48 | HSD | 1.0553 | HSD | 26760618.4
| Sylhet Zone |  |  | 23.329 | 0 | 0 | 0 | 0 | 0.055749 | 0 | 0 | 23.3847 | Hydro | 5.3155 | Hydro | 531554.4
| Khulna Zone |  |  | 0 | 25.5927 | 0.45024 | 0.54564 | 0 | 0.42624 | 22.0313 | 0 | 49.0461 | Solar | 3.8047 | Solar | 61449342.7192
| Barishal Zone |  |  | 8.1212 | 56.1089 | 1.4666 | 0 | 0 | 0.002735 | 0 | 0 | 65.6995 | Import | 53.2073 | Import | 330620488.32
| Rajshahi Zone |  |  | 10.6068 | 0 | 4.176 | 0 | 0 | 1.0556 | 27.84 | 0 | 43.6784 | Wind | 0.6024 | Wind | 8861304
| Rangpur Zone |  |  | 0 | 4.522 | 3.3286 | 0.50967 | 0 | 1.3411 | 0 | 0 | 9.7013
| Total |  |  | 94.8787 | 138.1945 | 49.8212 | 1.0553 | 5.3155 | 3.8047 | 53.2073 | 0.6024 | 346.8796
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 333258119.6624 |  | Hydro | 531554.4
|  |  |  | Coal | 927670101.6012 |  | Solar | 61449342.7192
|  |  |  | HFO | 914119223.792 |  | Import | 330620488.32
|  |  |  | HSD | 26760618.4 |  | Wind | 8861304
[5 empty] | Total: | 260,32,70,752 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.1193 | Peak Hr Flow | 872.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 55866400 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.84 | Peak Hr Flow | 1307.60 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2518 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.336 | Peak Hr Flow | 138.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2827 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.2953 | Peak Hr Flow | 2317.60 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 120 |  | 5802
|  |  |  | Chattogram |  | 116 |  | 1526
|  |  |  | Cumilla |  | 133 |  | 1519
|  |  |  | Mymensingh |  | 411 |  | 1524
|  |  |  | Sylhet |  | 235 |  | 829
|  |  |  | Khulna |  | 174 |  | 1986
|  |  |  | Barishal |  | 32 |  | 469
|  |  |  | Rajshahi |  | 146 |  | 1688
|  |  |  | Rangpur |  | 70 |  | 1159
|  |  |  | Total |  | 1437 |  | 16502
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 89
|  |  |  | Total Unavailable Capacity |  |  |  | 389
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:34 | 12:26 | Baroirhat-Feni 132 kV Ckt-2 Scheduled S/D from Feni 132/33kV end Due to Baroiarhat End
RedHot Maintenance and from Baroirhat 132/33kVend.
| 09:18 |  | Chattak-Sylhet 132 kV Ckt-1 Tripped from Sylhet 132/33kV end showing Distance B & C
phase, Z-1 relays.
| 09:24 | 14:13 | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Project Work S/D Due to Bus diff. Protection &
stability testing
|  | 09:29 | Kabirpur 132/33kV S/S XFR, T-I HT is restored.
|  | 09:30 | Kabirpur 132/33kV S/S XFR, T-I LT is restored.
| 09:41 | 10:29 | Ashuganj-Bhulta 400 kV Ckt-1 Project Work S/D from Bhulta 400/230/132kV end Due to
Shutdown taken by NLDC for project Work.
| 09:45 |  | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Sylhet 132/33kV end Due to CB fault
| 10:05 | 20:07 | Bogura 230/132kV S/S T-02 LT Scheduled S/D Due to Auxiliary Transformer Installation
| 10:05 | 20:06 | Bogura 230/132kV S/S T-02 HT Scheduled S/D Due to Auxiliary Transformer Installation
| 10:32 | 18:29 | Ashuganj-Bhulta 400 kV Ckt-2 Project Work S/D from Bhulta 400/230/132kV end Due to
Shutdown Taken by NLDC For project work
| 11:01 | 11:43 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) LT Forced S/D Due to LT Bushing Redhot
maintenance of Transformer T-1
| 11:02 | 11:42 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) HT Forced S/D Due to LT Bushing Redhot
maintenance of Transformer T-1
|  | 11:26 | Bhaluka-Mymensingh 132 kV Ckt-2 is restored.
| 11:56 | 12:43 | Bhaluka 132/33kV S/S 03. Transformer-03 HT Forced S/D Due to 33 kv Y phase Bushing red
hot minimize
| 12:35 | 17:36 | Baroirhat-PHP 132 kV Ckt-1 Scheduled S/D from Baroirhat 132/33kV end.
| 12:38 |  | Khulna (C) S/S Tr-3 405T LT Tripped showing instantaneous Earth fault relays Due to TR3
132/33KV under ground cable Burn.
| 12:38 |  | Khulna (C) S/S Tr-3 405T LT Tripped showing instantaneous Earth fault relays Due to TR3
132/33KV under ground cable Burn.
| 12:38 |  | Khulna (C) S/S Tr-3 405T HT Tripped showing No Relay. relays Due to TR3 132/33KV under
ground cable Burn.
|  | 12:40 | Bhaluka 132/33kV S/S Bus B is restored.
| 13:24 | 15:52 | Korerhat 400/230/132kV S/S ATR-4(7403T) LT Project Work S/D Due to For project work
| 13:26 | 15:51 | Korerhat 400/230/132kV S/S ATR-4(7403T) HT Project Work S/D Due to For project work
| 13:28 | 14:31 | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Kishoreganj 132/33kV end Due to Work
at Bajitpur substation.
| 13:29 | 14:31 | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Bajitpur 132/33kV end Due to Due
to Line DS B Phase clamp Maintenance
|  | 13:35 | Bhaluka 132/33kV S/S BR Powergen Ckt- 02 is restored.
| 14:36 | 15:39 | Bajitpur 132/33kV S/S 132 kV Bus-1 Scheduled S/D Due to Due to132 KV Bus coupler Bus-1
DS(B phase) Clamp maintenance
| 14:38 |  | Ashuganj-Kishoreganj 132kV Ckt-1 Scheduled S/D from Kishoreganj 132/33kV end Due to Work
at Bajitpur substation end.
| 14:40 | 15:37 | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Bajitpur 132/33kV end Due to Due
To Line DS (RYB) Phase clamp maintenance
| 15:10 | 16:18 | Kushtia 132/33kV S/S T-3 LT Forced S/D Due to Red Hot maintenance By PBS | [7 empty] | 10.0MW load
interrup.
| 15:10 | 16:17 | Kushtia 132/33kV S/S T-3 HT Forced S/D Due to Red Hot maintenance By PBS | [7 empty] | 10.0MW load
interrup.
| 17:28 | 17:38 | Pabna 132/33kV S/S T-1 LT Tripped showing Inst. E/F relays Due to 33 KV Pailanpur Trip ( | [7 empty] | 35.0MW load
|  |  | O/C+ E/F) | [7 empty] | interrup.
| 18:49 | 20:27 | Muradnagar 132/33kV S/S 132KV Transformar-02 HT Forced S/D Due to Red hot maintenance .
|  | 19:23 | Munshiganj 132/33kV S/S Transformer-1 HT is restored.
|  | 19:23 | Munshiganj 132/33kV S/S Transformer-1 LT is restored.
| 21:30 | 22:14 | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to Oil Leakage | [7 empty] | 50.0MW load
interrup.
| 21:33 | 22:12 | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to Oil Leakage | [7 empty] | 50.0MW load
interrup.
| 22:30 | 00:19 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to keranihut ds redhot | [7 empty] | 53.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 22:30 | 00:19 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to keranihut ds redhot | [7 empty] | 53.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 06:45 |  | Munshiganj 132/33kV S/S Transformer-1 HT Scheduled S/D Due to 33 KV CB Replacement work.
| 06:45 |  | Munshiganj 132/33kV S/S Transformer-1 LT Scheduled S/D Due to 33 KV CT Replacement work
| 07:02 |  | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T LT Scheduled S/D Due to Nesco. | [7 empty] | 35.0MW load
interrup.
| 07:04 |  | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T HT Scheduled S/D Due to Nesco work. | [7 empty] | 35.0MW load
interrup.
| 07:23 |  | Naogaon 132/33kV S/S T-4 LT Project Work S/D Due to Old Bay Dismentle work
| 07:23 |  | Naogaon 132/33kV S/S T-4 HT Project Work S/D Due to Old Bay Dismentle work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 351 | 8938800 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 146 | 3483287 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 393595 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 260 | 6864667 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 37 | 259200 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 127 | 2704800 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 601709 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 338321 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11 | 258600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 429840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 119040 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 81 | 1658258 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 1443600 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 51 | 1441920 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 802080 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 126780 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 903240 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 275 | 6981068 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 2935200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 1878.42 | 40684005
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 316918.8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 19845 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 708000 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5315544 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 212 | 4907644 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 92 | 2032363 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 74 | 920832 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 320763 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 586560 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 9 | 251040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 95 | 1604160 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20883 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 408982 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 404728 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 105 | 2581018 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 599040 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 89 | 1555636 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 104 | 2199636 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1000 | 24850907 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 27 | 602400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1140 | 27120000 | Machine Problem
Chattogram Area Total |  |  |  |  | 4898.863 | 3364.86 | 77326899.8
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 195 | 5070000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 358 | 8807000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 37 | 778320 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 20 | 955360 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1253086 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 2418763 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 142 | 3377293 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 187 | 2757600 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 138 | 3336000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 784090 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 465690 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 96 | 1597140 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 179760 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 88 | 697920 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 400618 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1561.2 | 32878640
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 109202 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 153 | 2251200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1300800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 235000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 126480 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 446400 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 250 | 4480032
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 55749 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 39 | 940000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 126 | 3345872.72 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1295040 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2412250 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 296832 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7447000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 307 | 7592000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 971 | 23384743.72
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 872 | 21119273 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 23 | 130560 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 319680 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 426240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 181 | 545644 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1080 | 25592730 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2244 | 49046127
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1050 | 24792727 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 1036992 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2836000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 894 | 24618181.82 | AGC
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5285220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 429600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6698000 | FGMO
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2735 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2624 | 65699455.82
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 239504 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 294408 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 184239 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 156 | 3763636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 292 | 6843127 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 190460 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 806462 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 610848 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1331136 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 90 | 758496 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 24360 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1307.6 | 27840000 | FGMO
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 260736 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 530990 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2203.8 | 43678402
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 509670 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4522000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 1107648 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44832.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 2220928 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 209785 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1086480 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 539 | 9701343.24
Eastern Grid Total |  |  |  |  | 17440.562 | 8025.48 | 178754320.52
Western Grid Total |  |  |  |  | 11731.125 | 7610.8 | 168125328.06
National Grid Total |  |  |  |  | 29171.687 | 15636.28 | 346879648.58
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10230.6 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4879.4 | MW
i) Dhaka area |  |  | 5682.1 |  | MW | i) Khulna area |  |  |  | 1811.5 | MW
ii) Chattogram area |  |  | 1455.5 |  | MW | ii) Barishal area |  |  |  | 437.3 | MW
iii) Cumilla area |  |  | 1386 |  | MW | iii) Rajshahi area |  |  |  | 1541.6 | MW
iv) Mymensingh area |  |  | 1113 |  | MW | iv) Rangpur area |  |  |  | 1089 | MW
v) Sylhet area |  |  | 594 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15110 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 11 | 21:00 | 67 | HaripurSBU | 145 | 04:00 | 133 | Narshingdi | 141 | 19:00 | 199 | Uttara | 103 | 13:00
2 | AKSML | 158.6 | 06:00 | 68 | Hasnabad | 95 | 00:00 | 134 | Natore | 137 | 19:30 | 200 | UttaraNew | 56 | 13:00
3 | Aftabnagar | 46 | 13:00 | 69 | Hathazari | 93 | 20:00 | 135 | Nawabganj | 63.9 | 21:00 | 201 | Zigatola | 96 | 13:00
4 | Agargaon | 129 | 13:00 | 70 | Hatirjheel | 88 | 13:00 | 136 | Netrakona | 113 | 18:30
5 | Agrabad | 74 | 16:00 | 71 | Ishurdi | 78 | 13:00 | 137 | New | 88 | 15:00
6 | Amnura | 30 | 00:00 | 72 | Jaldhaka | 100 | 21:00 | 138 | Niamatpur | 75 | 02:00
7 | Ashuganj | 105 | 01:00 | 73 | Jamalpur | 104 | 19:00 | 139 | Noapara | 45 | 13:00
8 | BSRM | 190 | 06:00 | 74 | Jashore | 152 | 20:00 | 140 | PHP | 5 | 15:00
9 | Bagerhat | 96 | 23:00 | 75 | Jhenaidah | 99 | 19:00 | 141 | Pabna | 107 | 20:00
10 | Bajitpur | 84 | 05:00 | 76 | Joydebpur | 169 | 07:00 | 142 | Palashbari | 143 | 23:00
11 | Bakerganj | 14.4 | 22:00 | 77 | Joypurhat | 65 | 03:00 | 143 | Panchagarh | 69 | 19:30
12 | Bakulia | 92 | 16:00 | 78 | Juldah | 16 | 09:00 | 144 | Patiya | 10.5 | 01:00
13 | Banani | 77 | 13:00 | 79 | KSRM | 27 | 00:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 18 | 11:00 | 80 | Kabirpur | 259 | 22:00 | 146 | Patuakhali | 64 | 00:00
15 | Barapukuria | 70 | 02:00 | 81 | Kachua | 92 | 00:00 | 147 | Payra | 34 | 00:00
16 | Barguna | 20 | 00:00 | 82 | Kaliganj | 42 | 19:30 | 148 | Postogola | 65 | 13:00
17 | Barishal | 104 | 12:00 | 83 | Kallyanpur | 126 | 20:00 | 149 | Pubail | 48 | 12:00
18 | Barishal-230 | 94 | 00:00 | 84 | Kalurghat | 42 | 16:00 | 150 | Purbachal | 33 | 13:00
19 | Baroaulia | 48 | 09:00 | 85 | Kamrangirchar | 80 | 19:00 | 151 | Purbasadipur | 136 | 02:00
20 | Baroirhat | 65 | 23:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 36 | 01:00
21 | Bashundhara | 218 | 14:00 | 87 | Kasba | 43 | 03:00 | 153 | Rahim | 58 | 08:00
22 | BashundharaCement | 1 | 00:00 | 88 | Kazla | 127 | 13:00 | 154 | Rajbari | 85 | 19:00
23 | Beanibazar | 90 | 18:30 | 89 | Keranigonj | 93 | 19:00 | 155 | Rajendrapur | 130 | 08:00
24 | Benapole | 69 | 14:00 | 90 | Khagrachori | 32 | 19:00 | 156 | Rajshahi | 112 | 01:00
25 | Bhaluka | 157 | 21:00 | 91 | Khulna | 54 | 11:00 | 157 | Rajshahi-230 | 105 | 13:00
26 | Bhandaria | 54 | 00:00 | 92 | Khulshi | 183 | 17:00 | 158 | Ramganj | 122 | 21:00
27 | Bhangura | 40 | 21:00 | 93 | Kishoreganj | 112 | 21:00 | 159 | Rampur | 44 | 19:00
28 | Bheramara(GK) | 63 | 02:00 | 94 | Kodda | 290 | 18:00 | 160 | Rangamati | 16 | 19:00
29 | Bhulta | 225 | 00:00 | 95 | Kulaura | 60 | 19:00 | 161 | Rangpur | 148 | 00:00
30 | Bog-Sherpur | 70 | 19:00 | 96 | Kurigram | 78 | 21:00 | 162 | Ruppur | 4.4 | 11:00
31 | Bogura | 195 | 21:00 | 97 | Kushtia | 171 | 21:00 | 163 | SSM | 11 | 07:00
32 | Borhanuddin | 72 | 00:00 | 98 | Laksam | 35 | 01:00 | 164 | Saidpur | 110 | 08:00
33 | Brahmanbaria | 100 | 00:00 | 99 | Lakshmipur | 46 | 19:00 | 165 | Santhia | 36 | 00:00
34 | Cantonment | 140 | 13:00 | 100 | Lalbag | 78 | 19:00 | 166 | Satkhira | 144 | 19:30
35 | Chandina | 40 | 00:00 | 101 | Lalmonirhat | 70 | 20:00 | 167 | Satmasjid | 109 | 14:00
36 | Chandpur | 88 | 22:00 | 102 | MI_Cement | 16.6 | 04:00 | 168 | Savar | 225 | 19:00
37 | Chandraghona | 39 | 23:00 | 103 | Madanganj | 50 | 19:30 | 169 | SevenRings | 16.36 | 03:00
38 | Chapai | 77 | 21:00 | 104 | Madaripur | 101 | 20:00 | 170 | ShahCement | 24 | 00:00
39 | Charfasson | 32 | 22:00 | 105 | Madartek | 84 | 00:00 | 171 | Shahjadpur | 76 | 15:00
40 | Charsaidpur | 43 | 18:30 | 106 | Madunaghat | 55 | 19:00 | 172 | Shahjibazar | 132 | 04:00
41 | Chauddagram | 74 | 00:00 | 107 | Magura | 62 | 02:00 | 173 | Shahmirpur | 53 | 19:00
42 | Chhatak | 39 | 06:00 | 108 | Mahasthangarh | 83 | 21:00 | 174 | Shariatpur | 80 | 21:00
43 | Chowmuhani | 157 | 23:00 | 109 | Maijdee | 36 | 19:00 | 175 | Sherpur | 140 | 23:00
44 | Chuadanga | 102 | 00:00 | 110 | Manikganj | 150 | 22:00 | 176 | Shikalbaha | 33.5 | 00:00
45 | Coxsbazar | 140 | 19:30 | 111 | Maniknagar | 89 | 14:00 | 177 | Shitalakhya | 79.7 | 13:00
46 | Cumilla(N) | 122 | 00:00 | 112 | Matarbari | 51 | 00:00 | 178 | Sholosohor | 48 | 11:00
47 | Cumilla(S) | 160 | 16:00 | 113 | Matuail | 80 | 12:00 | 179 | Shomvuganj | 35 | 19:30
48 | Daganbhuiyan | 57 | 16:00 | 114 | Metrorail_Motijheel | 28 | 15:00 | 180 | Shyampur | 170 | 09:00
49 | Daudkandi | 117 | 19:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 132 | 12:00
50 | DhakaUniversity | 102 | 13:00 | 116 | Millgate | 105 | 12:00 | 182 | Sirajganj | 128 | 21:00
51 | Dhamrai | 104 | 19:00 | 117 | Mirpur | 159 | 19:00 | 183 | Sitakunda | 36 | 19:00
52 | Dhanmondi | 106.5 | 17:00 | 118 | Mirsorai | 44 | 11:00 | 184 | Sonargaon | 150 | 21:00
53 | Dohazari | 104 | 00:00 | 119 | Mirzapur | 40 | 22:00 | 185 | Sreemongol | 82 | 01:00
54 | Faridpur | 193 | 21:00 | 120 | Mithapukur | 84 | 22:00 | 186 | Sreepur | 103 | 19:30
55 | Fatullah | 112 | 15:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 51.48 | 22:00
56 | Fenchuganj | 47 | 18:30 | 122 | Mogbazar | 43.6 | 14:00 | 188 | Sunamganj | 58 | 05:00
57 | Feni | 107 | 21:00 | 123 | Mongla | 44 | 10:00 | 189 | Sylhet | 130 | 18:30
58 | GPH | 1 | 00:00 | 124 | Motijheel | 53 | 13:00 | 190 | Sylhet_(South) | 71 | 23:00
59 | Ghatail | 88 | 20:00 | 125 | Muktagacha | 42 | 13:00 | 191 | TK | 24 | 00:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 115 | 20:00 | 192 | Tangail | 168 | 19:30
61 | Ghorashal-230 | 112 | 22:00 | 127 | Muradnagar | 53 | 22:00 | 193 | Taraganj | 34 | 18:30
62 | Goalpara | 39 | 14:00 | 128 | Mymensingh | 170 | 19:00 | 194 | Tasnim | 48 | 09:00
63 | Gollamari | 116 | 21:00 | 129 | Nabinagar | 106 | 19:30 | 195 | Thakurgaon | 122 | 20:00
64 | Gopalganj | 101 | 19:00 | 130 | Naogaon | 153 | 23:00 | 196 | Tongi | 170 | 09:00
65 | Gulshan | 124 | 13:00 | 131 | Narail | 57 | 22:00 | 197 | Ullahpara | 38 | 19:00
66 | Halishahar | 115 | 17:00 | 132 | Narinda | 90 | 13:00 | 198 | Ullon | 60 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15227.79 | 1690 |  | 16993.79
1:00 | 14847.84 | 1230 |  | 16133.19
2:00 | 14694.03 | 1022 |  | 15762.03
3:00 | 14410.63 | 720 |  | 15162.63
4:00 | 14259.21 | 676 |  | 14965.21
5:00 | 13937.74 | 561 |  | 14523.74
6:00 | 13696.46 | 546 |  | 14267.46
7:00 | 13689.36 | 591 |  | 14307.36
8:00 | 13555.33 | 535 |  | 14114.33
9:00 | 13414.89 | 512 |  | 13949.89
10:00 | 13530.75 | 703 |  | 14265.75
11:00 | 13553.76 | 833 |  | 14423.76
12:00 | 13996.92 | 1384 |  | 15442.92
13:00 | 14160.8 | 1227 |  | 15442.8
14:00 | 14348.22 | 1352 |  | 15761.22
15:00 | 14372.95 | 1326 |  | 15758.95
16:00 | 14287.36 | 1040 |  | 15374.36
17:00 | 14110.96 | 951 |  | 15104.96
18:00 | 13932.44 | 432 |  | 14383.44
19:00 | 14943.55 | 1093 |  | 16085.55
19:30 | 15244.8 | 1551 |  | 16865.8
20:00 | 15332.93 | 1625 |  | 17030.93
21:00 | 15636.28 | 1437 |  | 17138.28
22:00 | 15548.92 | 1116 |  | 16714.92
23:00 | 15296.69 | 1636 |  | 17006.69
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7788.82 | 7438.97 | 15227.79 | DAILY GENERATION CURVE
00:30 | 7728.82 | 7308.995 | 15037.815
01:00 | 7668.82 | 7179.02 | 14847.84 | 28-07-2026
01:30 | 7608.97 | 7161.965 | 14770.935
02:00 | 7549.12 | 7144.91 | 14694.03
02:30 | 7455.52 | 7096.81 | 14552.33
03:00 | 7361.92 | 7048.71 | 14410.63
03:30 | 7286.92 | 7048 | 14334.92
04:00 | 7211.92 | 7047.29 | 14259.21
04:30 | 7088.42 | 7010.055 | 14098.475
05:00 | 6964.92 | 6972.82 | 13937.74
05:30 | 6931.73 | 6885.37 | 13817.1
06:00 | 6898.54 | 6797.92 | 13696.46
06:30 | 6881.38 | 6811.53 | 13692.91
07:00 | 6864.22 | 6825.14 | 13689.36
07:30 | 6812.995 | 6809.35 | 13622.345
08:00 | 6761.77 | 6793.56 | 13555.33
08:30 | 6696.17 | 6788.94 | 13485.11
09:00 | 6630.57 | 6784.32 | 13414.89
09:30 | 6697.31 | 6775.51 | 13472.82
10:00 | 6764.05 | 6766.7 | 13530.75
10:30 | 6876.325 | 6665.93 | 13542.255
11:00 | 6988.6 | 6565.16 | 13553.76
11:30 | 7079.62 | 6695.72 | 13775.34
12:00 | 7170.64 | 6826.28 | 13996.92
12:30 | 7274.575 | 6804.285 | 14078.86
13:00 | 7378.51 | 6782.29 | 14160.8
13:30 | 7384.47 | 6870.04 | 14254.51
14:00 | 7390.43 | 6957.79 | 14348.22
14:30 | 7415.78 | 6944.805 | 14360.585
15:00 | 7441.13 | 6931.82 | 14372.95
15:30 | 7396.075 | 6934.08 | 14330.155
16:00 | 7351.02 | 6936.34 | 14287.36
16:30 | 7327.095 | 6872.065 | 14199.16
17:00 | 7303.17 | 6807.79 | 14110.96
17:30 | 7274.67 | 6747.03 | 14021.7
18:00 | 7246.17 | 6686.27 | 13932.44
18:30 | 7600.645 | 6837.35 | 14437.995
19:00 | 7955.12 | 6988.43 | 14943.55
19:30 | 8146.12 | 7098.68 | 15244.8
20:00 | 8175.48 | 7157.45 | 15332.93
20:30 | 8100.48 | 7384.125 | 15484.605 |  | Executive Engineer
21:00 | 8025.48 | 7610.8 | 15636.28 |  | Network Operation Division
21:30 | 7987.23 | 7605.37 | 15592.6
22:00 | 7948.98 | 7599.94 | 15548.92
22:30 | 7846.3 | 7576.505 | 15422.805
23:00 | 7743.62 | 7553.07 | 15296.69

## En-Curve
QF-LDC-12
Date | 28-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2611 | 1291.2 | 876 | 38 | 152 | 1414.77 | 222 | 5986 | 0 | 707.42 | 1892.4 | 0 | 0 | 37 | 1690 | DAILY ENERGY CURVE
00:30 | 2613.5 | 1290.2 | 876 | 38 | 148 | 1414.295 | 222 | 5979 | 0 | 642.42 | 1770.9 | 0 | 0 | 43.5 | 1460 | 28-07-2026
01:00 | 2616 | 1289.2 | 876 | 38 | 144 | 1413.82 | 222 | 5972 | 0 | 577.42 | 1649.4 | 0 | 0 | 50 | 1230
01:30 | 2624.5 | 1289.85 | 876 | 38 | 138 | 1419.765 | 222 | 5967.5 | 0 | 552.42 | 1602.9 | 0 | 0 | 40 | 1126 | Energy Generated | 346.8796 |  | MKWHr
02:00 | 2633 | 1290.5 | 876 | 38 | 132 | 1425.71 | 222 | 5963 | 0 | 527.42 | 1556.4 | 0 | 0 | 30 | 1022 | Energy not Served | 24.238 |  | MKWHr
02:30 | 2635 | 1282.5 | 876 | 38 | 134 | 1426.61 | 222 | 5951 | 0 | 466.42 | 1478.3 | 0 | 0 | 42.5 | 871 | Total Energy Requirement | 371.1176 |  | MKWHr
03:00 | 2637 | 1274.5 | 876 | 38 | 136 | 1427.51 | 222 | 5939 | 0 | 405.42 | 1400.2 | 0 | 0 | 55 | 720
03:30 | 2650.5 | 1294.5 | 876 | 38 | 137 | 1435.9 | 222 | 5950.5 | 0 | 389.42 | 1301.6 | 0 | 0 | 39.5 | 698
04:00 | 2664 | 1314.5 | 876 | 38 | 138 | 1444.29 | 222 | 5962 | 0 | 373.42 | 1203 | 0 | 0 | 24 | 676
04:30 | 2655.5 | 1300 | 876 | 38 | 136 | 1418.055 | 222 | 5980 | 0 | 373.42 | 1071 | 0 | 0 | 28.5 | 618.5
05:00 | 2647 | 1285.5 | 876 | 38 | 134 | 1391.82 | 222 | 5998 | 0 | 373.42 | 939 | 0 | 0 | 33 | 561
05:30 | 2645 | 1279 | 876 | 38 | 127 | 1314.98 | 222 | 5988 | 8.2 | 364.42 | 924.5 | 0 | 0 | 30 | 553.5
06:00 | 2643 | 1272.5 | 876 | 38 | 120 | 1238.14 | 222 | 5978 | 16.4 | 355.42 | 910 | 0 | 0 | 27 | 546
06:30 | 2642 | 1296.75 | 876 | 38 | 116 | 1229.235 | 222 | 5980 | 45.215 | 309.21 | 909 | 0 | 0 | 29.5 | 568.5
07:00 | 2641 | 1321 | 876 | 38 | 112 | 1220.33 | 222 | 5982 | 74.03 | 263 | 908 | 0 | 0 | 32 | 591
07:30 | 2647 | 1273.5 | 875.5 | 38 | 117 | 1220.845 | 222 | 5887.5 | 156 | 256 | 908 | 0 | 0 | 21 | 563
08:00 | 2653 | 1226 | 875 | 38 | 122 | 1221.36 | 222 | 5793 | 237.97 | 249 | 908 | 0 | 0 | 10 | 535
08:30 | 2619 | 1222.5 | 875.5 | 38 | 123 | 1217.29 | 222 | 5728 | 282.32 | 249 | 895.5 | 0 | 0 | 13 | 523.5
09:00 | 2585 | 1219 | 876 | 38 | 124 | 1213.22 | 222 | 5663 | 326.67 | 249 | 883 | 0 | 0 | 16 | 512
09:30 | 2602 | 1251 | 876 | 38 | 123 | 1164.37 | 222 | 5701.5 | 401.95 | 216 | 855.5 | 0 | 0 | 21.5 | 607.5
10:00 | 2619 | 1283 | 876 | 38 | 122 | 1115.52 | 222 | 5740 | 477.23 | 183 | 828 | 0 | 0 | 27 | 703
10:30 | 2620 | 1293 | 876 | 38 | 130 | 1030.555 | 222 | 5775.5 | 411.2 | 191 | 928 | 0 | 0 | 27 | 768
11:00 | 2621 | 1303 | 876 | 38 | 138 | 945.59 | 222 | 5811 | 345.17 | 199 | 1028 | 0 | 0 | 27 | 833
11:30 | 2605.5 | 1297 | 874.5 | 38 | 139 | 955.985 | 222 | 5721 | 412.755 | 210 | 1281.1 | 0 | 0 | 18.5 | 1108.5
12:00 | 2590 | 1291 | 873 | 38 | 140 | 966.38 | 222 | 5631 | 480.34 | 221 | 1534.2 | 0 | 0 | 10 | 1384
12:30 | 2588 | 1289 | 873.5 | 38 | 143 | 958.595 | 222 | 5648 | 437.005 | 231.71 | 1638.55 | 0 | 0 | 11.5 | 1305.5
13:00 | 2586 | 1287 | 874 | 38 | 146 | 950.81 | 222 | 5665 | 393.67 | 242.42 | 1742.9 | 0 | 0 | 13 | 1227
13:30 | 2578.5 | 1255.5 | 874 | 38 | 150 | 1029.93 | 221 | 5628.5 | 449.76 | 250.92 | 1763.4 | 0 | 0 | 15 | 1289.5
14:00 | 2571 | 1224 | 874 | 38 | 154 | 1109.05 | 220 | 5592 | 505.85 | 259.42 | 1783.9 | 0 | 0 | 17 | 1352
14:30 | 2600.5 | 1252.5 | 873 | 38 | 156 | 1106.74 | 219.5 | 5599 | 446.025 | 269.42 | 1784.9 | 0 | 0 | 15 | 1339
15:00 | 2630 | 1281 | 872 | 38 | 158 | 1104.43 | 219 | 5606 | 386.2 | 279.42 | 1785.9 | 0 | 0 | 13 | 1326
15:30 | 2638 | 1292 | 871.5 | 38 | 159 | 1103.74 | 219.5 | 5608 | 313.305 | 279.71 | 1791.9 | 0 | 0 | 15.5 | 1183
16:00 | 2646 | 1303 | 871 | 38 | 160 | 1103.05 | 220 | 5610 | 240.41 | 280 | 1797.9 | 0 | 0 | 18 | 1040
16:30 | 2645 | 1292.5 | 871.5 | 38 | 154 | 1100.865 | 220.5 | 5575 | 185.895 | 280 | 1818.4 | 0 | 0 | 17.5 | 995.5
17:00 | 2644 | 1282 | 872 | 38 | 148 | 1098.68 | 221 | 5540 | 131.38 | 280 | 1838.9 | 0 | 0 | 17 | 951
17:30 | 2582.5 | 1264.5 | 871.5 | 38 | 145 | 1098.95 | 221 | 5440.5 | 85.85 | 337.5 | 1919.9 | 0 | 0 | 16.5 | 691.5
18:00 | 2521 | 1247 | 871 | 38 | 142 | 1099.22 | 221 | 5341 | 40.32 | 395 | 2000.9 | 0 | 0 | 16 | 432
18:30 | 2566.5 | 1270 | 871.5 | 38 | 149 | 1116.225 | 221.5 | 5426.5 | 20.16 | 536.71 | 2199.9 | 0 | 0 | 22 | 762.5
19:00 | 2612 | 1293 | 872 | 38 | 156 | 1133.23 | 222 | 5512 | 0 | 678.42 | 2398.9 | 0 | 0 | 28 | 1093
19:30 | 2629 | 1322 | 871 | 38 | 136 | 1160.48 | 222 | 5547 | 0 | 745.42 | 2543.9 | 0 | 0 | 30 | 1551
20:00 | 2624 | 1288 | 871 | 38 | 130 | 1207.25 | 222 | 5612 | 0 | 748.42 | 2565.26 | 0 | 0 | 27 | 1625
20:30 | 2596.5 | 1291 | 871.5 | 38 | 134 | 1257.425 | 222 | 5631.5 | 0 | 738.42 | 2504.26 | 173 | 0 | 27 | 1531
21:00 | 2569 | 1294 | 872 | 38 | 138 | 1307.6 | 222 | 5651 | 0 | 728.42 | 2443.26 | 346 | 0 | 27 | 1437
21:30 | 2546.5 | 1300.5 | 871.5 | 38 | 138 | 1306.67 | 222 | 5647 | 0 | 720.42 | 2435.01 | 346 | 0 | 21 | 1276.5
22:00 | 2524 | 1307 | 871 | 38 | 138 | 1305.74 | 222 | 5643 | 0 | 712.42 | 2426.76 | 346 | 0 | 15 | 1116
22:30 | 2510 | 1315 | 871.5 | 38 | 142 | 1307.305 | 222 | 5565 | 0 | 720.42 | 2367.58 | 345.5 | 0 | 18.5 | 1376
23:00 | 2496 | 1323 | 872 | 38 | 146 | 1308.87 | 222 | 5487 | 0 | 728.42 | 2308.4 | 345 | 0 | 22 | 1636
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 28-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 140 | 39 | 440 | 200 | 1832 | 724 | Ishurdi-Ghorashal Ckt-1 | Export | 3790400
1:00 | 129 | 38 | 384 | 172 | 1778 | 696
2:00 | 124 | 31 | 380 | 172 | 1756 | 672 |  | Import | 0
3:00 | 123 | 32 | 388 | 180 | 1764 | 672
4:00 | 128 | 30 | 410 | 162 | 1870 | 676 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 136 | 35 | 400 | 160 | 1952 | 690
6:00 | 138 | 45 | 388 | 152 | 1892 | 698 |  | Import | 0
7:00 | 124 | 39 | 354 | 152 | 1816 | 664
8:00 | 156 | 52 | 464 | 186 | 2020 | 790 | Sirajganj-Sreepur Ckt-1 | Export | 3094000
9:00 | 181 | 69 | 540 | 232 | 2096 | 848
10:00 | 195 | 89 | 536 | 244 | 2096 | 924 |  | Import | 0
11:00 | 164 | 80 | 494 | 274 | 1944 | 938
12:00 | 173 | 79 | 440 | 232 | 1960 | 878 | Sirajganj-Sreepur Ckt-2 | Export | 3102000
13:00 | 147 | 63 | 388 | 220 | 1872 | 800
14:00 | 189 | 86 | 502 | 232 | 1944 | 900 |  | Import | 0
15:00 | 167 | 68 | 450 | 234 | 1904 | 832
16:00 | 180 | 77 | 512 | 250 | 2058 | 886 | Gopalganj-Aminbazar Ckt-1 | Export | 22920000
17:00 | 176 | 74 | 496 | 252 | 1974 | 822
18:00 | 178 | 78 | 520 | 274 | 1958 | 816 |  | Import | 0
18:30 | 186 | 81 | 530 | 258 | 1936 | 794
19:00 | 177 | 72 | 532 | 280 | 1748 | 744 | Gopalganj-Aminbazar Ckt-2 | Export | 22960000
19:30 | 144 | 62 | 408 | 214 | 1682 | 674
20:00 | 146 | 59 | 418 | 204 | 1740 | 660 |  | Import | 0
21:00 | 160 | 58 | 484 | 232 | 1874 | 746
22:00 | 165 | 59 | 470 | 198 | 1872 | 740 |  | Total Export | 55866400
23:00 | 166 | 51 | 488 | 196 | 1882 | 666 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 28-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 359 | 18:00 | 345 | 11:00 | Madunaghat | 394 | 20:00 | 382 | 11:00
Amtali | 407 | 18:00 | 401 | 05:00 | Meghnaghat | 368 | 20:00 | 349 | 11:00
Ashuganj | 387 | 19:30 | 365 | 11:00 | Payra | 410 | 18:30 | 404 | 02:00
Bhulta | 375 | 06:00 | 352 | 11:00 | Rahanpur | 404 | 18:30 | 383 | 02:00
Bibiana | 373 | 19:30 | 364 | 04:00 | Rampal | 391 | 18:30 | 378 | 01:00
BIPTC | 400 | 09:00 | 393 | 20:00
Bogura | 386 | 18:30 | 360 | 02:00
Gopalganj | 381 | 18:30 | 370 | 01:00
Kaliakoir | 354 | 19:30 | 334 | 12:00
Korerhat | 389 | 20:00 | 371 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 219 | 20:00 | 206 | 11:00 | Ishurdi | 235 | 18:30 | 217 | 03:00
AKSML | 230 | 21:00 | 223 | 10:00 | Jhenaidah | 228 | 18:30 | 210 | 02:00
Aminbazar | 218 | 18:00 | 207 | 11:00 | Kachua | 225 | 20:00 | 212 | 10:00
Ashuganj | 218 | 20:00 | 207 | 11:00 | Kaliakoir | 217 | 19:30 | 204 | 12:00
Ashuganj-400 | 218 | 20:00 | 207 | 11:00 | Keranigonj | 217 | 20:00 | 204 | 11:00
Baghabari | 231 | 18:30 | 218 | 01:00 | Khulna(S) | 225 | 18:30 | 212 | 01:00
Barapukuria | 227 | 19:00 | 211 | 02:00 | Korerhat | 223 | 20:00 | 211 | 10:00
Barapukuria-230 | 227 | 19:00 | 212 | 3:00 | Madunaghat | 236 | 19:30 | 227 | 10:00
Barishal | 222 | 08:00 | 217 | 01:00 | Madunaghat-400 | 237 | 20:00 | 229 | 11:00
Bheramara | 233 | 18:30 | 215 | 02:00 | Maniknagar | 214 | 06:00 | 201 | 11:00
Bhulta | 216 | 06:00 | 203 | 11:00 | Meghnaghat | 222 | 20:00 | 210 | 11:00
Bibiana | 216 | 19:30 | 209 | 00:00 | Meghnaghat-400 | 219 | 20:00 | 207 | 11:00
BIPTC | 237 | 18:30 | 215 | 04:00 | Mirsorai | 227 | 20:00 | 216 | 10:00
Bogura | 242 | 18:30 | 224 | 02:00 | Naogaon | 229 | 18:30 | 205 | 03:00
Bogura-400 | 242 | 18:30 | 224 | 03:00 | Purbasadipur | 225 | 19:00 | 207 | 02:00
Borhanuddin | 227 | 05:00 | 223 | 00:00 | Rajshahi | 233 | 18:30 | 213 | 04:00
BSRM | 224 | 20:00 | 212 | 11:00 | Rampal | 223 | 18:30 | 212 | 02:00
Charfasson | 228 | 00:00 | 224 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 224 | 20:00 | 211 | 11:00 | Rampura | 216 | 06:00 | 201 | 11:00
Cumilla(N) | 216 | 20:00 | 205 | 11:00 | Shikalbaha | 237 | 20:00 | 229 | 10:00
Faridpur | 217 | 18:00 | 209 | 03:00 | Shyampur | 217 | 20:00 | 204 | 11:00
Fenchuganj | 216 | 19:30 | 209 | 03:00 | Siddhirganj | 217 | 06:00 | 204 | 11:00
Feni | 220 | 19:30 | 208 | 11:00 | Sirajgonj | 235 | 19:00 | 224 | 00:00
Ghorashal | 220 | 19:30 | 210 | 10:00 | Sreepur | 216 | 20:00 | 208 | 03:00
Ghorashal-230 | 203 | 20:00 | 193 | 10:00 | Tongi | 206 | 19:30 | 194 | 11:00
Gopalganj | 217 | 18:30 | 210 | 13:00
GPH | 228 | 23:00 | 221 | 10:00
Haripur | 216 | 07:00 | 204 | 11:00
Hasnabad | 218 | 20:00 | 212 | 22:00
Hathazari | 232 | 19:00 | 223 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 06:00 | 122 | 11:00 | Madartek | 133 | 07:00 | 122 | 11:00
Agargaon | 127 | 06:00 | 119 | 11:00 | Madunaghat | 137 | 18:30 | 131 | 11:00
Agrabad | 136 | 19:00 | 129 | 11:00 | Magura | 137 | 18:30 | 125 | 02:00
AKS | 133 | 19:00 | 128 | 10:00 | Mahasthangarh | 137 | 18:30 | 123 | 01:00
Aminbazar | 124 | 23:00 | 116 | 14:00 | Maijdee | 126 | 20:00 | 117 | 11:00
Amnura | 137 | 18:30 | 123 | 03:00 | Manikganj | 128 | 02:00 | 116 | 11:00
Ashuganj | 125 | 20:00 | 120 | 00:00 | Maniknagar | 125 | 05:00 | 114 | 11:00
Ashuganj-230 | 128 | 19:30 | 123 | 11:00 | Matarbari | 129 | 19:00 | 118 | 00:00
Bagerhat | 126 | 18:30 | 118 | 01:00 | Matuail | 130 | 20:00 | 122 | 11:00
Bajitpur | 120 | 20:00 | 116 | 01:00 | Metrorail_Motijheel | 125 | 05:00 | 114 | 11:00
Bakerganj | 130 | 18:00 | 126 | 00:00 | Metrorail_Uttara | 123 | 18:30 | 115 | 10:00
Bakulia | 137 | 19:00 | 130 | 10:00 | Millgate | 124 | 18:00 | 116 | 11:00
Banani | 134 | 05:00 | 122 | 11:00 | Mirpur | 125 | 20:00 | 116 | 11:00
Bangabhaban | 125 | 07:00 | 114 | 11:00 | Mirzapur | 128 | 20:00 | 118 | 10:00
Barapukuria | 138 | 19:00 | 123 | 02:00 | Mithapukur | 135 | 19:00 | 119 | 02:00
Barguna | 129 | 07:00 | 125 | 00:00 | MI_Cement | 127 | 06:00 | 117 | 11:00
Barishal | 129 | 07:00 | 125 | 15:00 | Modern | N/A | N/A | N/A | N/A
Barishal-230 | 129 | 08:00 | 126 | 00:00 | Mogbazar | 136 | 04:00 | 123 | 13:00
Baroaulia | 135 | 19:00 | 129 | 11:00 | Mongla | 125 | 18:00 | 118 | 22:00
Baroirhat | 129 | 20:00 | 124 | 00:00 | Motijheel | 125 | 07:00 | 114 | 11:00
Bashundhara | 135 | 08:00 | 115 | 11:00 | Muktagacha | 126 | 10:00 | 112 | 02:00
BashundharaCement | 129 | 20:00 | 122 | 12:00 | Munshiganj | 129 | 19:30 | 121 | 10:00
Beanibazar | 121 | 20:00 | 112 | 18:30 | Muradnagar | 122 | 20:00 | 115 | 11:00
Benapole | 136 | 18:30 | 117 | 07:00 | Mymensingh | 129 | 19:00 | 106 | 18:00
Bhaluka | 121 | 07:00 | 115 | 18:00 | Nabinagar | 121 | 20:00 | 113 | 10:00
Bhandaria | 126 | 17:00 | 120 | 00:00 | Naogaon | 138 | 19:00 | 123 | 04:00
Bhangura | 132 | 18:30 | 124 | 03:00 | Narail | 136 | 09:00 | 121 | 00:00
Bheramara | 135 | 18:00 | 126 | 02:00 | Narinda | 125 | 5:00 | 114 | 11:00
Bheramara(GK) | 137 | 18:30 | 126 | 02:00 | Narshingdi | 120 | 20:00 | 112 | 14:00
Bhulta | 125 | 19:00 | 123 | 08:00 | Natore | 137 | 18:30 | 123 | 03:00
Bhulta-400 | 126 | 06:00 | 119 | 11:00 | Nawabganj | 130 | 20:00 | 123 | 11:00
Bog-Sherpur | 136 | 18:00 | 125 | 02:00 | Netrakona | 113 | 07:00 | 104 | 18:30
Bogura | 140 | 18:30 | 128 | 04:00 | New | 125 | 08:00 | 116 | 12:00
Bogura-230 | 140 | 18:30 | 127 | 02:00 | Niamatpur | 133 | 11:00 | 125 | 02:00
Brahmanbaria | 121 | 20:00 | 115 | 11:00 | Noapara | 131 | 18:30 | 123 | 00:00
Cantonment | 127 | 04:00 | 118 | 11:00 | Pabna | 134 | 18:00 | 124 | 03:00
Chandina | 126 | 20:00 | 117 | 11:00 | Palashbari | 133 | 19:00 | 120 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandpur | 133 | 20:00 | 120 | 11:00 | Panchagarh | 142 | 19:00 | 129 | 02:00
Chandraghona | 137 | 20:00 | 132 | 10:00 | Patiya | 136 | 18:30 | 129 | 10:00
Chapai | 133 | 19:00 | 123 | 02:00 | Patnitala | 135 | 19:00 | 119 | 03:00
Charsaidpur | 130 | 19:30 | 122 | 10:00 | Patuakhali | 130 | 18:00 | 126 | 01:00
Chauddagram | 127 | 19:30 | 119 | 10:00 | Payra | 134 | 18:30 | 131 | 00:00
Chhatak | 118 | 07:00 | 110 | 11:00 | PHP | 129 | 19:30 | 122 | 11:00
Chowmuhani | 126 | 20:00 | 118 | 11:00 | Postogola | 128 | 06:00 | 120 | 11:00
Chuadanga | 134 | 18:30 | 123 | 02:00 | Pubail | 123 | 04:00 | 111 | 14:00
Coxsbazar | 131 | 19:00 | 118 | 11:00 | Purbachal | 134 | 05:00 | 121 | 13:00
Cumilla(N) | 125 | 20:00 | 118 | 11:00 | Purbasadipur | 137 | 19:30 | 125 | 02:00
Cumilla(S) | 128 | 05:00 | 120 | 10:00 | Rahanpur | 135 | 18:30 | 130 | 00:00
Daganbhuiyan | 128 | 20:00 | 119 | 11:00 | Rahanpur-400 | 136 | 19:00 | 128 | 02:00
Daudkandi | 120 | 19:30 | 114 | 10:00 | Rahim | 130 | 19:30 | 122 | 11:00
DhakaUniversity | 134 | 05:00 | 122 | 11:00 | Rajbari | 122 | 18:00 | 117 | 03:00
Dhamrai | 123 | 20:00 | 113 | 11:00 | Rajendrapur | 120 | 19:30 | 115 | 02:00
Dhanmondi | 135 | 07:00 | 123 | 11:00 | Rajshahi | 134 | 18:30 | 126 | 00:00
Dohazari | 135 | 19:00 | 125 | 11:00 | Rajshahi-230 | 134 | 18:30 | 123 | 04:00
Faridpur | 125 | 08:00 | 121 | 02:00 | Ramganj | 127 | 20:00 | 117 | 11:00
Fatullah | 130 | 20:00 | 118 | 11:00 | Rampur | 135 | 19:00 | 128 | 10:00
Fenchuganj | 127 | 19:30 | 122 | 11:00 | Rampura | 134 | 06:00 | 122 | 11:00
Feni | 129 | 19:30 | 122 | 02:00 | Rangamati | 136 | 20:00 | 131 | 10:00
Feni-230 | 128 | 19:30 | 120 | 11:00 | Rangpur | 133 | 16:00 | 118 | 01:00
Ghatail | 122 | 13:00 | 112 | 01:00 | Ruppur | 137 | 18:00 | 1.4 | 04:00
Ghorashal | 122 | 19:30 | 116 | 11:00 | Saidpur | 136 | 19:00 | 122 | 02:00
Goalpara | 133 | 18:00 | 126 | 00:00 | Santhia | 134 | 18:30 | 128 | 00:00
Gollamari | 134 | 18:30 | 125 | 02:00 | Satkhira | 131 | 18:30 | 120 | 00:00
Gopalganj | 128 | 18:00 | 121 | 01:00 | Satmasjid | 127 | 20:00 | 118 | 13:00
Gopalganj-400 | 129 | 18:30 | 124 | 01:00 | Savar | 126 | 19:30 | 115 | 11:00
Gulshan | 134 | 06:00 | 122 | 11:00 | SevenRings | 122 | 06:00 | 115 | 10:00
Halishahar | 135 | 19:00 | 129 | 10:00 | ShahCement | 130 | 19:30 | 122 | 10:00
Haripur | 130 | 19:30 | 121 | 12:00 | Shahjadpur | 135 | 18:00 | 130 | 00:00
HaripurSBU | 130 | 19:30 | 122 | 12:00 | Shahjibazar | 123 | 19:30 | 115 | 00:00
Hasnabad | 129 | 21:00 | 120 | 11:00 | Shahmirpur | 136 | 22:00 | 132 | 06:00
Hathazari | 136 | 19:00 | 131 | 11:00 | Shariatpur | 130 | 00:00 | 122 | 01:00
Hatirjheel | 134 | 06:00 | 122 | 11:00 | Sherpur | 126 | 19:30 | 110 | 00:00
Ishurdi | 139 | 18:30 | 128 | 02:00 | Shikalbaha | 126 | 19:30 | 120 | 11:00
Jaldhaka | 134 | 17:00 | 120 | 02:00 | Shikalbaha-230 | 138 | 19:00 | 133 | 10:00
Jamalpur | 132 | 10:00 | 114 | 00:00 | Shitalakhya | 127 | 06:00 | 117 | 11:00
Jashore | 137 | 18:00 | 119 | 08:00 | Sholosohor | 136 | 20:00 | 130 | 11:00
Jhenaidah | 138 | 18:00 | 122 | 21:00 | Shomvuganj | 118 | 23:00 | 109 | 02:00
Jhenaidah-230 | 140 | 18:30 | 128 | 02:00 | Shyampur | 129 | 20:00 | 119 | 11:00
Joydebpur | 120 | 00:00 | 109 | 14:00 | Shyampur-230 | 130 | 20:00 | 121 | 12:00
Joypurhat | 136 | 19:00 | 121 | 02:00 | Siddhirganj | 130 | 20:00 | 122 | 11:00
Juldah | 136 | 19:00 | 130 | 10:00 | Sirajganj | 132 | 18:00 | 122 | 00:00
Kabirpur | 132 | 19:30 | 114 | 10:00 | Sitakunda | 135 | 19:30 | 129 | 10:00
Kachua | 128 | 18:30 | 119 | 11:00 | Sonargaon | 127 | 19:30 | 120 | 10:00
Kaliakoir | 132 | 19:30 | 118 | 11:00 | Sreemongol | 124 | 19:30 | 116 | 00:00
Kaliganj | 138 | 18:30 | 128 | 00:00 | Sreepur | 124 | 20:00 | 119 | 03:00
Kallyanpur | 123 | 23:00 | 115 | 13:00 | Srinagar | 131 | 20:00 | 123 | 11:00
Kalurghat | 136 | 19:00 | 131 | 10:00 | SSM | 140 | 00:00 | 132 | 10:00
Kamrangirchar | 130 | 05:00 | 113 | 11:00 | Sunamganj | 116 | 20:00 | 109 | 11:00
Kaptai | 138 | 19:00 | 135 | 10:00 | Sylhet | 123 | 19:30 | 117 | 11:00
Kasba | 121 | 19:30 | 114 | 11:00 | Sylhet_(South) | 123 | 19:30 | 117 | 00:00
Kazla | 125 | 06:00 | 113 | 13:00 | Tangail | 124 | 20:00 | 115 | 02:00
Keranigonj | 131 | 20:00 | 123 | 11:00 | Taraganj | 134 | 18:30 | 121 | 03:00
Khagrachori | 134 | 20:00 | 131 | 00:00 | Tasnim | 128 | 19:30 | 120 | 10:00
Khulna | 132 | 18:00 | 125 | 00:00 | Thakurgaon | 141 | 14:00 | 128 | 02:00
Khulna(S) | 134 | 18:30 | 125 | 02:00 | TK | 136 | 00:00 | 133 | 05:00
Khulshi | 134 | 19:00 | 127 | 11:00 | Tongi | 126 | 19:30 | 118 | 11:00
Kishoreganj | 118 | 08:00 | 111 | 18:00 | Ullahpara | 133 | 18:30 | 124 | 02:00
Kodda | 131 | 19:30 | 110 | 13:00 | Ullon | 133 | 04:00 | 123 | 11:00
Korerhat | 131 | 19:30 | 125 | 10:00 | Uttara | 124 | 23:00 | 113 | 14:00
KSRM | 136 | 23:00 | 130 | 11:00 | UttaraNew | 123 | 18:30 | 115 | 10:00
Kulaura | 127 | 19:30 | 121 | 01:00 | Zigatola | 130 | 06:00 | 123 | 11:00
Kurigram | 131 | 16:00 | 116 | 03:00
Kushtia | 131 | 18:00 | 121 | 02:00
Laksam | 127 | 19:00 | 119 | 11:00
Lakshmipur | 125 | 20:00 | 116 | 11:00
Lalbag | 130 | 20:00 | 122 | 11:00
Lalmonirhat | 130 | 17:00 | 120 | 04:00
Madanganj | 129 | 20:00 | 122 | 12:00
Madaripur | 128 | 18:00 | 125 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division