## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: June 2026
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2026-06-01 |  | 2026-05-01 |  | 2025-06-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 16193.27 | 2026-06-25 | 17200.79 | 2026-05-20 | 15691.42 | 2025-06-21 | 17200.79 | 2026-05-20
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr.
2 | Minimum Generation (MW) | 11665.13 | 2026-06-19 | 5755.52 | 2026-05-27 | 8827.15 | 2025-06-03 | - | -
|  |  | 10:00 Hr. |  | 09:00 Hr. |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 16193.27 | 2026-06-25 | 17200.79 | 2026-05-20 | 16365.8 | 2025-06-24 | 17200.79 | 2026-05-20
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 05:00 Hr. |  | 21:00 Hr.
4 | Maximum Day Peak Generation (MW) | 14920 | 2026-06-30 | 15418.78 | 2026-05-20 | 14156.82 | 2025-06-24 | 15418.78 | 2026-05-20
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 Hr.
5 | Maximum Evening Peak Demand (MW) Estimated | 18354.59 | 2026-06-28 | 17610.79 | 2026-05-20 | 15720.68 | 21:00 Hr. | 18354.59 | 2026-06-28
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr.
6 | Average Generation (MW) at Evening Peak | 15362.4037 |  | 14127.9116 |  | 14578.408 |  | - | -
7 | Average Generation (MW) at Day Peak | 14030.2117 |  | 12425.1735 |  | 12594.8343 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 976 | 2026-06-15 | 940 | 2026-05-04 | 981 | 2025-06-20 | 980 | 2026-02-20
|  |  | 9:30 |  | 10:40 |  | 2:00 |  | 0:30
9 | Maximum Power Import from Tripura, India (MW) | 194 | 2026-06-23 | 189 | 2026-05-19 | 55 | 2025-06-15 | 213 | 4/22/26
|  |  | 19:00 |  | 19:00 |  | 21:15 |  | 16:00
10 | Maximum Load Shed (MW) at Evening Peak | 2874 | 2026-06-27 | 674 | 2026-05-21 | 110 | 2025-06-13 | 4395 | 04/10/2022
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 15298.25 | 2026-06-27 | 16531.26 | 2026-05-21 | 15175.2 | 2025-06-13 | 16531.26 | 2026-05-21
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00 Hr.
12 | Minimum Load Shed (MW) at Evening Peak | 44 | 2026-06-21 | 5 | 2026-05-26 | 0 | 2025-06-01 | - | -
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 14649.64 | 2026-06-21 | 11164.63 | 2026-05-26 | 13631.03 | 2025-06-01 | - | -
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 2620 | 2026-06-21 | 449 | 2026-05-23 | 39 | 2025-06-20 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 14398.75 | 2026-06-21 | 14442.69 | 2026-05-23 | 11715.34 | 2025-06-20 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 9 | 2026-06-10 | 30 | 2026-05-11 | 0 | 2025-06-01 | - | -
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 13966.46 | 2026-06-10 | 13848.62 | 2026-05-11 | 12880.09 | 2025-06-01 | - | -
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 30 |  | 24 |  | 14 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 29 |  | 18 |  | 2 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 995.0699 |  | 932.8558 |  | 1336.914 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 20.0516 |  | 19.0718 |  | 51.8734 |  | - | -
22 | Net Generation of BPDB (MKWH) | 975.0183 |  | 913.784 |  | 1285.0406 |  | - | -
23 | Net Generation of IPP (MKWH) | 2617.3181 |  | 2521.7942 |  | 3779.248 |  | - | -
23b | Net Generation by Generation Companies | 4739.8645 |  | 4303.233 |  | 2803.8877
24 | Net Generation of REB (MKWH) | 53.7875 |  | 45.2413 |  | 39.5405 |  | - | -
25 | Net Generation of Rental Power Plant (MKWH) | 82.2671 |  | 85.8564 |  | 113.4342 |  | - | -
26 | Total Net Generation (MKHWh) (Excluding Import) | 8468.2556 |  | 7869.909 |  | 8021.151 |  | - | -
27 | Energy Generation by Gas (MKWH) | 3745.8602 |  | 3935.5908 |  | 4276.4107 |  | - | -
28 | Energy Generation by Diesel (MKWH) | 3.465 |  | 3.6008 |  | 0.026 |  | - | -
29 | Energy Generation by Furnace Oil (MKWH) | 1014.0995 |  | 615.5792 |  | 925.4855 |  | - | -
30 | Energy Generation by Hydro (MKWH) | 54.5607 |  | 37.396 |  | 119.0818 |  | - | -
31 | Energy Generation by Solar (MKWH) | 114.6082 |  | 123.8147 |  | 111.712 |  | 149.04 | 2026-04-25
31b | Energy Generation by Wind (MKWH) | 5.5723 |  | 6.8957 |  | 14.0246 |  | - | -
32 | Energy Generation by Coal (MKWH) | 3550.1413 |  | 3166.1036 |  | 2626.2838 |  | 3166.1036
33 | Enegry Import from India (MKWH) | 1755.2156 |  | 1528.8924 |  | 1378.3078 |  | - | -
34 | Monthly Load Factor (%) | 87.8696 |  | 73.5922 |  | 83.6562 |  | 86.52 | 2026-09-25

## QF-LDC-22
QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: June 2026
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 16193.27 | 2026-06-25 | 21:00 Hr.
Generation Period
| Dhaka | MW | 5834.79
| Chattogram | MW | 1523
| Cumilla | MW | 1555
| Mymensingh | MW | 1152
| Sylhet | MW | 635
a) | Total supply in East zone | MW | 10699.79
| Khulna | MW | 1788
| Barisal | MW | 488
| Rajshahi | MW | 1606.4
| Rangpur | MW | 1063
b) | Total supply in West zone | MW | 4945.4
c) | Total supply in both zone ( a+b) | MW | 15645.19
Ref: | 27.21.0000.603.16.087.20.983 | Date: 15/07/2026
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month: June 2026
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Maximum power Export through EWI/ NO-1
| a) Ishurdi end | AMPS | 597 | 2026-06-06 | 14:00
|  | MW | 242
| b) Ghorashal end | AMPS | 0
|  | MW | 0
18 | Maximum power Import through EWI/ NO-1 |  |  | -
| a) Ishurdi end | AMPS | 0
|  | MW | 0
| b) Ghorashal end | AMPS | 600 | 2026-06-06 | 14:00
|  | MW | 232
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ishurdi end | MWh | 4280.509 | 2026-06-16 | N/A
| b) Ghorashal end | MWh | 0
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 0
| b) Ghorashal end | MWh | 4186.578 | 2026-06-16 | N/A
21 | Total Energy Export through EWI/ NO-1
| a) Ishurdi end | MWh | 112273.4564
| b) Ghorashal end | MWh | 0
22 | Total Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 0
| b) Ghorashal end | MWh | 108905.2527
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Maximum power Export through EWI/ NO-2
| a) Sirajganj end | AMPS | 1860 | 2026-06-11
|  | MW | 730
| b) Sreepur end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
25 | Maximum power Import through EWI/ NO-2 |  | - | -
| a) Sirajganj end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
| b) Sreepur end | AMPS | 0 |  | -
|  | MW | 0
26 | Daily Maximum Energy Export through EWI/NO-2
| a) Sirajganj end | MWh | 7346 | 2026-06-16 | -
| b) Sreepur end | MWh |  | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Sirajganj end | MWh | 0 | - | -
| b) Sreepur end | MWh | 0 | - | -
28 | Total Energy Export through EWI/ NO-2
| a) Sirajganj end | MWh | 365112 | - | -
| b) Sreepur end | MWh | 0 | - | -
29 | Total Energy Import through EWI/ NO-2
| a) Sirajganj end | MWh | 0 | - | -
| b) Sreepur end | MWh | 353753.9 | - | -
30 | Transmission loss of EWI/ NO-2 | % | 3.11 | - | -
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 4054 | 2026-06-19 | 6:00
|  | MW | 2140
| b) Aminbazar end | AMPS | 0
|  | MW | 0
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | 0
|  | MW | 0
| b) Aminbazar end | AMPS | 4040 | 2026-06-19 | 6:00
|  | MW | 2139
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 47210 | 2026-06-26 | N/A
| a) Aminbazar end | MWh | 0
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0 | - | N/A
| a) Aminbazar end | MWh | 47042 | 2026-06-26
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 1220880
| b) Aminbazar end (ckt-1 ) | MWh | 0
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0
| b) Aminbazar end (ckt-2 ) | MWh | 1215843
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.413
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: June 2026
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH) |  |  | #REF!
Dhaka (North) Grid Circle : | [10 empty] | #REF!
Bajitpur 132/33kV | Tr-2(414T) | 2026-06-04 10:45 | 2026-06-04 11:40 | 0.038194 | T | OIL SURGED Trip Closed Blocked Signal show | 24 | 22 | Power interruption |  | #REF!
Bhaluka 132/33kV | 01. Transformer- 01 | 2026-06-03 14:24 | 2026-06-03 14:30 | 0.0041667 | T | Tripped | 59 | 5.9 | Power interruption |  | #REF!
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-06-03 14:24 | 2026-06-03 14:30 | 0.0041667 | T | Tripped | 59 | 5.9 | Power interruption |  | #REF!
Bhaluka 132/33kV | 01. Transformer- 01 | 2026-06-13 07:56 | 2026-06-13 08:30 | 0.023611 | T | Tripped | 50 | 28.3333 | Power interruption |  | #REF!
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-06-13 07:56 | 2026-06-13 08:30 | 0.023611 | T | Fault at 33kV PBS. | 50 | 28.3333 | Power interruption |  | #REF!
Bhaluka 132/33kV | 01. Transformer- 01 | 2026-06-21 18:19 | 2026-06-21 18:24 | 0.0034722 | T | BR Power plant trip. | 60 | 5 | Power interruption |  | #REF!
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-06-21 18:19 | 2026-06-21 18:24 | 0.0034722 | T | BR power plant trip. | 60 | 5 | Power interruption |  | #REF!
Bhaluka 132/33kV | 03. Transformer-03 | 2026-06-21 18:19 | 2026-06-21 18:24 | 0.0034722 | T | BR Power plant trip. | 19 | 1.5833 | Power interruption
Bhaluka 132/33kV | 01. Transformer- 01 | 2026-06-23 15:10 | 2026-06-23 15:17 | 0.0048611 | T | Fault at BR Powergen end | 59 | 6.8833 | Power interruption |  | #REF!
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-06-23 15:10 | 2026-06-23 15:17 | 0.0048611 | T | Fault at BR Powergen end. | 59 | 6.8833 | Power interruption |  | #REF!
Bhaluka 132/33kV | 01. Transformer- 01 | 2026-06-25 22:23 | 2026-06-25 22:32 | 0.00625 | T | Tripped | 53 | 7.95 | Power interruption
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-06-25 22:23 | 2026-06-25 22:32 | 0.00625 | T | Tripped | 53 | 7.95 | Power interruption
Bhaluka 132/33kV | 03. Transformer-03 | 2026-06-25 22:23 | 2026-06-25 22:32 | 0.00625 | T | Tripped | 17 | 2.55 | Power interruption
Dhamrai 132/33kV | Transformer-1 | 2026-06-25 08:22 | 2026-06-25 08:51 | 0.020139 | T | Pbs 33 kv feeder fault (over current) | 40 | 19.3333 | Power interruption
Dhamrai 132/33kV | Transformer-2 | 2026-06-25 08:22 | 2026-06-25 08:51 | 0.020139 | T | Pbs 33 kv feeder fault (over current) | 40 | 19.3333 | Power interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2026-06-07 17:54 | 2026-06-07 18:59 | 0.045139 | T | 33 kV ffder fault | 40 | 43.3333 | Power interruption
Kishoreganj 132/33kV | Tr-2 (414T) | 2026-06-07 17:54 | 2026-06-07 18:59 | 0.045139 | T | 33 kV ffder fault | 40 | 43.3333 | Power interruption
Nabinagar 132/33kV | T-1 | 2026-06-16 13:49 | 2026-06-16 22:55 | 0.37917 | T | T-1 PRD Trip due to rain water entered into the PRD Terminal box | 0 | 0 | No interruption
Nabinagar 132/33kV | T-1 | 2026-06-30 00:27 | 2026-06-30 00:30 | 0.0020833 | T | Tripped | 0 | 0 | No interruption
Tangail 132/33kV | Tr-2 | 2026-06-11 18:56 | 2026-06-12 10:38 | 0.65417 | T | 132 Kv LA Blast. | 30 | 471 | Power interruption
Aminbazar 400/230/132kV | 230/132kv Tr-03 | 2026-06-30 19:54 | 2026-06-30 21:21 | 0.060417 | E/O | Red Hot removed works | 0 | 0 | No interruption
Bajitpur 132/33kV | 132 kV Bus-2 | 2026-06-23 11:03 | 2026-06-23 11:03 | 0 | E/O | Emergency maint.work | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-2 (414T) | 2026-06-24 19:26 | 2026-06-25 11:36 | 0.67361 | E/O | T-2 transformer 33 kv side PT oill leakage | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-1 (404T) | 2026-06-28 11:09 | 2026-06-28 13:25 | 0.094444 | E/O | BPDB 33/11 kv transformer installation work. | 0 | 0 | No interruption
New Tongi | T1(403T) | 2026-06-19 05:42 | 2026-06-19 15:14 | 0.39722 | E/O | Tripping | 0 | 0 | No interruption
Tangail 132/33kV | Tr-2 | 2026-06-11 22:02 | 2026-06-12 10:56 | 0.5375 | E/O | LA Replacement Work | 0 | 0 | No interruption
Tangail 132/33kV | Tr-2 | 2026-06-18 11:15 | 2026-06-18 11:47 | 0.022222 | E/O | Removal rope of Kite | 0 | 0 | No interruption
Shomvuganj 400/132kV | Transformer-3 ( TR-3) | 2026-06-06 15:43 | 2026-06-06 16:20 | 0.025694 | E/O | Oil Leakage | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 02:38 |  | Unserved Energy: |  | 730.6
Dhaka (South) Grid Circle :
Munshiganj 132/33kV | Transformer-1 | 2026-06-26 15:22 | 2026-06-26 15:33 | 0.0076389 | T | ROCOF Trip | 53 | 9.7167 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2026-06-26 15:22 | 2026-06-26 15:33 | 0.0076389 | T | ROCOF trip | 53 | 9.7167 | Power interruption
Narshingdi 132/33kV | T-2 | 2026-06-21 17:56 | 2026-06-21 18:22 | 0.018056 | T | Over current | 45 | 19.5 | Power interruption
Nawabganj 132/33kV | TR-2 | 2026-06-06 16:05 | 2026-06-06 16:16 | 0.0076389 | T | 33kv incomer-02 tripped due to baruakhali feeder fault. | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-2 | 2026-06-18 07:24 | 2026-06-18 07:35 | 0.0076389 | T | Tripped | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-1 | 2026-06-06 06:58 | 2026-06-06 07:14 | 0.011111 | T | pbs 33kv side Everest Feeder trip due to isolator jumper blast | 30 | 8 | Power interruption
Madanganj 132/33kV | BUS Coupler | 2026-06-20 16:10 | 2026-06-20 17:48 | 0.068056 | E/O | 132 kv Haripur ckt-1 R phase Reserve Bus DS Finger Maintenance work | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-1 | 2026-06-05 20:37 | 2026-06-05 23:03 | 0.10139 | E/O | Red Hot 33 kV ACB Breaker Y-Phase Pole | 0 | 0 | No interruption
|  |  | Total : | 0.22917 |  | Unserved Energy: |  | 46.9333
Chattogram Grid Circle :
Dohazari 132/33kV | Power Transformer -T-2 | 2026-06-09 13:41 | 2026-06-09 14:02 | 0.014583 | T | Due to Sikalbaha 230 KV Transformer Trip | 58 | 20.3 | Power interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2026-06-14 05:56 | 2026-06-14 06:40 | 0.030556 | T | Due to PDB 33kV Feeder-3 ( PDB grid incomer-3) Showing Earth fault & Over current trip. | 10 | 7.3333 | Power interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2026-06-27 09:56 | 2026-06-27 12:20 | 0.1 | T | BPDB maintenance | 10 | 24 | Power interruption
Khagrachori 132/33kV | TR-1 | 2026-06-10 00:57 | 2026-06-10 01:13 | 0.011111 | T | Due to crackdown of Panchari 33 kV bus DS insulator. | 11 | 2.9333 | Power interruption
Khagrachori 132/33kV | TR-2 | 2026-06-10 00:57 | 2026-06-10 01:13 | 0.011111 | T | Due to crackdown of Panchari 33 kV bus DS insulator. | 11 | 2.9333 | Power interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-06-14 16:08 | 2026-06-14 16:23 | 0.010417 | T | 33kv TCS fault test | 0 | 0 | No interruption
Shikalbaha 230/132kV | ATR 02 | 2026-06-09 13:40 | 2026-06-09 13:41 | 0.00069444 | T | DC MCB trip. | 0 | 0 | No interruption
Baroaulia 132/33kV | T2(415T) | 2026-06-04 06:22 | 2026-06-04 08:26 | 0.086111 | E/O | Redhot maintanance CB & Line Isolator at Y-phase | 0 | 0 | No interruption
Chandraghona 132/33kV | TR-01(406T) | 2026-06-01 16:49 | 2026-06-01 17:53 | 0.044444 | E/O | Emergency maint.work | 25 | 26.6667 | Power interruption
Chandraghona 132/33kV | TR-02(416T) | 2026-06-02 10:30 | 2026-06-02 13:51 | 0.13958 | E/O | LT bushing melting | 0 | 0 | No interruption
Coxsbazar 132/33kV | T3 | 2026-06-07 13:57 | 2026-06-07 16:10 | 0.092361 | E/O | 33kv incomer fire | 70 | 155.1667 | Power interruption
Madunaghat 132/33kV | TR-2(517T) | 2026-06-01 13:41 | 2026-06-01 17:58 | 0.17847 | E/O | Emergency high temperature maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-2(517T) | 2026-06-27 10:03 | 2026-06-27 16:25 | 0.26528 | E/O | 33 kV grounding recovery and high temperature maintenance. | 0 | 0 | No interruption
|  |  | Total : | 0.98472 |  | Unserved Energy: |  | 239.3333
Cumilla Grid Circle :
Bibiana 400/230kV | ICT-01 | 2026-06-27 01:04 | 2026-06-27 01:04 | 0 | T | Tripped | 0 | 0 | No interruption
Bibiana 400/230kV | ICT-02 | 2026-06-27 01:46 | 2026-06-27 04:35 | 0.11736 | T | Tripped | 0 | 0 | No interruption
Brahmanbaria 132/33kV | 401T | 2026-06-12 17:33 | 2026-06-12 19:58 | 0.10069 | T | Tripped | 50 | 120.8333 | Power interruption
Chowmuhani 230/132/33kV | TR1-415T | 2026-06-12 14:08 | 2026-06-12 14:13 | 0.0034722 | T | Beg-2 33 kv feeder E/F, O/C tripped. | 54 | 4.5 | Power interruption
Chowmuhani 230/132/33kV | TR1-415T | 2026-06-12 21:09 | 2026-06-12 21:16 | 0.0048611 | T | 33 kV feeder Beg-2 O/C, E/F . | 40 | 4.6667 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2026-06-16 06:05 | 2026-06-16 06:23 | 0.0125 | T | PDB Donaitori feeder fault | 43 | 12.9 | Power interruption
Cumilla(S) 132/33kV | TR-4 | 2026-06-16 06:05 | 2026-06-16 06:23 | 0.0125 | T | same as Tr-03 | 42 | 12.6 | Power interruption
Daganbhuiyan 132/33kV | Transformer-2 | 2026-06-09 22:45 | 2026-06-10 18:24 | 0.81875 | T | PBS 33KV side B phase PT Broken & R phase conductor Broken | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) | 2026-06-03 16:24 | 2026-06-03 17:27 | 0.04375 | T | REB-1 33KV feeder CT blust | 58 | 60.9 | Power interruption
Feni 132/33kV | T-1(405T) | 2026-06-05 13:24 | 2026-06-05 14:21 | 0.039583 | T | Heavy rain. | 34 | 32.3 | Power interruption
Ramganj 132/33kV | Transformer-01 | 2026-06-30 20:26 | 2026-06-30 20:45 | 0.013194 | T | PBS 5 no feeder CT brust | 54 | 17.1 | Power interruption
Ramganj 132/33kV | Transformer -02 | 2026-06-30 20:26 | 2026-06-30 20:45 | 0.013194 | T | PBS 5no feeder CT brust | 54 | 17.1 | Power interruption
Shahjibazar 132/33kV | TR-06 | 2026-06-17 06:45 | 2026-06-17 06:59 | 0.0097222 | T | Bisic and Lakhai Feeder Trip | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-3 | 2026-06-01 11:18 | 2026-06-01 11:41 | 0.015972 | T | 33KV bus coupler fault | 11.5 | 4.4083 | Power interruption
Sreemongol 132/33kV | 132/33kv T-2 | 2026-06-01 11:18 | 2026-06-01 11:43 | 0.017361 | T | 132KV bus coupler fault | 11.5 | 4.7917 | Power interruption
Sylhet 132/33kV | T2 | 2026-06-24 08:17 | 2026-06-24 09:03 | 0.031944 | T | Tripped | 61 | 46.7667 | Power interruption
Sylhet_(South) 132/33kV | Trafo-1 | 2026-06-27 21:14 | 2026-06-27 21:19 | 0.0034722 | T | 33 kv Moglabazar feeder breaker insulator crack. and 33 kv gotatikor feeder fault. | 20.5 | 1.7083 | Power interruption
Sylhet_(South) 132/33kV | Trafo-2 | 2026-06-27 21:14 | 2026-06-27 21:19 | 0.0034722 | T | 33 kv Moglabazar feeder breaker insulator crack. and 33 kv gotatikor feeder fault. | 20.5 | 1.7083 | Power interruption
Chowmuhani 230/132/33kV | TR1-415T | 2026-06-05 22:55 | 2026-06-05 23:54 | 0.040972 | E/O | 33kV BUS Loop Redhot | 50 | 49.1667 | Power interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-06-06 10:58 | 2026-06-06 12:30 | 0.063889 | E/O | For 33kV LPBS-1 Feeder BUS Loop Maintenance. | 20 | 30.6667 | Power interruption
Chowmuhani 230/132/33kV | TR1-415T | 2026-06-07 08:40 | 2026-06-07 09:47 | 0.046528 | E/O | 33 KV Maijdee Feeder Raising Loop Red Hot Maintanence | 40 | 44.6667 | Power interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-06-08 14:55 | 2026-06-08 17:57 | 0.12639 | E/O | TR-03 transformer 33kV VCB R Phase Red-hot Maintenance. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | TR2-425T | 2026-06-12 22:22 | 2026-06-13 00:55 | 0.10625 | E/O | 33 KV L-Bus Red Hot Maintenance | 20 | 51 | Power interruption
Chowmuhani 230/132/33kV | TR1-415T | 2026-06-25 23:47 | 2026-06-26 01:05 | 0.054167 | E/O | Maijdee PDB red hot maintenance | 70 | 91 | Power interruption
Daganbhuiyan 132/33kV | Transformer-2 | 2026-06-11 12:40 | 2026-06-11 13:31 | 0.035417 | E/O | Tr-02 33 kv load side Earth Resistence test | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2026-06-22 15:44 | 2026-06-22 17:27 | 0.071528 | E/O | shutdown for Red Hot Maintenance | 0 | 0 | No interruption
Maijdee 132/33kV | Tr-02 | 2026-06-04 02:50 | 2026-06-04 03:30 | 0.027778 | E/O | Transformer-2 , 33kv Secendary shutdown is required from due to Read Hot Maintenence 33 kV bus source side of BREB. Noakhali Palli Bidyut Samity will carry out the work. | 0 | 0 | No interruption
Ramganj 132/33kV | Transformer -02 | 2026-06-01 14:35 | 2026-06-01 15:48 | 0.050694 | E/O | 33 kV lakshmipur feeder maintenance | 20 | 24.3333 | Power interruption
|  |  | Total : | 1899-12-31 21:15 |  | Unserved Energy: |  | 633.1167
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-1 (403T) | 2026-06-17 15:43 | 2026-06-17 19:08 | 0.14236 | T | 33kv B phase Underground cable fault. | 0 | 0 | No interruption
Barishal 230/132kV | T-5 | 2026-06-25 13:53 | 2026-06-25 14:35 | 0.029167 | T | For 33kv Hizal & Mehendigonj feeder fault. | 30 | 21 | Power interruption
Barishal 230/132kV | T-4 | 2026-06-25 13:53 | 2026-06-25 14:37 | 0.030556 | T | For 33kv Hizal & Mehendigonj feeder fault. | 30 | 22 | Power interruption
Benapole 132/33kV | Transformer-1(406T) | 2026-06-06 16:03 | 2026-06-06 16:17 | 0.0097222 | T | Due to 33 KV Benapole feeder fault(During trial). | 6 | 1.4 | Power interruption
Benapole 132/33kV | Transformer-1(406T) | 2026-06-08 18:51 | 2026-06-08 19:02 | 0.0076389 | T | Due to 33 kv Sharsha and Benapole feeder tripped for heavy thunderstorm and rain. | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-2(416T) | 2026-06-10 15:49 | 2026-06-10 15:58 | 0.00625 | T | Due to navaron and sutypur feeder fault | 17 | 2.55 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2026-06-14 08:55 | 2026-06-14 09:30 | 0.024306 | T | 33kv Bamna feeder fault | 20 | 11.6667 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2026-06-14 08:55 | 2026-06-14 09:30 | 0.024306 | T | 33 kv Bamna feeder fault | 20 | 11.6667 | Power interruption
Bhandaria 132/33kV | Transformer-1 | 2026-06-15 14:46 | 2026-06-15 15:01 | 0.010417 | T | 33 kv Bamna feeder fault | 28 | 7 | Power interruption
Bhandaria 132/33kV | Transformer-2 | 2026-06-15 14:46 | 2026-06-15 15:01 | 0.010417 | T | Bamna pbs 33 kv feeder fault | 28 | 7 | Power interruption
Gopalganj 132/33kV | T1 | 2026-06-29 19:44 | 2026-06-29 19:56 | 0.0083333 | T | Deu to Gopalganj REB-2 feder trip | 44 | 8.8 | Power interruption
Gopalganj 132/33kV | T2 | 2026-06-29 19:44 | 2026-06-29 19:57 | 0.0090278 | T |  | 46 | 9.9667 | Power interruption
Khulna (C) | TR-1 425T | 2026-06-26 11:40 | 2026-06-26 12:10 | 0.020833 | T | 33 kv PBS feeder fault | 29 | 14.5 | Power interruption
Khulna (C) | Tr-2 415 T | 2026-06-26 11:40 | 2026-06-26 12:12 | 0.022222 | T | 33 kv PBS feeder fault | 14 | 7.4667 | Power interruption
Madaripur 132/33kV | T2-415T | 2026-06-05 14:52 | 2026-06-05 15:11 | 0.013194 | T | Earth fault,under frequency takerhat 1 feeder | 0 | 0 | No interruption
Madaripur 132/33kV | T1-405T | 2026-06-05 14:52 | 2026-06-05 15:07 | 0.010417 | T | Earth fault,under frequency takerhat 1 feeder | 32 | 8 | Power interruption
Madaripur 132/33kV | T1-405T | 2026-06-07 16:02 | 2026-06-07 16:46 | 0.030556 | T | Thunderstorm | 0 | 0 | No interruption
Madaripur 132/33kV | T2-415T | 2026-06-07 16:02 | 2026-06-07 16:47 | 0.03125 | T | Thunderstorm | 0 | 0 | No interruption
Madaripur 132/33kV | T1-405T | 2026-06-09 16:52 | 2026-06-09 17:16 | 0.016667 | T | Due to pbs Agoiljhara fedder CT flash. | 0 | 0 | No interruption
Madaripur 132/33kV | T2-415T | 2026-06-09 16:52 | 2026-06-09 17:17 | 0.017361 | T | Due to pbs Agoiljhara fedder CT flash. | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-3 | 2026-06-11 14:06 | 2026-06-11 16:13 | 0.088194 | T | WTI TRIP | 19 | 40.2167 | Power interruption
Satkhira 132/33kV | Transformer-2 (T-2) | 2026-06-03 12:59 | 2026-06-03 13:15 | 0.011111 | T | Winding temperature trip | 60 | 16 | Power interruption
Satkhira 132/33kV | Transformer-2 (T-2) | 2026-06-03 15:24 | 2026-06-03 17:16 | 0.077778 | T | Winding temperature trip | 62 | 115.7333 | Power interruption
Satkhira 132/33kV | Transformer-3(T-3) | 2026-06-13 14:21 | 2026-06-13 14:21 | 0 | T | differential & overcurrent,earth fault. . | 0 | 0 | No interruption
Bagerhat 132/33kV | Transformer-1 (403T) | 2026-06-18 16:20 | 2026-06-19 16:49 | 1899-12-31 00:29 | E/O | 33kv B (RYB) phase Underground cable fault. | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-1(406T) | 2026-06-18 12:56 | 2026-06-18 14:10 | 0.051389 | E/O | Due to redhot maintenance of Tr 1 (33KV) source DS | 0 | 0 | No interruption
Gopalganj 132/33kV | Transformer-03 | 2026-06-06 09:53 | 2026-06-06 11:54 | 0.084028 | E/O | Red hot maintenance work of BPBS-2 Feder | 15 | 30.25 | Power interruption
Gopalganj 132/33kV | Transformer-03 | 2026-06-13 08:41 | 2026-06-13 11:06 | 0.10069 | E/O | Bus D's maintenance of Bpbs-1 | 17 | 41.0833 | Power interruption
Madaripur 132/33kV | T3-426T | 2026-06-05 08:29 | 2026-06-05 13:18 | 0.20069 | E/O | Differential relay trip due to restricted earth fault | 0 | 0 | No interruption
Madaripur 132/33kV | T3-426T | 2026-06-06 16:38 | 2026-06-06 17:56 | 0.054167 | E/O | O/C fault due to 33kv Takerhat-2 feeder fault | 0 | 0 | No interruption
Madaripur 132/33kV | T1-405T | 2026-06-06 16:54 | 2026-06-06 17:40 | 0.031944 | E/O | O/C and E/F | 0 | 0 | No interruption
Madaripur 132/33kV | T2-415T | 2026-06-06 16:54 | 2026-06-06 17:52 | 0.040278 | E/O | O/C and E/F | 0 | 0 | No interruption
Patuakhali 132/33kV | 425T (T-3) | 2026-06-05 22:57 | 2026-06-06 12:25 | 0.56111 | E/O | Red hot maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-01 | 2026-06-19 03:20 | 2026-06-19 08:16 | 0.20556 | E/O | Red Hot maintenance of Earth wire | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-02 | 2026-06-19 04:53 | 2026-06-19 08:16 | 0.14097 | E/O | Earth wire red hot of Bpcl gantry | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-3(T-3) | 2026-06-07 09:19 | 2026-06-09 11:06 | 1900-01-01 01:47 | E/O | Due to oil leakage from conservator tank. | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-3(T-3) | 2026-06-10 17:46 | 2026-06-10 19:35 | 0.075694 | E/O | Due to tap position change for manually | 0 | 0 | No interruption
|  |  |  | 1900-01-04 07:02 |  | Unserved Energy: |  | 376.3
HVDC Grid Circle :
BIPTC | 20DF13 | 2026-06-03 07:23 | 2026-06-04 12:22 | 1899-12-31 04:59 | T | 21R Impedance Trip | 0 | 0 | No interruption
BIPTC | 20DF23 | 2026-06-12 21:58 | 2026-06-14 15:50 | 1899-12-31 17:52 | T | C1 Unbalance 60/61 instant L2 Trip | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-3 | 2026-06-07 17:43 | 2026-06-07 18:32 | 0.034028 | T | WZPDCL 33kV Magura Feeder Fault. | 16 | 13.0667 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-06-02 21:01 | 2026-06-03 02:33 | 0.23056 | E/O | Red hot removing 33 kv ds | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) | 2026-06-06 20:20 | 2026-06-06 20:54 | 0.023611 | E/O | RED HOT | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-06-11 21:43 | 2026-06-11 22:05 | 0.015278 | E/O | 33 kv cb y phase redhot | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-02 | 2026-06-30 20:51 | 2026-06-30 22:22 | 0.063194 | E/O | DS-826M R-phase red hot maintenance | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-1 | 2026-06-05 07:14 | 2026-06-05 10:46 | 0.14722 | E/O | Maintainance of 'DS' Y-phase, 33kv T-1A Redhot. | 32 | 113.0667 | Power interruption
Kushtia 132/33kV | T2 | 2026-06-02 09:06 | 2026-06-02 11:40 | 0.10694 | E/O | Emergency maintenance work | 0 | 0 | No interruption
Kushtia 132/33kV | T-1 | 2026-06-25 10:39 | 2026-06-25 13:52 | 0.13403 | E/O | Emergency maintenance work | 0 | 0 | No interruption
Pabna 132/33kV | T-2 | 2026-06-20 08:53 | 2026-06-20 10:36 | 0.071528 | E/O | Emergency maintenance work | 0 | 0 | No interruption
Ruppur 132/11kV | TR-02 | 2026-06-29 09:45 | 2026-06-29 17:04 | 0.30486 | E/O | Emergency maintenance work | 0 | 0 | No interruption
Shahjadpur 132/33kV | T-2(415T) | 2026-06-02 21:10 | 2026-06-05 12:30 | 1900-01-01 15:20 | E/O | Redhot maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV | T-4(435T) | 2026-06-03 18:23 | 2026-06-03 18:55 | 0.022222 | E/O | SD Taken by New Bera 33kv Feeder for red hot maintenance at BUS DS. | 10 | 5.3333 | Power interruption
Shahjadpur 132/33kV | T-2(415T) | 2026-06-21 10:05 | 2026-06-21 10:40 | 0.024306 | E/O | SD taken by Shahjadpur -01 33Kv feeder for red hot maintenance | 8 | 4.6667 | Power interruption
Shahjadpur 132/33kV | T-2(415T) | 2026-06-22 09:20 | 2026-06-22 09:59 | 0.027083 | E/O | Maintenance | 9 | 5.85 | Power interruption
|  |  | Total : | 1900-01-05 19:06 |  | Unserved Energy: |  | 141.9833
Bogura Grid Circle:
Jaldhaka 132/33kV | 406T-1 | 2026-06-14 02:15 | 2026-06-14 02:59 | 0.030556 | T | Tripped | 20 | 14.6667 | Power interruption
Jaldhaka 132/33kV | 416T-2 | 2026-06-14 02:15 | 2026-06-14 03:00 | 0.03125 | T | Tripped | 20 | 15 | Power interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-06-04 08:50 | 2026-06-04 09:16 | 0.018056 | T | Durgapur 33 kv feeder fault. | 39 | 16.9 | Power interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-06-07 20:12 | 2026-06-07 20:43 | 0.021528 | T | PBS 33 kv Kalai feeder fault | 19 | 9.8167 | Power interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-06-21 17:05 | 2026-06-21 17:24 | 0.013194 | T | PBS Durgapur 33 kv feeder fault. | 38 | 12.0333 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-06-28 15:13 | 2026-06-28 15:36 | 0.015972 | T | Rajshahi 1 feeder fault | 18 | 6.9 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) | 2026-06-11 16:20 | 2026-06-11 18:37 | 0.095139 | T | 33 kV LA Blast (R- Phase) | 0 | 0 | No interruption
Rangpur 132/33kV | T-1(414T) | 2026-06-13 00:38 | 2026-06-13 01:55 | 0.053472 | T | Due to PRD Trip | 50 | 64.1667 | Power interruption
Saidpur 132/33kV | TR-5 (434T) | 2026-06-25 12:08 | 2026-06-25 12:17 | 0.00625 | T | 33kv feeder fault | 11 | 1.65 | Power interruption
Saidpur 132/33kV | TR-3 (424T) | 2026-06-27 05:45 | 2026-06-27 05:57 | 0.0083333 | T | 33 kv feeder fault due to heavy thundering. | 18 | 3.6 | Power interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2026-06-04 20:58 | 2026-06-04 20:58 | 0 | E/O | Emergency maint.work | 0 | 0 | No interruption
Chapai 132/33kV | T-4 (435T) | 2026-06-22 16:23 | 2026-06-22 16:45 | 0.015278 | E/O | Nest Remove | 8 | 2.9333 | Power interruption
Kurigram 132/33kV | Transformer T-1 (Tr-403T) | 2026-06-04 08:30 | 2026-06-04 08:54 | 0.016667 | E/O | Redhot maintenance of CT Connector nutbolt. | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-2 (415T) | 2026-06-29 15:35 | 2026-06-29 17:40 | 0.086806 | E/O | T-2 33 kV riser DS (R phase) emergency red hot maintenance work. | 5 | 10.4167 | Power interruption
Mithapukur 132/33kV | TR-2 (414T) | 2026-06-14 16:30 | 2026-06-14 17:50 | 0.055556 | E/O | red hot | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-06-09 08:29 | 2026-06-09 08:53 | 0.016667 | E/O | PBS auxiliary transformer replace | 20 | 8 | Power interruption
Saidpur 132/33kV | TR-01 | 2026-06-18 16:01 | 2026-06-18 16:16 | 0.010417 | E/O | 20MW side breaker work | 0 | 0 | No interruption
|  |  | Total : | 0.49514 |  | Unserved Energy: |  | 166.0833
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-17 19:02 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: June 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Manikgonj Power Plant-01 | 2026-06-21 16:55 | 2026-06-21 18:07 | 0.05 | T | Over load | 120 | 144 | Power interruption
Aminbazar 400/230/132kV | Manikgonj Power Plant-02 | 2026-06-21 17:53 | 2026-06-21 18:36 | 0.029861 | T | Distance Trip | 60 | 43 | Power interruption
Bajitpur 132/33kV | Kishoreganj Ckt-2 | 2026-06-19 09:01 | 2026-06-19 09:14 | 0.0090278 | T | Z-1,B-phase Trip | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2026-06-21 14:51 | 2026-06-21 15:47 | 0.038889 | T | Power plant trip | 63 | 58.8 | Power interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2026-06-21 18:19 | 2026-06-21 19:01 | 0.029167 | T | BR Power plant trip. | 45 | 31.5 | Power interruption
Bhaluka 132/33kV | BR Powergen Ckt- 02 | 2026-06-21 18:19 | 2026-06-21 19:02 | 0.029861 | T | power plant trip. | 45 | 32.25 | Power interruption
Bhaluka 132/33kV | BR Powergen Ckt- 01 | 2026-06-23 15:10 | 2026-06-23 15:31 | 0.014583 | T | BR Powergen end fault. | 41 | 14.35 | Power interruption
Kabirpur 132/33kV | Tongi-2 | 2026-06-09 13:03 | 2026-06-09 13:41 | 0.026389 | T | Tripped | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-06-09 13:03 | 2026-06-09 19:57 | 0.2875 | T | Tripped | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-06-30 17:36 | 2026-06-30 17:52 | 0.011111 | T | Tripped | 0 | 0 | No interruption
Ghatail 132/33kV | Tangail-1 | 2026-06-05 05:54 | 2026-06-05 10:32 | 0.19306 | E/O | OPGW Restringing in Tangail Grid Sub-Station. | 0 | 0 | No interruption
Ghatail 132/33kV | Tangail -2 | 2026-06-05 05:59 | 2026-06-05 10:32 | 0.18958 | E/O | OPGW Restringing in Tangail Grid Sub-Station. | 20 | 91 | Power interruption
Kaliakoir 400/230/132kV | Summit/Kodda PS | 2026-06-09 00:16 | 2026-06-09 14:14 | 0.58194 | E/O | hot sport temperature 663 Celsius | 0 | 0 | No interruption
Mymensingh 132/33kV | 50 MW Solar Plant | 2026-06-25 19:47 | 2026-06-25 20:47 | 0.041667 | E/O | Emergency amint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Tongi 80 MW PS | 2026-06-13 12:43 | 2026-06-15 12:48 | 1900-01-01 00:05 | E/O | Emergency amint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 12:52 |  | Unserved Energy: |  | 414.9
Dhaka (South) Grid Circle :
Bhulta 132/33kV | Haripur | 2026-06-29 12:04 | 2026-06-29 12:56 | 0.036111 | T | সূবর্ণগ্রাম পিকনিক স্পটে ১৩২কেভি লাইনের সাথে অ্যালুমিনিয়ামের মই লাগার কারণে ভুলতা নিউ সাবস্টেশনের ব্রেকার ট্রিপ করে এবং ভুলতা ওল্ড সাবস্টেশন ব্লাক আউট হয়ে যায়। | 160 | 138.6667 | Power interruption
Hasnabad 132/33kV | Shitallakhya | 2026-06-07 10:50 | 2026-06-08 21:37 | 1899-12-31 10:47 | T | The wire on the Shitalakkhya (Y - phase) line broke at From 88 to 91 Tower Spam. | 86 | 186.33 | Power interruption(10:50 to 13:00)
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2026-06-07 10:50 | 2026-06-07 11:28 | 0.026389 | T | The wire on the Shitalakkhya (Y - phase) line broke at From 88 to 91 Tower Spam. | 76 | 48.1333 | Power interruption
Keranigonj 230/132/33kV | 132 kV Sreenagar Ckt. 1 | 2026-06-21 17:34 | 2026-06-21 18:21 | 0.032639 | T | Bad weather and thundering. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Sreenagar Ckt. 2 | 2026-06-21 17:34 | 2026-06-21 18:45 | 0.049306 | T | Bad weather and thundering. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Hasnabad Ckt. 2 | 2026-06-21 17:34 | 2026-06-21 21:14 | 0.15278 | T | Bad weather and thundering. | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj -Summit 55 MW 132 kv Ckt | 2026-06-18 14:22 | 2026-06-18 14:40 | 0.0125 | T | Heavy rain and storm | 17 | 5.1 | Power interruption
Madanganj 132/33kV | Madanganj-Fatullah 132KV Ckt | 2026-06-18 14:22 | 2026-06-18 21:38 | 0.30278 | T | Heavy rain and storm | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2026-06-21 17:11 | 2026-06-21 21:06 | 0.16319 | T | Unknown | 0 | 0 | No interruption
Siddhirganj 132/33kV | 210MW PDB L3 | 2026-06-26 15:27 | 2026-06-26 16:37 | 0.048611 | T | Earth fault | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Shyampur-1 | 2026-06-18 16:14 | 2026-06-18 20:52 | 0.19306 | E/O | Madanganj Breaker was closed at 20:32 as per the instructions of NLDC | 0 | 0 | No interruption
Fatullah 132/33kV | 132 kV Shyampur-1 | 2026-06-22 09:33 | 2026-06-22 09:33 | 0 | E/O | By NLDC | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Siddhirganj-1 | 2026-06-02 23:33 | 2026-06-03 02:13 | 0.11111 | E/O | Red Hot Maintenance. | 0 | 0 | No interruption
Hasnabad 132/33kV | Shitallakhya | 2026-06-07 11:42 | 2026-06-08 21:37 | 1899-12-31 09:55 | E/O | The wire on the Shitalakkhya (Y - phase) line broke at From 88 to 91 Tower Spam. | 0 | 0 | No interruption
Siddhirganj 132/33kV | Matuail | 2026-06-14 01:07 | 2026-06-14 13:32 | 0.51736 | E/O | Due to red hot at Center break mid point of DS (431M). | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 12:12 |  | Unserved Energy: |  | 378.23
Chattogram Grid Circle :
Coxsbazar 132/33kV | Doh-Cox Ckt-2 | 2026-06-27 15:55 | 2026-06-27 16:13 | 0.0125 | T | Tripped | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-2 | 2026-06-27 15:56 | 2026-06-27 16:13 | 0.011806 | T | Tripped | 0 | 0 | No interruption
Khulshi 132/33kV | Khulshi-Sholoshahar CKT-1(Madunaghat) | 2026-06-03 12:20 | 2026-06-03 13:07 | 0.032639 | T | Trip from Sholoshahar Grid Sub-station. | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Kulshi-2 | 2026-06-29 09:17 | 2026-06-29 09:17 | 0 | T | Jumper out | 0 | 0 | No interruption
BSRM 230/33kV | GPH Ispat Ckt. -01 | 2026-06-04 13:11 | 2026-06-04 15:16 | 0.086806 | E/O | Emergency work by Mirshary 230kV ss | 0 | 0 | No interruption
Baroirhat 132/33kV | Feni-1 | 2026-06-23 15:27 | 2026-06-23 16:21 | 0.0375 | E/O | Order by NLDC | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona- Rangamati Ckt-01 | 2026-06-16 23:01 | 2026-06-17 00:18 | 0.053472 | E/O | Y-Phase Line Isolator higg temperature maintenance work | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-1 | 2026-06-04 13:09 | 2026-06-04 15:15 | 0.0875 | E/O | emergency tree trimming needed at mirsorai side . | 0 | 0 | No interruption
Khagrachori 132/33kV | RANGAMATI-1 | 2026-06-08 15:00 | 2026-06-08 15:29 | 0.020139 | E/O | Panel relay test | 0 | 0 | No interruption
|  |  | Total : | 0.34236 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2026-06-09 13:22 | 2026-06-09 18:26 | 0.21111 | T | Tripped | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2026-06-17 20:30 | 2026-06-17 23:25 | 0.12153 | T | Tripped | 95 | 277.0833 | Power interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-1 | 2026-06-17 11:04 | 2026-06-17 11:16 | 0.0083333 | T | Zone-1 trip | 0 | 0 | No interruption
Chandpur 132/33kV | Chandpur-Kachua Ckt-2 | 2026-06-17 11:04 | 2026-06-17 11:16 | 0.0083333 | T | Zone-1 trip | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Cumilla North-3 | 2026-06-09 16:33 | 2026-06-09 17:25 | 0.036111 | T | Storm | 0 | 0 | No interruption
Shahjibazar 132/33kV | BPDB 60 MW | 2026-06-17 20:30 | 2026-06-17 20:56 | 0.018056 | T | Voltage down for B.Baria-Ashuganj ckt 02 Faut | 0 | 0 | No interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-1 | 2026-06-14 05:40 | 2026-06-14 06:10 | 0.020833 | T | Rainy weather | 5 | 2.5 | Power interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-1 | 2026-06-24 01:27 | 2026-06-24 02:12 | 0.03125 | T | Thunderstorm | 0 | 0 | No interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2026-06-27 07:25 | 2026-06-27 09:33 | 0.088889 | T | Thundering | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-06-14 05:40 | 2026-06-14 05:59 | 0.013194 | T | Tripped | 19 | 6.0167 | Power interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-06-24 08:17 | 2026-06-24 08:47 | 0.020833 | T | Tripped | 32 | 16 | Power interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-06-27 01:06 | 2026-06-27 01:21 | 0.010417 | T | Distance protection operated. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-06-27 21:15 | 2026-06-27 21:25 | 0.0069444 | T | Distance protection Operated | 40 | 6.6667 | Power interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2026-06-17 20:15 | 2026-06-19 14:34 | 1899-12-31 18:19 | E/O | Emergency maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-1 | 2026-06-17 20:58 | 2026-06-19 09:12 | 1899-12-31 12:14 | E/O | Emergency maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-06-17 20:58 | 2026-06-19 09:12 | 1899-12-31 12:14 | E/O | Emergency maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2026-06-17 23:27 | 2026-06-21 13:11 | 1900-01-02 13:44 | E/O | Emergency maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2026-06-17 23:33 | 2026-06-21 13:11 | 1900-01-02 13:38 | E/O | Emergency maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-1 | 2026-06-21 17:35 | 2026-06-22 14:44 | 0.88125 | E/O | Emergency maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Narsingdi Circuit-2 | 2026-06-21 17:35 | 2026-06-22 14:44 | 0.88125 | E/O | Emergency maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-06-23 10:13 | 2026-06-23 11:58 | 0.072917 | E/O | Red-hot maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Cumilla North-2 | 2026-06-29 10:41 | 2026-06-29 11:47 | 0.045833 | E/O | Red hot maintenance at Cum (North) End | 0 | 0 | No interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2026-06-04 12:26 | 2026-06-04 13:45 | 0.054861 | E/O | Due to broken nest | 0 | 0 | No interruption
|  |  | Total : | 1900-01-13 10:55 |  | Unserved Energy: |  | 308.2667
Khulna Grid Circle :
Barishal 132/33kV | 132kv Bhandaria ckt | 2026-06-29 19:31 | 2026-06-29 21:43 | 0.091667 | T | Conductor cut | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2026-06-30 19:31 | 2026-06-30 19:40 | 0.00625 | T | The line has broken and fallen between tower no122 to 123, 27.1km away from Barishal 132kV SS | 52 | 7.8 | Power interruption
Barishal 230/132kV | Madaripur ckt-01 | 2026-06-15 14:08 | 2026-06-15 14:44 | 0.025 | T | Tripped | 0 | 0 | No interruption
Barishal 230/132kV | Madaripur ckt-02 | 2026-06-21 18:00 | 2026-06-21 20:09 | 0.089583 | T | Stormy weather | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Khulna Central-2 | 2026-06-15 12:57 | 2026-06-15 13:59 | 0.043056 | T | Thunderstorme | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2026-06-06 13:45 | 2026-06-06 17:15 | 0.14583 | T | Tripped | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Goalpara-2 | 2026-06-15 12:57 | 2026-06-15 13:58 | 0.042361 | T | Heavy rsin fall & thundering | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2026-06-13 13:23 | 2026-06-13 13:33 | 0.0069444 | T | Tripped | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2026-06-18 15:45 | 2026-06-18 16:11 | 0.018056 | T | Tripped | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-2 | 2026-06-28 17:01 | 2026-06-28 17:03 | 0.0013889 | T | ALDC Khulna, Tripping for Testing. | 0 | 0 | No interruption
Patuakhali 132/33kV | UPPL (150MW) 132kV LINE | 2026-06-18 18:48 | 2026-06-18 19:34 | 0.031944 | T | Tripped | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-1 | 2026-06-18 18:51 | 2026-06-19 17:53 | 0.95972 | T | Tripped | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2026-06-13 13:23 | 2026-06-13 13:32 | 0.00625 | T | Phase-c Earth fault. | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2026-06-18 15:45 | 2026-06-18 16:12 | 0.01875 | T | Bad weather | 0 | 0 | No interruption
Shariatpur 132/33kV | Madaripur-Shariatpur CKT-01 | 2026-06-21 17:26 | 2026-06-21 18:36 | 0.048611 | T | Distance Trip (Main Protection Operate). Zcom Trip. | 0 | 0 | No interruption
Bhandaria 132/33kV | Barishal (L4) | 2026-06-29 21:55 | 2026-06-30 12:42 | 0.61597 | E/O | Emergency Maint.work | 0 | 0 | No interruption
Bhandaria 132/33kV | Barishal (L4) | 2026-06-30 19:50 | 2026-07-01 07:17 | 0.47708 | E/O | The outage occurred due to the sanpping of the conductor on the barishal bhandaria transmission line. | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-1 | 2026-06-13 11:19 | 2026-06-13 13:25 | 0.0875 | E/O | CT Y-phase unusual sound trouble | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-02 | 2026-06-21 15:48 | 2026-06-21 17:10 | 0.056944 | E/O | Emergency Maint.work | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-1 | 2026-06-18 18:51 | 2026-06-19 17:53 | 0.95972 | E/O | By aldc khulana | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-2 | 2026-06-19 08:26 | 2026-06-19 17:46 | 0.38889 | E/O | By aldc khulana | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-01 | 2026-06-18 18:49 | 2026-06-19 17:54 | 0.96181 | E/O | R-phase burn out | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-02 | 2026-06-19 15:44 | 2026-06-19 17:45 | 0.084028 | E/O | Red Hot maintenance | 0 | 0 | No interruption
Payra 400kV | Line-2 (Amtoli) | 2026-06-19 03:21 | 2026-06-19 07:23 | 0.16806 | E/O | There is continuous flashing at the overhead lightining protection grounding cable on the top of the tower between Amtoli 2 Line & Payra 1 Line | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 08:03 |  | Unserved Energy: |  | 7.8
HVDC Grid Circle :
Ishurdi 132/33kV | 132 kv Natore-2 | 2026-06-15 04:42 | 2026-06-15 04:58 | 0.011111 | T | Tripped | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2026-06-15 14:28 | 2026-06-17 21:21 | 1900-01-01 06:53 | T | Tripped | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah1-Jhenaidah2,132kV Circuit-3(L5) | 2026-06-26 09:24 | 2026-06-26 22:03 | 0.52708 | E/O | Busbar extension of T-3 , 230kv Jhenaidah South end. | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Shahjadpur Line | 2026-06-14 10:20 | 2026-06-14 14:45 | 0.18403 | E/O | Redhot maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Pabna | 2026-06-14 10:32 | 2026-06-14 14:50 | 0.17917 | E/O | Red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 04:31 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Barapukuria 230/132/33kV | Saidpur 132 KV Ckt2 | 2026-06-15 03:50 | 2026-06-15 05:28 | 0.068056 | T | Thundering, storm & rain | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2026-06-03 17:35 | 2026-06-03 18:57 | 0.056944 | T | Tripped | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2026-06-04 17:36 | 2026-06-04 18:14 | 0.026389 | T | Bad Weather | 0 | 0 | No interruption
Joypurhat 132/33kV | Patnitola Ckt.-2 | 2026-06-03 16:43 | 2026-06-03 18:03 | 0.055556 | T | Due to Storm and thundering | 0 | 0 | No interruption
Kurigram 132/33kV | 132 Kv Rangpur-kurigram Ckt | 2026-06-18 04:06 | 2026-06-18 04:35 | 0.020139 | T | General Trip, Distance Z-1, | 54 | 26.1 | Power interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-2 | 2026-06-03 17:34 | 2026-06-03 18:58 | 0.058333 | T | Thundering. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-06-04 01:22 | 2026-06-04 13:12 | 0.49306 | T | Heavy storm,raining,thundering. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-06-04 17:35 | 2026-06-04 19:13 | 0.068056 | T | Thunderstorm | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Joypurhat Ckt-1 | 2026-06-04 17:35 | 2026-06-04 18:15 | 0.027778 | T | Over Voltage (Thunderstorm) | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-06-21 18:33 | 2026-06-21 19:29 | 0.038889 | T | Stormy weather | 0 | 0 | No interruption
Panchagarh 132/33kV | Thakurgaon-1 | 2026-06-08 18:23 | 2026-06-08 18:44 | 0.014583 | T | Heavy Rain and Thundering | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | EPVTL-2 | 2026-06-23 13:37 | 2026-06-23 17:14 | 0.15069 | T | Tripped | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2026-06-18 04:07 | 2026-06-18 04:35 | 0.019444 | T | Bad weather | 40 | 18.6667 | Power interruption
Rangpur 132/33kV | Rangpur-Kurigram | 2026-06-18 04:07 | 2026-06-18 04:31 | 0.016667 | T | Bad weather | 30 | 12 | Power interruption
Saidpur 132/33kV | Saidpur-Baropukuria CKT-02 | 2026-06-15 03:50 | 2026-06-15 05:29 | 0.06875 | T | Tripped | 0 | 0 | No interruption
Thakurgaon 132/33kV | Panchagar CKT-1 | 2026-06-08 18:22 | 2026-06-08 18:44 | 0.015278 | T | Huge thundering | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-1 | 2026-06-04 17:52 | 2026-06-04 21:01 | 0.13125 | E/O | Emergency maint.work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Kaliakoir 400 kV Ckt-2 | 2026-06-04 17:52 | 2026-06-04 21:01 | 0.13125 | E/O | Emergency maint.work | 0 | 0 | No interruption
Mithapukur 132/33kV | Palashbari-1 | 2026-06-26 06:58 | 2026-06-26 19:55 | 0.53958 | E/O | Only mithapukur side open. | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Bogura Ckt-1 | 2026-06-14 11:14 | 2026-06-14 13:05 | 0.077083 | E/O | It is necessary to shut down Naogaon Bogura Circuit-1 to remove the kite from the middle of tower number 62-63. | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | EPVTL-2 | 2026-06-24 17:10 | 2026-06-24 18:25 | 0.052083 | E/O | বাসাবাড়ির প্যানেল তুলতে গিয়ে কন্ডাকর ছিড়ে ফেলেছে। তাই আর্মারিং করার জন্য শাটডাউন প্রয়োজন। | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2026-06-13 00:29 | 2026-06-13 04:19 | 0.15972 | E/O | Due to Temperature rise | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 06:57 |  | Unserved Energy: |  | 56.7667
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-02-01 15:43 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:June 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Bus-1 (400kV) | 2026-06-05 09:17 | 2026-06-05 10:30 | 1:13 | S/O | 400kV Rupur bay jumper connection | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Bus-2 (400kV) | 2026-06-05 12:01 | 2026-06-05 14:15 | 2:14 | S/O | IDRNPP Prihect | 0 | 0 | No interruption
Bajitpur 132/33kV | 132 kV Bus-2 | 2026-06-04 08:47 | 2026-06-06 11:55 | 51:08 | S/O | Due To Reduce Temparature and Clamp Maintenance. | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-2(414T) | 2026-06-06 13:13 | 2026-06-06 14:22 | 1:09 | S/O | Ret hot maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-06-13 11:08 | 2026-06-13 13:15 | 2:07 | S/O | Maint.work | 30 | 63.5 | Power interruption
Dhamrai 132/33kV | Transformer-1 | 2026-06-22 06:21 | 2026-06-22 08:10 | 1:49 | S/O | Redhot maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-1 | 2026-06-23 06:26 | 2026-06-23 08:14 | 1:48 | S/O | Red-hot Maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-06-26 14:51 | 2026-06-26 17:20 | 2:29 | S/O | Red hot maintenance work by DPBS-1. | 65 | 161.4167 | Power interruption
Kaliakoir 400/230/132kV | 400/132kV TR-3 | 2026-06-19 09:20 | 2026-06-19 15:59 | 6:39 | S/O | Extension of Main Bus-2 | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2026-06-19 09:53 | 2026-06-19 15:40 | 5:47 | S/O | Extension of 400kV Bus-2 | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR-3 | 2026-06-20 09:24 | 2026-06-20 16:49 | 7:25 | S/O | BBK 400kV TL Project work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2026-06-20 09:36 | 2026-06-20 16:40 | 7:04 | S/O | B B K 400kV TL Project Work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400/132kV TR-3 | 2026-06-24 09:09 | 2026-06-26 18:26 | 57:17 | S/O | SAS Testing and Commissioning. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2026-06-28 08:47 | 2026-06-28 08:47 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-3 (424T) | 2026-06-04 07:41 | 2026-06-04 19:22 | 11:41 | S/O | LA Installation work of 33/0.4 KV Auxiliary T-03. | 0 | 0 | No interruption
Kodda 132/33kV | Tr-1 (406T) | 2026-06-11 12:32 | 2026-06-11 13:35 | 1:03 | S/O | 33 kV Section 01 maintenance by PBS | 30 | 31.5 | Power interruption
Kodda 132/33kV | Tr-2 (416T) | 2026-06-11 12:33 | 2026-06-11 13:35 | 1:02 | S/O | 33kV section 01 maintenance by PBS | 30 | 31 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2026-06-02 11:02 | 2026-06-02 12:29 | 1:27 | S/O | Red hot maintanence | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-3 (424T) | 2026-06-14 06:16 | 2026-06-14 08:32 | 2:16 | S/O | Maint.work | 0 | 0 | No interruption
Nabinagar 132/33kV | T-1 | 2026-06-10 10:12 | 2026-06-10 12:26 | 2:14 | S/O | এনার্জিপ্যাক কর্তৃক ১৩২/৩৩ কেভি ট্রান্সফরমারের ৩৩ কেভি সাইডে তাপমাত্রা বৃদ্ধি জনিত কারণে মেরামত কাজ। | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2026-06-05 05:41 | 2026-06-05 18:10 | 12:29 | S/O | Bushing CT control cable change work. | 0 | 0 | No interruption
Savar 132/33kV | T-3 | 2026-06-06 10:06 | 2026-06-06 14:12 | 4:06 | S/O | Control cable changing works | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 | 2026-06-23 10:52 | 2026-06-23 11:30 | 0:38 | S/O | Tr-03 132kv energy meter change works. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 | 2026-06-24 10:39 | 2026-06-24 16:23 | 5:44 | S/O | TR-03 132 KV DS box installation works. | 0 | 0 | No interruption
Shomvuganj 400/132kV | Transformer-3 ( TR-3) | 2026-06-06 15:43 | 2026-06-06 16:20 | 0:37 | S/O | Oil Leakage | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 23:26 |  | Unserved Energy: |  | 287.4167
Dhaka (South) Grid Circle :
Bhulta 132/33kV | GT1 | 2026-06-01 22:24 | 2026-06-02 00:19 | 1:55 | S/O | 132 KV Bus DS-126 red hot Shut down taken by Deepok kumar sutradhar, AE Bhulta 132 KV Grid SS | 0 | 0 | No interruption
Bhulta 132/33kV | 132kV BUS | 2026-06-01 22:24 | 2026-06-02 00:19 | 1:55 | S/O | 132 KV Bus DS-126 red hot Shut down taken by Deepok kumar sutradhar, AE Bhulta 132 KV Grid SS | 40 | 76.6667 | Power interruption
Bhulta 132/33kV | GT1 | 2026-06-05 06:18 | 2026-06-05 09:26 | 3:08 | S/O | Maintenance work at Narsingdi line DS-104 (Substation drawing identification number DS-201S) | 40 | 125.3333 | Power interruption
Bhulta 132/33kV | GT1 | 2026-06-05 18:44 | 2026-06-05 20:41 | 1:57 | S/O | For Redhot GT-01 HT side (R phase) bushing and shutdown taken by Deepok Kumar Sutradhar(AE), Bhulta 132 KV Grid substation | 54 | 105.3 | Power interruption
Bhulta 132/33kV | GT2 | 2026-06-26 06:06 | 2026-06-26 13:20 | 7:14 | S/O | For PBS Maintenance Work | 40 | 289.3333 | Power interruption
Bhulta 132/33kV | GT2 | 2026-06-27 07:00 | 2026-06-27 15:00 | 8:00 | S/O | PBS GIS swiching substation service working at bus section -02. | 50 | 400 | Power interruption
Haripur 230/132kV | 132kV Bus Coupler-2 | 2026-06-09 11:32 | 2026-06-29 13:58 | 482:26 | S/O | 132kV CRP Panel Shifting work from 100MW BPDB Control Room to 230/132kV Grid SS Control Room | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Main Bus Sec-1 | 2026-06-13 06:12 | 2026-06-15 07:30 | 49:18 | S/O | EGCB Bay Jack Bus Changing Work. | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-1 | 2026-06-14 21:18 | 2026-06-14 22:19 | 1:01 | S/O | Redhot on 132kV CB in Red Phase | 0 | 0 | No interruption
Haripur 230/132kV | Bus-1 | 2026-06-26 15:28 | 2026-06-26 16:29 | 1:01 | S/O | 230kV Bhulta-2 Bus DS Fingure Replacing Work | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Main Bus Sec-2 | 2026-06-28 12:58 | 2026-06-28 16:35 | 3:37 | S/O | busbar protection work. | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Reserve Bus Sec-2 | 2026-06-29 10:51 | 2026-06-29 13:58 | 3:07 | S/O | project work. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132kV Reserve Bus | 2026-06-02 06:23 | 2026-06-02 10:53 | 4:30 | S/O | Auto TR-2 R.Bus Alignment correction and Red hot maintenance. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132kV Main Bus | 2026-06-02 10:53 | 2026-06-07 12:28 | 121:35 | S/O | 230/132 kV Auto TR-3 bus D/S maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2026-06-08 14:38 | 2026-06-08 20:06 | 5:28 | S/O | Pangaon 33 kv Feeder Reserve Bus D/S maintenance by DPBS-4 | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 | 2026-06-10 11:26 | 2026-06-10 12:15 | 0:49 | S/O | CT Maintenance Work | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-2 | 2026-06-02 06:04 | 2026-06-02 07:36 | 1:32 | S/O | 132 kv bus maintenace | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-3 | 2026-06-02 07:40 | 2026-06-02 13:21 | 5:41 | S/O | 132 KV reserve bus maintenance done | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-1 | 2026-06-02 14:40 | 2026-06-02 18:24 | 3:44 | S/O | Tap changer maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-1 | 2026-06-15 07:23 | 2026-06-15 08:48 | 1:25 | S/O | ATR-1 132kV side bus DS maintenance, work done by 132kv S/s | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-1 | 2026-06-19 11:33 | 2026-06-19 13:07 | 1:34 | S/O | Dc supply replacement work with new charger /distribution panel for main and backup protection relay Work by DPDC.. | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-2 | 2026-06-19 15:16 | 2026-06-19 15:56 | 0:40 | S/O | New DC connection for control and relay panel | 0 | 0 | No interruption
Maniknagar 230/132kV | Auto Transformer-02 (715T) | 2026-06-05 10:03 | 2026-06-05 11:22 | 1:19 | S/O | Maint.work | 0 | 0 | No interruption
Meghnaghat 400/230kV | 230kV BUS Section 02 | 2026-06-09 07:16 | 2026-06-09 15:43 | 8:27 | S/O | Requested by NLDC | 0 | 0 | No interruption
Narshingdi 132/33kV | T-1 | 2026-06-16 11:45 | 2026-06-16 12:53 | 1:08 | S/O | Tr-1 Transformer shutdown for 33kV bushing B-Phase Oil leakage maintenance work. | 25 | 28.3333 | Power interruption
Siddhirganj 132/33kV | T-1 | 2026-06-12 08:01 | 2026-06-12 12:29 | 4:28 | S/O | 33 kV Vacuum Integrity Test | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-1 | 2026-06-02 08:39 | 2026-06-02 10:28 | 1:49 | S/O | Under ground Cable Heat shrink Ashtha Feed | 26 | 47.2333 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-06-02 15:01 | 2026-06-02 16:22 | 1:21 | S/O | PBS maintenance works | 35 | 47.25 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-06-19 09:01 | 2026-06-19 12:21 | 3:20 | S/O | PBS 33 kv Astha feeder cable heat shrink work | 40 | 133.3333 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-06-26 06:17 | 2026-06-28 07:30 | 49:13 | S/O | PBS 33 KV side Bus coupler By pass, maintenance work | 30 | 1476.5 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2026-06-26 06:18 | 2026-06-26 08:13 | 1:55 | S/O | PBS 33 KV side Bus coupler fault , Buscoupler Bypass work maintenance | 80 | 153.3333 | Power interruption
Sonargaon 132/33kV | Tr-2 | 2026-06-28 07:05 | 2026-06-28 07:24 | 0:19 | S/O | Due to PBS 33KV bus coupler bypass under T2. | 100 | 31.6667 | Power interruption
Srinagar 132/33kV | Tr-01 | 2026-06-12 20:55 | 2026-06-12 22:18 | 1:23 | S/O | Red Hot Maintenance at 33kv side. | 20 | 27.6667 | Power interruption
Srinagar 132/33kV | Tr-01 | 2026-06-22 09:07 | 2026-06-22 10:26 | 1:19 | S/O | 33 kv bus -01 shutdown for PBS red hot maintenance. | 20 | 26.3333 | Power interruption
Srinagar 132/33kV | 33 kV bus | 2026-06-22 09:19 | 2026-06-22 10:17 | 0:58 | S/O | 33 kv bus -01 shutdown for PBS red hot maintenance. | 20 | 19.3333 | Power interruption
|  |  | Total : | 1900-01-31 20:36 |  | Unserved Energy: |  | 2987.6167
Chattogram Grid Circle :
BSRM 230/33kV | 230/33 kV Transformer-1 (125/140 MVA) | 2026-06-12 12:54 | 2026-06-12 14:21 | 1:27 | S/O | BPDB Meter change | 0 | 0 | No interruption
BSRM 230/33kV | 230/33 kV Transformer-2 (125/140 MVA) | 2026-06-12 12:55 | 2026-06-12 14:22 | 1:27 | S/O | BPDB Meter change | 0 | 0 | No interruption
BSRM 230/33kV | 230/33 kV Transformer-3 (125/140 MVA) | 2026-06-12 12:56 | 2026-06-12 14:23 | 1:27 | S/O | BPDB Meter change | 0 | 0 | No interruption
Baroirhat 132/33kV | TR-1, 406T | 2026-06-25 07:40 | 2026-06-25 10:25 | 2:45 | S/O | Maintenance work | 0 | 0 | No interruption
Baroirhat 132/33kV | TR-2, 416T | 2026-06-25 11:00 | 2026-06-25 12:36 | 1:36 | S/O | Maintanance work due to high temperature. | 0 | 0 | No interruption
Chandraghona 132/33kV | TR-01(406T) | 2026-06-12 06:35 | 2026-06-12 09:27 | 2:52 | S/O | 33 kv bus loop change | 27 | 77.4 | Power interruption
Coxsbazar 132/33kV | 415T-T2 | 2026-06-07 15:40 | 2026-06-08 11:51 | 20:11 | S/O | 33kv LA installation | 0 | 0 | No interruption
Coxsbazar 132/33kV | 405T-T1 | 2026-06-08 05:40 | 2026-06-08 08:10 | 2:30 | S/O | Tr 01 & Tr 02 shutdown for supply separately to incomer 1 from Tr 01 and incomer 2 from Tr 2 | 48 | 120 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2026-06-04 08:34 | 2026-06-04 09:38 | 1:04 | S/O | Due to Keranihat 33 kv feeder redhot maintenance. Shutdown taken by Shahidul Islam AGM (Zonal office Satkania) Ctg pbs -01 | 63 | 67.2 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2026-06-19 09:15 | 2026-06-19 10:17 | 1:02 | S/O | Due to keranihat 33 kv feeder Redhot maintenance. | 33 | 34.1 | Power interruption
Halishahar 132/33kV | 405T(TR-1) | 2026-06-10 09:13 | 2026-06-10 13:14 | 4:01 | S/O | Maint.work | 0 | 0 | No interruption
Halishahar 132/33kV | 405T(TR-1) | 2026-06-19 06:28 | 2026-06-19 14:14 | 7:46 | S/O | Ct clamp replacement at 33 kv side | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-03 | 2026-06-22 07:51 | 2026-06-22 08:48 | 0:57 | S/O | Bushing inspection | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-03 | 2026-06-22 11:20 | 2026-06-22 11:30 | 0:10 | S/O | Bushing Measurement | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 | 2026-06-29 09:00 | 2026-06-29 16:56 | 7:56 | S/O | secondary CT (33kv side) maintenance | 0 | 0 | No interruption
Korerhat 400/230/132kV | 400kV BUS-2 | 2026-06-05 10:27 | 2026-06-06 15:58 | 29:31 | S/O | Due to project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7303T)-Three Ph | 2026-06-06 12:55 | 2026-06-06 15:54 | 2:59 | S/O | Project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-06-18 07:40 | 2026-06-18 18:32 | 10:52 | S/O | Due to project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-06-20 11:16 | 2026-06-20 19:33 | 8:17 | S/O | Project Work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-2(7203T)-Three Ph | 2026-06-24 09:54 | 2026-06-24 21:17 | 11:23 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-2(7203T)-Three Ph | 2026-06-25 09:17 | 2026-06-25 18:39 | 9:22 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7103T) | 2026-06-26 09:21 | 2026-06-26 18:52 | 9:31 | S/O | Due to project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7103T) | 2026-06-27 08:57 | 2026-06-27 19:32 | 10:35 | S/O | Project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-06-27 08:59 | 2026-06-27 19:30 | 10:31 | S/O | Project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7303T)-Three Ph | 2026-06-28 11:16 | 2026-06-28 17:27 | 6:11 | S/O | Due to project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-06-30 08:55 | 2026-06-30 19:34 | 10:39 | S/O | Project work | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-1(507T) | 2026-06-28 10:11 | 2026-06-28 15:23 | 5:12 | S/O | High temperature maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-2(517T) | 2026-06-29 09:48 | 2026-06-29 14:46 | 4:58 | S/O | B phase cable ceiling maintenance.full load served by T-01. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-06 19:12 |  |  |  | 298.7
Cumilla Grid Circle :
Chandpur 132/33kV | 422T(T-5) | 2026-06-07 16:02 | 2026-06-08 23:55 | 31:53 | S/O | OLTC oil centrifuging | 0 | 0 | No interruption
Chandpur 132/33kV | 33 kV T-1 Section | 2026-06-09 | 2026-06-09 00:56 | 0:56 | S/O | Red hot maintenance (CDR-2 DS) S/D taken by BPDB | 18 | 16.8 | Power interruption
Chandpur 132/33kV | 402T (T-01) | 2026-06-09 | 2026-06-09 00:56 | 0:56 | S/O | Red hot maintenance by BPDB (CDR-2 DS) | 0 | 0 | No interruption
Chandpur 132/33kV | 422T(T-5) | 2026-06-09 01:00 | 2026-06-11 07:08 | 54:08 | S/O | Maint.work | 0 | 0 | No interruption
Chandpur 132/33kV | 402T (T-01) | 2026-06-11 07:10 | 2026-06-11 08:28 | 1:18 | S/O | Maintenance work of BPDB | 0 | 0 | No interruption
Chandpur 132/33kV | 33 kV T-1 Section | 2026-06-11 07:12 | 2026-06-11 08:26 | 1:14 | S/O | Maitenance work of BPDB | 12 | 14.8 | Power interruption
Chandpur 132/33kV | 422T(T-5) | 2026-06-11 08:30 | 2026-06-27 07:02 | 382:32 | S/O | OLTC oil centrifuging | 0 | 0 | No interruption
Chandpur 132/33kV | 33 kV T-1 Section | 2026-06-27 07:05 | 2026-06-27 08:20 | 1:15 | S/O | Maintenance work of BPDB | 18 | 22.5 | Power interruption
Chandpur 132/33kV | 402T (T-01) | 2026-06-27 07:05 | 2026-06-27 08:20 | 1:15 | S/O | Maintenance work of BPDB | 0 | 0 | No interruption
Chandpur 132/33kV | 422T(T-5) | 2026-06-27 08:20 | 2026-06-27 08:20 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-1 | 2026-06-01 23:01 | 2026-06-02 00:46 | 1:45 | S/O | 33kv bus-1 redhot maintanace work by Md.Masud Miah AGM PBS-4 (O&M). | 40 | 70 | Power interruption
Chauddagram 132/33kV | 132 kv T-1 | 2026-06-11 21:59 | 2026-06-11 23:27 | 1:28 | S/O | 33kv bus-1 redhot maintanace work by Md.Abdul Rohim (junior Engineer feni pbs). | 35 | 51.3333 | Power interruption
Chhatak 132/33kV | T-1 | 2026-06-14 22:45 | 2026-06-15 00:06 | 1:21 | S/O | Red Hot Maintanance of 33 kv bus | 10 | 13.5 | Power interruption
Chhatak 132/33kV | T-3 | 2026-06-20 13:50 | 2026-06-20 17:47 | 3:57 | S/O | Shutdown for CB replacement of 33KV Companyganj PBS Feeder | 0 | 0 | No interruption
Chhatak 132/33kV | T-1 | 2026-06-22 10:22 | 2026-06-22 12:34 | 2:12 | S/O | Shutdown for 33KV T-1 Bus section red hot maintenance. | 12 | 26.4 | Power interruption
Chhatak 132/33kV | T-1 | 2026-06-29 22:50 | 2026-06-29 23:24 | 0:34 | S/O | For 33kV T-1 Bus DS Red Hot Maintenance Work. | 11 | 6.2333 | Power interruption
Cumilla(S) 132/33kV | TR-2 | 2026-06-03 07:20 | 2026-06-03 08:33 | 1:13 | S/O | 33Kv Palpara Feeder Redhot maintenance. | 31 | 37.7167 | Power interruption
Daganbhuiyan 132/33kV | Transformer-2 | 2026-06-12 07:43 | 2026-06-12 14:05 | 6:22 | S/O | Tr-02 33 KV load side PT change & loop jumpering | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-2 | 2026-06-20 09:57 | 2026-06-20 11:31 | 1:34 | S/O | Fuse Check & Change of Auxiliary X-Former -02 of X-former -02 | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-2 | 2026-06-21 11:07 | 2026-06-21 12:44 | 1:37 | S/O | HRC fuse change of auxilary transformer | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | TR-01 | 2026-06-22 16:06 | 2026-06-22 17:07 | 1:01 | S/O | PDB Feeder maintenance | 11 | 11.1833 | Power interruption
Feni 132/33kV | T-1(405T) | 2026-06-27 08:11 | 2026-06-27 10:34 | 2:23 | S/O | 33 KV PDB Salauddin Feeder Maintenance Work | 25 | 59.5833 | Power interruption
Feni 230/132kV | ATR-3 | 2026-06-13 11:10 | 2026-06-13 17:23 | 6:13 | S/O | Training work | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 AB | 2026-06-03 07:03 | 2026-06-03 09:04 | 2:01 | S/O | Reb take this shutdown for Reb-1 feeder Bus DS radhot maintenance | 24 | 48.4 | Power interruption
Kulaura 132/33kV | TR-1 AB | 2026-06-20 15:45 | 2026-06-20 16:40 | 0:55 | S/O | 33kv REB-1 feeder bus DS redhot maintenance.shutdown taken by Abdullah al Mamun,AGM Kulaura,PBS | 20 | 18.3333 | Power interruption
Lakshmipur 132/33kV | Transformer-1 | 2026-06-08 20:42 | 2026-06-08 22:20 | 1:38 | S/O | Fix Red Hot Problem. | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-2 | 2026-06-16 07:30 | 2026-06-16 13:04 | 5:34 | S/O | 33kV Load Side Redhot Work. | 0 | 0 | No interruption
Maijdee 132/33kV | Tr-02 | 2026-06-09 11:16 | 2026-06-09 11:43 | 0:27 | S/O | project work | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 | 2026-06-09 11:57 | 2026-06-09 12:14 | 0:17 | S/O | 132/33 kV Tr-02 HT S/D due to project work | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-06-03 08:24 | 2026-06-03 09:35 | 1:11 | S/O | Shutdown Taken by PBS for Redhot Maintenance. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-06-13 15:02 | 2026-06-13 18:38 | 3:36 | S/O | To connect new TR-06 transformer to the 33 kv bus | 60 | 216 | Power interruption
Shahjibazar 132/33kV | TR-06 | 2026-06-13 20:06 | 2026-06-14 21:13 | 25:07 | S/O | To connect 33kv cable with Transformer | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-06-14 18:44 | 2026-06-14 19:18 | 0:34 | S/O | Shutdown taken by PBS for Redhot Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 | 2026-06-18 10:45 | 2026-06-18 12:50 | 2:05 | S/O | New Olipur5 33 kV feeder Install. | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2026-06-20 09:00 | 2026-06-20 14:04 | 5:04 | S/O | Maint.work | 50 | 253.3333 | Power interruption
|  |  | Total : | 1900-01-22 03:36 |  |  |  | 866.1167
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-3 ( 423 T) | 2026-06-25 16:37 | 2026-06-25 18:46 | 2:09 | S/O | Remove the red hot Fakirhat-02 | 35 | 75.25 | Power interruption
Barguna 132/33kV | Transformer-2 | 2026-06-09 09:06 | 2026-06-09 19:41 | 10:35 | S/O | Replacement of Circuit Breaker of T2-A Incomer. | 0 | 0 | No interruption
Barishal 132/33kV | T-2 (415T) | 2026-06-04 06:16 | 2026-06-04 08:36 | 2:20 | S/O | Hot point maintenance. | 0 | 0 | No interruption
Barishal 132/33kV | Bus B | 2026-06-05 12:30 | 2026-06-28 08:52 | 548:22 | S/O | 132kv patuakhali &T3 Bay extention work | 0 | 0 | No interruption
Barishal 132/33kV | T-2 (415T) | 2026-06-14 16:14 | 2026-06-14 17:21 | 1:07 | S/O | WZPDCL Work. | 11 | 12.2833 | Power interruption
Barishal 132/33kV | T-1 (405T) | 2026-06-27 09:15 | 2026-06-27 10:56 | 1:41 | S/O | 33 kv Jhallokati Wzpdco feeder red hot maintenance Work | 40 | 67.3333 | Power interruption
Barishal 230/132kV | T-5 | 2026-06-07 07:46 | 2026-06-07 11:10 | 3:24 | S/O | red hot maintenance of 33 kVSwarupkathi-1 and Banaripara feeder by Pirojpur PBS | 38 | 129.2 | Power interruption
Barishal 230/132kV | T-4 | 2026-06-08 07:23 | 2026-06-08 09:23 | 2:00 | S/O | 33kv Babuganj Feeder R phase Ds problem | 0 | 0 | No interruption
Barishal 230/132kV | ATR-1 | 2026-06-08 11:26 | 2026-06-08 18:13 | 6:47 | S/O | Replacement of WTI & OTI | 0 | 0 | No interruption
Barishal 230/132kV | ATR-2 | 2026-06-09 11:33 | 2026-06-09 14:48 | 3:15 | S/O | WTI change | 0 | 0 | No interruption
Barishal 230/132kV | T-4 | 2026-06-10 06:20 | 2026-06-10 11:10 | 4:50 | S/O | 33 kV bus Section DS, Babuganj & Jhalakathi 33 kV feeder source DS Work. Work done by PBS | 29 | 140.1667 | Power interruption
Barishal 230/132kV | T-5 | 2026-06-10 06:21 | 2026-06-10 08:44 | 2:23 | S/O | 33 kV bus Section DS, Babuganj & Jhalakathi 33 kV feeder source DS Work. Work done by PBS | 29 | 69.1167 | Power interruption
Barishal 230/132kV | T-5 | 2026-06-13 06:18 | 2026-06-13 08:57 | 2:39 | S/O | Replacement of source DS of 33 kV Nobogram Feeder by Jhalokathi PBS. | 60 | 159 | Power interruption
Barishal 230/132kV | T-5 | 2026-06-15 15:01 | 2026-06-15 17:06 | 2:05 | S/O | Maintenance work of source DS of 33 kV Nobogram Feeder by Jhalokathi PBS. | 45 | 93.75 | Power interruption
Barishal 230/132kV | T-4 | 2026-06-15 17:27 | 2026-06-15 18:35 | 1:08 | S/O | T-4 incomer 33kv CT Nut bolt titining work purpose. | 0 | 0 | No interruption
Faridpur 132/33kV | 33 KV Bus | 2026-06-09 21:45 | 2026-06-09 22:30 | 0:45 | S/O | WZPDCO 33 kv Feeder Red-hot Maintenance. (33 kv Bus section-2, No 132 kv X-former Shutdown) | 0 | 0 | No interruption
Gopalganj 132/33kV | Transformer-03 | 2026-06-18 10:55 | 2026-06-18 11:56 | 1:01 | S/O | 33 kv energy meter change. | 0 | 0 | No interruption
Gopalganj 132/33kV | Transformer-03 | 2026-06-24 08:38 | 2026-06-24 10:27 | 1:49 | S/O | Md.Shakil Agm(A/C) Mollahat zonel office, Bagerhat Pbs. Breaker to ds clamp maintenance (B-Phase). | 14 | 25.4333 | Power interruption
Madaripur 132/33kV | T2-415T | 2026-06-04 07:42 | 2026-06-04 10:23 | 2:41 | S/O | Agoiljhora 33kv feeder source ds problem | 25 | 67.0833 | Power interruption
Narail 132/33kV | TR2 (413-T) | 2026-06-22 07:19 | 2026-06-22 08:49 | 1:30 | S/O | 33kV N6 Feeder Bus Side Red Hot Maintenance. | 7 | 10.5 | Power interruption
Noapara 132/33kV | T-1 | 2026-06-04 07:24 | 2026-06-04 10:55 | 3:31 | S/O | DUE TO RED HOT MAINTENANCE OF REB-3 FEEDER BY PBS. | 0 | 0 | No interruption
Noapara 132/33kV | Bus Section-1 | 2026-06-04 07:28 | 2026-06-04 10:56 | 3:28 | S/O | DUE TO RED HOT MAINTENANCE OF REB-3 FEEDER BY PBS. | 20 | 69.3333 | Power interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-01 | 2026-06-29 06:28 | 2026-06-29 18:10 | 11:42 | S/O | High temperature maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-02 | 2026-06-30 06:48 | 2026-06-30 18:15 | 11:27 | S/O | High Temparature Maintenance | 0 | 0 | No interruption
Charfasson 230/33kV | Power Transformer-2 | 2026-06-23 08:09 | 2026-06-23 09:44 | 1:35 | S/O | CT ratio with burden test. | 24 | 38 | Power interruption
|  |  | Total : | 1900-01-25 10:14 |  | Unserved Energy : |  | 956.45
HVDC Grid Circle
BIPTC | 20DF23 | 2026-06-17 10:40 | 2026-06-17 15:48 | 5:08 | S/O | Red hot maintenance of cell | 0 | 0 | No interruption
Chuadanga 132/33kV | 132kV Tr. T1(416T) | 2026-06-18 22:48 | 2026-06-19 00:33 | 1:45 | S/O | Red hot maintenance work. | 50 | 87.5 | Power interruption
Ishurdi 230/132kV | 230 kV Bus 1 | 2026-06-11 09:12 | 2026-06-11 12:52 | 3:40 | S/O | loop jumper connection of Transformer T-03 with bus-1 | 0 | 0 | No interruption
Ishurdi 230/132kV | 230/132 kV T-01 | 2026-06-17 10:07 | 2026-06-17 15:22 | 5:15 | S/O | CB 615B testing | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Bus 2 | 2026-06-24 10:17 | 2026-06-24 11:40 | 1:23 | S/O |  | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Bus 1 | 2026-06-24 12:23 | 2026-06-24 13:06 | 0:43 | S/O |  | 0 | 0 | No interruption
Jashore 132/33kV | T-1 | 2026-06-08 05:37 | 2026-06-08 09:48 | 4:11 | S/O | Repair work of 33/.04 kv 200 kVA Auxiliary transformer | 4 | 16.7333 | Power interruption
Jashore 132/33kV | T-1 | 2026-06-21 05:30 | 2026-06-21 10:40 | 5:10 | S/O | repair work of 33/.4 kv, 200 KVA Auxiliary Transformer. | 0 | 0 | No interruption
Jashore 132/33kV | T-1 | 2026-06-29 05:14 | 2026-06-29 06:16 | 1:02 | S/O | T1A CB Y-phase red hot maintenance | 0 | 0 | No interruption
Jashore 132/33kV | T-2 | 2026-06-29 06:35 | 2026-06-29 08:50 | 2:15 | S/O | T2A CB Y-phase red hot maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV | 230 kV Bus | 2026-06-24 06:34 | 2026-06-25 14:36 | 32:02 | S/O | 230 kV Bus-1 Shutdown (For project work) | 0 | 0 | No interruption
Jhenaidah 230/132kV | 132 kV Bus | 2026-06-26 06:33 | 2026-06-26 22:36 | 16:03 | S/O | 132Kv Bus bar extension for T-3 Installation. | 0 | 0 | No interruption
Jhenaidah 230/132kV | 230 kV Bus | 2026-06-27 07:19 | 2026-06-27 17:28 | 10:09 | S/O | 230 kv Bus -2 Shutdown Project Work | 0 | 0 | No interruption
Kushtia 132/33kV | 132 KV Bus-B | 2026-06-15 08:00 | 2026-06-18 10:36 | 74:36 | S/O | DWZTGE প্রকল্পের আওতায় কুষ্টিয়া-মেহেরপুর বে এর কাজের জন্য বাস A থেকে B তে শিফট | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 19:22 |  | Unserved Energy : |  | 104.2333
Bogura Grid Circle:
Amnura 132/33kV | T-1 (406T) | 2026-06-13 11:15 | 2026-06-13 15:39 | 4:24 | S/O | Maintenance in LT Bushing, Clearance, ALDC, Bogura. | 0 | 0 | No interruption
Lalmonirhat 132/33kV | T-1 (425T) | 2026-06-10 06:15 | 2026-06-10 07:02 | 0:47 | S/O | T-01 33KV incoming circuit breaker Red Hot maintenance | 0 | 0 | No interruption
Mahasthangarh 132/33kV | 406T MTR1 | 2026-06-20 11:16 | 2026-06-20 14:53 | 3:37 | S/O | NESCO 33kv feeder redhot | 10 | 36.1667 | Power interruption
Niamatpur 132/33kV | Transformer-3(426T) | 2026-06-09 09:50 | 2026-06-09 12:56 | 3:06 | S/O | T-3 33 kV source bus DS maintenance work | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-06-25 09:18 | 2026-06-25 14:48 | 5:30 | S/O | T-1 33 DS maintenance. | 0 | 0 | No interruption
Panchagarh 132/33kV | T-2(417T) | 2026-06-29 09:16 | 2026-06-29 10:31 | 1:15 | S/O | Red Hot Maintenance work on 33kv bus Section-02 (T-2) | 8 | 10 | Power interruption
Purbasadipur 230/132/33kV | AIS Old T-4 Transformer | 2026-06-20 10:30 | 2026-06-20 12:30 | 2:00 | S/O | Maintenance worj | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | TR-4 | 2026-06-25 07:36 | 2026-06-25 09:42 | 2:06 | S/O | Uthrail 33kv feeder red hot | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | TR-2 | 2026-06-29 12:40 | 2026-06-29 12:40 | 0:00 | S/O | old name T-1. project work. transformer in open condition | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | TR-3 | 2026-06-29 12:45 | 2026-06-29 12:45 | 0:00 | S/O | old name T-2. project work. transformer in open condition | 0 | 0 | No interruption
Rangpur 132/33kV | T-2 (404T) | 2026-06-14 06:07 | 2026-06-14 07:35 | 1:28 | S/O | Red hot Maintenance work | 0 | 0 | No interruption
Saidpur 132/33kV | TR-3 (424T) | 2026-06-19 09:04 | 2026-06-19 09:36 | 0:32 | S/O | 33kv parbatipur Nesco feeder Y-phase raiser loop change. | 20 | 10.6667 | Power interruption
Saidpur 132/33kV | TR-2 (404T) | 2026-06-30 06:08 | 2026-06-30 07:21 | 1:13 | S/O | 33 KV EPZ Feeder (Bus DS) red hot maintainance. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 01:58 |  | Unserved Energy : |  | 56.8333
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2546:24 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:June 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bajitpur 132/33kV | Kishoreganj Ckt-1 | 2026-06-04 08:42 | 2026-06-04 10:43 | 2:01 | S/O | Due to VT alarm Removal purpose. | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-1 | 2026-06-04 08:42 | 2026-06-04 10:43 | 2:01 | S/O | Due to VT alarm Removal purpose. | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-2 | 2026-06-06 09:16 | 2026-06-06 12:31 | 3:15 | S/O | Red hot maintenance | 20 | 65 | Power interruption
Bajitpur 132/33kV | Ashuganj Ckt-1 | 2026-06-11 07:18 | 2026-06-11 11:07 | 3:49 | S/O | Maint.work | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-1 | 2026-06-13 06:31 | 2026-06-13 12:57 | 6:26 | S/O | Maint.work | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Ghorashal ckt-2 | 2026-06-13 06:31 | 2026-06-13 12:58 | 6:27 | S/O | Maint.work | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Lalbag Ckt-01 | 2026-06-25 08:14 | 2026-06-25 13:37 | 5:23 | S/O | Disk Insulator Change Work | 0 | 0 | No interruption
Kallyanpur 132/33kV | 132Kv Kallyanpur-Lalbag Ckt-02 | 2026-06-25 13:42 | 2026-06-25 21:48 | 8:06 | S/O | line work | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-2 | 2026-06-11 09:55 | 2026-06-11 12:00 | 2:05 | S/O | Maint.work | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2026-06-12 07:15 | 2026-06-12 17:38 | 10:23 | S/O | S/D taken by RPCL | 0 | 0 | No interruption
Muktagacha 132/33kV | RPCL-1 | 2026-06-13 09:27 | 2026-06-13 16:42 | 7:15 | S/O | Work by RPCL | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-RPCL Ckt-1 | 2026-06-11 12:37 | 2026-06-11 13:55 | 1:18 | S/O | Maintenance work RPCL end. | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-RPCL Ckt-1 | 2026-06-17 10:44 | 2026-06-17 11:15 | 0:31 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-RPCL Ckt-2 | 2026-06-17 11:16 | 2026-06-17 11:35 | 0:19 | S/O | Relay testing of RPCL end. | 0 | 0 | No interruption
Tangail 132/33kV | RPCL-1 | 2026-06-05 06:00 | 2026-06-05 10:16 | 4:16 | S/O | OPGW Re-conductoring | 0 | 0 | No interruption
Tangail 132/33kV | RPCL-2 | 2026-06-05 06:00 | 2026-06-05 10:17 | 4:17 | S/O | OPGW Re-conductoring | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kaliakoir Ckt | 2026-06-07 23:28 | 2026-06-08 11:34 | 12:06 | S/O | Due to flashing on Tower no 96 | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kaliakoir Ckt | 2026-06-09 11:12 | 2026-06-09 14:19 | 3:07 | S/O | taken by kaliyakair via NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-06-09 16:21 | 2026-06-09 19:57 | 3:36 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 14:41 |  | Unserved Energy: |  | 65
Dhaka (South) Grid Circle :
Bhulta 132/33kV | Haripur | 2026-06-03 05:58 | 2026-06-03 08:05 | 2:07 | S/O | Fault Due to Redhot of DS of Y phase of 132 kV Line. | 80 | 169.3333 | Power interruption
Bhulta 132/33kV | Haripur | 2026-06-05 10:52 | 2026-06-05 12:50 | 1:58 | S/O | For changing DS(203) finger and maintenance riser point(B Phase) | 0 | 0 | No interruption
Bhulta 132/33kV | Narsingdi | 2026-06-05 12:53 | 2026-06-08 12:39 | 71:46 | S/O | This line using Only for backup time so it’s must be shutdown always from bhulta 132KV end. | 0 | 0 | No interruption
Bhulta 132/33kV | Haripur | 2026-06-08 12:44 | 2026-06-08 16:00 | 3:16 | S/O | For changing DS(203) finger | 35 | 114.3333 | Power interruption
Bhulta 132/33kV | Narsingdi | 2026-06-08 16:04 | 2026-06-08 16:04 | 0:00 | S/O | This line using Only for backup time so it’s must be shutdown always from bhulta 132KV end. | 0 | 0 | No interruption
Bhulta 400/230kV | Horipur-02 | 2026-06-18 09:20 | 2026-06-18 11:55 | 2:35 | S/O | Maintenance work | 0 | 0 | No interruption
Bhulta 400/230kV | Horipur-02 | 2026-06-26 09:03 | 2026-06-26 16:59 | 7:56 | S/O | Maintenance work | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2026-06-01 09:35 | 2026-06-01 09:35 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Bhulta-2 | 2026-06-18 09:25 | 2026-06-18 12:03 | 2:38 | S/O | Bus-1 Side CT Test by RTS. | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Bhulta-2 | 2026-06-26 09:01 | 2026-06-26 16:57 | 7:56 | S/O | Bus-1 Blue Phase CT Replacing Work | 0 | 0 | No interruption
Haripur 230/132kV | EGCB 412MW | 2026-06-13 06:23 | 2026-06-15 09:29 | 51:06 | S/O | Jack bus loop change. | 0 | 0 | No interruption
Maniknagar 132/33kV | Kazla Ckt -2 | 2026-06-05 11:38 | 2026-06-05 12:16 | 0:38 | S/O | Dc supply replacement work with new charger /distribution panel for main and backup protection relay.. Work by DPDC. | 0 | 0 | No interruption
Maniknagar 132/33kV | Kazla Ckt -1 | 2026-06-05 12:20 | 2026-06-05 13:09 | 0:49 | S/O | 132 kV Kazla Ckt -2 Scheduled S/D due to Dc supply replacement work with new charger /distribution panel for main and backup protection relay.. Work by DPDC.. | 0 | 0 | No interruption
Maniknagar 132/33kV | Mero Rail - 2 | 2026-06-19 08:56 | 2026-06-19 12:34 | 3:38 | S/O | Dc supply replacement work with new charger /distribution panel for main and backup protection relay.. Work by DPDC... | 0 | 0 | No interruption
Maniknagar 230/132kV | 230kV Siddhirganj-Maniknagar ckt-2 | 2026-06-20 06:52 | 2026-06-21 23:28 | 40:36 | S/O | Repair of sky wire | 0 | 0 | No interruption
Meghnaghat 230/132kV | Bus2 | 2026-06-09 07:45 | 2026-06-09 15:45 | 8:00 | S/O | rad hot maintenance | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-1 | 2026-06-24 09:29 | 2026-06-24 19:07 | 9:38 | S/O | Maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-1 | 2026-06-25 09:00 | 2026-06-25 18:22 | 9:22 | S/O | Maintenance work | 0 | 0 | No interruption
Shyampur 132/33kV | Shyampur Circuit-1 | 2026-06-22 09:20 | 2026-06-22 14:58 | 5:38 | S/O | working for circuit-1 | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-1(E07) | 2026-06-18 16:52 | 2026-06-18 20:52 | 4:00 | S/O | for connecting Pot Head to Line (Gantry) by Loop. (shutdown taken by DPDC). | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Shyampur old-1(E07) | 2026-06-22 09:20 | 2026-06-22 14:55 | 5:35 | S/O | Short span jumper opening between Shy-1 & Fat-1 circuit. | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV APR (D04) | 2026-06-28 06:05 | 2026-06-28 08:31 | 2:26 | S/O | NLDC Requirements | 0 | 0 | No interruption
Siddhirganj 230/132kV | Maniknagar 2 | 2026-06-20 06:54 | 2026-06-21 23:28 | 40:34 | S/O | OPGW Replacement work between 10-13 No tower. | 0 | 0 | No interruption
Sonargaon 132/33kV | OPSL(IEL-2) | 2026-06-07 10:40 | 2026-06-07 13:31 | 2:51 | S/O | OPSL end 132KV CB relay faulty signals. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-10 21:03 |  | Unserved Energy: |  | 283.6667
Chattogram Grid Circle :
Chandraghona 132/33kV | Chandraghona- Rangamati Ckt-01 | 2026-06-08 11:12 | 2026-06-08 13:31 | 2:19 | S/O | Relay test | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Khulshi-Ckt.-3 | 2026-06-01 12:53 | 2026-06-01 14:26 | 1:33 | S/O | To remove jute cloth from b phase conductor. | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Julda Ckt. line | 2026-06-26 06:13 | 2026-06-26 08:07 | 1:54 | S/O | Maint.work | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-06-26 06:14 | 2026-06-26 08:09 | 1:55 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Khagrachori 132/33kV | RANGAMATI-2 | 2026-06-08 13:47 | 2026-06-08 14:59 | 1:12 | S/O | Panel Realy test | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-06-24 09:30 | 2026-06-24 19:09 | 9:39 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-06-25 08:59 | 2026-06-25 18:23 | 9:24 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Mirsharai-2 | 2026-06-24 08:55 | 2026-06-24 21:13 | 12:18 | S/O | For project work | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Kulshi-2 | 2026-06-29 11:10 | 2026-06-29 11:10 | 0:00 | S/O | B-phase jumper maintenance at 822 tower by Khulsi SS | 0 | 0 | No interruption
Rangamati 132/33kV | Chandraghona Ckt-01 | 2026-06-08 11:11 | 2026-06-08 13:32 | 2:21 | S/O | Rangamati - Chandraghona Ckt-01 has taken Shutdown due to annual relay testing works. | 0 | 0 | No interruption
Rangamati 132/33kV | Khagrachari Ckt-02 | 2026-06-08 13:47 | 2026-06-08 14:57 | 1:10 | S/O | Rangamati-Khagrachori Ckt-02 has taken Shutdown due annual relay testing works. | 0 | 0 | No interruption
Rangamati 132/33kV | Khagrachari Ckt-01 | 2026-06-08 15:03 | 2026-06-08 15:28 | 0:25 | S/O | Rangamati-Khagrachori Ckt-01 has taken Shutdown due to annual relay testing works. | 0 | 0 | No interruption
Rangamati 132/33kV | Chandraghona Ckt-02 | 2026-06-08 15:31 | 2026-06-08 16:04 | 0:33 | S/O | Rangamati-Chardraghona Ckt-01 has taken shutdown due to annual relay testing works. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 20:43 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Chowmuhani 230/132/33kV | Maijdee-01 | 2026-06-07 09:13 | 2026-06-07 18:27 | 9:14 | S/O | Project work | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Maijdee-01 | 2026-06-08 08:20 | 2026-06-08 10:45 | 2:25 | S/O | 132 kv GIS control Room painting . | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Maijdee-01 | 2026-06-09 08:35 | 2026-06-09 18:45 | 10:10 | S/O | Maint.work | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Maijdee-02 | 2026-06-10 08:25 | 2026-06-10 18:51 | 10:26 | S/O | GIS building outside painting. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Maijdee-02 | 2026-06-11 07:36 | 2026-06-11 19:53 | 12:17 | S/O | 132 KV GIS Building Outdoor Painting | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Maijdee-02 | 2026-06-12 08:20 | 2026-06-12 17:47 | 9:27 | S/O | Building Outside Painting. | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-2 | 2026-06-28 09:33 | 2026-06-28 17:58 | 8:25 | S/O | Project work at feni 230kv end . FES1 Is not close due to problem at Daganbhuiyan end . Feni 230kv s/s done local grounding . | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Chowmuhuni ckt-1 | 2026-06-29 08:40 | 2026-06-29 15:29 | 6:49 | S/O | Shutdown taken at feni 230 kv end due to project work. | 0 | 0 | No interruption
Feni 132/33kV | Barayerhat Ckt | 2026-06-23 15:25 | 2026-06-23 16:22 | 0:57 | S/O | For Breaker Gas Refilling. | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-4 | 2026-06-30 09:05 | 2026-06-30 14:46 | 5:41 | S/O | For project work at Feni 230kv grid end | 0 | 0 | No interruption
Feni 230/132kV | Cumilla(North)-1 | 2026-06-29 12:46 | 2026-06-29 14:45 | 1:59 | S/O | Red hot maintainance Cumilla north Grid end | 0 | 0 | No interruption
Feni 230/132kV | Feni-4 | 2026-06-30 09:05 | 2026-06-30 14:47 | 5:42 | S/O | project work | 0 | 0 | No interruption
Feni 230/132kV | Dagonbhuyan-2 | 2026-06-28 09:35 | 2026-06-28 17:56 | 8:21 | S/O | 132kv daghunbuiya circuit-2 s/d due to project work at breaker wiring mismatch | 0 | 0 | No interruption
Feni 230/132kV | Dagonbhuyan-1 | 2026-06-29 08:44 | 2026-06-29 16:29 | 7:45 | S/O | project work | 0 | 0 | No interruption
Maijdee 132/33kV | Chowmuhoni-Maijdee ckt -01 | 2026-06-07 09:12 | 2026-06-07 18:27 | 9:15 | S/O | project work | 0 | 0 | No interruption
Maijdee 132/33kV | Chowmuhoni-Maijdee ckt -01 | 2026-06-08 09:14 | 2026-06-08 10:47 | 1:33 | S/O | Due to project work at Chowmuhani 230/132/33 KV Grid. | 0 | 0 | No interruption
Maijdee 132/33kV | Chowmuhoni-Maijdee ckt -01 | 2026-06-09 08:34 | 2026-06-09 18:46 | 10:12 | S/O | Project work | 0 | 0 | No interruption
Maijdee 132/33kV | Chowmuhoni-Maijdee ckt -02 | 2026-06-10 08:20 | 2026-06-10 18:52 | 10:32 | S/O | project work | 0 | 0 | No interruption
Maijdee 132/33kV | Chowmuhoni-Maijdee ckt -02 | 2026-06-11 07:42 | 2026-06-11 19:54 | 12:12 | S/O | Project work at chowmuhani 230/132/33 KV S/S. | 0 | 0 | No interruption
Maijdee 132/33kV | Chowmuhoni-Maijdee ckt -02 | 2026-06-12 08:19 | 2026-06-12 17:48 | 9:29 | S/O | Due to Project Work at Chowmuhoni 230/132/33 KV Grid Substation. | 0 | 0 | No interruption
Muradnagar 132/33kV | 132 KV Muradnagar- Cumilla(N) Ckt-01 | 2026-06-29 07:34 | 2026-06-29 08:20 | 0:46 | S/O | Line maintenance work. | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-06-23 10:14 | 2026-06-23 12:00 | 1:46 | S/O | Shutdown taken by B.Baria | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2026-06-04 10:30 | 2026-06-04 11:11 | 0:41 | S/O | bird's nest remove. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 12:04 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Amtali 400/132kV | Amtali - Payra 400 kV Ckt - 2 | 2026-06-19 03:26 | 2026-06-19 07:24 | 3:58 | S/O | Work at Payra end | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-06-05 06:05 | 2026-06-05 13:00 | 6:55 | S/O | Suspension Disc insulator change of 5 no. Tower. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Mongla 2 | 2026-06-20 20:08 | 2026-06-20 21:18 | 1:10 | S/O | R Phase Disc insulator change | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-06-30 15:47 | 2026-06-30 17:25 | 1:38 | S/O | Project work in Bhandaria. instructions from ALDC | 0 | 0 | No interruption
Bakerganj 132/33kV | 132 kV Bakerganj Barguna Ckt | 2026-06-26 06:59 | 2026-06-26 08:31 | 1:32 | S/O | 132 kV Barishal ckt jumper out. | 0 | 0 | No interruption
Bakerganj 132/33kV | 132 kV Bakerganj Patuakhali Ckt | 2026-06-26 07:02 | 2026-06-26 08:29 | 1:27 | S/O | 132 kV Barishal ckt jumper out. | 10.6 | 15.37 | Power interruption
Barguna 132/33kV | Barguna-Bakergonj 132kv line | 2026-06-26 06:58 | 2026-06-26 08:31 | 1:33 | S/O | Project work at Barishal Patuakhali line | 18 | 27.9 | Power interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2026-06-01 12:56 | 2026-06-01 13:45 | 0:49 | S/O | Bhandaria CT secondary short | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2026-06-04 09:29 | 2026-06-04 11:22 | 1:53 | S/O | High temperature maintenance at different points | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2026-06-29 21:44 | 2026-06-30 19:40 | 21:56 | S/O | for repair the line | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2026-06-30 19:50 | 2026-07-01 07:15 | 11:25 | S/O | Joining the broken conductor | 0 | 0 | No interruption
Barishal 132/33kV | 132 kv Summit power | 2026-06-28 10:38 | 2026-06-28 12:19 | 1:41 | S/O | Summit end work, B phase mct post | 0 | 0 | No interruption
Barishal 230/132kV | Madaripur ckt-02 | 2026-06-21 20:10 | 2026-06-22 08:39 | 12:29 | S/O | Tripped line conductor repair work | 0 | 0 | No interruption
Bhandaria 132/33kV | Barishal (L4) | 2026-06-04 09:28 | 2026-06-04 11:23 | 1:55 | S/O | Shutdown taken by Barishal 132/33 kV Grid SS | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2026-06-21 15:47 | 2026-06-21 17:11 | 1:24 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-1 | 2026-06-30 12:22 | 2026-06-30 13:12 | 0:50 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2026-06-30 13:13 | 2026-06-30 14:04 | 0:51 | S/O | Maint.work | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Khulna Central-1 | 2026-06-16 10:11 | 2026-06-16 15:10 | 4:59 | S/O | y phase 0 Amp | 0 | 0 | No interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2026-06-25 09:37 | 2026-06-27 21:16 | 59:39 | S/O | Lilo at rupsha ss | 0 | 0 | No interruption
Gollamari 132/33kV | E07 Gollamari-Gopalgonj Line - 2 | 2026-06-25 09:37 | 2026-06-27 21:16 | 59:39 | S/O | Lilo at rupsha ss | 0 | 0 | No interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2026-06-30 15:10 | 2026-06-30 17:28 | 2:18 | S/O | Due to Satkhira-Rupsha line charge for trail basis | 0 | 0 | No interruption
Gollamari 132/33kV | E07 Gollamari-Gopalgonj Line - 2 | 2026-06-30 15:11 | 2026-06-30 17:30 | 2:19 | S/O | Due to Satkhira-Rupsha line charge for trail basis | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-2 | 2026-06-02 09:29 | 2026-06-02 11:24 | 1:55 | S/O | CB Closing circuit troubling shooting | 0 | 0 | No interruption
Gopalganj 132/33kV | Gopalganj North-2 | 2026-06-17 09:43 | 2026-06-17 13:52 | 4:09 | S/O | Clamp and Loop Change | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-1 | 2026-06-25 09:33 | 2026-06-27 21:15 | 59:42 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-2 | 2026-06-25 09:33 | 2026-06-27 21:15 | 59:42 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-1 | 2026-06-30 15:10 | 2026-06-30 15:10 | 0:00 | S/O | project work | 0 | 0 | No interruption
Gopalganj 132/33kV | Gallamari-2 | 2026-06-30 15:19 | 2026-06-30 15:19 | 0:00 | S/O | project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-1 | 2026-06-04 10:04 | 2026-06-04 17:00 | 6:56 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-2 | 2026-06-04 10:04 | 2026-06-04 17:00 | 6:56 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Gopalganj Ckt-1 | 2026-06-13 11:20 | 2026-06-13 13:24 | 2:04 | S/O | Gopalganj 132 KV SS has taken S/D for CT maintenance at their end | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Gopalganj Ckt-2 | 2026-06-17 09:44 | 2026-06-17 13:52 | 4:08 | S/O |  | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-1 | 2026-06-29 08:47 | 2026-06-29 08:47 | 0:00 | S/O |  | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-01 | 2026-06-30 12:23 | 2026-06-30 13:10 | 0:47 | S/O |  | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-02 | 2026-06-30 13:13 | 2026-06-30 14:02 | 0:49 | S/O |  | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Goalpara-1 | 2026-06-15 15:37 | 2026-06-15 17:07 | 1:30 | S/O | Y phase current missing DS & CB Goalpara ckt 1 | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Goalpara-1 | 2026-06-16 10:12 | 2026-06-16 15:10 | 4:58 | S/O | S/D ordered by ALDC | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -2 | 2026-06-28 15:41 | 2026-06-28 17:05 | 1:24 | S/O | Relay test by spmd, khulna | 45 | 63 | Power interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2026-06-23 08:46 | 2026-06-23 10:01 | 1:15 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Jhenaidah Ckt-1 | 2026-06-27 06:56 | 2026-06-27 18:02 | 11:06 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | PDB 330MW CCPP | 2026-06-22 10:23 | 2026-06-22 14:26 | 4:03 | S/O | Maintenance Work at power Plant end. | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-01 | 2026-06-04 10:02 | 2026-06-04 17:01 | 6:59 | S/O | Schedule shutdown | 0 | 0 | No interruption
Madaripur 132/33kV | Gopaganj North CKT-02 | 2026-06-04 10:03 | 2026-06-04 17:01 | 6:58 | S/O | Schedule shutdown | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 1 | 2026-06-29 23:55 | 2026-06-30 00:12 | 0:17 | S/O | By the instruction of ALDC. | 0 | 0 | No interruption
Patuakhali 132/33kV | Bakergonj-Pautakhali 132kV Line | 2026-06-26 07:01 | 2026-06-26 08:29 | 1:28 | S/O | Loop connection at Barishal and Loop disconnect at BakergonJ | 26 | 38.1333 | Power interruption
Payra 400/132/33kV | Payra Patuakhali Line-01 | 2026-06-25 06:00 | 2026-06-25 15:07 | 9:07 | S/O | High temperature Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-02 | 2026-06-25 15:37 | 2026-06-25 17:34 | 1:57 | S/O | High Temperature Maintenance | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2026-06-23 08:45 | 2026-06-28 10:02 | 121:17 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-20 17:47 |  | Unserved Energy: |  | 144.4033
HVDC Grid Circle :
BIPTC | Baharampur-3 | 2026-06-25 10:14 | 2026-06-25 18:42 | 8:28 | S/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2026-06-26 10:33 | 2026-06-26 20:49 | 10:16 | S/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2026-06-27 10:12 | 2026-06-27 18:18 | 8:06 | S/O | Shutdown is taken by baharampur end. | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Ishurdi -1 | 2026-06-06 09:18 | 2026-06-18 21:35 | 300:17 | S/O | Relay Testing Ishurdi end. | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari- Ishurdi-2 | 2026-06-23 09:41 | 2026-06-23 15:03 | 5:22 | S/O | SS Upgradation | 0 | 0 | No interruption
Bheramara 230/132kV | Kushtia 1 | 2026-06-13 06:08 | 2026-06-13 20:31 | 14:23 | S/O | Kushtia Grid maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Baghabari 1 | 2026-06-06 09:21 | 2026-06-18 21:35 | 300:14 | S/O | maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Baghabari 2 | 2026-06-23 09:41 | 2026-06-23 09:41 | 0:00 | S/O | Bay equipment upgradation | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Jhenaidah (Old) Ckt-3 | 2026-06-26 09:26 | 2026-06-26 22:03 | 12:37 | S/O | 132kV Bus bar Relay Protection testing | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-Khulna (South) Ckt-1 | 2026-06-27 06:56 | 2026-06-27 18:04 | 11:08 | S/O | project work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Jashore Ckt-1 | 2026-06-27 09:30 | 2026-06-27 10:49 | 1:19 | S/O | Project Work | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia -Bheramara-1 | 2026-06-13 06:07 | 2026-06-13 20:33 | 14:26 | S/O | maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-27 14:36 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bog-Sherpur 132/33kV | Sherpur-Sirajgonj Ckt-2 | 2026-06-24 09:17 | 2026-06-24 12:38 | 3:21 | S/O | maint.work | 0 | 0 | No interruption
Bogura 132/33kV | New Bogura-2 | 2026-06-26 07:08 | 2026-06-26 19:42 | 12:34 | S/O | OPGW Maintenance work | 0 | 0 | No interruption
Bogura 230/132kV | Bogra 132KV Line-2 | 2026-06-26 07:08 | 2026-06-26 19:43 | 12:35 | S/O | OPW replacement | 0 | 0 | No interruption
Bogura 230/132kV | Naogaon 132 KV Line-1 | 2026-06-28 15:58 | 2026-06-28 15:58 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-1 | 2026-06-18 06:59 | 2026-06-18 18:05 | 11:06 | S/O | Jumpering works | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Naogaon 230 kV Ckt-2 | 2026-06-18 06:59 | 2026-06-18 18:04 | 11:05 | S/O | Jumpering works | 0 | 0 | No interruption
Joypurhat 132/33kV | Naogaon Ckt.-1 | 2026-06-27 12:44 | 2026-06-27 18:56 | 6:12 | S/O | S/D taken at Noagaon ss end | 0 | 0 | No interruption
Joypurhat 132/33kV | Patnitola Ckt.-1 | 2026-06-27 14:12 | 2026-06-27 21:16 | 7:04 | S/O | Poject Work | 0 | 0 | No interruption
Joypurhat 132/33kV | Patnitola Ckt.-2 | 2026-06-27 14:13 | 2026-06-27 21:17 | 7:04 | S/O | Poject Work | 0 | 0 | No interruption
Joypurhat 132/33kV | Patnitola Ckt.-1 | 2026-06-28 11:13 | 2026-06-28 16:19 | 5:06 | S/O | Maint.work | 0 | 0 | No interruption
Joypurhat 132/33kV | Patnitola Ckt.-2 | 2026-06-28 11:14 | 2026-06-28 16:20 | 5:06 | S/O | Maint.work | 0 | 0 | No interruption
Joypurhat 132/33kV | Patnitola Ckt.-1 | 2026-06-30 14:54 | 2026-06-30 15:02 | 0:08 | S/O | 132 kv circuit demarkkation | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Rangpur-Lalmonirhat | 2026-06-09 10:54 | 2026-06-09 19:49 | 8:55 | S/O | Installation of distance relay | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Joypurhat Ckt-1 | 2026-06-27 12:45 | 2026-06-27 18:54 | 6:09 | S/O | AIS bay dismantled | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-1 | 2026-06-20 08:47 | 2026-06-20 14:43 | 5:56 | S/O | Maint.work | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-2 | 2026-06-20 08:48 | 2026-06-20 14:40 | 5:52 | S/O | Maint.work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Confidence-1 | 2026-06-05 09:24 | 2026-06-05 13:11 | 3:47 | S/O | Temperature Rises | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Confidence-2 | 2026-06-12 08:54 | 2026-06-16 17:35 | 104:41 | S/O | CT and Breaker change from 12/06/2026 to 15/06/2026 | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Teesta Solar-1 | 2026-06-26 15:15 | 2026-06-26 23:53 | 8:38 | S/O | OPGW Replace | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Teesta Solar-2 | 2026-06-26 15:16 | 2026-06-26 23:53 | 8:37 | S/O | OPGW Replace | 0 | 0 | No interruption
Sirajganj 132/33kV | Sherpur-2 | 2026-06-24 09:17 | 2026-06-24 12:39 | 3:22 | S/O | Conductor Armoring Work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-08 21:18 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-03-24 02:12 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:June 2026
| Area | Previous Month (May' 2026) |  |  |  | Current Month (June'2026)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 37 | 15 | 104 | 156 | 30 | 13 | 44 | 87
2 | Dhaka (South) Grid Circle. | 50 | 25 | 58 | 133 | 16 | 7 | 59 | 82
3 | Chattogram Grid Circle. | 24 | 10 | 49 | 83 | 11 | 11 | 41 | 63
4 | Cumilla Grid Circle. | 38 | 26 | 67 | 131 | 31 | 20 | 58 | 109
5 | Khulna Grid Circle. | 31 | 17 | 120 | 168 | 39 | 22 | 73 | 134
6 | HVDC Grid Circle | 20 | 32 | 46 | 98 | 5 | 16 | 26 | 47
7 | Bogura Grid Circle. | 43 | 41 | 70 | 154 | 26 | 13 | 34 | 73
8 | Others
9 | Total | 243 | 166 | 514 | 923 | 158 | 102 | 335 | 595
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month: June 2026
| Area | Previous Month (May' 2026) |  |  |  | Current Month (June '2026)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 867.78 | 273.47 | 2634.07 | 3775.32 | 1054.5 | 91 | 352.42 | 1497.92
2 | Dhaka (South) Grid Circle. | 875.26 | 530.73 | 752.45 | 2158.44 | 425.16 | - | 3271.29 | 3696.45
3 | Chattogram Grid Circle. | 90.47 | 44.8 | 3148.76 | 3284.03 | 57.5 | 181.83 | 298.7 | 538.03
4 | Cumilla Grid Circle. | 164.53 | 277.17 | 1153.75 | 1595.45 | 650.55 | 290.83 | 866.12 | 1807.5
5 | Khulna Grid Circle. | 262.05 | 94.18 | 2668.35 | 3024.58 | 312.77 | 71.33 | 1100.85 | 1484.95
6 | HVDC Grid Circle | 66.57 | 384.83 | 566.68 | 1018.08 | 13.07 | 128.92 | 104.23 | 246.22
7 | Bogura Grid Circle. | 360.95 | 389.48 | 561.58 | 1312.01 | 201.5 | 21.35 | 56.83 | 279.68
8 | Others | bar: Energy unserved ( MWH ) due to Total; Energy unserved ( MWH ) due to Total
9 | Total | 2687.61 | 1994.66 | 11485.64 | 16167.91 | 2715.05 | 785.26 | 6050.44 | 9550.75
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:June 2026
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 18 | 4 | 22 | 12 | 3 | 7 | 1018.02
2 | Dhaka (South) | 5031.6 | 4 | 15 | 19 | 5 | 1 | 13 | 3034.55
3 | Chattogram | 2042 | 7 | 4 | 11 | 3 | 1 | 7 | 538.03
4 | Cumilla | 2981 | 20 | 15 | 35 | 10 | 6 | 19 | 1499.23
5 | Khulna | 2434 | 18 | 13 | 31 | 9 | 5 | 17 | 1332.75
6 | HVDC | 5954.3 | 5 | 2 | 7 | - | 4 | 3 | 246.22
7 | Bogura | 3145.6 | 12 | 3 | 15 | 7 | 4 | 4 | 222.92
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 7891.72
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 98.97%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | HVDC | 99.99%
6 | Bogura | 99.99%
7 | Cumilla | 99.98% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:June 2026
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 7 | 1 | 8 | 1 | 4 | 3 | 479.9
2 | Dhaka (South) | 990.29 | - | 4 | 2 | 6 | 1 | 2 | 3 | 661.9
3 | Chattogram | 917 | - | - | - | - | - | - | - | -
4 | Cumilla | 1648.16 | - | 5 | - | 5 | 4 |  | 1 | 308.27
5 | Khulna | 1238.4 | - | 1 | 4 | 5 | 1 | - | 4 | 152.2
6 | HVDC | 1325 | - | - | - | - | - | - | - | -
7 | Bogura | 1803.3 |  | 3 | - | 3 | 3 | - | - | 56.7667
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 1659.0367
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 100%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.99%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:June 2026
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2026-06-01 | 36 | - | 3 | 2 hr 05 min | 1 | 4 hr 33 min
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | S/O | Due to emergency maint.work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:June 2026
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Bajitpur 132/33kV | 1 | 0.038194 | 22
Bhaluka 132/33kV | 12 | 2:16 | 112.27
Dhamrai 132/33kV | 2 | 0:58 | 38.67
Kishoreganj 132/33kV | 2 | 2:10 | 86.67
Tangail 132/33kV | 1 | 15:42 | 471
Aminbazar 400/230/132kV | 2 | 1:55 | 187
Bhaluka 132/33kV | 4 | 2:42 | 136.9
Ghatail 132/33kV | 1 | 4:33 | 91
Bhaluka 132/33kV | 1 | 2:07 | 63.5
Kabirpur 132/33kV | 1 | 2:29 | 161.4167
Kodda 132/33kV | 2 | 2:05 | 62.5
Bajitpur 132/33kV | 1 | 3:15 | 65
Munshiganj 132/33kV | 2 | 0:22 | 19.43
Narshingdi 132/33kV | 1 | 0:26 | 19.5
Sonargaon 132/33kV | 1 | 0:16 | 8
Bhulta 132/33kV | 1 | 0:52 | 138.6667
Hasnabad 132/33kV | 2 |  | 234.46
Madanganj 132/33kV | 1 | 0:18 | 5.1
Bhulta 132/33kV | 5 | 22:14 | 996.63
Narshingdi 132/33kV | 1 | 1:08 | 28.3333
Sonargaon 132/33kV | 6 |  | 1889.32
Srinagar 132/33kV | 3 | 3:40 | 73.33
Bhulta 132/33kV | 2 | 5:23 | 283.67
Dohazari 132/33kV | 1 | 0:21 | 20.3
Kalurghat 132/33kV | 2 | 3:08 | 31.33
Khagrachori 132/33kV | 2 | 0:32 | 5.87
Chandraghona 132/33kV | 1 | 1:04 | 26.6667
Coxsbazar 132/33kV | 1 | 2:13 | 155.1667
Chandraghona 132/33kV | 1 | 2:52 | 77.4
Coxsbazar 132/33kV | 1 | 2:30 | 120
Dohazari 132/33kV | 2 | 2:06 | 101.3
Brahmanbaria 132/33kV | 1 | 2:25 | 120.8333
Chowmuhani 230/132/33kV | 2 | 0:12 | 9.17
Cumilla(S) 132/33kV | 2 | 0:36 | 25.5
Feni 132/33kV | 2 | 2:00 | 93.2
Ramganj 132/33kV | 2 | 0:38 | 34.2
Sreemongol 132/33kV | 2 | 0:48 | 9.2
Sylhet 132/33kV | 1 | 0:46 | 46.7667
Sylhet_(South) 132/33kV | 2 | 0:10 | 3.42
Chowmuhani 230/132/33kV | 5 | 7:29 | 266.5
Ramganj 132/33kV | 1 | 1:13 | 24.3333
Brahmanbaria 132/33kV | 1 | 2:55 | 277.0833
Sunamganj 132/33kV | 1 | 0:30 | 2.5
Sylhet 132/33kV | 3 | 0:59 | 28.68
Chandpur 132/33kV | 3 | 3:25 | 54.1
Chauddagram 132/33kV | 2 | 3:13 | 121.33
Chhatak 132/33kV | 3 | 4:07 | 46.13
Cumilla(S) 132/33kV | 1 | 1:13 | 37.7167
Fenchuganj 230/132/33kV | 1 | 1:01 | 11.1833
Feni 132/33kV | 1 | 2:23 | 59.5833
Kulaura 132/33kV | 2 | 2:56 | 66.73
Shahjibazar 132/33kV | 2 | 8:40 | 469.33
Barishal 230/132kV | 2 | 1:26 | 43
Benapole 132/33kV | 2 | 0:23 | 3.95
Bhandaria 132/33kV | 4 | 1:40 | 37.33
Gopalganj 132/33kV | 2 | 0:25 | 18.77
Khulna (C) | 2 | 0.043056 | 21.97
Madaripur 132/33kV | 1 | 0.010417 | 8
Rajbari 132/33kV | 1 | 0.088194 | 40.2167
Satkhira 132/33kV | 2 | 2:08 | 131.73
Gopalganj 132/33kV | 2 | 4:26 | 71.33
Barishal 132/33kV | 1 | 0:09 | 7.8
Bagerhat 132/33kV | 1 | 2:09 | 75.25
Barishal 132/33kV | 2 | 2:48 | 79.62
Barishal 230/132kV | 5 | 15:21 | 591.23
Gopalganj 132/33kV | 1 | 1:49 | 25.4333
Madaripur 132/33kV | 1 | 2:41 | 67.0833
Narail 132/33kV | 1 | 1:30 | 10.5
Noapara 132/33kV | 1 | 3:28 | 69.3333
Charfasson 230/33kV | 1 | 1:35 | 38
Bakerganj 132/33kV | 1 | 1:27 | 15.37
Barguna 132/33kV | 1 | 1:33 | 27.9
Khulna (C) | 1 | 1:24 | 63
Patuakhali 132/33kV | 1 | 1:28 | 38.1333
Jhenaidah 132/33kV | 2 | 4:21 | 126.13
Shahjadpur 132/33kV | 3 | 1:46 | 15.85
Chuadanga 132/33kV | 1 | 1:45 | 87.5
Jashore 132/33kV | 1 | 4:11 | 16.7333
Jaldhaka 132/33kV | 2 | 1:29 | 29.67
Mahasthangarh 132/33kV | 3 | 1:16 | 38.75
Niamatpur 132/33kV | 1 | 0:23 | 6.9
Rangpur 132/33kV | 1 | 1:17 | 64.1667
Saidpur 132/33kV | 2 | 0:21 | 5.25
Chapai 132/33kV | 1 | 0:22 | 2.9333
Lalmonirhat 132/33kV | 1 | 2:05 | 10.4167
Niamatpur 132/33kV | 1 | 0:24 | 8
Kurigram 132/33kV | 1 | 0:29 | 26.1
Rangpur 132/33kV | 2 | 0:52 | 30.67
Mahasthangarh 132/33kV | 1 | 3:37 | 36.1667
Panchagarh 132/33kV | 1 | 1:15 | 10
Saidpur 132/33kV | 1 | 0:32 | 10.6667
| 167 | 215:50 | 9550.7433
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: June 2026
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 0 | 2026-06-01 00:00
2 | AKSML | 176.6 | 2026-06-24 16:00
3 | Aftabnagar | 50 | 2026-06-28 23:00
4 | Agargaon | 138 | 2026-06-28 15:00
5 | Agrabad | 80 | 2026-06-11 14:00
6 | Amnura | 47 | 2026-06-09 04:00
7 | Ashuganj | 111 | 2026-06-04 02:00
8 | BSRM | 205 | 2026-06-15 18:30
9 | Bagerhat | 108 | 2026-06-04 19:30
10 | Bajitpur | 108 | 2026-06-01 00:00
11 | Bakerganj | 18 | 2026-06-05 00:00
12 | Bakulia | 108 | 2026-06-09 14:00
13 | Banani | 76 | 2026-06-28 13:00
14 | Bangabhaban | 23 | 2026-06-02 10:00
15 | Barapukuria | 76 | 2026-06-02 21:00
16 | Barguna | 28 | 2026-06-01 00:00
17 | Barishal | 122 | 2026-06-09 19:00
18 | Barishal-230 | 132 | 2026-06-02 23:00
19 | Baroaulia | 74 | 2026-06-17 14:00
20 | Baroirhat | 81 | 2026-06-15 19:00
21 | Bashundhara | 230 | 2026-06-28 14:00
22 | BashundharaCement | 12 | 2026-06-08 01:00
23 | Beanibazar | 92 | 2026-06-30 23:00
24 | Benapole | 81 | 2026-06-05 01:00
25 | Bhaluka | 178 | 2026-06-22 19:00
26 | Bhandaria | 70 | 2026-06-02 22:00
27 | Bhangura | 49 | 2026-06-03 06:00
28 | Bheramara(GK) | 80 | 2026-06-04 20:00
29 | Bhulta | 236 | 2026-06-25 21:00
30 | Bog-Sherpur | 86 | 2026-06-02 23:00
31 | Bogura | 206 | 2026-06-29 00:00
32 | Borhanuddin | 108 | 2026-06-02 02:00
33 | Brahmanbaria | 156 | 2026-06-02 21:00
34 | Cantonment | 160 | 2026-06-29 12:00
35 | Chandina | 48 | 2026-06-07 19:30
36 | Chandpur | 104 | 2026-06-02 22:00
37 | Chandraghona | 38 | 2026-06-04 19:30
38 | Chapai | 86 | 2026-06-21 21:00
39 | Charfasson | 40 | 2026-06-27 00:00
40 | Charsaidpur | 46 | 2026-06-18 10:00
41 | Chauddagram | 91 | 2026-06-04 19:00
42 | Chhatak | 46 | 2026-06-07 19:30
43 | Chowmuhani | 186 | 2026-06-04 03:00
44 | Chuadanga | 136 | 2026-06-02 19:30
45 | Coxsbazar | 157 | 2026-06-11 19:00
46 | Cumilla(N) | 135 | 2026-06-03 19:00
47 | Cumilla(S) | 194 | 2026-06-23 19:00
48 | Daganbhuiyan | 42 | 2026-06-03 23:00
49 | Daudkandi | 166 | 2026-06-25 20:00
50 | DhakaUniversity | 104 | 2026-06-28 13:00
51 | Dhamrai | 126 | 2026-06-13 19:00
52 | Dhanmondi | 140.4 | 2026-06-21 13:00
53 | Dohazari | 121 | 2026-06-06 19:00
54 | Faridpur | 202 | 2026-06-03 23:00
55 | Fatullah | 112 | 2026-06-23 16:00
56 | Fenchuganj | 49 | 2026-06-06 19:00
57 | Feni | 132 | 2026-06-02 00:00
58 | GPH | 89 | 2026-06-30 03:00
59 | Ghatail | 101 | 2026-06-01 19:30
60 | Ghorashal | 0 | 2026-06-01 00:00
61 | Ghorashal-230 | 118 | 2026-06-27 18:30
62 | Goalpara | 48 | 2026-06-03 19:30
63 | Gollamari | 128 | 2026-06-04 13:00
64 | Gopalganj | 136.2 | 2026-06-02 22:00
65 | Gulshan | 156 | 2026-06-04 13:00
66 | Halishahar | 112 | 2026-06-28 09:00
67 | HaripurSBU | 150 | 2026-06-25 10:00
68 | Hasnabad | 99 | 2026-06-18 12:00
69 | Hathazari | 102 | 2026-06-04 19:30
70 | Hatirjheel | 55 | 2026-06-08 12:00
71 | Ishurdi | 94 | 2026-06-08 19:30
72 | Jaldhaka | 97 | 2026-06-02 20:00
73 | Jamalpur | 147 | 2026-06-25 23:00
74 | Jashore | 173 | 2026-06-20 19:30
75 | Jhenaidah | 136 | 2026-06-02 20:00
76 | Joydebpur | 170 | 2026-06-21 19:00
77 | Joypurhat | 80 | 2026-06-03 00:00
78 | Juldah | 22 | 2026-06-29 15:00
79 | KSRM | 33 | 2026-06-30 20:00
80 | Kabirpur | 284 | 2026-06-25 19:30
81 | Kachua | 116 | 2026-06-02 22:00
82 | Kaliganj | 41 | 2026-06-24 20:00
83 | Kallyanpur | 141 | 2026-06-28 00:00
84 | Kalurghat | 130 | 2026-06-08 04:00
85 | Kamrangirchar | 85 | 2026-06-16 13:00
86 | Kaptai | N/A | N/A
87 | Kasba | 44 | 2026-06-02 22:00
88 | Kazla | 126 | 2026-06-25 12:00
89 | Keranigonj | 95 | 2026-06-24 21:00
90 | Khagrachori | 38 | 2026-06-02 19:00
91 | Khulna | 76 | 2026-06-07 13:00
92 | Khulshi | 201 | 2026-06-15 19:30
93 | Kishoreganj | 157 | 2026-06-02 22:00
94 | Kodda | 356 | 2026-06-21 18:30
95 | Kulaura | 66 | 2026-06-02 19:00
96 | Kurigram | 76 | 2026-06-07 19:30
97 | Kushtia | 186 | 2026-06-04 00:00
98 | Laksam | 42 | 2026-06-06 23:00
99 | Lakshmipur | 48 | 2026-06-03 23:00
100 | Lalbag | 85 | 2026-06-17 13:00
101 | Lalmonirhat | 73 | 2026-06-07 19:30
102 | MI_Cement | 15.9 | 2026-06-07 10:00
103 | Madanganj | 52 | 2026-06-22 09:00
104 | Madaripur | 144 | 2026-06-05 00:00
105 | Madartek | 96 | 2026-06-28 00:00
106 | Madunaghat | 62 | 2026-06-11 15:00
107 | Magura | 84 | 2026-06-04 19:30
108 | Mahasthangarh | 105 | 2026-06-03 00:00
109 | Maijdee | 50 | 2026-06-06 00:00
110 | Manikganj | 153 | 2026-06-17 22:00
111 | Maniknagar | 86 | 2026-06-30 14:00
112 | Matarbari | 62 | 2026-06-04 20:00
113 | Matuail | 99 | 2026-06-16 05:00
114 | Metrorail_Motijheel | 47 | 2026-06-30 18:30
115 | Metrorail_Uttara | 1 | 2026-06-19 18:00
116 | Millgate | 150 | 2026-06-21 12:00
117 | Mirpur | 170 | 2026-06-27 19:30
118 | Mirsorai | 64 | 2026-06-20 10:00
119 | Mirzapur | 52 | 2026-06-29 12:00
120 | Mithapukur | 84 | 2026-06-14 17:00
121 | Modern | N/A | N/A
122 | Mogbazar | 127.8 | 2026-06-21 13:00
123 | Mongla | 54 | 2026-06-23 11:00
124 | Motijheel | 58 | 2026-06-21 13:00
125 | Muktagacha | 43 | 2026-06-01 21:00
126 | Munshiganj | 127 | 2026-06-04 23:00
127 | Muradnagar | 57 | 2026-06-03 22:00
128 | Mymensingh | 194 | 2026-06-04 23:00
129 | Nabinagar | 126 | 2026-06-27 11:00
130 | Naogaon | 165 | 2026-06-24 22:00
131 | Narail | 72 | 2026-06-04 20:00
132 | Narinda | 80 | 2026-06-21 13:00
133 | Narshingdi | 196 | 2026-06-25 20:00
134 | Natore | 181 | 2026-06-02 01:00
135 | Nawabganj | 73 | 2026-06-03 22:00
136 | Netrakona | 154 | 2026-06-05 19:00
137 | New | 88 | 2026-06-17 12:00
138 | Niamatpur | 90 | 2026-06-01 22:00
139 | Noapara | 64 | 2026-06-02 20:00
140 | PHP | 15 | 2026-06-23 17:00
141 | Pabna | 115 | 2026-06-03 21:00
142 | Palashbari | 152 | 2026-06-01 22:00
143 | Panchagarh | 77 | 2026-06-27 19:30
144 | Patiya | 13 | 2026-06-06 21:00
145 | Patnitala | 0 | 2026-06-30 16:00
146 | Patuakhali | 89.7 | 2026-06-01 00:00
147 | Payra | 44 | 2026-06-05 00:00
148 | Postogola | 69 | 2026-06-28 00:00
149 | Pubail | 43 | 2026-06-29 14:00
150 | Purbachal | 38 | 2026-06-04 13:00
151 | Purbasadipur | 159 | 2026-06-07 20:00
152 | Rahanpur | 49 | 2026-06-06 00:00
153 | Rahim | 56 | 2026-06-07 01:00
154 | Rajbari | 99 | 2026-06-02 23:00
155 | Rajendrapur | 118 | 2026-06-03 15:00
156 | Rajshahi | 153 | 2026-06-24 22:00
157 | Rajshahi-230 | 132 | 2026-06-19 19:30
158 | Ramganj | 126 | 2026-06-05 02:00
159 | Rampur | 76 | 2026-06-14 00:00
160 | Rangamati | 20 | 2026-06-02 19:00
161 | Rangpur | 158 | 2026-06-07 19:30
162 | Ruppur | 5 | 2026-06-03 10:00
163 | SSM | 14 | 2026-06-23 01:00
164 | Saidpur | 115 | 2026-06-08 18:30
165 | Santhia | 44 | 2026-06-27 19:30
166 | Satkhira | 171 | 2026-06-04 20:00
167 | Satmasjid | 118 | 2026-06-28 19:30
168 | Savar | 224 | 2026-06-08 16:00
169 | SevenRings | 24.14 | 2026-06-14 13:00
170 | ShahCement | 42 | 2026-06-09 07:00
171 | Shahjadpur | 90 | 2026-06-03 19:00
172 | Shahjibazar | 137 | 2026-06-24 21:00
173 | Shahmirpur | 67 | 2026-06-10 00:00
174 | Shariatpur | 116 | 2026-06-04 23:00
175 | Sherpur | 160 | 2026-06-22 19:30
176 | Shikalbaha | 36 | 2026-06-11 01:00
177 | Shitalakhya | 92.9 | 2026-06-15 15:00
178 | Sholosohor | 53 | 2026-06-13 12:00
179 | Shomvuganj | 42 | 2026-06-29 22:00
180 | Shyampur | 200 | 2026-06-11 01:00
181 | Siddhirganj | 142 | 2026-06-27 15:00
182 | Sirajganj | 132 | 2026-06-28 21:00
183 | Sitakunda | 21 | 2026-06-26 21:00
184 | Sonargaon | 160 | 2026-06-29 12:00
185 | Sreemongol | 94 | 2026-06-30 19:30
186 | Sreepur | 139 | 2026-06-29 19:30
187 | Srinagar | 58.8 | 2026-06-03 22:00
188 | Sunamganj | 66 | 2026-06-02 20:00
189 | Sylhet | 144 | 2026-06-14 19:00
190 | Sylhet_(South) | 86 | 2026-06-06 19:00
191 | TK | 28 | 2026-06-07 00:00
192 | Tangail | 196 | 2026-06-22 20:00
193 | Taraganj | 31 | 2026-06-25 21:00
194 | Tasnim | 44 | 2026-06-20 18:30
195 | Thakurgaon | 128 | 2026-06-02 22:00
196 | Tongi | 169 | 2026-06-24 11:00
197 | Ullahpara | 45 | 2026-06-01 20:00
198 | Ullon | 73 | 2026-06-04 00:00
199 | Uttara | 113 | 2026-06-28 15:00
200 | UttaraNew | 62 | 2026-06-28 00:00
201 | Zigatola | 104 | 2026-06-28 15:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: June 2026
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 6269.43 | 2026-06-29 | 1:00
Chattogram | 1769.7 | 2026-06-11 | 14:00
Cumilla | 1717 | 2026-06-03 | 23:00
Mymensingh | 1226 | 2026-06-01 | 19:00
Sylhet | 708 | 2026-06-06 | 23:00
Khulna | 2166 | 2026-06-04 | 0:00
Barishal | 586.7 | 2026-06-02 | 0:00
Rajshahi | 1772.8 | 2026-06-03 | 0:00
Rangpur | 1158 | 2026-06-07 | 20:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: June 2026
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 400 | 2026-06-01 06:00 | 346 | 2026-06-19 22:00
2 | Amtali | 400 | 415 | 2026-06-01 07:00 | 400 | 2026-06-29 19:30
3 | Ashuganj | 400 | N/A | N/A | N/A | N/A
4 | Bhulta | 400 | 406 | 2026-06-01 06:00 | 368 | 2026-06-08 15:00
5 | Bibiana | 400 | 408 | 2026-06-01 07:00 | 377 | 2026-06-30 23:00
6 | BIPTC | 400 | 408 | 2026-06-29 17:00 | 387 | 2026-06-01 23:00
7 | Bogura | 400 | 392 | 2026-06-01 09:00 | 365 | 2026-06-04 23:00
8 | Gopalganj | 400 | 402 | 2026-06-01 07:00 | 368 | 2026-06-18 12:00
9 | Kaliakoir | 400 | 398 | 2026-06-01 00:00 | 346 | 2026-06-07 15:00
10 | Korerhat | 400 | 407 | 2026-06-02 18:00 | 371 | 2026-06-30 13:00
11 | Madunaghat | 400 | 405 | 2026-06-02 19:00 | 378 | 2026-06-30 13:00
12 | Meghnaghat | 400 | 403 | 2026-06-01 00:00 | 347 | 2026-06-30 11:00
13 | Payra | 400 | 416 | 2026-06-02 18:00 | 402 | 2026-06-23 12:00
14 | Rahanpur | 400 | 408 | 2026-06-01 09:00 | 384 | 2026-06-04 23:00
15 | Rampal | 400 | 404 | 2026-06-02 18:30 | 369 | 2026-06-29 11:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 235 | 2026-06-01 18:30 | 207 | 2026-06-18 11:00
2 | AKSML | 230 | 237 | 2026-06-02 00:00 | 216.3 | 2026-06-30 10:00
3 | Aminbazar | 230 | 235 | 2026-06-01 18:30 | 206 | 2026-06-18 11:00
4 | Ashuganj | 230 | 234 | 2026-06-05 18:00 | 212 | 2026-06-07 15:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 236 | 2026-06-02 18:00 | 216 | 2026-06-28 20:00
7 | Barapukuria | 230 | 230 | 2026-06-04 18:00 | 198 | 2026-06-01 00:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 235 | 2026-06-06 18:00 | 213 | 2026-06-29 19:30
10 | Bheramara | 230 | 235 | 2026-06-22 05:00 | 205 | 2026-06-30 21:00
11 | Bhulta | 230 | 235 | 2026-06-01 06:00 | 208 | 2026-06-08 15:00
12 | Bibiana | 230 | 239 | 2026-06-16 06:00 | 215 | 2026-06-30 12:00
13 | BIPTC | 230 | 237 | 2026-06-02 18:30 | 203 | 2026-06-30 23:00
14 | Bogura | 230 | 243 | 2026-06-04 18:30 | 224 | 2026-06-04 23:00
15 | Bogura-400 | 230 | 243 | 2026-06-04 18:30 | 225 | 2026-06-04 23:00
16 | Borhanuddin | 230 | 238 | 2026-06-16 10:00 | 222 | 2026-06-25 00:00
17 | BSRM | 230 | 231 | 2026-06-02 18:00 | 211 | 2026-06-30 16:00
18 | Charfasson | 230 | 237 | 2026-06-16 18:00 | 221 | 2026-06-29 19:00
19 | Chowmuhani | 230 | 232 | 2026-06-02 18:30 | 210 | 2026-06-30 15:00
20 | Cumilla(N) | 230 | 232 | 2026-06-12 20:00 | 210 | 2026-06-29 11:00
21 | Faridpur | 230 | 234 | 2026-06-06 18:00 | 207 | 2026-06-29 19:30
22 | Fenchuganj | 230 | 238 | 2026-06-01 08:00 | 216 | 2026-06-30 13:00
23 | Feni | 230 | 230 | 2026-06-02 18:00 | 210 | 2026-06-30 12:00
24 | Ghorashal | 230 | 235 | 2026-06-12 17:00 | 210 | 2026-06-25 12:00
25 | Ghorashal-230 | 230 | 223 | 2026-06-12 18:30 | 193 | 2026-06-08 15:00
26 | Gopalganj | 230 | 235 | 2026-06-06 18:00 | 209 | 2026-06-29 19:00
27 | GPH | 230 | 235 | 2026-06-02 18:00 | 215 | 2026-06-30 12:00
28 | Haripur | 230 | 235 | 2026-06-01 06:00 | 209 | 2026-06-29 11:00
29 | Hasnabad | 230 | 233 | 2026-06-01 03:00 | 209 | 2026-06-18 11:00
30 | Hathazari | 230 | 235 | 2026-06-02 19:00 | 216 | 2026-06-30 11:00
31 | Ishurdi | 230 | 237 | 2026-06-01 10:00 | 206 | 2026-06-30 23:00
32 | Jhenaidah | 230 | 229 | 2026-06-06 15:00 | 197 | 2026-06-29 23:00
33 | Kachua | 230 | 233 | 2026-06-15 19:00 | 210 | 2026-06-30 15:00
34 | Kaliakoir | 230 | 241 | 2026-06-08 19:30 | 206 | 2026-06-18 11:00
35 | Keranigonj | 230 | 233 | 2026-06-01 18:30 | 206 | 2026-06-18 11:00
36 | Khulna(S) | 230 | 232 | 2026-06-05 11:00 | 201 | 2026-06-29 07:00
37 | Korerhat | 230 | 231 | 2026-06-02 18:00 | 200 | 2026-06-22 13:00
38 | Madunaghat | 230 | 238 | 2026-06-02 19:00 | 218 | 2026-06-30 13:00
39 | Madunaghat-400 | 230 | 238 | 2026-06-02 19:00 | 220 | 2026-06-30 13:00
40 | Maniknagar | 230 | 234 | 2026-06-01 06:00 | 207 | 2026-06-18 11:00
41 | Meghnaghat | 230 | 241 | 2026-06-01 01:00 | 216 | 2026-06-18 11:00
42 | Meghnaghat-400 | 230 | 235 | 2026-06-01 00:00 | 210 | 2026-06-30 12:00
43 | Mirsorai | 230 | 235 | 2026-06-12 19:30 | 215 | 2026-06-30 13:00
44 | Naogaon | 230 | 226 | 2026-06-20 18:30 | 195 | 2026-06-04 23:00
45 | Purbasadipur | 230 | 230 | 2026-06-04 18:30 | 195 | 2026-06-01 00:00
46 | Rajshahi | 230 | 235 | 2026-06-17 19:30 | 204 | 2026-06-30 21:00
47 | Rampal | 230 | 229 | 2026-06-01 08:00 | 205 | 2026-06-29 19:30
48 | Rampur | 230 | N/A | N/A | N/A | N/A
49 | Rampura | 230 | 234 | 2026-06-01 06:00 | 206 | 2026-06-08 15:00
50 | Shikalbaha | 230 | 237 | 2026-06-02 18:00 | 218 | 2026-06-30 10:00
51 | Shyampur | 230 | 234 | 2026-06-12 18:00 | 209 | 2026-06-08 15:00
52 | Siddhirganj | 230 | 235 | 2026-06-01 04:00 | 210 | 2026-06-08 15:00
53 | Sirajgonj | 230 | 242 | 2026-06-01 18:30 | 224 | 2026-06-29 02:00
54 | Sreepur | 230 | 235 | 2026-06-16 20:00 | 209 | 2026-06-29 12:00
54 | Tongi | 230 | 231 | 2026-06-01 04:00 | 195 | 2026-06-07 15:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 139 | 2026-06-30 06:00 | 119 | 2026-06-07 12:00
2 | Agargaon | 132 | 140 | 2026-06-19 06:00 | 120 | 2026-06-29 11:00
3 | Agrabad | 132 | 137 | 2026-06-02 19:00 | 123 | 2026-06-30 13:00
4 | AKS | 132 | 134 | 2026-06-02 18:00 | 123 | 2026-06-30 10:00
5 | Aminbazar | 132 | 137 | 2026-06-01 18:30 | 117 | 2026-06-18 11:00
6 | Amnura | 132 | 139 | 2026-06-17 19:30 | 118 | 2026-06-29 12:00
7 | Ashuganj | 132 | N/A | N/A | N/A | N/A
8 | Ashuganj-230 | 132 | 140 | 2026-06-17 22:00 | 126 | 2026-06-07 15:00
9 | Bagerhat | 132 | 136 | 2026-06-18 16:00 | 106 | 2026-06-29 23:00
10 | Bajitpur | 132 | 133 | 2026-06-21 17:00 | 115 | 2026-06-28 11:00
11 | Bakerganj | 132 | 136 | 2026-06-05 11:00 | 122 | 2026-06-04 22:00
12 | Bakulia | 132 | 137 | 2026-06-02 18:00 | 123 | 2026-06-30 10:00
13 | Banani | 132 | 139 | 2026-06-19 06:00 | 119 | 2026-06-07 12:00
14 | Bangabhaban | 132 | 138 | 2026-06-26 08:00 | 117 | 2026-06-04 11:00
0 | Barapukuria | 132 | 141 | 2026-06-04 18:00 | 117 | 2026-06-01 00:00
16 | Barguna | 132 | 136 | 2026-06-05 11:00 | 120 | 2026-06-25 15:00
17 | Barishal | 132 | 137 | 2026-06-02 18:30 | 122 | 2026-06-25 12:00
18 | Barishal-230 | 132 | 138 | 2026-06-18 19:00 | 122 | 2026-06-29 19:30
19 | Baroaulia | 132 | 136 | 2026-06-02 18:00 | 123 | 2026-06-30 12:00
20 | Baroirhat | 132 | 134 | 2026-06-02 18:00 | 122 | 2026-06-30 12:00
21 | Bashundhara | 132 | 140 | 2026-06-02 02:00 | 115 | 2026-06-07 15:00
22 | BashundharaCement | 132 | 137 | 2026-06-06 18:00 | 120 | 2026-06-18 12:00
23 | Beanibazar | 132 | 132 | 2026-06-05 07:00 | 116 | 2026-06-29 19:00
24 | Benapole | 132 | 137 | 2026-06-25 17:00 | 108 | 2026-06-29 23:00
25 | Bhaluka | 132 | 133 | 2026-06-21 17:00 | 114 | 2026-06-25 12:00
26 | Bhandaria | 132 | 135 | 2026-06-18 17:00 | 102 | 2026-06-29 23:00
27 | Bhangura | 132 | 136 | 2026-06-21 18:30 | 121 | 2026-06-30 13:00
28 | Bheramara | 132 | 137 | 2026-06-02 18:30 | 119 | 2026-06-26 19:30
29 | Bheramara(GK) | 132 | 137 | 2026-06-01 09:00 | 118 | 2026-06-28 21:00
30 | Bhulta | 132 | 132 | 2026-06-06 18:00 | 117 | 2026-06-18 11:00
31 | Bog-Sherpur | 132 | 139 | 2026-06-04 18:00 | 124 | 2026-06-24 22:00
32 | Bogura | 132 | 142 | 2026-06-04 18:30 | 123 | 2026-06-01 01:00
33 | Bogura-230 | 132 | 142 | 2026-06-04 18:30 | 127 | 2026-06-30 23:00
34 | Brahmanbaria | 132 | 133 | 2026-06-05 08:00 | 113 | 2026-06-18 11:00
35 | Cantonment | 132 | 140 | 2026-06-19 06:00 | 119 | 2026-06-29 11:00
36 | Chandina | 132 | 134 | 2026-06-06 18:30 | 120 | 2026-06-30 12:00
37 | Chandpur | 132 | 136 | 2026-06-02 19:00 | 117 | 2026-06-18 08:00
39 | Chandraghona | 132 | 138 | 2026-06-02 19:00 | 120 | 2026-06-18 08:00
40 | Chapai | 132 | 135 | 2026-06-04 17:00 | 124 | 2026-06-04 13:00
41 | Charsaidpur | 132 | 136 | 2026-06-01 05:00 | 119 | 2026-06-18 12:00
42 | Chauddagram | 132 | 132 | 2026-06-02 18:00 | 120 | 2026-06-28 19:00
43 | Chhatak | 132 | 130 | 2026-06-05 06:00 | 113 | 2026-06-29 19:00
44 | Chowmuhani | 132 | 131 | 2026-06-09 18:00 | 118 | 2026-06-30 10:00
45 | Chuadanga | 132 | 137 | 2026-06-10 16:00 | 108 | 2026-06-29 23:00
46 | Coxsbazar | 132 | 128 | 2026-06-07 06:00 | 108 | 2026-06-04 20:00
47 | Cumilla(N) | 132 | 135 | 2026-06-05 13:00 | 120 | 2026-06-30 12:00
48 | Cumilla(S) | 132 | 134 | 2026-06-06 18:30 | 117 | 2026-06-01 13:00
49 | Daganbhuiyan | 132 | 132 | 2026-06-09 18:00 | 119 | 2026-06-29 11:00
50 | Daudkandi | 132 | 134 | 2026-06-06 18:00 | 113 | 2026-06-30 13:00
51 | DhakaUniversity | 132 | 139 | 2026-06-19 06:00 | 119 | 2026-06- 12:00
52 | Dhamrai | 132 | 136 | 2026-06-05 14:00 | 114 | 2026-06-06 12:00
53 | Dhanmondi | 132 | 140 | 2026-06-26 08:00 | 120.7 | 2026-06-04 13:00
54 | Dohazari | 132 | 134 | 2026-06-02 19:00 | 117 | 2026-06-30 13:00
55 | Faridpur | 132 | 135 | 2026-06-06 18:30 | 120 | 2026-06-25 13:00
56 | Fatullah | 132 | 141 | 2026-06-12 18:00 | 115 | 2026-06-18 11:00
57 | Fenchuganj | 132 | 137 | 2026-06-05 08:00 | 124 | 2026-06-29 19:00
58 | Feni | 132 | 132 | 2026-06-05 14:00 | 109 | 2026-06-14 18:30
59 | Feni-230 | 132 | 132 | 2026-06-02 18:00 | 120 | 2026-06-30 16:00
60 | Ghatail | 132 | 133 | 2026-06-29 13:00 | 112 | 2026-06-08 19:30
61 | Ghorashal | 132 | 136 | 2026-06-23 22:00 | 117 | 2026-06-28 11:00
62 | Goalpara | 132 | 139 | 2026-06-11 18:00 | 116 | 2026-06-29 07:00
63 | Gollamari | 132 | 138 | 2026-06-12 18:00 | 117 | 2026-06-29 19:30
64 | Gopalganj | 132 | 136 | 2026-06-06 17:00 | 117 | 2026-06-29 19:30
65 | Gopalganj-400 | 132 | 139 | 2026-06-26 11:00 | 119 | 2026-06-11 16:00
66 | Gulshan | 132 | 138 | 2026-06-26 07:00 | 119 | 2026-06-07 12:00
67 | Halishahar | 132 | 138 | 2026-06-02 19:00 | 120 | 2026-06-27 23:00
68 | Haripur | 132 | 136 | 2026-06-06 18:00 | 121 | 2026-06-18 12:00
69 | HaripurSBU | 132 | 136 | 2026-06-06 18:00 | 121 | 2026-06-18 12:00
70 | Hasnabad | 132 | 139 | 2026-06-19 18:00 | 117 | 2026-06-18 11:00
71 | Hathazari | 132 | 137 | 2026-06-02 19:00 | 126 | 2026-06-30 17:00
72 | Hatirjheel | 132 | 139 | 2026-06-19 06:00 | 120 | 2026-06-07 12:00
73 | Ishurdi | 132 | 139 | 2026-06-19 09:00 | 120 | 2026-06-30 23:00
74 | Jaldhaka | 132 | 138 | 2026-06-04 18:30 | 113 | 2026-06-01 00:00
75 | Jamalpur | 132 | 138 | 2026-06-29 12:00 | 112 | 2026-06-04 17:00
76 | Jashore | 132 | 138 | 2026-06-25 17:00 | 110 | 2026-06-29 19:30
77 | Jhenaidah | 132 | 140 | 2026-06-27 09:00 | 108 | 2026-06-28 20:00
78 | Jhenaidah-230 | 132 | 140 | 2026-06-18 15:00 | 117 | 2026-06-24 22:00
79 | Joydebpur | 132 | 134 | 2026-06-09 08:00 | 110 | 2026-06-29 12:00
80 | Joypurhat | 132 | 141 | 2026-06-04 18:30 | 114 | 2026-06-04 13:00
81 | Juldah | 132 | 137 | 2026-06-02 19:00 | 109 | 2026-06-11 01:00
82 | Kabirpur | 132 | 139 | 2026-06-12 18:30 | 111 | 2026-06-25 09:00
83 | Kachua | 132 | 132 | 2026-06-02 18:30 | 119 | 2026-06-30 10:00
84 | Kaliakoir | 132 | 140 | 2026-06-12 06:00 | 124 | 2026-06-01 15:00
85 | Kaliganj | 132 | 138 | 2026-06-10 16:00 | 116 | 2026-06-24 22:00
86 | Kallyanpur | 132 | 137 | 2026-06-01 18:30 | 116 | 2026-06-18 11:00
87 | Kalurghat | 132 | 138 | 2026-06-02 19:00 | 126 | 2026-06-30 10:00
88 | Kamrangirchar | 132 | 141 | 2026-06-18 18:30 | 113 | 2026-06-18 11:00
89 | Kaptai | 132 | N/A | N/A | N/A | N/A
90 | Kasba | 132 | 133 | 2026-06-06 18:00 | 115 | 2026-06-30 12:00
91 | Kazla | 132 | 136 | 2026-06-10 06:00 | 118 | 2026-06-04 11:00
92 | Keranigonj | 132 | 142 | 2026-06-18 18:30 | 118 | 2026-06-23 20:00
93 | Khagrachori | 132 | 135 | 2026-06-13 05:00 | 123 | 2026-06-30 12:00
94 | Khulna | 132 | 138 | 2026-06-12 18:00 | 115 | 2026-06-29 23:00
95 | Khulna(S) | 132 | 139 | 2026-06-12 18:00 | 117 | 2026-06-29 23:00
96 | Khulshi | 132 | 135 | 2026-06-02 18:00 | 122 | 2026-06-18 12:00
97 | Kishoreganj | 132 | 131 | 2026-06-21 17:00 | 112 | 2026-06-28 11:00
98 | Kodda | 132 | 138 | 2026-06-12 18:30 | 119 | 2026-06-01 15:00
99 | Korerhat | 132 | 136 | 2026-06-02 18:00 | 125 | 2026-06-29 11:00
100 | KSRM | 132 | 136 | 2026-06-02 18:00 | 124 | 2026-06-30 11:00
101 | Kulaura | 132 | 135 | 2026-06-05 07:00 | 122 | 2026-06-29 19:00
102 | Kurigram | 132 | 134 | 2026-06-29 07:00 | 107 | 2026-06-01
103 | Kushtia | 132 | 137 | 2026-06-07 18:00 | 113 | 2026-06-28 19:30
104 | Laksam | 132 | 132 | 2026-06-06 18:30 | 118 | 2026-06-24 23:00
105 | Lakshmipur | 132 | 129 | 2026-06-02 18:30 | 116 | 2026-06-30 02:00
106 | Lalbag | 132 | 141 | 2026-06-18 18:00 | 124 | 2026-06-02 13:00
107 | Lalmonirhat | 132 | 133 | 2026-06-04 18:30 | 109 | 2026-06-01 00:00
108 | Madanganj | 132 | 137 | 2026-06-06 18:00 | 120 | 2026-06-18 12:00
109 | Madaripur | 132 | 137 | 2026-06-06 18:00 | 120 | 2026-06-29 19:30
110 | Madartek | 132 | 138 | 2026-06-22 05:00 | 118 | 2026-06-07 12:00
111 | Madunaghat | 132 | 138 | 2026-06-02 19:00 | 112 | 2026-06-30 17:00
112 | Magura | 132 | 137 | 2026-06-06 15:00 | 101 | 2026-06-28 19:30
113 | Mahasthangarh | 132 | 140 | 2026-06-04 18:30 | 123 | 2026-06-03 00:00
114 | Maijdee | 132 | 130 | 2026-06-09 18:00 | 117 | 2026-06-30 02:00
115 | Manikganj | 132 | 135 | 2026-06-12 18:30 | 119 | 2026-06-01 15:00
116 | Maniknagar | 132 | 138 | 2026-06-12 18:00 | 118 | 2026-06-04 11:00
117 | Matarbari | 132 | 127 | 2026-06-07 06:00 | 105 | 2026-06-05 04:00
118 | Matuail | 132 | 136 | 2026-06-26 08:00 | 119 | 2026-06-14 12:00
119 | Metrorail_Motijheel | 132 | 138 | 2026-06-12 18:00 | 118 | 2026-06-04 11:00
120 | Metrorail_Uttara | 132 | 140 | 2026-06-02 02:00 | 114 | 2026-06-07 15:00
121 | Millgate | 132 | 140 | 2026-06-02 01:00 | 115 | 2026-06-07 15:00
122 | Mirpur | 132 | 135 | 2026-06-01 18:00 | 116 | 2026-06-18 11:00
123 | Mirzapur | 132 | 133 | 2026-06-05 14:00 | 119 | 2026-06-07 15:00
124 | Mithapukur | 132 | 138 | 2026-06-04 18:30 | 116 | 2026-06-01 00:00
125 | MI_Cement | 132 | 137 | 2026-06-19 18:00 | 113 | 2026-06-18 11:00
126 | Modern | 132 | N/A | N/A | N/A | N/A
127 | Mogbazar | 132 | 140 | 2026-06-19 18:00 | 120 | 2026-06-07 12:00
128 | Mongla | 132 | 136 | 2026-06-12 18:00 | 107 | 2026-06-29 19:30
129 | Motijheel | 132 | 138 | 2026-06-26 08:00 | 117 | 2026-06-04 11:00
130 | Muktagacha | 132 | 135 | 2026-06-29 13:00 | 112 | 2026-06-08 22:00
131 | Munshiganj | 132 | 136 | 2026-06-06 18:00 | 118 | 2026-06-18 12:00
132 | Muradnagar | 132 | 134 | 2026-06-06 18:30 | 116 | 2026-06-28 21:00
133 | Mymensingh | 132 | 135 | 2026-06-18 09:00 | 111 | 2026-06-08 19:00
134 | Nabinagar | 132 | 136 | 2026-06-12 06:00 | 113 | 2026-06-18 11:00
135 | Naogaon | 132 | 138 | 2026-06-06 13:00 | 118 | 2026-06-02 23:00
136 | Narail | 132 | 138 | 2026-06-18 15:00 | 101 | 2026-06-28 20:00
137 | Narinda | 132 | 0 | 2026-06-01 00:00 | N/A | N/A
139 | Narshingdi | 132 | 133 | 2026-06-05 12:00 | 113 | 2026-06-18 11:00
140 | Natore | 132 | 137 | 2026-06-03 01:00 | 116 | 2026-06-26 19:30
141 | Nawabganj | 132 | 141 | 2026-06-18 18:00 | 122 | 2026-06-07 12:00
142 | Netrakona | 132 | 125 | 2026-06-15 06:00 | 100 | 2026-06-28 11:00
143 | New | 132 | 140 | 2026-06-02 18:00 | 116 | 2026-06-07 15:00
144 | Niamatpur | 132 | 136 | 2026-06-04 17:00 | 121 | 2026-06-04 23:00
145 | Noapara | 132 | 138 | 2026-06-25 17:00 | 113 | 2026-06-29 19:30
146 | Pabna | 132 | 136 | 2026-06-04 18:00 | 118 | 2026-06-30 23:00
147 | Palashbari | 132 | 136 | 2026-06-04 18:30 | 114 | 2026-06-01 00:00
148 | Panchagarh | 132 | 142 | 2026-06-29 04:00 | 123 | 2026-06-04 23:00
149 | Patiya | 132 | 139 | 2026-06-12 04:00 | 121 | 2026-06-30 13:00
150 | Patnitala | 132 | 131 | 2026-06-30 18:30 | 119 | 2026-06-30 23:00
151 | Patuakhali | 132 | 135 | 2026-06-02 18:30 | 121 | 2026-06-19 12:00
152 | Payra | 132 | 137 | 2026-06-02 18:30 | 127 | 2026-06-19 08:00
153 | PHP | 132 | 133 | 2026-06-02 18:30 | 121 | 2026-06-30 13:00
154 | Postogola | 132 | 139 | 2026-06-19 18:00 | 116 | 2026-06-18 11:00
155 | Pubail | 132 | 133 | 2026-06-02 05:00 | 113 | 2026-06-29 12:00
156 | Purbachal | 132 | 140 | 2026-06-02 02:00 | 115 | 2026-06-07 15:00
157 | Purbasadipur | 132 | 140 | 2026-06-04 18:00 | 118 | 2026-06-01 00:00
158 | Rahanpur | 132 | 137 | 2026-06-04 17:00 | 127 | 2026-06-02 23:00
159 | Rahanpur-400 | 132 | 137 | 2026-06-04 17:00 | 127 | 2026-06-04 23:00
160 | Rahim | 132 | 136 | 2026-06-26 08:00 | 120 | 2026-06-18 11:00
161 | Rajbari | 132 | 133 | 2026-06-06 18:00 | 116 | 2026-06-28 23:00
162 | Rajendrapur | 132 | 135 | 2026-06-21 16:00 | 115 | 2026-06-25 10:00
163 | Rajshahi | 132 | 134 | 2026-06-11 16:00 | 114 | 2026-06-30 23:00
164 | Rajshahi-230 | 132 | 135 | 2026-06-03 18:30 | 112 | 2026-06-30 03:00
165 | Ramganj | 132 | 131 | 2026-06-06 18:30 | 115 | 2026-06-04 23:00
166 | Rampur | 132 | 137 | 2026-06-02 19:00 | 123 | 2026-06-18 11:00
167 | Rampura | 132 | 139 | 2026-06-26 08:00 | 120 | 2026-06-07 12:00
168 | Rangamati | 132 | 135 | 2026-06-02 18:00 | 124 | 2026-06-30 12:00
169 | Rangpur | 132 | 139 | 2026-06-04 18:30 | 116 | 2026-06-01 19:30
170 | Ruppur | 132 | 137 | 2026-06-03 18:00 | 119 | 2026-06-30 23:00
171 | Saidpur | 132 | 140 | 2026-06-04 18:30 | 119 | 2026-06-01 00:00
172 | Santhia | 132 | 136 | 2026-06-16 18:00 | 122 | 2026-06-24 22:00
173 | Satkhira | 132 | 136 | 2026-06-18 16:00 | 108 | 2026-06-03 23:00
174 | Satmasjid | 132 | 139 | 2026-06-19 06:00 | 120 | 2026-06-24 13:00
175 | Savar | 132 | 137 | 2026-06-01 18:30 | 114 | 2026-06-29 11:00
176 | SevenRings | 132 | 133 | 2026-06-01 18:00 | 115 | 2026-06-29 12:00
177 | ShahCement | 132 | 136 | 2026-06-06 18:00 | 119 | 2026-06-18 12:00
178 | Shahjadpur | 132 | 139 | 2026-06-12 18:00 | 128 | 2026-06-24 22:00
179 | Shahjibazar | 132 | 135 | 2026-06-05 08:00 | 119 | 2026-06-17 21:00
180 | Shahmirpur | 132 | 138 | 2026-06-02 19:00 | 123 | 2026-06-30 13:00
181 | Shariatpur | 132 | 137 | 2026-06-06 18:00 | 118 | 2026-06-29 19:30
182 | Sherpur | 132 | 138 | 2026-06-29 12:00 | 107 | 2026-06-03 00:00
183 | Shikalbaha | 132 | 126 | 2026-06-02 18:30 | 114 | 2026-06-30 13:00
184 | Shikalbaha-230 | 132 | 137 | 2026-06-02 18:00 | 124 | 2026-06-30 13:00
185 | Shitalakhya | 132 | 137 | 2026-06-19 18:00 | 113 | 2026-06-18 11:00
186 | Sholosohor | 132 | 137 | 2026-06-02 19:00 | 125 | 2026-06-09 11:00
187 | Shomvuganj | 132 | 128 | 2026-06-22 17:00 | 110 | 2026-06-30 23:00
188 | Shyampur | 132 | 139 | 2026-06-12 18:30 | 117 | 2026-06-07 15:00
189 | Shyampur-230 | 132 | 141 | 2026-06-12 18:00 | 118 | 2026-06-07 15:00
190 | Siddhirganj | 132 | 139 | 2026-06-07 01:00 | 121 | 2026-06-18 11:00
191 | Sirajganj | 132 | 134 | 2026-06-03 18:00 | 120 | 2026-06-24 22:00
192 | Sitakunda | 132 | 133 | 2026-06-26 06:00 | 124 | 2026-06-30 13:00
193 | Sonargaon | 132 | 136 | 2026-06-06 18:00 | 118 | 2026-06-18 12:00
194 | Sreemongol | 132 | 135 | 2026-06-05 07:00 | 119 | 2026-06-29 19:00
195 | Sreepur | 132 | 134 | 2026-06-21 17:00 | 118 | 2026-06-25 10:00
196 | Srinagar | 132 | 141 | 2026-06-18 14:00 | 122 | 2026-06-07 12:00
197 | SSM | 132 | 140 | 2026-06-02 18:30 | 128 | 2026-06-22 11:00
198 | Sunamganj | 132 | 129 | 2026-06-05 06:00 | 112 | 2026-06-30 20:00
199 | Sylhet | 132 | 131 | 2026-06-05 07:00 | 119 | 2026-06-29 19:00
200 | Sylhet_(South) | 132 | 132 | 2026-06-05 07:00 | 119 | 2026-06-29 19:00
201 | Tangail | 132 | 130 | 2026-06-05 15:00 | 113 | 2026-06-08 19:00
202 | Taraganj | 132 | 139 | 2026-06-04 18:30 | 116 | 2026-06-01 01:00
203 | Tasnim | 132 | 136 | 2026-06-06 18:00 | 117 | 2026-06-08 01:00
204 | Thakurgaon | 132 | 141 | 2026-06-29 04:00 | 120 | 2026-06-04 23:00
205 | TK | 132 | 139 | 2026-06-02 19:00 | 125 | 2026-06-30 12:00
206 | Tongi | 132 | 141 | 2026-06-02 04:00 | 119 | 2026-06-08 15:00
207 | Ullahpara | 132 | 136 | 2026-06-21 18:30 | 121 | 2026-06-24 22:00
208 | Ullon | 132 | 139 | 2026-06-26 08:00 | 120 | 2026-06-07 12:00
209 | Uttara | 132 | 140 | 2026-06-02 02:00 | 114 | 2026-06-08 15:00
210 | UttaraNew | 132 | 140 | 2026-06-02 01:00 | 114 | 2026-06-07 15:00
211 | Zigatola | 132 | 142 | 2026-06-18 18:30 | 123 | 2026-06-07 13:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Month: June 2026
Maximum load of 400/230 & 400/132 kV Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 21-06-2026 | 12:00 | 427 | 159 | 87.6235
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 21-06-2026 | 12:00 | 427 | 159 | 87.6235
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 21-06-2026 | 12:00 | 427 | 159 | 87.6235
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 30-06-2026 | 00:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 14-06-2026 | 13:00 | 287 | 148 | 62.0987
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 14-06-2026 | 13:00 | 287 | 148 | 62.0987
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 02-06-2026 | 19:30 | 163 | 69 | 34.039
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 30-06-2026 | 19:00 | 196 | 125 | 44.7052
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 21-06-2026 | 22:00 | 396 | 124 | 55.328
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 21-06-2026 | 22:00 | 396 | 124 | 55.328
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 21-06-2026 | 22:00 | 396 | 124 | 55.328
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 29-06-2026 | 19:30 | 169 | 57 | 54.878
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 29-06-2026 | 19:30 | 169 | 57 | 54.878
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 29-06-2026 | 19:30 | 169 | 57 | 54.878
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 19-06-2026 | 13:00 | 233 | 25 | 31.245
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 18-06-2026 | 10:00 | 336 | 290 | 85.3543
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 18-06-2026 | 10:00 | 336 | 290 | 85.3543
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 22-06-2026 | 02:00 | 286 | 90 | 92.2543
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 22-06-2026 | 06:00 | 294 | 95 | 95.067
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 08-06-2026 | 20:00 | 390 | 250 | 61.7666
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 09-06-2026 | 11:00 | 349 | 136 | 49.9417
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 09-06-2026 | 11:00 | 349 | 136 | 49.9417
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 21-06-2026 | 13:00 | 475 | 198 | 68.6154
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 21-06-2026 | 13:00 | 474 | 198 | 68.4923
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750 | 21-06-2026 | 13:00 | 488 | 193 | 69.9705
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 21-06-2026 | 23:00 | 405 | 96 | 80.0427
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 21-06-2026 | 23:00 | 400 | 96 | 79.1074
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 04-06-2026 | 22:00 | 205 | 68 | 66.4566
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 04-06-2026 | 22:00 | 205 | 68 | 66.4566
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 03-06-2026 | 00:00 | 181 | 51 | 36.1631
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 03-06-2026 | 00:00 | 181 | 51 | 36.1631
Koerhat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 1000 | 18-06-2026 | 08:00 | 485 | 7 | 48.5051
Koerhat 400/132kV Grid Sub-Station | ATR-4 | 400/230 | 1000 | 26-06-2026 | 17:00 | 401 | 58 | 40.5173
Koerhat 400/132kV Grid Sub-Station | ATR-2 | 400/132 | 325 | 06-06-2026 | 15:00 | 138 | 41 | 44.2959
Koerhat 400/132kV Grid Sub-Station | ATR-3 | 400/132 | 325 | 24-06-2026 | 15:00 | 135 | 22 | 42.0864
Mirsharai 400/230 kV Grid Sub-Station | ATR-1 | 400/230 | 1000 | 13-06-2026 | 14:00 | 91 | 48 | 10.2883
Mirsharai 400/230 kV Grid Sub-Station | ATR-2 | 400/230 | 1000 | 13-06-2026 | 14:00 | 91 | 48 | 10.2883
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-1 | 400/230 | 325 | - | - | 0 | 0 | 0
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-2 | 400/230 | 325 | - | - | 0 | 0 | 0
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 28-06-2026 | 15:00 | 204 | 87 | 73.9256
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 28-06-2026 | 15:00 | 204 | 84 | 73.5391
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 08-06-2026 | 09:00 | 192 | 59 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 08-06-2026 | 09:00 | 192 | 59 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 08-06-2026 | 09:00 | 192 | 59 | 83.2263
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 26-06-2026 | 22:00 | 205 | 122 | 79.5187
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 23-06-2026 | 19:00 | 260 | 60 | 88.9444
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 02-06-2026 | 00:00 | 181 | 55 | 63.0573
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 01-06-2026 | 20:00 | 135 | 43 | 62.9701
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 26-06-2026 | 19:30 | 180 | 52 | 83.2714
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 26-06-2026 | 19:30 | 110 | 37 | 51.5805
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 26-06-2026 | 19:30 | 143 | 39 | 49.4076
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 19-06-2026 | 13:00 | 139 | 51 | 49.3536
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 19-06-2026 | 13:00 | 139 | 51 | 49.3536
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 30-06-2026 | 21:00 | 141 | 43 | 65.516
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 30-06-2026 | 21:00 | 141 | 43 | 65.516
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 05-06-2026 | 22:00 | 158 | 55 | 74.3552
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 05-06-2026 | 22:00 | 158 | 55 | 74.3552
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 05-06-2026 | 22:00 | 212 | 77 | 75.1835
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 05-06-2026 | 22:00 | 212 | 77 | 75.1835
Naogaon 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | - | - | 0 | 0 | 0
Naogaon 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | - | - | 0 | 0 | 0
Naogaon 230/132kV Grid Sub-Station | ATR-3 | 230/132 | 300 | - | - | 0 | 0 | 0
Purbasadipur 230/132kV Grid Sub-Station | ATR-01 | 230/132 | 300 | 26-06-2026 | 19:30 | 121 | 18 | 40.7772
Purbasadipur 230/132kV Grid Sub-Station | ATR-02 | 230/132 | 300 | 26-06-2026 | 19:30 | 121 | 18 | 40.7772
Purbasadipur 230/132kV Grid Sub-Station | ATR-03 | 230/132 | 300 | 26-06-2026 | 19:30 | 121 | 18 | 40.7772
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 03-06-2026 | 10:00 | 110 | 53 | 54.2677
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 03-06-2026 | 10:00 | 106 | 53 | 52.6718
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 03-06-2026 | 10:00 | 110 | 56 | 54.8596
Chowmohani 230/132 kV Grid Sub-Station | ATR-01 | 230/132 | 350 | 05-06-2026 | 02:00 | 95 | 23 | 27.927
Chowmohani 230/132 kV Grid Sub-Station | ATR-02 | 230/132 | 350 | 05-06-2026 | 02:00 | 95 | 23 | 27.927
Chowmohani 230/132 kV Grid Sub-Station | ATR-03 | 230/132 | 350 | 05-06-2026 | 02:00 | 95 | 23 | 27.927
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 16-06-2026 | 23:00 | 190 | 74 | 67.9673
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 30-06-2026 | 19:00 | 229 | 99 | 83.1612
Feni 230/132 kV GIS Grid Sub-Station | ATR-1 | 230/132 | 300 | 01-06-2026 | 19:00 | 55 | 25 | 20.1384
Feni 230/132 kV GIS Grid Sub-Station | ATR-2 | 230/132 | 300 | 01-06-2026 | 19:00 | 55 | 25 | 20.1384
Feni 230/132 kV GIS Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-06-2026 | 19:00 | 55 | 25 | 20.1384
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 01-06-2026 | 17:00 | 86 | 0 | 68.8
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 01-06-2026 |  | 0 | 0 | 0
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 13-06-2026 | 07:00 | 150 | 94 | 78.6755
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 13-06-2026 | 07:00 | 164 | 95 | 84.2348
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 13-06-2026 | 07:00 | 155 | 99 | 81.7415
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 18-06-2026 | 13:00 | 124 | 67 | 62.6414
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 15-06-2026 | 08:00 | 134 | 60 | 65.2532
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 15-06-2026 | 08:00 | 134 | 60 | 65.2532
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 10-06-2026 | 19:00 | 98 | 43 | 71.3458
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 01-06-2026 | 00:00 | 0 | 0 | 0
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 10-06-2026 | 19:00 | 98 | 43 | 71.3458
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 10-06-2026 | 19:00 | 98 | 43 | 71.3458
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 30-06-2026 | 21:00 | 131 | 55 | 63.1455
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 12-06-2026 | 19:30 | 117 | 63 | 59.0593
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 30-06-2026 | 21:00 | 128 | 53 | 61.5728
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 03-06-2026 | 00:00 | 228 | -85 | 81.1097
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 03-06-2026 | 00:00 | 228 | -85 | 81.1097
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 08-06-2026 | 20:00 | 234 | 102 | 85.0882
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 27-06-2026 | 19:00 | 136 | 46 | 47.8563
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 27-06-2026 | 19:00 | 136 | 46 | 47.8563
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 27-06-2026 | 19:00 | 136 | 46 | 47.8563
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 26-06-2026 | 19:30 | 184 | 57 | 85.6118
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 26-06-2026 | 19:30 | 184 | 57 | 85.6118
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 26-06-2026 | 19:30 | 240 | 66 | 82.9699
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 18-06-2026 | 15:00 | 125 | 15 | 41.9656
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 18-06-2026 | 15:00 | 125 | 15 | 41.9656
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 18-06-2026 | 15:00 | 125 | 15 | 41.9656
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 13-06-2026 | 21:00 | 238 | 55 | 81.4241
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 13-06-2026 | 21:00 | 238 | 55 | 81.4241
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 05-06-2026 | 23:00 | 110 | 26 | 37.677
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 05-06-2026 | 23:00 | 110 | 26 | 37.677
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-06-2026 | 00:00 | 1 | 0 | 0.33333
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-06-2026 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 21-06-2026 | 13:00 | 306 | 56 | 69.1293
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 21-06-2026 | 13:00 | 306 | 56 | 69.1293
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 21-06-2026 | 13:00 | 306 | 56 | 69.1293
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 10-06-2026 | 14:00 | 230 | 121 | 86.6288
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 10-06-2026 | 14:00 | 230 | 121 | 86.6288
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 08-06-2026 | 23:00 | 131 | 50 | 46.7392
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 19-06-2026 | 00:00 | 132 | 50 | 47.0508
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 01-06-2026 | 00:00 | 0 | 0 | 0
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 18-06-2026 | 19:00 | 192 | 6 | 64.0312
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 23-06-2026 | 10:00 | 294 | 53 | 99.5797
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 23-06-2026 | 10:00 | 294 | 53 | 99.5797
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 28-06-2026 | 21:00 | 155 | 62 | 74.1956
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 28-06-2026 | 21:00 | 150 | 57 | 71.3178
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 28-06-2026 | 21:00 | 150 | 57 | 71.3178
Tongi 230/132/33kV Grid Sub-Station | T-04 | 230/132 | 450 | 27-06-2026 | 15:00 | 290 | 120 | 69.7438
Bhulta 230/132kV Grid Sub-Station | TR1 | 230/132 | 300 | 13-06-2026 | 8:45 | 160 | 51 | 55.9772
Bhulta 230/132kV Grid Sub-Station | TR2 | 230/132 | 300 | 14-06-2026 | 8:45 | 160 | 51 | 55.9772
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: June 2026 |  |  |  | (For Evening Peak) | [10 empty] | Month: June 2026 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2026-06-01 | 15128.26 | 15281.26 | 146 | 21:00 Hr. | 0 | 0 | 16 | 121 | 9 | 0 | 0 | 0 | 0 | - | 2026-06-01 | 13150.4 | 13166.08 | 15 | 12:00 Hr. | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | -
2026-06-02 | 15820.76 | 16212.76 | 375 | 21:00 Hr. | 14 | 0 | 23 | 319 | 11 | 0 | 0 | 0 | 8 | - | 2026-06-02 | 13824.9 | 13849.9 | 24 | 12:00 Hr. | 9 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | -
2026-06-03 | 15870.67 | 16289.67 | 401 | 21:00 Hr. | 13 | 5 | 15 | 355 | 10 | 0 | 3 | 0 | 0 | - | 2026-06-03 | 14553.08 | 14871.08 | 304 | 12:00 Hr. | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | -
2026-06-04 | 14900.03 | 15275.03 | 359 | 21:00 Hr. | 12 | 9 | 16 | 308 | 10 | 0 | 4 | 0 | 0 | - | 2026-06-04 | 14743.95 | 14971.95 | 218 | 12:00 Hr. | 8 | 0 | 2 | 208 | 0 | 0 | 0 | 0 | 0 | -
2026-06-05 | 14449.5 | 14730.5 | 269 | 21:00 Hr. | 12 | 10 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | - | 2026-06-05 | 12461.11 | 12671.11 | 201 | 09:00 Hr. | 8 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | -
2026-06-06 | 15289.62 | 15684.62 | 378 | 21:00 Hr. | 19 | 7 | 2 | 340 | 10 | 0 | 0 | 0 | 0 | - | 2026-06-06 | 13987.35 | 14280.35 | 280 | 12:00 Hr. | 24 | 0 | 0 | 256 | 0 | 0 | 0 | 0 | 0 | -
2026-06-07 | 15621.23 | 16048.23 | 409 | 21:00 Hr. | 130 | 8 | 8 | 231 | 17 | 0 | 0 | 0 | 15 | - | 2026-06-07 | 14729.93 | 15190.93 | 441 | 12:00 Hr. | 226 | 0 | 0 | 214 | 0 | 0 | 0 | 1 | 0 | -
2026-06-08 | 15773.2 | 16451.2 | 649 | 19:30 Hr. | 150 | 8 | 0 | 476 | 0 | 0 | 0 | 0 | 15 | - | 2026-06-08 | 14850.02 | 15348.02 | 477 | 12:00 Hr. | 282 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | -
2026-06-09 | 14520 | 14707.06 | 179 | 20:00 Hr. | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | - | 2026-06-09 | 14141 | 14194.3 | 51 | 12:00 Hr. | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-06-10 | 15203.2 | 15393.2 | 182 | 21:00 Hr. | 9 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | - | 2026-06-10 | 13966.46 | 13975.46 | 9 | 12:00 Hr. | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0
2026-06-11 | 15068.4 | 15556.4 | 467 | 20:00 Hr. | 172 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | - | 2026-06-11 | 14464.11 | 14684.11 | 211 | 12:00 Hr. | 106 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | -
2026-06-12 | 15007.4 | 15424.4 | 399 | 21:00 Hr. | 3 | 0 | 0 | 347 | 0 | 33 | 0 | 0 | 16 | - | 2026-06-12 | 13213.87 | 13363.87 | 144 | 12:00 Hr. | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | -
2026-06-13 | 15031.7 | 16615.7 | 1516 | 21:00 Hr. | 220 | 23 | 197 | 269 | 102 | 280 | 130 | 124 | 171 | - | 2026-06-13 | 13863.2 | 14165.2 | 289 | 12:00 Hr. | 212 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | -
2026-06-14 | 15047.9 | 17189.9 | 2050 | 21:00 Hr. | 403 | 83 | 201 | 310 | 114 | 297 | 34 | 361 | 247 | - | 2026-06-14 | 14136.76 | 15248.76 | 1064 | 12:00 Hr. | 472 | 88 | 102 | 205 | 105 | 0 | 0 | 0 | 92 | -
2026-06-15 | 15150.5 | 16930.5 | 1703 | 21:00 Hr. | 250 | 120 | 245 | 314 | 81 | 210 | 93 | 209 | 181 | - | 2026-06-15 | 14247.86 | 15542.8 | 608 | 11:00 Hr. | 363 | 0 | 127 | 118 | 0 | 0 | 0 | 0 | 0 | -
2026-06-16 | 14579.39 | 17553.39 | 2846 | 21:00 Hr. | 439 | 186 | 398 | 448 | 103 | 464 | 142 | 360 | 306 | - | 2026-06-16 | 13655.83 | 16012.2 | 1862 | 11:00 Hr. | 518 | 200 | 196 | 207 | 77 | 242 | 26 | 200 | 196 | -
2026-06-17 | 15461.46 | 17328.46 | 1787 | 21:00 Hr. | 112 | 129 | 214 | 316 | 20 | 475 | 97 | 229 | 195 | - | 2026-06-17 | 13880.15 | 16058.15 | 2084 | 12:00 Hr. | 516 | 249 | 213 | 217 | 0 | 336 | 42 | 317 | 194 | -
2026-06-18 | 14783.7 | 14852.7 | 66 | 19:30 Hr. | 0 | 0 | 37 | 29 | 0 | 0 | 0 | 0 | 0 | - | 2026-06-18 | 14101.96 | 14351.27 | 24 | 11:00 Hr. | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-06-19 | 14958.07 | 15057.35 | 95 | 21:00 Hr. | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | - | 2026-06-19 | 12701.44 | 12701.44 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-06-20 | 15782.47 | 17749.16 | 1882 | 21:00 Hr. | 192 | 86 | 325 | 322 | 2 | 401 | 9 | 322 | 223 | - | 2026-06-20 | 13823.66 | 13903.66 | 77 | 12:00 Hr. | 32 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | -
2026-06-21 | 14649.64 | 14695.64 | 44 | 21:00 Hr. | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 10 | 0 | - | 2026-06-21 | 14066.19 | 15930.43 | 560 | 09:00 Hr. | 254 | 0 | 55 | 211 | 0 | 0 | 0 | 40 | 0 | -
2026-06-22 | 16154.41 | 16854.11 | 496 | 21:00 Hr. | 88 | 0 | 110 | 241 | 0 | 31 | 0 | 0 | 26 | - | 2026-06-22 | 14171.86 | 14610.86 | 420 | 12:00 Hr. | 256 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | -
2026-06-23 | 15506.14 | 17593.14 | 1997 | 21:00 Hr. | 290 | 129 | 229 | 359 | 128 | 380 | 116 | 210 | 156 | - | 2026-06-23 | 14580.7 | 15596.7 | 972 | 12:00 Hr. | 415 | 137 | 68 | 245 | 107 | 0 | 0 | 0 | 0 | -
2026-06-24 | 15700.01 | 17565.01 | 1785 | 21:00 Hr. | 219 | 31 | 342 | 449 | 47 | 349 | 85 | 58 | 205 | - | 2026-06-24 | 14441.07 | 15598.07 | 1107 | 12:00 Hr. | 529 | 79 | 244 | 225 | 30 | 0 | 0 | 0 | 0 | -
2026-06-25 | 16193.27 | 16753.27 | 536 | 21:00 Hr. | 124 | 0 | 111 | 282 | 19 | 0 | 0 | 0 | 0 | - | 2026-06-25 | 14318.96 | 15886.96 | 1500 | 12:00 Hr. | 663 | 94 | 266 | 378 | 99 | 0 | 0 | 0 | 0 | -
2026-06-26 | 15650.06 | 16347.06 | 667 | 21:00 Hr. | 77 | 0 | 30 | 468 | 0 | 77 | 0 | 15 | 0 | - | 2026-06-26 | 13116.69 | 13729.69 | 587 | 12:00 Hr. | 134 | 0 | 25 | 428 | 0 | 0 | 0 | 0 | 0 | -
2026-06-27 | 15298.25 | 18301.25 | 2874 | 21:00 Hr. | 538 | 162 | 343 | 519 | 247 | 375 | 142 | 352 | 196 | - | 2026-06-27 | 13725.37 | 14831.37 | 1058 | 12:00 Hr. | 382 | 103 | 192 | 353 | 28 | 0 | 0 | 0 | 0 | -
2026-06-28 | 16038.59 | 18354.59 | 2216 | 21:00 Hr. | 385 | 122 | 257 | 420 | 211 | 298 | 133 | 288 | 102 | - | 2026-06-28 | 14398.75 | 17136.65 | 2620 | 12:00 Hr. | 574 | 172 | 315 | 492 | 216 | 354 | 9 | 342 | 146 | -
2026-06-29 | 16082.14 | 16487.88 | 267 | 19:30 Hr. | 30 | 0 | 48 | 93 | 96 | 0 | 0 | 0 | 0 | - | 2026-06-29 | 14669.72 | 15023.72 | 339 | 12:00 Hr. | 206 | 0 | 45 | 48 | 0 | 40 | 0 | 0 | 0 | -
2026-06-30 | 16152.14 | 16726.14 | 549 | 19:30 Hr. | 77 | 0 | 96 | 308 | 14 | 51 | 3 | 0 | 0 | - | 2026-06-30 | 14920 | 15378 | 438 | 12:00 Hr. | 214 | 0 | 3 | 221 | 0 | 0 | 0 | 0 | 0 | -
[16 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: June 2026
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 16193.27 | 2026-06-25 | 21:00 Hr.
2 | Maximum Day Peak Genaration | MW | 14920 | 2026-06-30 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 18354.59 | 2026-06-28 | 21:00 Hr.
4 | Minimum Generation | MW | 11665.13 | 2026-06-19 | 10:00 Hr.
5 | Average of the daily evening peak Genaration | MW | 15362.4037 | - | -
6 | Average of the daily day peak Genaration | MW | 14030.2117 | - | -
7 | Maximum load shed (Evening Peak) | MW | 2874 | 2026-06-27 | 21:00 Hr.
8 | Minimum load shed | MW | 44 | 2026-06-21 | 21:00 Hr.
9 | Total nos. of load shed days | Day | 30 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 919.6333 | - | -
11 | Total Generation | MkWh | 10243.5228 | - | -
12 | Total Generation by BPDB | MkWh | 995.0699 | % of total Gen. | 9.714%
13 | Total Generation by IPP | MkWh | 2617.3181 | '' | 25.55%
14 | A) Total Generation by Generation Companies | MkWh | 4739.8645 | '' | 46.27%
| B) Total Generation by REB | MkWh | 53.7875 | " | 0.5251%
| C) Total Generation by RENTAL | MkWh | 82.2671 | " | 0.8031%
| D) Total Imported from India (BIPTC) | MkWh | 625.288 | " | 6.104%
| E) Total Imported from Tripura, India (A.C) | MkWh | 111.2392 | " | 1.086%
| F) Total Imported from Nepal | MkWh | 14.592 | " | 0.1425%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 1004.0964 | " | 9.802%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3745.8602 | % of total Gen. | 36.57%
| B) Oil | MkWh | 1017.5645 | '' | 9.934%
| C) Hydro | MkWh | 54.5607 | '' | 0.5326%
| D) Solar | MkWh | 114.6082 | '' | 1.119%
| E) Coal | MkWh | 3550.1413 | '' | 34.66%
| F) BIPTC (Import from India) | MkWh | 625.288 | '' | 6.104%
| G) A.C (Import from Tripura, India) | MkWh | 111.2392 | '' | 1.086%
| H) Total Imported from Nepal | MkWh | 14.592 | '' | 0.1425%
| I) Adani (Import from India) | MkWh | 1004.0964 | '' | 9.802%
| J) Wind | MkWh | 5.5723 | '' | 0.0544%
16 | Maximun of the daily total Generation . | MkWh | 358.0682 | 2026-06-30
17 | Monthly Load factor | % | 87.8696 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 66964.4025 | - | -
| A) Gas | M.Taka | 12996.981 | - | -
| B) Coal | M.Taka | 23462.4079 | - | -
| C) HFO | M.Taka | 18058.5936 | - | -
| D) HSD | M.Taka | 72.1081 | - | -
| E) Hydro | M.Taka | 29.6672 | - | -
| F) Solar | M.Taka | 1814.8035 | - | -
| G) Total Import | M.Taka | 10447.8725 | - | -
| H) Wind | M.Taka | 81.9688 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2396.3645 | 2026-06-23
| A) Gas | M.Taka | 515.0649 | 2026-06-01
| B) Coal | M.Taka | 887.427 | 2026-06-30
| C) HFO | M.Taka | 780.1551 | 2026-06-20
| D) HSD | M.Taka | 13.8517 | 2026-06-27 | -
| E) Hydro | M.Taka | 8.8787 | 2026-06-30 | -
| F) Solar | M.Taka | 81.1036 | 2026-06-03 | -
| G) Total Import | M.Taka | 382.9308 | 2026-06-25
| H) Wind | M.Taka | 6.9125 | 2026-06-21
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.5364
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.6498
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 83.73 | 30/6/2026 | 06:00
b) | Actual | FT (MSL) | 76.31 | 30/6/2026 | 06:00
22 | Peak Genaration of June 2025 | MW | 15691.42 | 2025-06-21 | 21:00 Hr.
23 | Peak Demand of June 2025 | MW | 15720.68 | 2025-06-21 | 21:00 Hr.
24 | Maximum peak Generation recorded upto 30/06/2026 | MW | 17200.79 | 2026-05-20 | 21:00 Hr.
25 | Maximum peak Demand recorded upto 30/06/2026 | MW | 17610.79 | 2026-05-20 | 21:00 Hr.
26 | Maximum load shed recorded upto 30/06/2026 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [70 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Fuel | Installed capacity (MW) | Capability Status of Last Week | 25.06.2026 | 18.06.2026 | 11.06.2026 | 04.06.2026 | 28.05.2026 | 21.05.2026 | 14.05.2026 | 07.05.2026 | 30.04.2026 | 23.04.2026 | 16.04.2026 | 09.04.2026 | 02.04.2026 | 26.03.2026 | 19.03.2026 | 12.03.2026 | 05.03.2026 | 26.02.2026 | 19.02.2026 | 12.02.2026 | 05.02.2026 | 29.01.2026 | 22.01.2026 | 15.01.2026 | 08.01.2026 | 01.01.2026 | 25.12.2025 | 18.12.2025 | 11.12.2025 | 04.12.2025 | 27.11.2025 | 20.11.2025 | 13.11.2025 | 06.11.2025 | 30.10.2025 | 23.10.2025 | 16.10.2025 | 09.10.2025 | 02.10.2025 | 25.09.2025 | 18.09.2025 | 11.09.2025 | 04.09.2025 | 28.08.2025 | 21.08.2025 | 14.08.2025 | 07.08.2025 | 31.07.2025 | 24.07.2025 | 17.07.2025 | 10.07.2025 | 03.07.2025 | 26.06.2025 | 19.06.2025 | 12.06.2025 | 05.06.2025 | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | Capable | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | Capable |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | Capable | [45 empty] | 20 | 20 | [7 empty] | 20 | [41 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 | Capable | [26 empty] | 20 | 20 | [18 empty] | 20 | [5 empty] | 20 | 20 | 20 | 20 | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | Capable | [36 empty] | 7 | 7 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | Capable | [16 empty] | 30 | 30 | 30 | 30 | 30 | [56 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | Capable |  |  |  | 20 | 20 | 20 | 20 | [5 empty] | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410 | Capable | [46 empty] | 45 | [47 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 | Capable | [9 empty] | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97 | Capable | 2 | 2 |  |  |  | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [24 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163 | Capable
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210 | Capable
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225 | Capable
14 | Shikalbaha Peaking GT | BPDB | Gas | 150 | Capable
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330 | Capable | [70 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 | Capable | [12 empty] | 20 | 20 | 20 | [52 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104 | Capable | [9 empty] | 2 | 2 | 2 | [32 empty] | 2 |  |  | 2 | 2 | [18 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
18 | Bhola 225 MW CCPP | BPDB | Gas | 194 | Capable | [49 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365 | Capable
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | Capable | [18 empty] | 16 | 16 |  |  | 20 | 20 | 20 | 20 |  |  | 20 | 20 | 20 |  |  |  | 20 | [10 empty] | 20 | 16 | [7 empty] | 20 | 20 | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | Capable | 30 | 30 | 30 |  |  | 30 | 30 | 30 | [47 empty] | 30 | 30 | 30 | 30 |  | 30 | 30
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | Capable | [10 empty] | 30 | 30 | 30 | 30 | 30 | 35 | 35 | 35 | 35 | [11 empty] | 30 | 30 | 30 | 30 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231 | Capable
24 | RPCL 210 MW CCPP | IPP | Gas | 210 | Capable but not tested recently
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100 | Not Capable but feasible
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50 | Not Capable but feasible
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410 | Not Capable but feasible
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400 | Capable | [75 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274 | Not Capable but feasible
16 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | Capable | 60 | 60 | 30 | 30 | 30 | 30 | 30 | [5 empty] | 20 | 20 | 20 | 30 | 30 | 30 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 60 |  |  |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [7 empty] | 20 | 20
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | Capable | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 16 | 16 | 30 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
32 | Bhola Nutan Bidyut | IPP | Gas | 220 | Capable
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360 | Not Capable but feasible
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450 | Not Capable but feasible
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150 | Capable | [44 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30
36 | Anwara 300 MW PP (United) | IPP | HFO | 300 | Capable
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | Capable
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104 | Capable
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105 | Capable
40 | Gazipur 100 MW PP | IPP | HFO | 105 | Capable
41 | United Payra Power Ltd. | IPP | HFO | 150 | Capable
42 | Madhumati 100 MW PP | IPP | HFO | 100 | Capable
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | Capable
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | Capable
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300 | Capable
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55 | Capable
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | HFO | 149 | Capable
48 | Feni Lanka Power | IPP | HFO | 114 | Capable
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110 | Capable
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | Capable
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55 | Capable
52 | Zodiac 54 MW | IPP | HFO | 54 | Capable
53 | Anlima Energy Ltd | IPP | HFO | 116 | Capable
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115 | Capable
55 | Confidence Unit-2 Bogura | IPP | HFO | 113 | Capable
56 | Confidence Unit-1 Bogura | IPP | HFO | 113 | Capable
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | Capable
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55 | Capable
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149 | Capable
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | Capable
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55 | Capable
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | Capable |  | 33 | 33 | 33 | 16.5 | 33 | 33 | 33 | 33 | 33 |  | 40 | 20 | 20 | 40 | 66 | 66 | 66 | 66 |  | 66 | 33 | 66 | 66 | 66 | 66 | 66 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | Capable | 20 | 20 | 20 | 20 | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 66 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  | 50 | 50 | 50 | 50 | 20 | 20 | 40 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | Capable | 30 | 30 | 30 | 30 | 15 | 15 | 30 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 50 | 50 | 50 | 50 | 25 | 40 | 25 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 50 | 50 | 50 | 50
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | Capable | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 25 | 30 | 30 | 30 | 30 | [11 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
66 | Unique Meghnaghat Power Ltd(UMPL) | IPP | Gas | 584 | Capable | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 |  | 30 | [12 empty] | 24 | 24 | 24 |  |  |  |  | 50 | 24 | 24 | 50
67 | Meghnaghat CCPP Unit 2 (Summit) | IPP | Gas | 583 | Capable | 30 | 30 | 30 | [10 empty] | 25 | 25 | 50 | 50 | 50 | 50 |  |  |  | 50 | 50 | 50 | 50 | 50 | 50
68 | Jera Meghnaghat Power Ltd. | IPP | Gas | 718 | Capable |  |  |  | 20 | 20 | 20 | 20 | 20 | [11 empty] | 50 | 70
| Payra 1320 MW Unit-2 | BCPCL |  | 622 | Capable | [59 empty] | 20 | 20
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70 | Capable
| Shajibazar 100 MW PP | BPDB |  | 100 | Not Capable but feasible
| Khulna 225 MW CCPP | NWPGCL |  | 230 | Capable but not tested recently
Total Installed capacity | [5 empty] | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 20506 | 20506 | 20506 | 20506 | 20506 | 20506 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19739 | 19739 | 19739 | 19739 | 14388 | 14388 | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity | [5 empty] | 6093 | 7377 | 6744 | 6794 | 4864 | 6567 | 6861 | 6051 | 4051 | 4051 | 4246 | 4752 | 5680 | 6978 | 8164 | 7834 | 8174 | 8174 | 7698 | 7298 | 6286 | 4146 | 5722 | 6660 | 6754 | 7086 | 6756 | 5564 | 5851 | 5937 | 5232 | 5185 | 3503 | 3503 | 6403 | 6525 | 5821 | 6221 | 6871 | 7523 | 8031 | 7313 | 7523 | 6939 | 8121 | 8527 | 9061 | 8099 | 8099 | 7580 | 8537 | 6163 | 6795 | 6632 | 2862 | 3135 | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve | [5 empty] | 263 | 296 | 264 | 274 | 232.5 | 291 | 286 | 236 | 186 | 186 | 198 | 238 | 304 | 349 | 394 | 489 | 519 | 519 | 490 | 455 | 419 | 256 | 359 | 399 | 429 | 443 | 398 | 365 | 358 | 358 | 328 | 324 | 228 | 228 | 351 | 372 | 349 | 379 | 427 | 477 | 471 | 451 | 477 | 427 | 459 | 452 | 503 | 386 | 404 | 382 | 452 | 356 | 424 | 408 | 262 | 288 | 218 | 193 | 193 | 202 | 232 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO | [5 empty] | 10 | 11 | 10 | 11 | 11 | 13 | 12 | 10 | 8 | 8 | 9 | 10 | 14 | 15 | 15 | 14 |  |  | 15 | 14 | 12 | 10 | 11 | 12 | 12 | 11 | 10 | 10 | 9 | 9 | 9 | 9 | 7 | 7 | 9 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 12 | 14 | 13 | 15 | 12 | 12 | 12 | 13 | 11 | 14 | 13 | 11 | 12 | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list | [5 empty] | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 68 | 68 | 68 | 68 | 64 | 64 | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list | [5 empty] | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 74 | 74 | 74 | 74 | 70 | 70 | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable | [5 empty] | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 63 | 63 | 61 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 58 | 58 | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible | [5 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: June 2026
SL | Plant Name | Owner | Fuel | Installed capacity | FGMO Status
|  |  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ | √ | √ | √ | √ | √ |  |  | √
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | √ | √ | √
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 | √
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | √ | √
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  |  | √ |  |  |  | √ | √
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410 | √
9 | Haripur 412 MW CCPP | EGCB | Gas | 412
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225
14 | Shikalbaha Peaking GT | BPDB | Gas | 150
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104
18 | Bhola 225 MW CCPP | BPDB | Gas | 194
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | √ | √
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | [24 empty] | √
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231
24 | RPCL 210 MW CCPP | IPP | Gas | 210
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | √ | [13 empty] | √ |  | √ | [7 empty] | √ | √ | √ | √ | √
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 |  |  |  |  | √ | √ | √ | √
32 | Bhola Nutan Bidyut | IPP | Gas | 220
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150
36 | Anwara 300 MW PP (United) | IPP | HFO | 300
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105
40 | Gazipur 100 MW PP | IPP | HFO | 105
41 | United Payra Power Ltd. | IPP | HFO | 150
42 | Madhumati 100 MW PP | IPP | HFO | 100 | √ | √ | √ | √ | √ | √ | √ | √
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | √ | v | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | √ | v | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55
47 | Kodda 150 MW PP BRPL | IPP | HFO | 149
48 | Feni Lanka Power | IPP | HFO | 114 | √ | v | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55
52 | Jodiac Power | IPP | HFO | 54
53 | Anlima Energy Ltd | IPP | HFO | 116 | √ | v | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115
55 | Confidence Unit-2 Bogura | IPP | HFO | 113
56 | Confidence Unit-1 Bogura | IPP | HFO | 113
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | √ | [6 empty] | √ | √ | √
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 |  |  |  | √ | √ | √ | √ | √ |  |  |  | √ | [14 empty] | √ | √ | √
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | √
66 | Unique Meghnaghat Power Limited (UMPL) | IPP | Gas | 584 | √
67 | Meghnaghat CCPP(Summit)-2 | IPP | Gas/HSD | 583 | [6 empty] | √ | √ | [5 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| JERA Meghnaghat Power Limited | IPP | Gas | 718
| United Payra Power Ltd. | IPP |  | 150
| Mirsharai 150 MW | IPP | HFO/Gas | 150 | √ |  |  | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | [6 empty] | √ | √
Jangalia 52 MW PP (Lakdanavi)
| Ashuganj 420 MW CCPP(East) | APSCL |  | 400 | √ | √ | √
| Ashuganj 55 MW PP (Precision) | QRPP |  | 55
| Bagura 113 MW PP (Confidence)-2 | IPP |  | 113
| Energypac Power Venture Thakurgaon Ltd. | IPP |  | 115
| Chandpur 150 MW CCPP | BPDB |  | 163
| Khulna 225 MW CCPP | NWPGCL |  | 230
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70
| Shajibazar 100 MW PP | BPDB |  | 100
| Payra 1320 MW Unit-1 | BCPCL |  | 622