## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 31-07-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-07-2026 | during | 31-07-2026 | during | 31-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 251 | 361 | 412 | 412 | 371 | 371 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 141 | 140 | 335 | 335 | 150 | 150 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 305 | 282 | 335 | 335 | 320 | 320 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 128 | 144 | 149.36 | 149.36 | 125 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 9 | 11 | 33 | 33 | 11 | 11 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 0 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 81 | 81 | 300 | 300 | 48 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 106 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 105 | 105 | 52 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 24 | 0 | 23 | 0 | 23 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 325 | 280 | 583 | 583 | 330 | 330 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1650.42 | 2075.42 | 5798.64 | 5775.64 | 1750.42 | 2182.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 10 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 222 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 202 | 204 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 89 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 23 | 56 | 40 | 72 | 40 | 72 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 5 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 50 | 79 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.97 | 0 | 1.9 | 0 | 1.9 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 54 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 105 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 100 | 108 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 35 | 86 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 900 | 1224 | 1224 | 1224 | 900 | 900 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 59 | 15 | 8 | 4 | 8 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1145 | 1150 | 1150 | 1150 | 1145 | 1145 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 3063.97 | 3592.36 | 4113.76 | 4198.86 | 3188.9 | 3299
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 213 | 188 | 221.25 | 221.25 | 218 | 218 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 352 | 280 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 0 | 342.01 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 30 | 40 | 41.65 | 41.65 | 30 | 30 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 39 | 24 | 40 | 40 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 85 | 163 | 163 | 87 | 87 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 16 | 17 | 200 | 200 | 80 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 148 | 132 | 84 | 78 | 150 | 150 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 106 | 114 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 47 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 3 | 88 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 51 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1315.2 | 1287.2 | 2752.44 | 2696.44 | 1423.21 | 1516.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-07-2026 | during | 31-07-2026 | during | 31-07-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 22.11 | 0 | 15 | 0 | 15 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.7 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 155 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 32.62 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 32 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 269.43 | 279 | 532.7 | 516.5 | 275.2 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 42 | 41 | 41 | 40 | 40 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 137 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 53 | 84 | 86 | 86 | 53 | 53 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 101 | 100 | 100 | 100 | 100 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 0 | 25 | 25 | 17 | 17 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 305 | 341 | 341 | 307 | 307 | Machine Problem
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 313 | 312 | 250 | 260 | 315 | 315 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 991 | 981 | 1086 | 1096 | 979 | 979
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 896 | 899 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 30 | 30 | 30 | 30 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 105 | 105 | 50 | 50 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 37 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 240 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 555 | 547 | 1080 | 1080 | 555 | 555 | U-2 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1526 | 1785 | 3450 | 3380 | 1743 | 1673
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1040 | 1100 | 1050 | 1050 | 700 | 1050 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 880 | 882 | 581.53 | 581.53 | 895 | 895 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 232 | 236 | 307 | 307 | 250 | 250 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.08 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2525.08 | 2591 | 2549.53 | 2548.53 | 2219 | 2568
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 48.48 | 0 | 43.25 | 0 | 43.25 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 156 | 150 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 250 | 240 | 413.79 | 413.79 | 280 | 280 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 26 | 26 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 113 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 3.83 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1273.03 | 1475.61 | 1469.13 | 1469.13 | 1320 | 1320 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 28.6 | 0 | 38 | 0 | 38 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 5 | 0 | 90 | 0 | 90 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1822.94 | 2200.61 | 3195.87 | 3019.12 | 2171.95 | 2165.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 140 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 190 | 190 | 190 | 190 | 190 | 190 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 86 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.7 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 24 | 115 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 22 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 204 | 0 | 153.72 | 0 | 153.72 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 447.7 | 531 | 624.72 | 438 | 491.72 | 340
System Total |  |  |  |  | 28843.2 | 29171.687 | 13611.74 | 15322.59 | 24103.66 | 23669.09 | 14242.4 | 14981.83
Forecast Scenario (31-07-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14840 |  | 1871.8 |  | 16800
|  |  |  | 1:00 | 14210 |  | 2139.2 |  | 16450
|  |  |  | 2:00 | 14150 |  | 1871.8 |  | 16110
|  |  |  | 3:00 | 13980 |  | 1594.85 |  | 15650
|  |  |  | 4:00 | 13920 |  | 1155.55 |  | 15130
|  |  |  | 5:00 | 13730 |  | 945.45 |  | 14720
|  |  |  | 6:00 | 13340 |  | 563.45 |  | 13930
|  |  |  | 7:00 | 13390 |  | 276.95 |  | 13680
|  |  |  | 8:00 | 13450 |  | 9.55 |  | 13460
|  |  |  | 9:00 | 13190 |  | 181.45 |  | 13380
|  |  |  | 10:00 | 13200 |  | 28.65 |  | 13230
|  |  |  | 11:00 | 13340 |  | 19.1 |  | 13360
|  |  |  | 12:00 | 13620 |  | 229.2 |  | 13860
|  |  |  | 13:00 | 13750 |  | 716.25 |  | 14500
|  |  |  | 14:00 | 13440 |  | 534.8 |  | 14000
|  |  |  | 15:00 | 13490 |  | 401.1 |  | 13910
|  |  |  | 16:00 | 13420 |  | 38.2 |  | 13460
|  |  |  | 17:00 | 13100 |  | 19.1 |  | 13120
|  |  |  | 18:00 | 12900 |  | 9.55 |  | 12910
|  |  |  | 18:30 | 13450 |  | 47.75 |  | 13500
|  |  |  | 19:00 | 14180 |  | 9.55 |  | 14190
|  |  |  | 19:30 | 14960 |  | 391.55 |  | 15370
|  |  |  | 20:00 | 14940 |  | 515.7 |  | 15480
|  |  |  | 21:00 | 15320 |  | 515.7 |  | 15860
|  |  |  | 22:00 | 15200 |  | 668.5 |  | 15900
|  |  |  | 23:00 | 15100 |  | 859.5 |  | 16000
Probable Maximum Temperature: |  |  | 30.4°C
Probable Maximum Demand at Day Peak: |  |  | 13860.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 516
Probable Maximum Demand at Evening Peak: |  |  | 15860.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15320.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 333.20 MKWHr. |  | 110 | 30 | 50 | 116 | 40 | 70 | 20 | 45 | 35 | 516
*** This report is generated digitally from Operation Information System (OIS) at 11:47 hrs on 31-07-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 30-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13611.74 | MW | 12:00 Hr. | Energy Generated |  |  | 334.8669 |  | MKWHr.
| Day Peak Demand |  |  | 15648.45 | MW | 12:00 Hr. | Energy Unserverd |  |  | 36.324 |  | MKWHr.
| Evening Peak Generation |  |  | 15322.59 | MW | 21:00 Hr. | Energy Demand |  |  | 371.1909 |  | MKWHr.
| Evening Peak Demand |  |  | 16868.59 | MW | 21:00 Hr. | Maximum Temperature |  |  | 30.4 |  | °C
| Minimum Generation of the Day |  |  | 13080.48 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 660.56 |  | MMCFD
| Maximum Generation of the Day |  |  | 15322.59 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.6395 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.0707 | 0 | 14.4117 | 0 | 0 | 0.088919 | 0 | 0 | 40.5712 | Gas | 89.9724 | Gas | 312623889.1344
| Chattogram Zone |  |  | 5.0233 | 50.1909 | 14.9042 | 0 | 5.2871 | 0.10386 | 0 | 0.65088 | 76.1603 | Coal | 125.3416 | Coal | 835198001.7432
| Cumilla Zone |  |  | 17.4539 | 0 | 9.5665 | 0 | 0 | 0.24464 | 3.2794 | 0 | 30.5444 | HFO | 51.6013 | HFO | 955158625.99
| Mymensingh Zone |  |  | 0 | 0 | 4.5791 | 0 | 0 | 0.39973 | 0 | 0 | 4.9788 | HSD | 1.3356 | HSD | 32781933.528
| Sylhet Zone |  |  | 23.4992 | 0 | 0 | 0 | 0 | 0.046778 | 0 | 0 | 23.546 | Hydro | 5.2871 | Hydro | 528713.5
| Khulna Zone |  |  | 0 | 17.4982 | 0.32856 | 0.7922 | 0 | 0.34776 | 22.5985 | 0 | 41.5652 | Solar | 3.127 | Solar | 50734914.034
| Barishal Zone |  |  | 8.1503 | 52.9525 | 0.83616 | 0 | 0 | 0.000987 | 0 | 0 | 61.94 | Import | 57.5509 | Import | 361623733.8
| Rajshahi Zone |  |  | 9.775 | 0 | 3.5851 | 0 | 0 | 0.91279 | 31.673 | 0 | 45.946 | Wind | 0.65088 | Wind | 9574444.8
| Rangpur Zone |  |  | 0 | 4.7 | 3.39 | 0.54338 | 0 | 0.98154 | 0 | 0 | 9.6149
| Total |  |  | 89.9724 | 125.3416 | 51.6013 | 1.3356 | 5.2871 | 3.127 | 57.5509 | 0.65088 | 334.8669
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 312623889.1344 |  | Hydro | 528713.5
|  |  |  | Coal | 835198001.7432 |  | Solar | 50734914.034
|  |  |  | HFO | 955158625.99 |  | Import | 361623733.8
|  |  |  | HSD | 32781933.528 |  | Wind | 9574444.8
[5 empty] | Total: | 255,82,24,256 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6865 | Peak Hr Flow | 899.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51472109.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.673 | Peak Hr Flow | 1475.61 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2283 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.2794 | Peak Hr Flow | 132.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2626 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 56.6389 | Peak Hr Flow | 2506.61 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 234 |  | 5827
|  |  |  | Chattogram |  | 66 |  | 1545
|  |  |  | Cumilla |  | 201 |  | 1585
|  |  |  | Mymensingh |  | 311 |  | 1473
|  |  |  | Sylhet |  | 103 |  | 690
|  |  |  | Khulna |  | 249 |  | 1914
|  |  |  | Barishal |  | 45 |  | 468
|  |  |  | Rajshahi |  | 185 |  | 1672
|  |  |  | Rangpur |  | 85 |  | 1076
|  |  |  | Total |  | 1479 |  | 16250
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 89
|  |  |  | Total Unavailable Capacity |  |  |  | 389
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- U2
| 08:10 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- Unit-1 false
|  | 08:50 | Mymensingh 132/33kV S/S Transformer-2 (414T) HT is restored.
|  | 08:50 | Mymensingh 132/33kV S/S Transformer-2 (414T) LT is restored.
| 09:24 |  | Barapukuria-Rangpur 132 kV Ckt-1 Forced S/D from Barapukuria 230/132/33kV end Due to SOTF
Fault
|  | 09:25 | Benapole 132/33kV S/S Transformer-1(406T) HT is restored.
|  | 09:26 | Benapole 132/33kV S/S Transformer-1(406T) LT is restored.
|  | 09:35 | Shahjibazar 132/33kV S/S TR-06 HT is restored.
| 09:48 | 17:44 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-1 Project Work S/D Due to Project work
at Gopalganj ss end.
| 09:54 | 17:44 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 Project Work S/D
| 09:54 | 14:53 | Aminbazar 400/230/132kV S/S Bus-1 (400kV) Project Work S/D Due to Bus diff. protection
and stability testing for IDRNP project.
| 09:55 | 17:45 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-2 Project Work S/D Due to Project work
at Gopalganj ss end
| 09:55 | 17:45 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 Project Work S/D
| 10:07 | 16:50 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Shahjibazar 132/33kV end Due to
E/S Maintenance Work
|  | 10:10 | Chowmuhani 230/132/33kV S/S Lakshmipur-02 is restored.
| 10:19 | 18:35 | Madunaghat-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
taken by korerhat
| 10:26 | 12:25 | BIPTC S/S Baharampur-3 Scheduled S/D Due to Shutdown is taken from baharampur end.
| 10:44 | 18:35 | Korerhat 400/230/132kV S/S Meghnaghat-1 Project Work S/D Due to Shunt reactor /DFDR
| 10:53 | 17:44 | BSRM-Cumilla(N) 230 kV Ckt-2 Project Work S/D from Feni 230/132kV end Due to DFDR testing
at Korerhat SS end.
|  | 10:56 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
| 10:57 | 17:44 | Korerhat 400/230/132kV S/S Feni -2 Project Work S/D Due to DFDR Work
| 11:02 | 18:48 | Chowmuhani 230/132/33kV S/S Korerhat-03 Project Work S/D Due to Shutdown Taken by
Korerhat 400/230 kV Substation.
| 11:07 | 18:47 | Korerhat 400/230/132kV S/S Chowmuhani-3 Project Work S/D Due to DFDR WORK
| 11:18 | 17:23 | Korerhat 400/230/132kV S/S ATR-4(7403T) LT Project Work S/D Due to CAF/DFDR
| 11:19 | 17:22 | Korerhat 400/230/132kV S/S ATR-4(7403T) HT Project Work S/D Due to CAF/DFDR
| 12:00 |  | Day Peak Generation: 13612 MW.
| 12:20 | 14:17 | Lakshmipur 132/33kV S/S Lakshmipur-Chowmuhani Circuit 1 Project Work S/D Due to
Lakshmipur-Chowmuhani Circuit-1 has taken Shutdown to fix Scada Integration work via
Project(CNEEC).
| 12:20 | 14:10 | Chowmuhani 230/132/33kV S/S Lakshmipur-01 Project Work S/D Due to Project Work.
| 12:26 | 15:04 | Bhulta 400/230/132kV S/S 132kV Narsingdi Scheduled S/D | [7 empty] | 104.0MW load
interrup.
| 12:35 | 13:42 | Maijdee 132/33kV S/S Chowmuhoni-Maijdee ckt -02 Project Work S/D Due to project work
| 12:36 | 13:43 | Chowmuhani 230/132/33kV S/S Maijdee-02 Project Work S/D Due to Project Work.
| 13:17 | 15:24 | Sreepur 230/132/33kV S/S 132 kV BUS-1 Scheduled S/D Due to PTR-3 Project Work
| 13:30 | 16:38 | Meghnaghat 230/132kV S/S Bus2 Scheduled S/D Due to maintanence work
| 13:40 | 16:34 | Meghnaghat 400/230kV S/S 230kV BUS Section 02 Scheduled S/D Due to 230 kv old ss work
| 14:19 | 16:02 | Chowmuhani 230/132/33kV S/S Lakshmipur-02 Project Work S/D Due to Project Work.
| 14:19 | 16:02 | Lakshmipur 132/33kV S/S Lakshmipur-Chowmuhani Circuit 2 Project Work S/D Due to
Lakshmipur-Chowmuhani Circuit-2 has taken Shutdown to fix Scada Integration work via
Project(CNEEC).
|  | 14:42 | Fenchuganj 230/132/33kV S/S TR-01 HT is restored.
| 14:46 | 16:59 | BIPTC S/S Baharampur-4 Scheduled S/D Due to Shutdown taken from Berhampore End.
|  | 14:51 | Fenchuganj 230/132/33kV S/S TR-01 LT is restored.
| 16:11 | 18:31 | Lakshmipur 132/33kV S/S MAIN BUS-2 Project Work S/D Due to To fixing SCADA Integration
work via Project(CNEEC).
|  | 16:25 | Juldah-Sikalbaha 132kV Ckt-1 is restored.
|  | 16:38 | Meghnaghat 230/132kV S/S Meghnaghat-ST (MPL) is restored.
| 18:28 | 18:50 | Kulaura 132/33kV S/S TR-1 AB HT Tripped showing 1.Differential Protection 2. Overcurrent | [7 empty] | 20.0MW load
|  |  | Protection relays Due to 33KV PBS feeder fault | [7 empty] | interrup.
| 18:28 | 18:54 | Kulaura 132/33kV S/S TR-1 AB LT Tripped showing 1.Differential Protection 2. Overcurrent | [7 empty] | 20.0MW load
|  |  | Protection relays Due to 33KV PBS feeder fault | [7 empty] | interrup.
| 19:28 | 19:31 | Sylhet 132/33kV S/S T2 LT Tripped showing over current c phase. relays Due to over | [7 empty] | 60.0MW load
|  |  | current c phase. | [7 empty] | interrup.
| 19:28 | 19:31 | Sylhet 132/33kV S/S T2 HT Tripped showing over current c phase. relays Due to over | [7 empty] | 60.0MW load
|  |  | current c phase. | [7 empty] | interrup.
| 21:00 |  | Evening peak generation is 15323 MW.
| 21:15 | 21:55 | Palashbari 132/33kV S/S TR1-414T LT Tripped showing Micom P142 relays Due to chatra 33kv | [7 empty] | 70.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 21:15 | 21:30 | Palashbari 132/33kV S/S TR2-404T LT Tripped showing Micom P142 relays Due to chatra 33 Kv | [7 empty] | 70.0MW load
|  |  | Feeder Fault | [7 empty] | interrup.
|  | 21:31 | Niamatpur 132/33kV S/S 132 kV Naogaon ckt-2 is restored.
|  | 21:32 | Naogaon 132/33kV S/S Naogaon-Niamatpur Ckt-2 is restored.
| 23:52 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U2
| 06:28 | 07:00 | Bheramara(GK) 132/33kV S/S TR-2 LT Tripped showing OC/EF relays Due to Fault due to 33KV | [7 empty] | 18.0MW load
|  |  | Douloatpur Feeder | [7 empty] | interrup.
| 06:28 | 07:00 | Bheramara(GK) 132/33kV S/S TR-1 LT Tripped showing OC/EF relays Due to fault due to 33kv | [7 empty] | 18.0MW load
|  |  | Douloatpur feeder | [7 empty] | interrup.
| 06:32 |  | Mymensingh 132/33kV S/S Transformer-3 (424T) LT Project Work S/D
| 06:32 |  | Mymensingh 132/33kV S/S Transformer-3 (424T) HT Project Work S/D
| 07:00 |  | Minimum Generation: 12957 MW.
| 07:15 |  | Mymensingh 132/33kV S/S Bus A Project Work S/D
| 07:20 | 07:55 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing Overcurrent Relay relays Due to | [7 empty] | 60.0MW load
|  |  | Earth Fault | [7 empty] | interrup.
| 07:27 |  | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 LT Project Work S/D Due to DFDR Commissioning.
| 07:28 |  | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 HT Project Work S/D Due to DFDR Commissioning.
| 07:36 |  | Sreepur 230/132/33kV S/S 132 kV BUS-2 Scheduled S/D Due to Project Work
| 07:47 |  | Kulaura 132/33kV S/S TR-1 AB LT Scheduled S/D Due to PBS bus DS redhot maintenance | [7 empty] | 24.0MW load
interrup.
| 07:48 |  | Kulaura 132/33kV S/S TR-1 AB HT Scheduled S/D Due to PBS bus DS redhot maintenance | [7 empty] | 24.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 30-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 361 | 7614000 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 140 | 3424407 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 384963 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 282 | 7123312 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 339120 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 144 | 3181440 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 679172 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 469270 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11 | 246000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 499320 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 264960 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 81 | 1655247 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 106 | 1448640 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 665280 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1136160 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 88919 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 696600 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 280 | 7163636 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3490800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2075.42 | 40571246
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 105156 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 80730 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1190880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5287135 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 204 | 4803953 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2305018 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 56 | 899280 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 362984 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 591360 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 219360 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 79 | 1446720 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 23125 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 378873 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 399865 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2577673 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 584640 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2251909 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 86 | 1809891 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 22990907 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 15 | 650880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1150 | 27200000 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 3592.36 | 76160339
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 188 | 5110000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 280 | 7838100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 40 | 780552 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1220481 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 3649890 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 24 | 875600 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2034618 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 444960 | -
| Import (Tripura) |  | Import | 0 | 160 | 132 | 3279360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1224130 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 470150 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2337000 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 47 | 282240 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 88 | 752640 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 244636 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1287.2 | 30544357
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 119070 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 155 | 2241600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1347600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 269310 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 422160 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 32 | 567720 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 279 | 4978810
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 46778 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 970000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 137 | 3375981.82 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1312320 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2408210 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 318720 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7508000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 312 | 7606000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 981 | 23546009.82
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 899 | 21686545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 129120 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 199440 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 347760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 240 | 792203.64 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 547 | 17498180 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1785 | 41565248.64
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 25141818 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 396960 | FGMO
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2827000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 882 | 21592727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5323270 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 439200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 236 | 6218000 | Line Overload
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 987 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2591 | 61939962.27
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 222472 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 395425 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 259811 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 150 | 3669545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 240 | 6105454 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 192154 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 606160 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1474368 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 50 | 657216 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 21780 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1475.61 | 31673044 | Coal transportation prob
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 279552 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 388990 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2200.61 | 45945971
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 140 | 543375 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 190 | 4700000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 86 | 825456 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 25459.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2564531 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 123045 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 833040 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 531 | 9614906.8
Eastern Grid Total |  |  |  |  | 17440.562 | 8214.98 | 175800761.82
Western Grid Total |  |  |  |  | 11731.125 | 7107.61 | 159066088.71
National Grid Total |  |  |  |  | 29171.687 | 15322.59 | 334866850.53
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 30-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10251.38 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4566 | MW
i) Dhaka area |  |  | 5592.98 |  | MW | i) Khulna area |  |  |  | 1665 | MW
ii) Chattogram area |  |  | 1525.4 |  | MW | ii) Barishal area |  |  |  | 422.6 | MW
iii) Cumilla area |  |  | 1384 |  | MW | iii) Rajshahi area |  |  |  | 1487.4 | MW
iv) Mymensingh area |  |  | 1162 |  | MW | iv) Rangpur area |  |  |  | 991 | MW
v) Sylhet area |  |  | 587 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14817.38 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 20:00 | 67 | HaripurSBU | 130 | 06:00 | 133 | Narshingdi | 197 | 00:00 | 199 | Uttara | 95 | 13:00
2 | AKSML | 134.9 | 08:00 | 68 | Hasnabad | 91 | 21:00 | 134 | Natore | 144 | 21:00 | 200 | UttaraNew | 54 | 00:00
3 | Aftabnagar | 42 | 00:00 | 69 | Hathazari | 91 | 22:00 | 135 | Nawabganj | 52.8 | 05:00 | 201 | Zigatola | 94 | 13:00
4 | Agargaon | 121 | 13:00 | 70 | Hatirjheel | 88 | 15:00 | 136 | Netrakona | 127 | 06:00
5 | Agrabad | 74 | 12:00 | 71 | Ishurdi | 78 | 21:00 | 137 | New | 86 | 12:00
6 | Amnura | 30 | 00:00 | 72 | Jaldhaka | 84 | 05:00 | 138 | Niamatpur | 72 | 22:00
7 | Ashuganj | 94 | 00:00 | 73 | Jamalpur | 116 | 19:30 | 139 | Noapara | 43 | 19:00
8 | BSRM | 196 | 05:00 | 74 | Jashore | 149 | 19:30 | 140 | PHP | 14 | 17:00
9 | Bagerhat | 87 | 19:00 | 75 | Jhenaidah | 91 | 22:00 | 141 | Pabna | 99 | 19:30
10 | Bajitpur | 83 | 23:00 | 76 | Joydebpur | 160 | 19:00 | 142 | Palashbari | 114 | 02:00
11 | Bakerganj | 13.8 | 23:00 | 77 | Joypurhat | 57 | 20:00 | 143 | Panchagarh | 67 | 00:00
12 | Bakulia | 98 | 19:00 | 78 | Juldah | 18 | 22:00 | 144 | Patiya | 10 | 19:00
13 | Banani | 68 | 12:00 | 79 | KSRM | 31 | 09:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 16 | 10:00 | 80 | Kabirpur | 250 | 21:00 | 146 | Patuakhali | 56 | 21:00
15 | Barapukuria | 63 | 05:00 | 81 | Kachua | 82 | 22:00 | 147 | Payra | 30 | 22:00
16 | Barguna | 22 | 23:00 | 82 | Kaliganj | 36 | 19:00 | 148 | Postogola | 61 | 12:00
17 | Barishal | 98 | 19:00 | 83 | Kallyanpur | 117 | 00:00 | 149 | Pubail | 40 | 19:00
18 | Barishal-230 | 94 | 22:00 | 84 | Kalurghat | 41 | 11:00 | 150 | Purbachal | 29 | 12:00
19 | Baroaulia | 48 | 23:00 | 85 | Kamrangirchar | 80 | 13:00 | 151 | Purbasadipur | 142 | 20:00
20 | Baroirhat | 67 | 23:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 35 | 05:00
21 | Bashundhara | 212 | 12:00 | 87 | Kasba | 39 | 20:00 | 153 | Rahim | 50 | 05:00
22 | BashundharaCement | 12 | 00:00 | 88 | Kazla | 114 | 14:00 | 154 | Rajbari | 83 | 19:00
23 | Beanibazar | 74 | 22:00 | 89 | Keranigonj | 79 | 21:00 | 155 | Rajendrapur | 124 | 08:00
24 | Benapole | 58 | 23:00 | 90 | Khagrachori | 32 | 19:00 | 156 | Rajshahi | 113 | 23:00
25 | Bhaluka | 163 | 17:00 | 91 | Khulna | 53 | 12:00 | 157 | Rajshahi-230 | 90 | 00:00
26 | Bhandaria | 50 | 19:00 | 92 | Khulshi | 184 | 19:30 | 158 | Ramganj | 100 | 22:00
27 | Bhangura | 35 | 00:00 | 93 | Kishoreganj | 128 | 06:00 | 159 | Rampur | 42 | 23:00
28 | Bheramara(GK) | 60 | 22:00 | 94 | Kodda | 290 | 20:00 | 160 | Rangamati | 14 | 10:00
29 | Bhulta | 224 | 19:30 | 95 | Kulaura | 52 | 20:00 | 161 | Rangpur | 132 | 20:00
30 | Bog-Sherpur | 68 | 04:00 | 96 | Kurigram | 74 | 21:00 | 162 | Ruppur | 4.6 | 10:00
31 | Bogura | 192 | 22:00 | 97 | Kushtia | 150 | 21:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 72 | 22:00 | 98 | Laksam | 34 | 21:00 | 164 | Saidpur | 108 | 09:00
33 | Brahmanbaria | 146 | 00:00 | 99 | Lakshmipur | 46 | 02:00 | 165 | Santhia | 38 | 20:00
34 | Cantonment | 128 | 13:00 | 100 | Lalbag | 81 | 13:00 | 166 | Satkhira | 134 | 21:00
35 | Chandina | 38 | 02:00 | 101 | Lalmonirhat | 70 | 04:00 | 167 | Satmasjid | 102 | 13:00
36 | Chandpur | 70 | 19:00 | 102 | MI_Cement | 15.8 | 02:00 | 168 | Savar | 209 | 19:00
37 | Chandraghona | 32 | 22:00 | 103 | Madanganj | 41 | 10:00 | 169 | SevenRings | 19.08 | 17:00
38 | Chapai | 74 | 22:00 | 104 | Madaripur | 102 | 21:00 | 170 | ShahCement | 33 | 18:00
39 | Charfasson | 30 | 23:00 | 105 | Madartek | 80 | 00:00 | 171 | Shahjadpur | 68 | 20:00
40 | Charsaidpur | 36 | 00:00 | 106 | Madunaghat | 52 | 23:00 | 172 | Shahjibazar | 141 | 19:30
41 | Chauddagram | 68 | 22:00 | 107 | Magura | 62 | 19:00 | 173 | Shahmirpur | 44 | 00:00
42 | Chhatak | 25 | 19:00 | 108 | Mahasthangarh | 76 | 04:00 | 174 | Shariatpur | 86 | 19:00
43 | Chowmuhani | 140 | 22:00 | 109 | Maijdee | 30 | 21:00 | 175 | Sherpur | 156 | 20:00
44 | Chuadanga | 106 | 22:00 | 110 | Manikganj | 130 | 21:00 | 176 | Shikalbaha | 34 | 11:00
45 | Coxsbazar | 132 | 20:00 | 111 | Maniknagar | 77 | 13:00 | 177 | Shitalakhya | 72.5 | 13:00
46 | Cumilla(N) | 117 | 21:00 | 112 | Matarbari | 52 | 22:00 | 178 | Sholosohor | 48 | 19:00
47 | Cumilla(S) | 156 | 16:00 | 113 | Matuail | 76 | 00:00 | 179 | Shomvuganj | 50 | 19:00
48 | Daganbhuiyan | 38 | 19:00 | 114 | Metrorail_Motijheel | 26 | 21:00 | 180 | Shyampur | 170 | 00:00
49 | Daudkandi | 135 | 06:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 128 | 12:00
50 | DhakaUniversity | 96 | 13:00 | 116 | Millgate | 106 | 12:00 | 182 | Sirajganj | 118 | 21:00
51 | Dhamrai | 100 | 05:00 | 117 | Mirpur | 149 | 12:00 | 183 | Sitakunda | 33 | 21:00
52 | Dhanmondi | 114 | 13:00 | 118 | Mirsorai | 49 | 09:00 | 184 | Sonargaon | 151 | 06:00
53 | Dohazari | 102 | 22:00 | 119 | Mirzapur | 42 | 21:00 | 185 | Sreemongol | 79 | 05:00
54 | Faridpur | 167 | 00:00 | 120 | Mithapukur | 72 | 23:00 | 186 | Sreepur | 107 | 19:00
55 | Fatullah | 111 | 12:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 45.5 | 22:00
56 | Fenchuganj | 39 | 23:00 | 122 | Mogbazar | 40.6 | 13:00 | 188 | Sunamganj | 41 | 04:00
57 | Feni | 96 | 21:00 | 123 | Mongla | 47 | 09:00 | 189 | Sylhet | 121 | 18:30
58 | GPH | 1 | 00:00 | 124 | Motijheel | 46 | 12:00 | 190 | Sylhet_(South) | 67 | 05:00
59 | Ghatail | 93 | 22:00 | 125 | Muktagacha | 41 | 12:00 | 191 | TK | 23 | 21:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 106 | 23:00 | 192 | Tangail | 186 | 21:00
61 | Ghorashal-230 | 93 | 05:00 | 127 | Muradnagar | 47 | 22:00 | 193 | Taraganj | 32 | 08:00
62 | Goalpara | 33 | 00:00 | 128 | Mymensingh | 159 | 00:00 | 194 | Tasnim | 41 | 08:00
63 | Gollamari | 102 | 13:00 | 129 | Nabinagar | 104 | 18:30 | 195 | Thakurgaon | 115 | 19:30
64 | Gopalganj | 103 | 22:00 | 130 | Naogaon | 131 | 22:00 | 196 | Tongi | 152 | 00:00
65 | Gulshan | 112 | 12:00 | 131 | Narail | 58 | 22:00 | 197 | Ullahpara | 34 | 01:00
66 | Halishahar | 116 | 11:00 | 132 | Narinda | 78 | 13:00 | 198 | Ullon | 56 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 30-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14435.51 | 2465 |  | 17011.44
1:00 | 13906.1 | 2334 |  | 16345.1
2:00 | 13740.79 | 2191 |  | 16030.39
3:00 | 13689.2 | 2115 |  | 15899.38
4:00 | 13623.02 | 2045 |  | 15760.05
5:00 | 13536.46 | 1170 |  | 14759.46
6:00 | 13147.93 | 413 |  | 13579.93
7:00 | 13282.86 | 467 |  | 13770.86
8:00 | 13362.91 | 444 |  | 13826.89
9:00 | 13080.48 | 576 |  | 13682.4
10:00 | 13425.6 | 990 |  | 14460.15
11:00 | 13473.16 | 1354 |  | 14888.09
12:00 | 13611.74 | 1949 |  | 15648.45
13:00 | 13738.11 | 1987 |  | 15814.11
14:00 | 13435.16 | 2002 |  | 15527.16
15:00 | 13481.23 | 2330 |  | 15916.23
16:00 | 13421.15 | 1829 |  | 15332.15
17:00 | 13403.34 | 1637 |  | 15114.34
18:00 | 13431.83 | 1232 |  | 14718.83
19:00 | 14788.97 | 1406 |  | 16258.24
19:30 | 14964.27 | 1643 |  | 16681.27
20:00 | 14940.79 | 1371 |  | 16373.79
21:00 | 15322.59 | 1479 |  | 16868.59
22:00 | 15207.1 | 1054 |  | 16308.1
23:00 | 14812.99 | 1484 |  | 16363.99
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 30-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 144 | 48 | 404 | 200 | 1762 | 666 | Ishurdi-Ghorashal Ckt-1 | Export | 3986109.09
1:00 | 136 | 45 | 400 | 162 | 1774 | 628
2:00 | 128 | 40 | 378 | 162 | 1740 | 616 |  | Import | 0
3:00 | 132 | 42 | 388 | 162 | 1736 | 604
4:00 | 134 | 46 | 398 | 172 | 1788 | 590 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 141 | 49 | 420 | 188 | 1750 | 612
6:00 | 142 | 45 | 444 | 204 | 1836 | 598 |  | Import | 0
7:00 | 132 | 40 | 382 | 146 | 1758 | 586
8:00 | 149 | 46 | 450 | 172 | 1876 | 626 | Sirajganj-Sreepur Ckt-1 | Export | 2933000
9:00 | 179 | 69 | 520 | 186 | 1712 | 636
10:00 | 202 | 76 | 580 | 204 | 1844 | 692 |  | Import | 0
11:00 | 198 | 75 | 556 | 218 | 1822 | 806
12:00 | 184 | 69 | 540 | 220 | 1772 | 830 | Sirajganj-Sreepur Ckt-2 | Export | 2943000
13:00 | 198 | 78 | 540 | 240 | 1772 | 810
14:00 | 192 | 79 | 550 | 250 | 1730 | 806 |  | Import | 0
15:00 | 194 | 77 | 530 | 216 | 1816 | 808
16:00 | 194 | 76 | 550 | 246 | 1804 | 816 | Gopalganj-Aminbazar Ckt-1 | Export | 20780000
17:00 | 199 | 77 | 590 | 244 | 1786 | 824
18:00 | 178 | 65 | 530 | 210 | 1694 | 760 |  | Import | 0
18:30 | 184 | 68 | 550 | 234 | 1702 | 774
19:00 | 179 | 59 | 560 | 260 | 1648 | 702 | Gopalganj-Aminbazar Ckt-2 | Export | 20830000
19:30 | 180 | 65 | 520 | 214 | 1712 | 740
20:00 | 172 | 57 | 510 | 210 | 1656 | 706 |  | Import | 0
21:00 | 165 | 51 | 500 | 220 | 1618 | 700
22:00 | 157 | 43 | 500 | 210 | 1540 | 632 |  | Total Export | 51472109.09
23:00 | 172 | 51 | 530 | 224 | 1570 | 628 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 30-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7524.62 | 6910.89 | 14435.51 | DAILY GENERATION CURVE
00:30 | 7366.62 | 6804.185 | 14170.805
01:00 | 7208.62 | 6697.48 | 13906.1 | 30-07-2026
01:30 | 7122.62 | 6700.825 | 13823.445
02:00 | 7036.62 | 6704.17 | 13740.79
02:30 | 7004.62 | 6710.375 | 13714.995
03:00 | 6972.62 | 6716.58 | 13689.2
03:30 | 6948.62 | 6707.49 | 13656.11
04:00 | 6924.62 | 6698.4 | 13623.02
04:30 | 6906.12 | 6673.62 | 13579.74
05:00 | 6887.62 | 6648.84 | 13536.46
05:30 | 6719.36 | 6622.835 | 13342.195
06:00 | 6551.1 | 6596.83 | 13147.93
06:30 | 6611.305 | 6604.09 | 13215.395
07:00 | 6671.51 | 6611.35 | 13282.86
07:30 | 6663.53 | 6659.355 | 13322.885
08:00 | 6655.55 | 6707.36 | 13362.91
08:30 | 6725.875 | 6495.82 | 13221.695
09:00 | 6796.2 | 6284.28 | 13080.48
09:30 | 6967.09 | 6285.95 | 13253.04
10:00 | 7137.98 | 6287.62 | 13425.6
10:30 | 7161.265 | 6288.115 | 13449.38
11:00 | 7184.55 | 6288.61 | 13473.16
11:30 | 7237.285 | 6305.165 | 13542.45
12:00 | 7290.02 | 6321.72 | 13611.74
12:30 | 7292.875 | 6382.05 | 13674.925
13:00 | 7295.73 | 6442.38 | 13738.11
13:30 | 7258.945 | 6327.69 | 13586.635
14:00 | 7222.16 | 6213 | 13435.16
14:30 | 7226.13 | 6232.065 | 13458.195
15:00 | 7230.1 | 6251.13 | 13481.23
15:30 | 7188.18 | 6263.01 | 13451.19
16:00 | 7146.26 | 6274.89 | 13421.15
16:30 | 7150.66 | 6261.585 | 13412.245
17:00 | 7155.06 | 6248.28 | 13403.34
17:30 | 7161.455 | 6256.13 | 13417.585
18:00 | 7167.85 | 6263.98 | 13431.83
18:30 | 7518.735 | 6591.665 | 14110.4
19:00 | 7869.62 | 6919.35 | 14788.97
19:30 | 8004.12 | 6960.15 | 14964.27
20:00 | 7982.52 | 6958.27 | 14940.79
20:30 | 8098.75 | 7032.94 | 15131.69 |  | Executive Engineer
21:00 | 8214.98 | 7107.61 | 15322.59 |  | Network Operation Division
21:30 | 8228.98 | 7035.865 | 15264.845
22:00 | 8242.98 | 6964.12 | 15207.1
22:30 | 8051.8 | 6958.245 | 15010.045
23:00 | 7860.62 | 6952.37 | 14812.99

## En-Curve
QF-LDC-12
Date | 30-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2427 | 1306 | 898 | 38 | 150 | 1249.89 | 222 | 5662 | 0 | 629.42 | 1802.2 | 0 | 0 | 51 | 2465 | DAILY ENERGY CURVE
00:30 | 2431 | 1303 | 898 | 38 | 148 | 1247.185 | 220 | 5599.5 | 0 | 558.92 | 1679.2 | 0 | 0 | 48 | 2399.5 | 30-07-2026
01:00 | 2435 | 1300 | 898 | 38 | 146 | 1244.48 | 218 | 5537 | 0 | 488.42 | 1556.2 | 0 | 0 | 45 | 2334
01:30 | 2444 | 1304 | 898 | 38 | 140 | 1244.325 | 218 | 5544 | 0 | 459.92 | 1495.2 | 0 | 0 | 38 | 2262.5 | Energy Generated | 334.8669 |  | MKWHr
02:00 | 2453 | 1308 | 898 | 38 | 134 | 1244.17 | 218 | 5551 | 0 | 431.42 | 1434.2 | 0 | 0 | 31 | 2191 | Energy not Served | 36.324 |  | MKWHr
02:30 | 2451 | 1309 | 898 | 38 | 133.5 | 1246.375 | 216.5 | 5548.5 | 0 | 431.42 | 1414.2 | 0 | 0 | 28.5 | 2153 | Total Energy Requirement | 371.1909 |  | MKWHr
03:00 | 2449 | 1310 | 898 | 38 | 133 | 1248.58 | 215 | 5546 | 0 | 431.42 | 1394.2 | 0 | 0 | 26 | 2115
03:30 | 2455 | 1294 | 894 | 38 | 134.5 | 1239.49 | 215 | 5547 | 0 | 431.42 | 1383.7 | 0 | 0 | 24 | 2080
04:00 | 2461 | 1278 | 890 | 38 | 136 | 1230.4 | 215 | 5548 | 0 | 431.42 | 1373.2 | 0 | 0 | 22 | 2045
04:30 | 2462 | 1252 | 894 | 38 | 132 | 1240.62 | 215.5 | 5526 | 0 | 431.42 | 1364.2 | 0 | 0 | 24 | 1607.5
05:00 | 2463 | 1226 | 898 | 38 | 128 | 1250.84 | 216 | 5504 | 0 | 431.42 | 1355.2 | 0 | 0 | 26 | 1170
05:30 | 2430 | 1256 | 898 | 38 | 126 | 1250.715 | 218 | 5463.5 | 5.36 | 370.92 | 1258.2 | 0 | 0 | 27.5 | 791.5
06:00 | 2397 | 1286 | 898 | 38 | 124 | 1250.59 | 220 | 5423 | 10.72 | 310.42 | 1161.2 | 0 | 0 | 29 | 413
06:30 | 2423.5 | 1314.5 | 898 | 38 | 118 | 1250.42 | 220.5 | 5453.5 | 37.855 | 312.42 | 1123.7 | 0 | 0 | 25 | 440
07:00 | 2450 | 1343 | 898 | 38 | 112 | 1250.25 | 221 | 5484 | 64.99 | 314.42 | 1086.2 | 0 | 0 | 21 | 467
07:30 | 2438.5 | 1336 | 898 | 38 | 118 | 1252.655 | 221.5 | 5508.5 | 116.61 | 320.92 | 1055.7 | 0 | 0 | 18.5 | 455.5
08:00 | 2427 | 1329 | 898 | 38 | 124 | 1255.06 | 222 | 5533 | 168.23 | 327.42 | 1025.2 | 0 | 0 | 16 | 444
08:30 | 2437 | 1323.5 | 898 | 38 | 123 | 1247.955 | 222 | 5267 | 218.06 | 327.42 | 1099.76 | 0 | 0 | 20 | 510
09:00 | 2447 | 1318 | 898 | 38 | 122 | 1240.85 | 222 | 5001 | 267.89 | 327.42 | 1174.32 | 0 | 0 | 24 | 576
09:30 | 2432 | 1330.5 | 898 | 38 | 123 | 1245.605 | 222 | 4982.5 | 303.255 | 341.42 | 1308.26 | 0 | 0 | 28.5 | 783
10:00 | 2417 | 1343 | 898 | 38 | 124 | 1250.36 | 222 | 4964 | 338.62 | 355.42 | 1442.2 | 0 | 0 | 33 | 990
10:30 | 2416.5 | 1330 | 898 | 38 | 123 | 1247.17 | 222 | 4954.5 | 363.59 | 360.92 | 1452.7 | 0 | 0 | 43 | 1172
11:00 | 2416 | 1317 | 898 | 38 | 122 | 1243.98 | 222 | 4945 | 388.56 | 366.42 | 1463.2 | 0 | 0 | 53 | 1354
11:30 | 2417.5 | 1316 | 897 | 38 | 135 | 1258.505 | 222 | 4943.5 | 447.825 | 366.42 | 1444.7 | 0 | 0 | 56 | 1651.5
12:00 | 2419 | 1315 | 896 | 38 | 148 | 1273.03 | 222 | 4942 | 507.09 | 366.42 | 1426.2 | 0 | 0 | 59 | 1949
12:30 | 2436.5 | 1298 | 897.5 | 38 | 146 | 1293.805 | 221.5 | 4937 | 480.5 | 366.42 | 1509.2 | 0 | 0 | 50.5 | 1968
13:00 | 2454 | 1281 | 899 | 38 | 144 | 1314.58 | 221 | 4932 | 453.91 | 366.42 | 1592.2 | 0 | 0 | 42 | 1987
13:30 | 2433 | 1248 | 898 | 38 | 143 | 1307.32 | 219 | 4884 | 409.695 | 366.42 | 1606.7 | 0 | 0 | 33.5 | 1994.5
14:00 | 2412 | 1215 | 897 | 38 | 142 | 1300.06 | 217 | 4836 | 365.48 | 366.42 | 1621.2 | 0 | 0 | 25 | 2002
14:30 | 2400.5 | 1241.25 | 897.5 | 38 | 148 | 1308.985 | 217 | 4881.5 | 299.44 | 366.42 | 1626.6 | 0 | 0 | 33 | 2166
15:00 | 2389 | 1267.5 | 898 | 38 | 154 | 1317.91 | 217 | 4927 | 233.4 | 366.42 | 1632 | 0 | 0 | 41 | 2330
15:30 | 2366 | 1263.5 | 898 | 38 | 155 | 1308.38 | 217 | 4931 | 245.79 | 365.92 | 1627.6 | 0 | 0 | 35 | 2079.5
16:00 | 2343 | 1259.5 | 898 | 38 | 156 | 1298.85 | 217 | 4935 | 258.18 | 365.42 | 1623.2 | 0 | 0 | 29 | 1829
16:30 | 2335.5 | 1239.5 | 898 | 38 | 153 | 1327.935 | 217.5 | 4916.5 | 205.29 | 373.92 | 1678.6 | 0 | 0 | 28.5 | 1733
17:00 | 2328 | 1219.5 | 898 | 38 | 150 | 1357.02 | 218 | 4898 | 152.4 | 382.42 | 1734 | 0 | 0 | 28 | 1637
17:30 | 2327.5 | 1202 | 898.5 | 38 | 138 | 1354.785 | 218.5 | 4866 | 99.78 | 424.42 | 1824.6 | 0 | 0 | 25.5 | 1434.5
18:00 | 2327 | 1184.5 | 899 | 38 | 126 | 1352.55 | 219 | 4834 | 47.16 | 466.42 | 1915.2 | 0 | 0 | 23 | 1232
18:30 | 2356 | 1224.75 | 898.5 | 38 | 136 | 1414.45 | 219.5 | 5036 | 23.58 | 602.92 | 2019.2 | 122.5 | 0 | 19 | 1319
19:00 | 2385 | 1265 | 898 | 38 | 146 | 1476.35 | 220 | 5238 | 0 | 739.42 | 2123.2 | 245 | 0 | 15 | 1406
19:30 | 2412 | 1254 | 898 | 38 | 140 | 1479.15 | 220 | 5238 | 0 | 736.42 | 2217.7 | 321 | 0 | 10 | 1643
20:00 | 2387 | 1208.4 | 899 | 38 | 136 | 1482.27 | 222 | 5293 | 0 | 738.42 | 2226.7 | 300 | 0 | 10 | 1371
20:30 | 2396 | 1240.7 | 899 | 38 | 134 | 1478.94 | 222 | 5311 | 0 | 755.42 | 2304.13 | 340 | 0 | 12.5 | 1425
21:00 | 2405 | 1273 | 899 | 38 | 132 | 1475.61 | 222 | 5329 | 0 | 772.42 | 2381.56 | 380 | 0 | 15 | 1479
21:30 | 2422.5 | 1233 | 898 | 38 | 131 | 1481.365 | 222 | 5311.5 | 0 | 771.92 | 2416.06 | 325 | 0 | 14.5 | 1266.5
22:00 | 2440 | 1193 | 897 | 38 | 130 | 1487.12 | 222 | 5294 | 0 | 771.42 | 2450.56 | 270 | 0 | 14 | 1054
22:30 | 2447 | 1219.5 | 897.5 | 38 | 132 | 1488.245 | 222 | 5114.5 | 0 | 735.92 | 2432.38 | 270.5 | 0 | 12.5 | 1269
23:00 | 2454 | 1246 | 898 | 38 | 134 | 1489.37 | 222 | 4935 | 0 | 700.42 | 2414.2 | 271 | 0 | 11 | 1484
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 30-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 392 | 09:00 | 349 | 13:00 | Madunaghat | 395 | 04:00 | 388 | 21:00
Amtali | 408 | 06:00 | 404 | 12:00 | Meghnaghat | 373 | 06:00 | 350 | 16:00
Ashuganj | 383 | 05:00 | 371 | 12:00 | Mirsorai | N/A | N/A | N/A | N/A
Bhulta | 387 | 07:00 | 362 | 12:00 | Payra | 410 | 02:00 | 406 | 13:00
Bibiana | 375 | 07:00 | 365 | 16:00 | Rahanpur | 402 | 10:00 | 391 | 21:00
BIPTC | 399 | 04:00 | 391 | 12:00 | Rampal | 389 | 07:00 | 376 | 12:00
Bogura | 384 | 09:00 | 374 | 21:00
Gopalganj | 383 | 05:00 | 371 | 12:00
Kaliakoir | 357 | 07:00 | 342 | 11:00
Korerhat | 392 | 03:00 | 381 | 19:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 06:00 | 209 | 13:00 | Ishurdi | 234 | 10:00 | 223 | 21:00
AKSML | 261 | 00:00 | 227.5 | 21:00 | Jhenaidah | 227 | 10:00 | 214 | 19:00
Aminbazar | 225 | 07:00 | 211 | 12:00 | Kachua | 224 | 08:00 | 218 | 19:00
Ashuganj | 223 | 07:00 | 212 | 16:00 | Kaliakoir | 221 | 04:00 | 209 | 12:00
Ashuganj-400 | 223 | 07:00 | 212 | 16:00 | Keranigonj | 221 | 04:00 | 208 | 12:00
Baghabari | 231 | 06:00 | 223 | 19:00 | Khulna(S) | 222 | 05:00 | 215 | 12:00
Barapukuria | 225 | 18:00 | 218 | 12:00 | Korerhat | 223 | 01:00 | 218 | 19:00
Barapukuria-230 | 225 | 18:00 | 218 | 12:00 | Madunaghat | 237 | 02:00 | 232 | 21:00
Barishal | 223 | 10:00 | 218 | 19:00 | Madunaghat-400 | 238 | 04:00 | 233 | 21:00
Bheramara | 233 | 10:00 | 221 | 19:00 | Maniknagar | 220 | 04:00 | 205 | 12:00
Bhulta | 223 | 07:00 | 206 | 12:00 | Meghnaghat | 228 | 07:00 | 212 | 15:00
Bibiana | 217 | 03:00 | 211 | 16:00 | Meghnaghat-400 | 224 | 07:00 | 206 | 16:00
BIPTC | 236 | 10:00 | 222 | 19:00 | Mirsorai | 228 | 01:00 | 221 | 19:30
Bogura | 240 | 10:00 | 234 | 02:00 | Naogaon | 226 | 10:00 | 208 | 21:00
Bogura-400 | 239 | 09:00 | 235 | 07:00 | Purbasadipur | 223 | 18:30 | 203 | 10:00
Borhanuddin | 228 | 10:00 | 223 | 23:00 | Rajshahi | 234 | 10:00 | 221 | 21:00
BSRM | 224 | 01:00 | 218 | 19:30 | Rampal | 222 | 09:00 | 214 | 12:00
Charfasson | 227 | 17:00 | 225 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 222 | 01:00 | 217 | 21:00 | Rampura | 222 | 04:00 | 205 | 12:00
Cumilla(N) | 219 | 02:00 | 210 | 12:00 | Shikalbaha | 239 | 23:00 | 233 | 16:00
Faridpur | 218 | 06:00 | 205 | 16:00 | Shyampur | 221 | 04:00 | 208 | 12:00
Fenchuganj | 220 | 08:00 | 213 | 21:00 | Siddhirganj | 223 | 05:00 | 207 | 13:00
Feni | 222 | 04:00 | 215 | 13:00 | Sirajgonj | 235 | 09:00 | 230 | 19:00
Ghorashal | 220 | 00:00 | 210 | 12:00 | Sreepur | 219 | 07:00 | 212 | 12:00
Ghorashal-230 | 207 | 04:00 | 195 | 17:00 | Tongi | 210 | 04:00 | 195 | 11:00
Gopalganj | 218 | 05:00 | 212 | 12:00
GPH | 230 | 08:00 | 224 | 01:00
Haripur | 222 | 06:00 | 207 | 12:00
Hasnabad | 222 | 05:00 | 208 | 15:00
Hathazari | 234 | 05:00 | 229 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 04:00 | 126 | 11:00 | Madartek | 137 | 04:00 | 124 | 12:00
Agargaon | 132 | 06:00 | 121 | 13:00 | Madunaghat | 137 | 00:00 | 134 | 19:30
Agrabad | 136 | 00:00 | 132 | 11:00 | Magura | 138 | 10:00 | 126 | 19:00
AKS | 135 | 23:00 | 130 | 10:00 | Mahasthangarh | 136 | 10:00 | 130 | 01:00
Aminbazar | 128 | 23:00 | 118 | 16:00 | Maijdee | 125 | 04:00 | 121 | 21:00
Amnura | 135 | 10:00 | 128 | 06:00 | Manikganj | 125 | 00:00 | 121 | 21:00
Ashuganj | 127 | 07:00 | 120 | 19:00 | Maniknagar | 131 | 05:00 | 117 | 13:00
Ashuganj-230 | 129 | 07:00 | 125 | 13:00 | Matarbari | 132 | 09:00 | 119 | 22:00
Bagerhat | 125 | 10:00 | 118 | 19:00 | Matuail | 133 | 07:00 | 124 | 12:00
Bajitpur | 121 | 05:00 | 116 | 19:00 | Metrorail_Motijheel | 131 | 05:00 | 117 | 13:00
Bakerganj | 130 | 10:00 | 127 | 19:00 | Metrorail_Uttara | 129 | 03:00 | 116 | 13:00
Bakulia | 137 | 23:00 | 133 | 12:00 | Millgate | 130 | 03:00 | 117 | 13:00
Banani | 138 | 05:00 | 125 | 12:00 | Mirpur | 126 | 05:00 | 118 | 11:00
Bangabhaban | 131 | 06:00 | 117 | 12:00 | Mirzapur | 128 | 10:00 | 119 | 21:00
Barapukuria | 137 | 18:00 | 130 | 07:00 | Mithapukur | 133 | 17:00 | 126 | 07:00
Barguna | 130 | 14:00 | 8 | 01:00 | MI_Cement | 132 | 21:00 | 120 | 12:00
Barishal | 130 | 06:00 | 125 | 19:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal-230 | 129 | 04:00 | 125 | 19:00 | Mogbazar | 139 | 04:00 | 126 | 12:00
Baroaulia | 135 | 00:00 | 133 | 11:00 | Mongla | 125 | 10:00 | 118 | 19:00
Baroirhat | 131 | 05:00 | 126 | 12:00 | Motijheel | 131 | 06:00 | 117 | 12:00
Bashundhara | 138 | 04:00 | 118 | 15:00 | Muktagacha | 130 | 10:00 | 115 | 05:00
BashundharaCement | 133 | 07:00 | 123 | 16:00 | Munshiganj | 131 | 03:00 | 122 | 16:00
Beanibazar | 122 | 11:00 | 116 | 21:00 | Muradnagar | 127 | 08:00 | 119 | 21:00
Benapole | 136 | 09:00 | 120 | 07:00 | Mymensingh | 131 | 10:00 | 107 | 23:00
Bhaluka | 124 | 07:00 | 116 | 19:00 | Nabinagar | 125 | 06:00 | 116 | 18:30
Bhandaria | 126 | 01:00 | 120 | 19:00 | Naogaon | 136 | 10:00 | 125 | 21:00
Bhangura | 133 | 10:00 | 129 | 21:00 | Narail | 138 | 10:00 | 124 | 23:00
Bheramara | 137 | 10:00 | 130 | 19:00 | Narinda | 131 | 05:00 | 117 | 13:00
Bheramara(GK) | 138 | 10:00 | 130 | 19:00 | Narshingdi | 127 | 06:00 | 115 | 13:00
Bhulta | 128 | 06:00 | 120 | 11:00 | Natore | 135 | 10:00 | 128 | 21:00
Bhulta-400 | 129 | 04:00 | 119 | 12:00 | Nawabganj | 134 | 07:00 | 124 | 16:00
Bog-Sherpur | 136 | 10:00 | 131 | 07:00 | Netrakona | 120 | 07:00 | 104 | 06:00
Bogura | 139 | 10:00 | 134 | 00:00 | New | 129 | 01:00 | 119 | 12:00
Bogura-230 | 138 | 10:00 | 134 | 02:00 | Niamatpur | 133 | 10:00 | 127 | 21:00
Brahmanbaria | 123 | 04:00 | 118 | 13:00 | Noapara | 130 | 05:00 | 124 | 12:00
Cantonment | 131 | 03:00 | 121 | 12:00 | Pabna | 135 | 10:00 | 128 | 21:00
Chandina | 128 | 04:00 | 122 | 13:00 | Palashbari | 131 | 08:00 | 126 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandpur | 129 | 06:00 | 125 | 10:00 | Panchagarh | 139 | 01:00 | 126 | 12:00
Chandraghona | 137 | 00:00 | 135 | 11:00 | Patiya | 137 | 00:00 | 132 | 20:00
Chapai | 133 | 09:00 | 129 | 19:30 | Patnitala | 133 | 10:00 | 127 | 20:00
Charsaidpur | 133 | 07:00 | 123 | 16:00 | Patuakhali | 130 | 10:00 | 126 | 19:00
Chauddagram | 127 | 01:00 | 123 | 21:00 | Payra | 134 | 10:00 | 131 | 11:00
Chhatak | 166 | 13:00 | 115 | 19:00 | PHP | 130 | 04:00 | 126 | 13:00
Chowmuhani | 126 | 03:00 | 122 | 21:00 | Postogola | 132 | 06:00 | 121 | 12:00
Chuadanga | 136 | 10:00 | 124 | 21:00 | Pubail | 120 | 05:00 | 114 | 17:00
Coxsbazar | 132 | 19:00 | 122 | 20:00 | Purbachal | 138 | 04:00 | 125 | 12:00
Cumilla(N) | 128 | 02:00 | 122 | 21:00 | Purbasadipur | 135 | 18:00 | 128 | 12:00
Cumilla(S) | 130 | 03:00 | 122 | 15:00 | Rahanpur | 134 | 09:00 | 130 | 21:00
Daganbhuiyan | 128 | 04:00 | 125 | 12:00 | Rahanpur-400 | 135 | 10:00 | 130 | 21:00
Daudkandi | 126 | 05:00 | 119 | 20:00 | Rahim | 133 | 04:00 | 124 | 12:00
DhakaUniversity | 138 | 04:00 | 124 | 12:00 | Rajbari | 123 | 05:00 | 118 | 11:00
Dhamrai | 126 | 06:00 | 118 | 11:00 | Rajendrapur | 123 | 09:00 | 115 | 19:00
Dhanmondi | 139 | 07:00 | 125 | 12:00 | Rajshahi | 133 | 10:00 | 127 | 21:00
Dohazari | 138 | 08:00 | 129 | 19:30 | Rajshahi-230 | 134 | 10:00 | 127 | 21:00
Faridpur | 126 | 04:00 | 120 | 16:00 | Ramganj | 124 | 01:00 | 122 | 10:00
Fatullah | 131 | 04:00 | 121 | 12:00 | Rampur | 136 | 00:00 | 132 | 11:00
Fenchuganj | 128 | 02:00 | 125 | 21:00 | Rampura | 138 | 04:00 | 126 | 12:00
Feni | 129 | 00:00 | 125 | 22:00 | Rangamati | 136 | 00:00 | 133 | 21:00
Feni-230 | 129 | 01:00 | 125 | 19:00 | Rangpur | 131 | 17:00 | 122 | 07:00
Ghatail | 128 | 10:00 | 115 | 02:00 | Ruppur | 138 | 10:00 | 130 | 21:00
Ghorashal | 123 | 07:00 | 118 | 12:00 | Saidpur | 134 | 01:00 | 129 | 08:00
Goalpara | 134 | 10:00 | 127 | 19:00 | Santhia | 135 | 15:00 | 129 | 21:00
Gollamari | 132 | 05:00 | 127 | 19:00 | Satkhira | 129 | 06:00 | 122 | 19:00
Gopalganj | 127 | 06:00 | 123 | 12:00 | Satmasjid | 131 | 04:00 | 119 | 13:00
Gopalganj-400 | 129 | 05:00 | 125 | 12:00 | Savar | 125 | 22:00 | 116 | 16:00
Gulshan | 138 | 07:00 | 125 | 12:00 | SevenRings | 123 | 07:00 | 115 | 17:00
Halishahar | 137 | 04:00 | 133 | 11:00 | ShahCement | 133 | 07:00 | 123 | 16:00
Haripur | 133 | 03:00 | 124 | 12:00 | Shahjadpur | 136 | 03:00 | 133 | 18:30
HaripurSBU | 133 | 04:00 | 125 | 15:00 | Shahjibazar | 125 | 09:00 | 118 | 19:00
Hasnabad | 132 | 06:00 | 122 | 12:00 | Shahmirpur | 138 | 08:00 | 134 | 11:00
Hathazari | 137 | 05:00 | 133 | 19:00 | Shariatpur | 127 | 04:00 | 122 | 19:00
Hatirjheel | 138 | 04:00 | 125 | 12:00 | Sherpur | 126 | 10:00 | 109 | 01:00
Ishurdi | 138 | 10:00 | 131 | 21:00 | Shikalbaha | 127 | 00:00 | 122 | 11:00
Jaldhaka | 131 | 17:00 | 125 | 07:00 | Shikalbaha-230 | 140 | 23:00 | 135 | 11:00
Jamalpur | 128 | 10:00 | 113 | 03:00 | Shitalakhya | 131 | 05:00 | 120 | 12:00
Jashore | 137 | 09:00 | 122 | 19:00 | Sholosohor | 136 | 00:00 | 133 | 16:00
Jhenaidah | 139 | 08:00 | 122 | 21:00 | Shomvuganj | 120 | 07:00 | 108 | 19:00
Jhenaidah-230 | 139 | 10:00 | 130 | 21:00 | Shyampur | 132 | 07:00 | 122 | 12:00
Joydebpur | 118 | 03:00 | 111 | 17:00 | Shyampur-230 | 133 | 06:00 | 124 | 12:00
Joypurhat | 133 | 17:00 | 126 | 01:00 | Siddhirganj | 133 | 04:00 | 124 | 12:00
Juldah | 138 | 23:00 | 134 | 10:00 | Sirajganj | 132 | 04:00 | 127 | 21:00
Kabirpur | 131 | 03:00 | 113 | 12:00 | Sitakunda | 136 | 23:00 | 132 | 20:00
Kachua | 128 | 08:00 | 124 | 19:00 | Sonargaon | 128 | 05:00 | 122 | 11:00
Kaliakoir | 131 | 07:00 | 122 | 18:30 | Sreemongol | 124 | 02:00 | 119 | 19:00
Kaliganj | 138 | 07:00 | 128 | 19:00 | Sreepur | 127 | 07:00 | 120 | 19:00
Kallyanpur | 126 | 05:00 | 117 | 16:00 | Srinagar | 134 | 04:00 | 125 | 12:00
Kalurghat | 137 | 00:00 | 135 | 11:00 | SSM | 140 | 17:00 | 138 | 00:00
Kamrangirchar | 134 | 05:00 | 116 | 11:00 | Sunamganj | 166 | 02:00 | 113 | 21:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 123 | 01:00 | 120 | 20:00
Kasba | 126 | 04:00 | 118 | 21:00 | Sylhet_(South) | 123 | 01:00 | 120 | 21:00
Kazla | 130 | 06:00 | 117 | 13:00 | Tangail | 126 | 10:00 | 115 | 22:00
Keranigonj | 134 | 04:00 | 125 | 13:00 | Taraganj | 133 | 08:00 | 125 | 11:00
Khagrachori | 135 | 01:00 | 132 | 19:30 | Tasnim | 129 | 01:00 | 122 | 17:00
Khulna | 132 | 04:00 | 127 | 12:00 | Thakurgaon | 138 | 01:00 | 127 | 12:00
Khulna(S) | 133 | 05:00 | 128 | 12:00 | TK | 136 | 01:00 | 133 | 14:00
Khulshi | 135 | 04:00 | 131 | 10:00 | Tongi | 130 | 04:00 | 122 | 11:00
Kishoreganj | 123 | 07:00 | 112 | 19:00 | Ullahpara | 133 | 10:00 | 128 | 21:00
Kodda | 128 | 00:00 | 115 | 00:00 | Ullon | 138 | 07:00 | 125 | 12:00
Korerhat | 132 | 03:00 | 128 | 19:30 | Uttara | 130 | 06:00 | 116 | 16:00
KSRM | 138 | 23:00 | 133 | 15:00 | UttaraNew | 129 | 03:00 | 116 | 13:00
Kulaura | 127 | 00:00 | 124 | 22:00 | Zigatola | 135 | 06:00 | 124 | 13:00
Kurigram | 129 | 10:00 | 122 | 08:00
Kushtia | 133 | 10:00 | 124 | 21:00
Laksam | 126 | 00:00 | 26 | 05:00
Lakshmipur | 124 | 04:00 | 121 | 13:00
Lalbag | 132 | 07:00 | 125 | 12:00
Lalmonirhat | 130 | 10:00 | 125 | 00:00
Madanganj | 133 | 07:00 | 123 | 16:00
Madaripur | 129 | 07:00 | 125 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 30-07-2026 | [28 empty] | Date: | 30-07-2026 | [28 empty] | Date: | 30-07-2026 | [28 empty] | Date: | 30-07-2026 | [28 empty] | Date: | 30-07-2026 | [18 empty] | Date: | 30-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [18 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 35 | 107 | 142 | 81 | 15 | 35 | 17 | 0 | 0 | 144 | 300 | 0 | 0 | 275 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 100 | 16 | 87 | 0 | 51 | 51 | 61 | 17 | 25 | 25 | 0 | 222 | 110 | 8 | 1145 | 163 | 0 | 50 | 0 | 102 | 201 | 0 | 0 | 0 | 1000 | 0 | 150 | 0 | 0 | 300 | 0 | 51 | 0 | 213 | 20 | 34 | 86 | 40 | 5 | 19 | 105 | 150 | 52.2 | 0 | 39 | 310 | 0 | 312 | 40 | 0 | 152 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 35 | 48 | 0 | 48 | 0 | 0 | 0 | 15 | 7524.62 | 898 | 0 | 0 | 27 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1249.89 | 0 | 40 | 0 | 50 | 50 | 0 | 100 | 26 | 8 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 244 | 0 | 0 | 190 | 0 | 110 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1050 | 890 | 17 | 6910.89 | 14435.51 | 102.45
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 20 | 73 | 128 | 48 | 15 | 35 | 0 | 0 | 0 | 146 | 295 | 0 | 0 | 280 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 99 | 16 | 65 | 0 | 45 | 51 | 61 | 0 | 25 | 25 | 0 | 218 | 105 | 5 | 1145 | 155 | 0 | 50 | 0 | 100 | 201 | 0 | 0 | 0 | 900 | 0 | 150 | 0 | 0 | 300 | 0 | 51 | 0 | 212 | 20 | 34 | 87 | 17 | 0 | 19 | 103 | 146 | 52.2 | 0 | 39 | 315 | 0 | 312 | 40 | 0 | 147 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 35 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 7208.62 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1244.48 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 26 | 8 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 190 | 0 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1050 | 865 | 17 | 6697.48 | 13906.1 | 102.44
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 35 | 128 | 48 | 15 | 35 | 0 | 0 | 0 | 144 | 300 | 0 | 0 | 288 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 96 | 16 | 52 | 0 | 31 | 0 | 61 | 0 | 25 | 25 | 0 | 218 | 101 | 8 | 1145 | 125 | 0 | 50 | 0 | 101 | 201 | 0 | 0 | 0 | 909 | 0 | 150 | 0 | 0 | 300 | 0 | 51 | 0 | 214 | 20 | 0 | 86 | 17 | 0 | 19 | 105 | 134 | 52.2 | 0 | 39 | 315 | 0 | 312 | 40 | 0 | 149 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 35 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7036.62 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1244.17 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 0 | 190 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1050 | 870 | 17 | 6704.17 | 13740.79 | 102.43
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 35 | 128 | 48 | 15 | 0 | 0 | 0 | 0 | 140 | 300 | 0 | 0 | 277 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 99 | 16 | 50 | 0 | 26 | 0 | 61 | 0 | 25 | 25 | 0 | 215 | 101 | 19 | 1145 | 123 | 0 | 50 | 0 | 98 | 201 | 0 | 0 | 0 | 904 | 0 | 150 | 0 | 0 | 300 | 0 | 51 | 0 | 214 | 20 | 0 | 86 | 17 | 0 | 19 | 103 | 133 | 52.2 | 0 | 39 | 310 | 0 | 312 | 40 | 0 | 149 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 35 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6972.62 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1248.58 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 263 | 0 | 0 | 190 | 0 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1050 | 870 | 17 | 6716.58 | 13689.2 | 102.42
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 35 | 128 | 48 | 15 | 0 | 0 | 0 | 0 | 138 | 285 | 0 | 0 | 280 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 92 | 16 | 50 | 0 | 22 | 0 | 61 | 0 | 25 | 25 | 0 | 215 | 105 | 33 | 1145 | 112 | 0 | 50 | 0 | 95 | 201 | 0 | 0 | 0 | 906 | 0 | 150 | 0 | 0 | 300 | 0 | 51 | 0 | 214 | 20 | 0 | 86 | 17 | 0 | 19 | 100 | 136 | 52.2 | 0 | 39 | 300 | 0 | 312 | 40 | 0 | 130 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 35 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6924.62 | 890 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1230.4 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 190 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1050 | 870 | 17 | 6698.4 | 13623.02 | 102.41
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 35 | 128 | 48 | 15 | 0 | 0 | 0 | 0 | 134 | 280 | 0 | 0 | 267 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 87 | 16 | 50 | 0 | 26 | 0 | 61 | 0 | 25 | 25 | 0 | 216 | 107 | 36 | 1145 | 101 | 0 | 50 | 0 | 92 | 200 | 0 | 0 | 0 | 904 | 0 | 150 | 0 | 0 | 300 | 0 | 51 | 0 | 215 | 30 | 0 | 86 | 18 | 0 | 19 | 98 | 128 | 52.2 | 0 | 39 | 300 | 0 | 313 | 40 | 0 | 124 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 35 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6887.62 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 1250.84 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 190 | 0 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 265 | 120 | 180 | 0 | 1050 | 870 | 17 | 6648.84 | 13536.46 | 102.4
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 17 | 35 | 128 | 48 | 15 | 0 | 0 | 0 | 0 | 149 | 275 | 0 | 0 | 316 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 47 | 16 | 50 | 0 | 29 | 0 | 0 | 0 | 25 | 25 | 0 | 220 | 102 | 38 | 1050 | 70 | 0 | 50 | 0 | 93 | 201 | 0 | 0 | 0 | 905 | 1 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 213 | 30 | 0 | 86 | 16 | 0 | 19 | 17 | 124 | 52.2 | 1 | 39 | 305 | 0 | 313 | 40 | 0 | 127 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 0 | 49 | 0.84 | 48 | 0 | 0.1 | 1.54 | 11 | 6551.1 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0.86 | 1080 | 0 | 0 | 0 | 1250.59 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 0.07 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 190 | 0 | 115 | 1 | 34 | 0 | 0 | 0 | 0.3 | 4 | 0.01 | 16 | 281 | 100 | 220 | 0 | 1047 | 870 | 17 | 6596.83 | 13147.93 | 102.39
07:00 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 17 | 35 | 128 | 48 | 15 | 0 | 0 | 0 | 0 | 143 | 325 | 0 | 0 | 294 | 0 | 0 | 1 | 143.42 | 11 | 21 | 0 | 0 | 48 | 16 | 50 | 0 | 21 | 0 | 0 | 0 | 25 | 25 | 0 | 221 | 106 | 39 | 1145 | 70 | 0 | 50 | 0 | 90 | 201 | 0 | 0 | 0 | 905 | 1 | 150 | 0 | 0 | 320 | 0 | 51 | 0 | 216 | 30 | 0 | 86 | 16 | 0 | 19 | 17 | 112 | 52.2 | 8 | 39 | 315 | 0 | 313 | 40 | 0 | 146 | 1 | 0 | 0 | 53 | 0 | 0 | 0 | 100 | 0 | 49 | 2.5 | 48 | 0 | 0.2 | 5.19 | 3 | 6671.51 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 11 | 1080 | 0 | 0 | 0 | 1250.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 3.45 | 7 | 0 | 0 | 3.03 | 156 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0.28 | 190 | 0 | 115 | 3 | 0 | 0 | 0 | 0 | 0.3 | 18 | 0.04 | 16 | 273 | 120 | 220 | 0 | 1021 | 870 | 17 | 6611.35 | 13282.86 | 102.38
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 17 | 35 | 128 | 48 | 15 | 0 | 0 | 0 | 0 | 149 | 325 | 0 | 0 | 320 | 0 | 0 | 3 | 143.42 | 11 | 21 | 0 | 0 | 47 | 16 | 50 | 0 | 16 | 0 | 0 | 0 | 25 | 25 | 1.42 | 222 | 107 | 16 | 1145 | 34 | 0 | 50 | 0 | 51 | 201 | 0 | 0 | 0 | 905 | 3 | 150 | 0 | 0 | 320 | 0 | 51 | 0 | 216 | 30 | 0 | 86 | 17 | 0 | 19 | 17 | 124 | 52.2 | 44 | 39 | 310 | 0 | 313 | 40 | 0 | 146 | 1 | 8 | 0 | 53 | 0 | 0 | 0 | 100 | 0 | 49 | 4.15 | 48 | 0 | 0.9 | 9.46 | 16 | 6655.55 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 1080 | 0 | 0 | 0 | 1255.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 7.84 | 18 | 0 | 0 | 7.68 | 156 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0.78 | 190 | 0 | 115 | 6 | 0 | 0 | 0 | 0 | 1.9 | 45 | 0.1 | 16 | 283 | 120 | 220 | 0 | 1050 | 880 | 17 | 6707.36 | 13362.91 | 102.37
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 17 | 35 | 128 | 48 | 15 | 0 | 17 | 0 | 0 | 140 | 325 | 0 | 0 | 320 | 0 | 0 | 4 | 143.42 | 9 | 21 | 0 | 0 | 75 | 16 | 50 | 0 | 24 | 0 | 0 | 0.12 | 25 | 25 | 2.83 | 222 | 106 | 2 | 1145 | 33 | 0 | 50 | 0 | 80 | 202 | 0 | 0 | 0 | 903 | 7 | 150 | 0 | 0 | 353 | 0 | 51 | 0 | 216 | 30 | 0 | 86 | 20 | 0 | 19 | 97 | 122 | 52.2 | 3 | 39 | 315 | 0 | 313 | 41 | 0 | 147 | 2 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 0 | 49 | 7.62 | 48 | 0 | 0.8 | 9.21 | 15 | 6796.2 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34 | 555 | 0 | 0 | 0 | 1240.85 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 8.71 | 31 | 0 | 0 | 16.67 | 156 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 1.58 | 191 | 0 | 115 | 13 | 0 | 0 | 0 | 0 | 3.4 | 123 | 0.07 | 16 | 277 | 120 | 220 | 0 | 1050 | 880 | 17 | 6284.28 | 13080.48 | 102.36
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 24 | 35 | 128 | 81 | 15 | 17 | 17 | 0 | 0 | 145 | 335 | 0 | 0 | 310 | 0 | 0 | 11 | 143.42 | 9 | 21 | 0 | 0 | 102 | 16 | 50 | 0 | 33 | 0 | 12 | 17 | 25 | 25 | 3.64 | 222 | 104 | 0 | 1145 | 33 | 0 | 50 | 0 | 90 | 199 | 0 | 0 | 0 | 906 | 0 | 150 | 0 | 0 | 354 | 0 | 51 | 0 | 212 | 30 | 0 | 86 | 16 | 0 | 19 | 108 | 124 | 52.2 | 37 | 39 | 325 | 0 | 313 | 40 | 0 | 149 | 10 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 14 | 58 | 15.53 | 113 | 0 | 1.9 | 39.29 | 24 | 7137.98 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 38 | 555 | 0 | 0 | 0 | 1250.36 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 14.53 | 43 | 0 | 0 | 34.31 | 156 | 0 | 0 | 0 | 0 | 0 | 266 | 0 | 4.26 | 190 | 0 | 115 | 10 | 0 | 0 | 0 | 0 | 3.1 | 73 | 0.06 | 16 | 249 | 120 | 220 | 0 | 1039 | 880 | 17 | 6287.62 | 13425.6 | 102.35
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 17 | 35 | 50 | 128 | 81 | 15 | 17 | 17 | 0 | 0 | 148 | 325 | 0 | 0 | 315 | 0 | 0 | 11 | 143.42 | 9 | 21 | 0 | 0 | 97 | 16 | 50 | 0 | 53 | 0 | 23 | 17 | 25 | 25 | 3.74 | 222 | 103 | 0 | 1145 | 35 | 0 | 45 | 0 | 92 | 200 | 0 | 0 | 0 | 906 | 15 | 150 | 0 | 0 | 352 | 0 | 51 | 0 | 213 | 30 | 0 | 85 | 17 | 0 | 19 | 105 | 122 | 52.2 | 32 | 39 | 315 | 0 | 313 | 42 | 0 | 140 | 5 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 58 | 21.78 | 114 | 0 | 2.6 | 26.81 | 24 | 7184.55 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36 | 555 | 0 | 0 | 0 | 1243.98 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 46.5 | 61 | 0 | 0 | 44.72 | 156 | 0 | 0 | 0 | 0 | 0 | 259 | 0 | 3.48 | 190 | 0 | 98 | 9 | 0 | 0 | 0 | 0 | 2.9 | 67 | 0.03 | 16 | 219 | 120 | 220 | 0 | 1050 | 880 | 17 | 6288.61 | 13473.16 | 102.34
12:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 17 | 35 | 52 | 128 | 81 | 15 | 35 | 35 | 0 | 0 | 141 | 325 | 0 | 0 | 305 | 0 | 0 | 24 | 143.42 | 9 | 21 | 0 | 0 | 100 | 16 | 50 | 0 | 59 | 0 | 23 | 17 | 25 | 25 | 2.97 | 222 | 105 | 0 | 1145 | 35 | 0 | 38 | 0 | 89 | 202 | 0 | 0 | 0 | 900 | 10 | 150 | 0 | 0 | 352 | 0 | 51 | 0 | 213 | 30 | 3 | 85 | 16 | 0 | 19 | 106 | 148 | 52.2 | 51 | 39 | 320 | 0 | 313 | 42 | 0 | 140 | 7 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 58 | 22.11 | 115 | 0 | 0.7 | 32.62 | 24 | 7290.02 | 896 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 37 | 555 | 0 | 0 | 0 | 1273.03 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 48.48 | 5 | 0 | 0 | 28.6 | 156 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 3.83 | 190 | 0 | 24 | 22 | 0 | 0 | 0 | 0 | 7.7 | 204 | 0.08 | 16 | 232 | 120 | 220 | 0 | 1040 | 880 | 17 | 6321.72 | 13611.74 | 102.33
13:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 17 | 35 | 52 | 128 | 81 | 15 | 35 | 35 | 0 | 0 | 140 | 300 | 0 | 17 | 296 | 0 | 0 | 11 | 143.42 | 9 | 21 | 0 | 0 | 97 | 16 | 50 | 0 | 42 | 0 | 23 | 17 | 25 | 25 | 2.21 | 221 | 93 | 0 | 1145 | 33 | 0 | 46 | 8 | 91 | 203 | 0 | 0 | 0 | 900 | 19 | 150 | 0 | 0 | 355 | 0 | 51 | 0 | 216 | 30 | 33 | 85 | 17 | 0 | 19 | 104 | 144 | 52.2 | 56 | 39 | 315 | 0 | 313 | 42 | 0 | 137 | 5 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 19 | 57 | 11.98 | 116 | 0 | 1.7 | 30.22 | 15 | 7295.73 | 899 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 46 | 555 | 0 | 0 | 0 | 1314.58 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 8 | 31.73 | 22 | 0 | 0 | 37.91 | 155 | 0 | 0 | 0 | 0 | 0 | 251 | 0 | 3.54 | 190 | 0 | 100 | 3 | 0 | 0 | 0 | 0 | 5.5 | 167 | 0.12 | 16 | 232 | 120 | 220 | 0 | 1030 | 880 | 17 | 6442.38 | 13738.11 | 102.32
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 0 | 35 | 52 | 128 | 81 | 15 | 55 | 35 | 0 | 0 | 139 | 280 | 0 | 35 | 285 | 0 | 0 | 6 | 143.42 | 9 | 21 | 0 | 0 | 92 | 16 | 49 | 0 | 25 | 0 | 23 | 17 | 25 | 25 | 1.86 | 217 | 102 | 0 | 1150 | 35 | 0 | 49 | 8 | 96 | 202 | 0 | 0 | 0 | 900 | 17 | 150 | 0 | 0 | 354 | 0 | 51 | 0 | 214 | 30 | 35 | 85 | 16 | 0 | 19 | 101 | 142 | 52.2 | 15 | 39 | 310 | 0 | 313 | 42 | 0 | 137 | 5 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 23 | 59 | 19.25 | 115 | 0 | 1 | 40.43 | 12 | 7222.16 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 540 | 0 | 0 | 0 | 1300.06 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 8 | 24.29 | 66 | 0 | 0 | 49.34 | 154 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 4.12 | 190 | 0 | 95 | 7 | 0 | 0 | 0 | 0 | 0.1 | 32 | 0.09 | 16 | 233 | 120 | 180 | 0 | 943 | 880 | 17 | 6213 | 13435.16 | 102.31
15:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 35 | 60 | 128 | 81 | 15 | 55 | 35 | 0 | 0 | 137 | 285 | 0 | 35 | 284 | 0 | 0 | 6 | 143.42 | 8.5 | 14 | 0 | 0 | 97 | 16 | 50 | 0 | 41 | 0 | 23 | 17 | 25 | 25 | 1.02 | 217 | 108 | 0 | 1150 | 33 | 0 | 50 | 8 | 97 | 203 | 0 | 0 | 0 | 900 | 8 | 150 | 0 | 0 | 340 | 0 | 51 | 0 | 193 | 32 | 33 | 85 | 17 | 0 | 19 | 106 | 154 | 43 | 10 | 39 | 315 | 0 | 313 | 40 | 0 | 149 | 4 | 16 | 0 | 53 | 0 | 0 | 0 | 100 | 19 | 58 | 19.74 | 116 | 0 | 1.3 | 30.12 | 12 | 7230.1 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 551 | 0 | 0 | 0 | 1317.91 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 8 | 18.89 | 51 | 0 | 0 | 24.41 | 151 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 2.35 | 190 | 0 | 95 | 7 | 0 | 0 | 0 | 0 | 1.4 | 22 | 0.17 | 16 | 233 | 120 | 220 | 0 | 1026 | 877 | 17 | 6251.13 | 13481.23 | 102.31
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 35 | 71 | 128 | 81 | 15 | 35 | 35 | 0 | 0 | 136 | 275 | 0 | 35 | 281 | 0 | 0 | 7 | 143.42 | 8.5 | 21 | 0 | 0 | 91 | 16 | 50 | 0 | 29 | 0 | 22 | 17 | 25 | 25 | 1.02 | 217 | 106 | 0 | 1150 | 35 | 0 | 50 | 8 | 91 | 203 | 0 | 0 | 0 | 900 | 5 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 192 | 40 | 34 | 85 | 16 | 0 | 19 | 100 | 156 | 52.2 | 23 | 39 | 305 | 0 | 313 | 40 | 0 | 154 | 4 | 17 | 0 | 53 | 0 | 0 | 0 | 100 | 17 | 58 | 8.1 | 115 | 0 | 0.3 | 26.72 | 15 | 7146.26 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 554 | 0 | 0 | 0 | 1298.85 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 8 | 15.68 | 38 | 0 | 0 | 17.68 | 150 | 0 | 0 | 0 | 0 | 0 | 237 | 0 | 1.57 | 190 | 0 | 104 | 14 | 0 | 0 | 0 | 0 | 2 | 74 | 0.11 | 16 | 235 | 120 | 220 | 0 | 1016 | 890 | 17 | 6274.89 | 13421.15 | 102.3
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 35 | 71 | 143 | 81 | 15 | 35 | 60 | 0 | 0 | 144 | 280 | 0 | 35 | 285 | 0 | 0 | 4 | 143.42 | 8.5 | 21 | 0 | 0 | 92 | 16 | 57 | 0 | 28 | 0 | 24 | 17 | 25 | 25 | 0.69 | 218 | 105 | 0 | 1150 | 33 | 0 | 50 | 8 | 91 | 204 | 0 | 0 | 0 | 902 | 2 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 197 | 40 | 34 | 85 | 17 | 3 | 14 | 102 | 150 | 43 | 7 | 39 | 310 | 0 | 313 | 41 | 0 | 141 | 2 | 17 | 0 | 53 | 0 | 0 | 0 | 100 | 19 | 58 | 2.9 | 115 | 0 | 0.3 | 10.25 | 24 | 7155.06 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 552 | 0 | 0 | 0 | 1357.02 | 0 | 0 | 0 | 50 | 55 | 0 | 0 | 0 | 8 | 15.9 | 23 | 0 | 0 | 14.18 | 150 | 0 | 0 | 0 | 0 | 0 | 238 | 0 | 1.18 | 190 | 0 | 112 | 3 | 60 | 0 | 0 | 0 | 0.9 | 51 | 0.1 | 16 | 236 | 100 | 180 | 0 | 991 | 877 | 17 | 6248.28 | 13403.34 | 102.29
18:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 17 | 35 | 70 | 144 | 80 | 15 | 35 | 108 | 0 | 0 | 146 | 275 | 0 | 35 | 288 | 0 | 0 | 1 | 143.42 | 10.5 | 21 | 0 | 0 | 94 | 16 | 64 | 0 | 23 | 0 | 58 | 17 | 25 | 25 | 0.15 | 219 | 106 | 0 | 1050 | 35 | 0 | 50 | 8 | 99 | 204 | 0 | 0 | 0 | 915 | 1 | 150 | 0 | 0 | 280 | 0 | 20 | 0 | 197 | 40 | 34 | 85 | 16 | 34 | 19 | 101 | 126 | 52.2 | 3 | 39 | 310 | 0 | 313 | 41 | 0 | 133 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 100 | 27 | 58 | 1.8 | 116 | 0 | 0.2 | 3.58 | 22 | 7167.85 | 899 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 5 | 551 | 0 | 0 | 0 | 1352.55 | 0 | 0 | 0 | 50 | 90 | 0 | 0 | 0 | 8 | 0.37 | 4 | 0 | 0 | 3.79 | 150 | 0 | 0 | 0 | 0 | 0 | 236 | 0 | 0.34 | 190 | 0 | 115 | 2 | 75 | 0 | 0 | 0 | 0.9 | 20 | 0.03 | 16 | 235 | 100 | 180 | 0 | 1015 | 878 | 17 | 6263.98 | 13431.83 | 102.29
19:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 54 | 35 | 84 | 144 | 81 | 15 | 55 | 108 | 0 | 0 | 141 | 285 | 0 | 35 | 290 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 107 | 16 | 78 | 0 | 15 | 50 | 64 | 35 | 25 | 25 | 0 | 220 | 110 | 0 | 1150 | 33 | 0 | 46 | 12 | 105 | 204 | 0 | 0 | 0 | 1135 | 0 | 150 | 0 | 0 | 280 | 0 | 37 | 0 | 200 | 40 | 42 | 85 | 17 | 42 | 19 | 114 | 146 | 52.2 | 0 | 39 | 315 | 0 | 301 | 42 | 0 | 146 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 29 | 58 | 0 | 134 | 0 | 0 | 0 | 23 | 7869.62 | 898 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 175 | 0 | 32 | 0 | 550 | 0 | 0 | 0 | 1476.35 | 0 | 0 | 0 | 50 | 113 | 0 | 100 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 238 | 0 | 0 | 190 | 0 | 115 | 0 | 84 | 0 | 70 | 0 | 0 | 0 | 0 | 16 | 235 | 120 | 220 | 0 | 1099 | 879 | 17 | 6919.35 | 14788.97 | 102.28
19:30 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 54 | 35 | 87 | 144 | 81 | 15 | 55 | 108 | 0 | 0 | 139 | 271 | 0 | 35 | 284 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 107 | 16 | 79 | 0 | 10 | 50 | 64 | 35 | 25 | 25 | 0 | 220 | 110 | 5 | 1150 | 33 | 0 | 46 | 25.5 | 105 | 204 | 0 | 0 | 0 | 1170 | 0 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 190 | 40 | 89 | 85 | 17 | 42 | 19 | 114 | 140 | 52.2 | 0 | 39 | 300 | 0 | 314 | 42 | 0 | 137 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 101 | 29 | 68 | 0 | 152 | 0 | 0 | 0 | 24 | 8004.12 | 898 | 0 | 0 | 17 | 0 | 38 | 0 | 0 | 201 | 0 | 32 | 0 | 555 | 0 | 0 | 0 | 1479.15 | 0 | 0 | 0 | 50 | 113 | 0 | 100 | 26 | 8 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 237 | 0 | 0 | 190 | 0 | 115 | 0 | 85 | 0 | 120 | 0 | 0 | 0 | 0 | 16 | 234 | 120 | 220 | 0 | 1061 | 878 | 17 | 6960.15 | 14964.27 | 102.28
20:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 54 | 35 | 86 | 144 | 81 | 15 | 55 | 108 | 0 | 0 | 135 | 270 | 0 | 35 | 272 | 0 | 0 | 0 | 143.42 | 11.4 | 21 | 0 | 0 | 107 | 16 | 79 | 0 | 10 | 50 | 56 | 36 | 25 | 25 | 0 | 222 | 110 | 2 | 1150 | 35 | 0 | 50 | 25.5 | 105 | 204 | 0 | 0 | 0 | 1192 | 0 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 178 | 40 | 87 | 85 | 16 | 46 | 19 | 114 | 136 | 52.2 | 0 | 24 | 305 | 0 | 314 | 42 | 0 | 130 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 101 | 32 | 68 | 0 | 152 | 0 | 0 | 0 | 24 | 7982.52 | 899 | 0 | 0 | 17 | 0 | 38 | 0 | 0 | 180 | 0 | 32 | 0 | 555 | 0 | 0 | 0 | 1482.27 | 0 | 21 | 0 | 50 | 113 | 0 | 100 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 190 | 0 | 115 | 0 | 84 | 0 | 120 | 0 | 0 | 0 | 0 | 16 | 235 | 120 | 180 | 0 | 1094 | 877 | 17 | 6958.27 | 14940.79 | 102.28
21:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 54 | 35 | 106 | 144 | 81 | 15 | 55 | 162 | 0 | 0 | 140 | 280 | 0 | 55 | 282 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 108 | 16 | 79 | 0 | 15 | 50 | 56 | 54.36 | 25 | 25 | 0 | 222 | 110 | 5 | 1150 | 86 | 0 | 50 | 8 | 105 | 204 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 188 | 40 | 88 | 85 | 17 | 47 | 19 | 114 | 132 | 52.2 | 0 | 24 | 305 | 0 | 312 | 42 | 0 | 137 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 101 | 32 | 68 | 0 | 155 | 0 | 0 | 0 | 24 | 8214.98 | 899 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 240 | 0 | 32 | 0 | 547 | 0 | 0 | 0 | 1475.61 | 0 | 34 | 0 | 50 | 113 | 0 | 100 | 30 | 8 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 190 | 0 | 115 | 0 | 86 | 0 | 140 | 0 | 0 | 0 | 0 | 16 | 236 | 120 | 220 | 0 | 1100 | 882 | 17 | 7107.61 | 15322.59 | 102.26
22:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 54 | 35 | 106 | 144 | 81 | 15 | 55 | 162 | 0 | 0 | 137 | 275 | 0 | 55 | 288 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 108 | 16 | 85 | 0 | 14 | 50 | 58 | 54.36 | 25 | 25 | 0 | 222 | 110 | 4 | 1150 | 150 | 0 | 50 | 8 | 105 | 203 | 0 | 0 | 0 | 1190 | 0 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 216 | 40 | 88 | 85 | 16 | 46 | 19 | 114 | 130 | 52.2 | 0 | 24 | 300 | 0 | 312 | 42 | 0 | 125 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 34 | 68 | 0 | 155 | 0 | 0 | 0 | 24 | 8242.98 | 897 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 150 | 0 | 32 | 0 | 549 | 0 | 0 | 0 | 1487.12 | 0 | 40 | 0 | 50 | 113 | 0 | 100 | 27 | 8 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 190 | 0 | 115 | 0 | 85 | 0 | 120 | 0 | 0 | 0 | 0 | 16 | 235 | 120 | 180 | 0 | 1100 | 880 | 17 | 6964.12 | 15207.1 | 102.26
23:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 54 | 35 | 106 | 144 | 81 | 15 | 55 | 162 | 0 | 0 | 136 | 280 | 0 | 55 | 310 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 109 | 16 | 86 | 0 | 11 | 50 | 57 | 17 | 25 | 25 | 0 | 222 | 110 | 2 | 1055 | 162 | 0 | 50 | 0 | 105 | 203 | 0 | 0 | 0 | 975 | 0 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 215 | 40 | 89 | 85 | 17 | 47 | 19 | 114 | 134 | 52.2 | 0 | 24 | 305 | 0 | 312 | 42 | 0 | 140 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 101 | 25 | 69 | 0 | 155 | 0 | 0 | 0 | 24 | 7860.62 | 898 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 151 | 0 | 32 | 0 | 550 | 0 | 0 | 0 | 1489.37 | 0 | 40 | 0 | 50 | 113 | 0 | 100 | 27 | 8 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 190 | 0 | 115 | 0 | 85 | 0 | 120 | 0 | 0 | 0 | 0 | 16 | 235 | 120 | 220 | 0 | 1050 | 880 | 17 | 6952.37 | 14812.99 | 102.25
Total KWH | 0 | 665280 | 264960 | 0 | 0 | 0 | 0 | 0 | 7614000 | 0 | 0 | 339120 | 696600 | 1448640 | 3181440 | 1655247 | 384963 | 679172 | 1136160 | 0 | 0 | 3424407 | 7163636 | 0 | 469270 | 7123312 | 0 | 0 | 88919 | 3490800 | 246000 | 499320 | 0 | 0 | 2251909 | 378873 | 1446720 | 0 | 650880 | 362984 | 899280 | 399865 | 591360 | 584640 | 23125 | 5287135 | 2577673 | 219360 | 27200000 | 1809891 | 0 | 1190880 | 105156 | 2305018 | 4803953 | 0 | 0 | 0 | 22990907 | 80730 | 3649890 | 0 | 0 | 7838100 | 0 | 1220481 | 0 | 5110000 | 780552 | 752640 | 2034618 | 444960 | 282240 | 470150 | 2337000 | 3279360 | 1224130 | 244636 | 875600 | 7508000 | 0 | 7606000 | 970000 | 0 | 3375981.82 | 46778 | 318720 | 0 | 1312320 | 0 | 0 | 0 | 2408210 | 567720 | 1347600 | 119070 | 2241600 | 0 | 11350 | 269310 | 422160 | 175800761.82 | 21686545 | 0 | 0 | 129120 | 0 | 912000 | 0 | 0 | 792203.64 | 0 | 199440 | 347760 | 17498180 | 0 | 0 | 0 | 31673044 | 0 | 395425 | 0 | 657216 | 1474368 | 0 | 606160 | 259811 | 192154 | 222472 | 388990 | 0 | 0 | 279552 | 3669545 | 0 | 0 | 0 | 0 | 0 | 6105454 | 0 | 21780 | 4700000 | 0 | 2564531 | 123045 | 825456 | 0 | 543375 | 0 | 25459.8 | 833040 | 987 | 396960 | 6218000 | 2827000 | 5323270 | 0 | 25141818 | 21592727.27 | 439200 | 159066088.71 | 334866850.53 | 102.24