## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 31-07-2026 | [28 empty] | Date: | 31-07-2026 | [28 empty] | Date: | 31-07-2026 | [28 empty] | Date: | 31-07-2026 | [28 empty] | Date: | 31-07-2026 | [18 empty] | Date: | 31-07-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 54 | 35 | 72 | 144 | 81 | 16 | 55 | 162 | 0 | 0 | 138 | 280 | 0 | 55 | 300 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 107 | 16 | 85 | 0 | 8 | 50 | 57 | 17 | 25 | 25 | 0 | 222 | 110 | 5 | 935 | 162 | 0 | 50 | 0 | 105 | 203 | 0 | 0 | 0 | 900 | 0 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 215 | 40 | 88 | 84 | 48 | 10 | 19 | 114 | 146 | 52.2 | 0 | 24 | 315 | 0 | 312 | 42 | 0 | 141 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 35 | 49 | 0 | 48 | 0 | 0 | 0 | 14 | 7501.62 | 897 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 598 | 0 | 0 | 0 | 1480.01 | 0 | 40 | 0 | 50 | 113 | 0 | 100 | 27 | 8 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 190 | 0 | 115 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 234 | 120 | 220 | 0 | 890 | 880 | 17 | 6526.01 | 14027.63 | 102.23
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 20 | 21 | 46 | 144 | 48 | 54 | 55 | 162 | 0 | 0 | 138 | 285 | 0 | 35 | 290 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 108 | 16 | 60 | 0 | 8 | 50 | 57 | 0 | 25 | 25 | 0 | 222 | 110 | 11 | 855 | 162 | 0 | 50 | 0 | 105 | 203 | 0 | 0 | 0 | 900 | 0 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 215 | 40 | 74 | 85 | 160 | 0 | 19 | 114 | 142 | 52.2 | 0 | 24 | 310 | 0 | 312 | 40 | 0 | 140 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 35 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7349.62 | 898 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 0 | 0 | 1451.35 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 27 | 52.2 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 246 | 0 | 0 | 190 | 0 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 230 | 120 | 220 | 0 | 800 | 875 | 17 | 6312.55 | 13662.17 | 102.23
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 17 | 17 | 34 | 127 | 48 | 55 | 55 | 162 | 0 | 0 | 141 | 275 | 0 | 35 | 302 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 107 | 16 | 56 | 0 | 7 | 0 | 57 | 0 | 25 | 25 | 0 | 220 | 97 | 25 | 770 | 160 | 0 | 50 | 0 | 105 | 203 | 0 | 0 | 0 | 900 | 0 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 216 | 40 | 40 | 85 | 177 | 0 | 19 | 114 | 140 | 52.2 | 0 | 24 | 310 | 0 | 312 | 40 | 0 | 136 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 35 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7145.62 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 873 | 0 | 0 | 0 | 1479.42 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 27 | 52.2 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 247 | 0 | 0 | 190 | 0 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 291 | 120 | 220 | 0 | 800 | 875 | 17 | 6483.62 | 13629.24 | 102.22
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 34 | 143 | 48 | 55 | 55 | 144 | 0 | 0 | 138 | 285 | 0 | 35 | 288 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 109 | 16 | 50 | 0 | 6 | 0 | 57 | 0 | 25 | 25 | 0 | 215 | 94 | 28 | 730 | 143 | 0 | 50 | 0 | 95 | 203 | 0 | 0 | 0 | 900 | 0 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 216 | 40 | 0 | 85 | 175 | 0 | 19 | 114 | 140 | 52.2 | 0 | 24 | 315 | 0 | 312 | 40 | 0 | 146 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 35 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6998.62 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 928 | 0 | 0 | 0 | 1478.21 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 27 | 52.2 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 190 | 0 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 700 | 875 | 17 | 6459.41 | 13458.03 | 102.22
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 34 | 143 | 48 | 55 | 55 | 0 | 0 | 0 | 149 | 290 | 0 | 35 | 314 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 107 | 16 | 50 | 0 | 11 | 0 | 50 | 0 | 25 | 25 | 0 | 214 | 93 | 39 | 730 | 143 | 0 | 50 | 0 | 91 | 203 | 0 | 0 | 0 | 900 | 0 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 214 | 37 | 0 | 85 | 181 | 0 | 19 | 114 | 128 | 52.2 | 0 | 24 | 315 | 0 | 312 | 40 | 0 | 146 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 35 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6886.62 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 1476.1 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 27 | 52.2 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 190 | 0 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 700 | 875 | 17 | 6496.3 | 13382.92 | 102.21
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 34 | 143 | 48 | 55 | 55 | 0 | 0 | 0 | 142 | 290 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 107 | 16 | 50 | 0 | 10 | 0 | 50 | 0 | 25 | 25 | 0 | 215 | 94 | 40 | 735 | 142 | 0 | 50 | 0 | 91 | 204 | 0 | 0 | 0 | 900 | 0 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 216 | 37 | 0 | 86 | 178 | 0 | 19 | 114 | 136 | 8 | 0 | 24 | 315 | 0 | 312 | 40 | 0 | 146 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 103 | 35 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6833.42 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 1471.43 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 27 | 52.2 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 190 | 0 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 700 | 875 | 17 | 6502.63 | 13336.05 | 102.21
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 17 | 34 | 126 | 48 | 55 | 55 | 0 | 0 | 0 | 138 | 270 | 0 | 0 | 288 | 0 | 0 | 0 | 143.42 | 11 | 15 | 0 | 0 | 109 | 16 | 50 | 0 | 15 | 0 | 50 | 0 | 25 | 25 | 0.19 | 216 | 94 | 40 | 730 | 143 | 0 | 50 | 0 | 91 | 204 | 0 | 0 | 0 | 900 | 0 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 216 | 37 | 0 | 86 | 100 | 0 | 19 | 114 | 126 | 8 | 5 | 24 | 290 | 0 | 312 | 40 | 0 | 127 | 1 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 35 | 49 | 0.61 | 48 | 0 | 0 | 1.79 | 12 | 6619.01 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.41 | 950 | 0 | 0 | 0 | 1470.71 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 27 | 52.2 | 0.9 | 1 | 0 | 0 | 1.12 | 152 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0.13 | 190 | 0 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 3 | 0 | 16 | 307 | 120 | 180 | 0 | 700 | 875 | 17 | 6478.47 | 13097.48 | 102.2
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 34 | 127 | 48 | 55 | 35 | 0 | 0 | 0 | 143 | 285 | 0 | 0 | 307 | 0 | 0 | 3 | 143.42 | 11 | 15 | 0 | 0 | 106 | 16 | 50 | 0 | 7 | 0 | 0 | 5 | 25 | 25 | 0.71 | 221 | 94 | 34 | 730 | 70 | 0 | 50 | 0 | 91 | 204 | 0 | 0 | 0 | 900 | 1 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 216 | 37 | 0 | 85 | 51 | 0 | 19 | 52 | 116 | 8 | 12 | 24 | 310 | 0 | 312 | 42 | 0 | 138 | 3 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 35 | 49 | 3.31 | 48 | 0 | 0.2 | 10.25 | 12 | 6435.89 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 13.55 | 950 | 0 | 0 | 0 | 1478.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 12.38 | 18 | 0 | 0 | 4.15 | 152 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0.49 | 190 | 0 | 115 | 4 | 35 | 0 | 0 | 0 | 0.9 | 43 | 0.09 | 16 | 307 | 120 | 220 | 0 | 700 | 850 | 17 | 6521.12 | 12957.01 | 102.2
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 17 | 34 | 127 | 48 | 55 | 0 | 0 | 0 | 0 | 140 | 280 | 0 | 0 | 300 | 0 | 0 | 6 | 143.42 | 11 | 15 | 0 | 0 | 107 | 16 | 49 | 0 | 0 | 0 | 0 | 17 | 25 | 25 | 1.45 | 222 | 92 | 35 | 735 | 33 | 0 | 50 | 0 | 91 | 204 | 0 | 0 | 0 | 900 | 2 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 216 | 40 | 0 | 86 | 51 | 0 | 19 | 17 | 118 | 8 | 21 | 24 | 305 | 0 | 312 | 42 | 0 | 138 | 5 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 35 | 49 | 4.24 | 48 | 0 | 0.5 | 11.09 | 14 | 6346.7 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19.39 | 950 | 0 | 0 | 0 | 1469.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 26.53 | 24 | 0 | 0 | 10.7 | 154 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 1.4 | 190 | 0 | 115 | 17 | 35 | 0 | 0 | 0 | 0 | 99 | 0.14 | 16 | 307 | 120 | 220 | 0 | 700 | 800 | 17 | 6564.69 | 12911.39 | 102.19
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 17 | 34 | 127 | 48 | 55 | 0 | 17 | 0 | 0 | 143 | 285 | 0 | 0 | 295 | 0 | 0 | 11 | 143.42 | 11 | 15 | 0 | 0 | 109 | 16 | 50 | 0 | 8 | 0 | 0 | 17 | 25 | 25 | 2.22 | 222 | 93 | 36 | 735 | 33 | 0 | 50 | 0 | 91 | 204 | 0 | 0 | 0 | 900 | 4 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 215 | 37 | 0 | 86 | 58 | 0 | 11 | 16 | 114 | 8 | 50 | 24 | 310 | 0 | 312 | 42 | 0 | 141 | 8 | 17 | 0 | 53 | 0 | 0 | 0 | 103 | 35 | 49 | 15.08 | 48 | 0 | 1.1 | 25.94 | 24 | 6444.76 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 57.61 | 950 | 0 | 0 | 0 | 1461.61 | 0 | 0 | 0 | 10 | 4 | 0 | 0 | 0 | 8 | 40.7 | 54 | 0 | 0 | 20.21 | 154 | 0 | 0 | 0 | 0 | 0 | 246 | 0 | 1.82 | 190 | 0 | 113 | 17 | 0 | 0 | 0 | 0 | 0 | 131 | 0.62 | 16 | 279 | 100 | 180 | 0 | 700 | 704 | 17 | 6391.57 | 12836.33 | 102.19
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 34 | 126 | 81 | 55 | 0 | 17 | 0 | 0 | 135 | 275 | 0 | 0 | 270 | 0 | 0 | 5 | 143.42 | 11.5 | 15 | 0 | 0 | 92 | 16 | 49 | 0 | 0 | 0 | 0 | 17 | 25 | 25 | 4.05 | 222 | 94 | 36 | 735 | 33 | 0 | 44 | 0 | 91 | 204 | 0 | 0 | 0 | 903 | 7 | 150 | 0 | 0 | 280 | 0 | 51 | 0 | 216 | 37 | 0 | 85 | 64 | 0 | 11 | 14 | 110 | 8 | 62 | 24 | 315 | 0 | 312 | 42 | 0 | 139 | 12 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 35 | 58 | 11.69 | 104 | 0 | 2.3 | 25.57 | 24 | 6491.53 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 80 | 1045 | 0 | 0 | 0 | 1407.24 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 8 | 52.17 | 15 | 0 | 0 | 19.15 | 154 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 5.37 | 190 | 0 | 112 | 28 | 0 | 0 | 0 | 0 | 3.2 | 179 | 0.35 | 16 | 277 | 100 | 180 | 0 | 631 | 542 | 17 | 6322.48 | 12814.01 | 102.18
11:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 17 | 34 | 125 | 81 | 55 | 0 | 17 | 0 | 0 | 143 | 285 | 0 | 0 | 300 | 0 | 0 | 23 | 143.42 | 12 | 0 | 0 | 0 | 75 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 25 | 25 | 4.51 | 222 | 94 | 36 | 735 | 33 | 0 | 50 | 0 | 91 | 204 | 0 | 0 | 0 | 900 | 5 | 150 | 0 | 0 | 285 | 0 | 51 | 0 | 213 | 37 | 37 | 85 | 67 | 0 | 11 | 80 | 126 | 0 | 73 | 24 | 310 | 0 | 292 | 42 | 0 | 144 | 8 | 17 | 0 | 52 | 0 | 0 | 0 | 102 | 35 | 58 | 22.16 | 115 | 0 | 2 | 42.02 | 24 | 6672.11 | 899 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 26 | 1070 | 0 | 0 | 0 | 1445.01 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 8 | 21.11 | 116 | 0 | 0 | 43.55 | 154 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 4.7 | 0 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 6.9 | 153 | 0.78 | 16 | 280 | 100 | 220 | 0 | 692 | 566 | 17 | 6351.05 | 13023.16 | 102.19
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 35 | 125 | 81 | 45 | 0 | 17 | 0 | 0 | 134 | 285 | 0 | 0 | 285 | 0 | 0 | 24 | 143.42 | 12 | 9 | 0 | 0 | 85 | 16 | 50 | 0 | 0 | 0 | 15 | 17 | 25 | 25 | 4.09 | 222 | 94 | 34 | 735 | 16 | 0 | 50 | 1 | 91 | 203 | 0 | 0 | 0 | 900 | 8 | 150 | 0 | 0 | 300 | 0 | 51 | 0 | 213 | 36 | 51 | 85 | 131 | 0 | 11 | 98 | 144 | 0 | 74 | 24 | 315 | 0 | 292 | 42 | 0 | 148 | 12 | 17 | 0 | 52 | 0 | 0 | 0 | 102 | 35 | 58 | 22.22 | 115 | 0 | 1.7 | 30.8 | 24 | 6838.23 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34 | 1069 | 0 | 0 | 0 | 1452.87 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 8 | 18.97 | 105 | 0 | 0 | 41.19 | 154 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 2.24 | 0 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 6.2 | 193 | 0.31 | 16 | 277 | 120 | 220 | 0 | 1001 | 560 | 17 | 6704.78 | 13543.01 | 102.18
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 55 | 123 | 81 | 15 | 0 | 17 | 0 | 0 | 146 | 285 | 0 | 0 | 307 | 0 | 0 | 23 | 143.42 | 12 | 9 | 0 | 0 | 91 | 16 | 49 | 0 | 0 | 0 | 16 | 17 | 25 | 25 | 4.8 | 222 | 102 | 30 | 735 | 16 | 0 | 50 | 8 | 90 | 203 | 0 | 0 | 0 | 1025 | 9 | 150 | 0 | 0 | 300 | 0 | 51 | 0 | 211 | 36 | 51 | 85 | 157 | 0 | 11 | 106 | 148 | 0 | 72 | 24 | 320 | 0 | 270 | 42 | 0 | 146 | 6 | 17 | 0 | 52 | 0 | 0 | 0 | 102 | 35 | 58 | 8.27 | 115 | 0 | 1.5 | 6.21 | 24 | 6972.2 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 61 | 1069 | 0 | 0 | 0 | 1443.81 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 8 | 25.88 | 80 | 0 | 0 | 40.8 | 154 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 4.28 | 0 | 0 | 113 | 34 | 0 | 0 | 0 | 0 | 7.1 | 173 | 0.11 | 16 | 277 | 120 | 220 | 0 | 1040 | 562 | 17 | 6736.98 | 13709.18 | 102.16
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 17 | 17 | 70 | 123 | 81 | 15 | 17 | 17 | 0 | 0 | 143 | 280 | 0 | 17 | 309 | 0 | 0 | 12 | 143.42 | 14 | 15 | 0 | 0 | 89 | 16 | 49 | 0 | 12 | 0 | 16 | 17 | 12 | 25 | 2.94 | 222 | 110 | 24 | 735 | 16 | 0 | 50 | 8 | 91 | 203 | 0 | 0 | 0 | 1020 | 15 | 150 | 0 | 0 | 290 | 0 | 51 | 0 | 190 | 36 | 51 | 85 | 169 | 0 | 11 | 101 | 142 | 43 | 16 | 24 | 305 | 0 | 267 | 42 | 0 | 142 | 3 | 8 | 0 | 52 | 0 | 0 | 0 | 101 | 35 | 59 | 15.41 | 116 | 0 | 2.3 | 27.88 | 24 | 6970.95 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25 | 1062 | 0 | 0 | 0 | 1450.63 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 8 | 54.54 | 72 | 0 | 0 | 37.49 | 154 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 2.61 | 0 | 0 | 113 | 35 | 0 | 0 | 0 | 0 | 5.5 | 175 | 0.66 | 16 | 243 | 120 | 180 | 0 | 1012 | 560 | 17 | 6594.43 | 13565.38 | 102.16
15:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 17 | 17 | 66 | 122 | 81 | 15 | 35 | 17 | 0 | 0 | 139 | 285 | 0 | 35 | 287 | 0 | 0 | 4 | 143.42 | 13 | 15 | 0 | 0 | 90 | 16 | 50 | 0 | 16 | 0 | 16 | 17 | 12 | 12 | 3.07 | 216 | 110 | 30 | 735 | 16 | 0 | 50 | 8 | 90 | 202 | 0 | 0 | 0 | 900 | 10 | 150 | 0 | 0 | 350 | 0 | 51 | 0 | 210 | 36 | 50 | 85 | 167 | 0 | 11 | 103 | 144 | 43 | 46 | 24 | 320 | 0 | 277 | 41 | 0 | 147 | 9 | 16 | 0 | 53 | 0 | 0 | 0 | 102 | 35 | 59 | 15 | 115 | 0 | 0.4 | 45.93 | 24 | 6959.82 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 1025 | 0 | 0 | 0 | 1449.69 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 8 | 22.39 | 14 | 0 | 0 | 47.01 | 155 | 0 | 0 | 0 | 0 | 0 | 264 | 0 | 3.06 | 0 | 0 | 113 | 10 | 0 | 0 | 0 | 0 | 4.4 | 119 | 0.26 | 16 | 278 | 120 | 220 | 0 | 700 | 565 | 17 | 6193.81 | 13153.63 | 102.16
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 17 | 17 | 52 | 121 | 81 | 15 | 35 | 17 | 0 | 0 | 142 | 280 | 0 | 35 | 289 | 0 | 0 | 2 | 129 | 13 | 15 | 0 | 0 | 94 | 16 | 50 | 0 | 29 | 0 | 16 | 17 | 12 | 12 | 0.64 | 216 | 110 | 21 | 735 | 16 | 0 | 50 | 8 | 91 | 212 | 0 | 0 | 0 | 900 | 4 | 150 | 0 | 0 | 348 | 0 | 51 | 0 | 197 | 34 | 52 | 85 | 170 | 0 | 11 | 106 | 132 | 52.2 | 25 | 24 | 305 | 0 | 280 | 41 | 0 | 138 | 1 | 16 | 0 | 53 | 0 | 0 | 0 | 101 | 35 | 58 | 0.87 | 115 | 0 | 0.9 | 30.9 | 24 | 6883.51 | 897 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 37 | 1076 | 0 | 0 | 0 | 1433.52 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 8 | 15.2 | 14 | 0 | 0 | 11.45 | 155 | 0 | 0 | 0 | 0 | 0 | 269 | 0 | 1.03 | 0 | 0 | 113 | 16 | 60 | 0 | 0 | 0 | 4.2 | 52 | 0.25 | 16 | 277 | 120 | 220 | 0 | 700 | 560 | 17 | 6195.65 | 13079.16 | 102.15
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 60 | 136 | 81 | 15 | 35 | 17 | 0 | 0 | 139 | 275 | 0 | 35 | 289 | 0 | 0 | 3 | 126 | 13 | 15 | 0 | 0 | 45 | 16 | 50 | 0 | 19 | 0 | 16 | 17 | 12 | 12 | 0 | 216 | 110 | 21 | 735 | 16 | 0 | 50 | 8 | 91 | 213 | 0 | 0 | 0 | 900 | 2 | 150 | 0 | 0 | 354 | 0 | 51 | 0 | 198 | 34 | 67 | 85 | 176 | 3 | 11 | 55 | 134 | 25 | 22 | 24 | 310 | 0 | 281 | 41 | 0 | 134 | 1 | 16 | 0 | 53 | 0 | 0 | 0 | 101 | 35 | 59 | 0.75 | 115 | 0 | 0.3 | 0.26 | 22 | 6763.31 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 14 | 1070 | 0 | 0 | 0 | 1432.94 | 0 | 0 | 0 | 35 | 50 | 0 | 0 | 0 | 8 | 9.79 | 27 | 0 | 0 | 14.18 | 155 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 1.4 | 47 | 0 | 114 | 3 | 83 | 0 | 0 | 0 | 2.5 | 29 | 0.17 | 16 | 277 | 120 | 220 | 0 | 700 | 550 | 17 | 6204.98 | 12968.29 | 102.15
18:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 0 | 70 | 138 | 81 | 15 | 35 | 40 | 0 | 0 | 139 | 280 | 0 | 35 | 291 | 0 | 0 | 1 | 127 | 13 | 15 | 0 | 0 | 48 | 16 | 50 | 0 | 17 | 0 | 16 | 17 | 12 | 12 | 0 | 218 | 85 | 23 | 735 | 16 | 0 | 26 | 8 | 51 | 213 | 0 | 0 | 0 | 900 | 0 | 150 | 0 | 0 | 355 | 0 | 51 | 0 | 193 | 32 | 69 | 85 | 120 | 27 | 11 | 34 | 122 | 25 | 4 | 24 | 300 | 0 | 280 | 41 | 0 | 134 | 1 | 17 | 0 | 53 | 0 | 0 | 0 | 101 | 35 | 59 | 0.6 | 115 | 0 | 0.1 | 0.46 | 22 | 6622.16 | 898 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4.65 | 1040 | 0 | 0 | 0 | 1412.19 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 12 | 8 | 1.78 | 5 | 0 | 0 | 2.4 | 155 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 0.2 | 0 | 0 | 50 | 1 | 92 | 0 | 0 | 0 | 0.6 | 7 | 0.03 | 16 | 276 | 120 | 220 | 0 | 850 | 528 | 17 | 6132.85 | 12755.01 | 102.14
19:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 11 | 95 | 139 | 81 | 15 | 35 | 75 | 0 | 0 | 146 | 285 | 0 | 35 | 318 | 0 | 0 | 0 | 143.42 | 13 | 15 | 0 | 0 | 52 | 16 | 53 | 0 | 10 | 50 | 48 | 35 | 12 | 12 | 0 | 220 | 76 | 23 | 735 | 16 | 0 | 31 | 13 | 78 | 213 | 0 | 0 | 0 | 1105 | 0 | 150 | 0 | 0 | 349 | 0 | 51 | 0 | 211 | 35 | 73 | 85 | 141 | 27 | 8 | 83 | 140 | 27 | 0 | 23 | 310 | 0 | 280 | 41 | 0 | 137 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 35 | 59 | 0 | 133 | 0 | 0 | 0 | 14 | 7313.42 | 897 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1023 | 0 | 0 | 0 | 1431.9 | 0 | 0 | 0 | 55 | 58 | 0 | 100 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 115 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 289 | 120 | 220 | 0 | 1050 | 535 | 17 | 6559.9 | 13873.32 | 102.12
19:30 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 17 | 106 | 139 | 81 | 15 | 35 | 90 | 0 | 0 | 139 | 305 | 0 | 35 | 316 | 0 | 0 | 0 | 143.42 | 13 | 15 | 0 | 0 | 92 | 16 | 65 | 0 | 10 | 50 | 55 | 35 | 12 | 12 | 0 | 220 | 93 | 25 | 786 | 16 | 0 | 50 | 25.5 | 90 | 213 | 0 | 0 | 0 | 1210 | 0 | 150 | 0 | 0 | 354 | 0 | 51 | 0 | 208 | 36 | 89 | 85 | 190 | 37 | 19 | 105 | 144 | 52.2 | 0 | 23 | 330 | 0 | 280 | 41 | 0 | 142 | 0 | 17 | 0 | 86 | 0 | 0 | 0 | 101 | 35 | 68 | 0 | 152 | 0 | 0 | 0 | 16 | 7861.12 | 898 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1055 | 0 | 0 | 0 | 1480.07 | 0 | 0 | 0 | 55 | 90 | 0 | 92 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1050 | 560 | 17 | 6714.07 | 14575.19
20:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 54 | 0 | 106 | 142 | 81 | 15 | 35 | 90 | 0 | 0 | 137 | 280 | 0 | 35 | 274 | 0 | 0 | 0 | 143.42 | 13 | 15 | 0 | 0 | 97 | 16 | 72 | 0 | 9 | 50 | 55 | 36 | 12 | 12 | 0 | 220 | 97 | 24 | 785 | 16 | 0 | 50 | 25.5 | 91 | 213 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 0 | 315 | 0 | 51 | 0 | 179 | 36 | 89 | 85 | 172 | 32 | 19 | 106 | 140 | 52.2 | 0 | 23 | 315 | 0 | 280 | 41 | 0 | 140 | 0 | 17 | 0 | 86 | 0 | 0 | 0 | 102 | 35 | 68 | 0 | 152 | 0 | 0 | 0 | 18 | 7695.12 | 898 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1080 | 0 | 0 | 0 | 1475.82 | 0 | 37 | 0 | 55 | 90 | 0 | 92 | 23 | 8 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 180 | 0 | 1050 | 581 | 17 | 6751.82 | 14446.94 | 102.12
21:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 54 | 0 | 106 | 142 | 81 | 15 | 35 | 90 | 0 | 0 | 140 | 290 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 13 | 22 | 0 | 0 | 97 | 16 | 82 | 0 | 11 | 50 | 55 | 54.36 | 12 | 12 | 0 | 222 | 110 | 34 | 855 | 20 | 0 | 50 | 8 | 91 | 213 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 0 | 355 | 0 | 51 | 0 | 194 | 36 | 88 | 85 | 182 | 31 | 19 | 106 | 138 | 52.2 | 0 | 23 | 315 | 0 | 280 | 41 | 0 | 146 | 0 | 17 | 0 | 86 | 0 | 0 | 0 | 101 | 35 | 68 | 0 | 154 | 0 | 0 | 0 | 24 | 7919.98 | 898 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1080 | 0 | 0 | 0 | 1453.54 | 0 | 40 | 0 | 57 | 90 | 0 | 92 | 23 | 8 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1050 | 581 | 17 | 6782.54 | 14702.52 | 102.11
22:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 18 | 106 | 143 | 81 | 15 | 35 | 90 | 0 | 0 | 147 | 280 | 0 | 17 | 295 | 0 | 0 | 0 | 143.42 | 13 | 22 | 0 | 0 | 95 | 16 | 81 | 0 | 16 | 50 | 55 | 54.36 | 12 | 12 | 0 | 222 | 110 | 34 | 930 | 103 | 0 | 50 | 8 | 91 | 205 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 0 | 354 | 0 | 51 | 0 | 199 | 36 | 72 | 85 | 178 | 27 | 19 | 106 | 134 | 52.2 | 0 | 23 | 305 | 0 | 284 | 41 | 0 | 138 | 0 | 17 | 0 | 53 | 0 | 0 | 0 | 102 | 35 | 68 | 0 | 154 | 0 | 0 | 0 | 24 | 7997.98 | 898 | 0 | 0 | 22 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1080 | 0 | 0 | 0 | 1457.76 | 0 | 40 | 0 | 57 | 90 | 0 | 92 | 23 | 8 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1039 | 581 | 17 | 6777.76 | 14775.74 | 102.1
23:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 54 | 35 | 106 | 143 | 81 | 15 | 35 | 90 | 0 | 0 | 144 | 290 | 0 | 0 | 310 | 0 | 0 | 0 | 143.42 | 13 | 22 | 0 | 0 | 102 | 16 | 82 | 0 | 9 | 50 | 50 | 17 | 12 | 12 | 0 | 222 | 110 | 36 | 940 | 142 | 0 | 50 | 0 | 91 | 203 | 0 | 0 | 0 | 1205 | 0 | 150 | 0 | 0 | 354 | 0 | 51 | 0 | 210 | 37 | 49 | 85 | 189 | 27 | 19 | 106 | 134 | 52.2 | 0 | 24 | 315 | 0 | 294 | 41 | 0 | 144 | 0 | 16 | 0 | 53 | 0 | 0 | 0 | 102 | 35 | 68 | 0 | 154 | 0 | 0 | 0 | 24 | 7961.62 | 898 | 0 | 0 | 22 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1080 | 0 | 0 | 0 | 1461.95 | 0 | 40 | 0 | 57 | 90 | 0 | 92 | 23 | 8 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 120 | 220 | 0 | 1050 | 581 | 35 | 6807.95 | 14769.57 | 102.08
Total KWH | 0 | 663350 | 212755 | 0 | 0 | 0 | 0 | 0 | 8488800 | 0 | 0 | 389520 | 431640 | 1448640 | 3191680 | 1648473 | 852758 | 735274 | 1189440 | 0 | 0 | 3395636 | 6900455 | 0 | 468866 | 7193149 | 0 | 0 | 136628 | 3442800 | 297000 | 393840 | 0 | 0 | 2278255 | 381382 | 1373760 | 0 | 238080 | 354255 | 657504 | 430618 | 463680 | 457920 | 24480 | 1940000 | 2426291 | 715680 | 18581818.18 | 1736291 | 0 | 1174560 | 110032.2 | 2194618 | 4835240 | 0 | 0 | 0 | 23459998 | 60480 | 3664945 | 0 | 0 | 7848500 | 0 | 1255669 | 0 | 5145000 | 876600 | 982080 | 2034425 | 3523680 | 184800 | 391910 | 2104440 | 3145920 | 732043 | 509555 | 569088 | 7544000 | 0 | 7236000 | 975000 | 0 | 3391036.36 | 70070 | 380928 | 0 | 1325760 | 0 | 0 | 0 | 2430110 | 866160 | 1348800 | 105732 | 2217600 | 0 | 11000 | 276380 | 460800 | 166983677.74 | 21664727 | 0 | 0 | 150720 | 0 | 912000 | 0 | 0 | 0 | 0 | 84528 | 421920 | 24254550 | 0 | 0 | 0 | 34959163 | 0 | 409653 | 0 | 692064 | 1119360 | 0 | 529552 | 293852 | 538901 | 296328 | 492390 | 0 | 0 | 309744 | 3730182 | 0 | 0 | 0 | 0 | 0 | 6450036 | 0 | 27000 | 2086000 | 0 | 2615302 | 201023 | 1140278 | 0 | 0 | 0 | 43411.8 | 1305360 | 3651 | 399264 | 6960000 | 2836000 | 5316940 | 0 | 20203636 | 16613818.18 | 439200 | 157500553.98 | 324484231.72

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-07-2026 | during | 01-08-2026 | during | 01-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 350 | 344 | 412 | 412 | 371 | 371 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 134 | 140 | 335 | 335 | 150 | 150 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 45 | 15 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 285 | 295 | 335 | 335 | 320 | 320 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 17 | 35 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 125 | 142 | 149.36 | 149.36 | 125 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 13 | 33 | 33 | 11 | 11 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 9 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 0 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 81 | 81 | 300 | 300 | 48 | 195 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 106 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 52 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 90 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 24 | 0 | 22 | 0 | 22 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 285 | 290 | 583 | 583 | 330 | 330 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1612.42 | 1926.42 | 5800.16 | 5778.16 | 1749.42 | 2182.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 1 | 8 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 8 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 222 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 203 | 213 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 91 | 91 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 15 | 55 | 24 | 56 | 40 | 72 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 12 | 100 | 100 | 25 | 25 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 34 | 34 | 5 | 24 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 50 | 82 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.09 | 0 | 4.42 | 0 | 4.42 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 54 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 94 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 12 | 100 | 100 | 25 | 25 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 85 | 97 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 16 | 20 | 163 | 163 | 147 | 147 | FGMO
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 900 | 1224 | 1224 | 1224 | 900 | 900 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 11 | 5 | 3 | 5 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 735 | 855 | 775 | 1150 | 1145 | 1145 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2591.09 | 3216.36 | 3712.28 | 4181.86 | 3178.42 | 3298
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 213 | 194 | 221.25 | 221.25 | 218 | 218 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 300 | 355 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 0 | 342.01 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 36 | 36 | 41.65 | 41.65 | 30 | 30 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 24 | 23 | 24 | 24 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 85 | 0 | 0 | 87 | 87 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 131 | 182 | 200 | 200 | 80 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 144 | 138 | 84 | 78 | 150 | 150 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 19 | 17.53 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 106 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 31 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 88 | 115 | 115 | 34 | 68 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 74 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1368 | 1510.2 | 2566.47 | 2517.44 | 1423.21 | 1516.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-07-2026 | during | 01-08-2026 | during | 01-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 22.22 | 0 | 15 | 0 | 15 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.7 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 154 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 30.8 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 35 | 35 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 286.72 | 281 | 532.6 | 516.5 | 275.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 42 | 41 | 0 | 0 | 40 | 40 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 148 | 146 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 52 | 86 | 86 | 86 | 53 | 53 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 101 | 100 | 100 | 100 | 100 | Machine Problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 17 | 17 | 18 | 18 | 17 | 17 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | Machine Problem
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 292 | 280 | 250 | 260 | 315 | 315 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 980 | 986 | 988 | 998 | 979 | 979
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 897 | 898 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 23 | 32 | 32 | 30 | 30 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 50 | 50 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 34 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1069 | 1080 | 1080 | 1080 | 555 | 555 | U-2 Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2038 | 2054 | 3457 | 3382 | 1748 | 1673
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1001 | 1050 | 800 | 1050 | 700 | 1050 | AGC
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 560 | 581 | 581.53 | 581.53 | 895 | 895 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 277 | 307 | 307 | 307 | 250 | 250 | Machine Problem
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.31 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2211.31 | 2311 | 2299.53 | 2548.53 | 2219 | 2568
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 18.97 | 0 | 48.25 | 0 | 48.25 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 154 | 156 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 250 | 278 | 413.79 | 413.79 | 280 | 280 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 26 | 26 | 26 | 26 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 100 | 100 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 90 | 113 | 113 | 50 | 113 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 57 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 2.24 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1452.87 | 1453.54 | 1469.13 | 1469.13 | 1389.13 | 1389.13 | AGC+FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 41.19 | 0 | 53 | 0 | 53 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 105 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2117.27 | 2197.54 | 3251.87 | 3045.12 | 2271.08 | 2234.33
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 190 | 190 | 190 | 190 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 105 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.2 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 105 | 115 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 193 | 0 | 172.81 | 0 | 172.81 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 338.2 | 220 | 657.81 | 452 | 524.81 | 354
System Total |  |  |  |  | 28843.2 | 29171.687 | 13543.01 | 14702.52 | 23265.72 | 23419.61 | 14368.04 | 15063.96
Forecast Scenario (01-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14440 |  | 1967.3 |  | 16500
|  |  |  | 1:00 | 13910 |  | 2081.9 |  | 16090
|  |  |  | 2:00 | 13750 |  | 1843.15 |  | 15680
|  |  |  | 3:00 | 13690 |  | 1499.35 |  | 15260
|  |  |  | 4:00 | 13630 |  | 1136.45 |  | 14820
|  |  |  | 5:00 | 13540 |  | 907.25 |  | 14490
|  |  |  | 6:00 | 13150 |  | 859.5 |  | 14050
|  |  |  | 7:00 | 13290 |  | 840.4 |  | 14170
|  |  |  | 8:00 | 13370 |  | 840.4 |  | 14250
|  |  |  | 9:00 | 13090 |  | 1317.9 |  | 14470
|  |  |  | 10:00 | 13430 |  | 1040.95 |  | 14520
|  |  |  | 11:00 | 13480 |  | 1270.15 |  | 14810
|  |  |  | 12:00 | 13620 |  | 1623.5 |  | 15320
|  |  |  | 13:00 | 13740 |  | 1776.3 |  | 15600
|  |  |  | 14:00 | 13440 |  | 2015.05 |  | 15550
|  |  |  | 15:00 | 13490 |  | 2196.5 |  | 15790
|  |  |  | 16:00 | 13430 |  | 2062.8 |  | 15590
|  |  |  | 17:00 | 13410 |  | 1661.7 |  | 15150
|  |  |  | 18:00 | 13440 |  | 1308.35 |  | 14810
|  |  |  | 18:30 | 13660 |  | 1757.2 |  | 15500
|  |  |  | 19:00 | 13880 |  | 2377.95 |  | 16370
|  |  |  | 19:30 | 14580 |  | 2406.6 |  | 17100
|  |  |  | 20:00 | 14450 |  | 2549.85 |  | 17120
|  |  |  | 21:00 | 14710 |  | 2607.15 |  | 17440
|  |  |  | 22:00 | 14780 |  | 2253.8 |  | 17140
|  |  |  | 23:00 | 14770 |  | 2320.65 |  | 17200
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 15320.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2607
Probable Maximum Demand at Evening Peak: |  |  | 17440.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14710.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 329.93 MKWHr. |  | 357 | 250 | 370 | 420 | 160 | 330 | 140 | 300 | 280
*** This report is generated digitally from Operation Information System (OIS) at 10:28 hrs on 01-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 31-07-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13543.01 | MW | 12:00 Hr. | Energy Generated |  |  | 324.4842 |  | MKWHr.
| Day Peak Demand |  |  | 13923.01 | MW | 12:00 Hr. | Energy Unserverd |  |  | 23.065 |  | MKWHr.
| Evening Peak Generation |  |  | 14702.52 | MW | 21:00 Hr. | Energy Demand |  |  | 347.5492 |  | MKWHr.
| Evening Peak Demand |  |  | 16286.52 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.6 |  | °C
| Minimum Generation of the Day |  |  | 12814.01 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 673.12 |  | MMCFD
| Maximum Generation of the Day |  |  | 14775.74 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 7.7498 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.6689 | 0 | 14.6752 | 0 | 0 | 0.13663 | 0 | 0 | 41.4807 | Gas | 91.3879 | Gas | 319330126.4512
| Chattogram Zone |  |  | 5.5509 | 42.0418 | 14.0392 | 0 | 1.94 | 0.08496 | 0 | 0.23808 | 63.8949 | Coal | 112.1598 | Coal | 757574790.1242
| Cumilla Zone |  |  | 17.5521 | 0 | 11.7611 | 0 | 0 | 0.50955 | 3.1459 | 0 | 32.9687 | HFO | 53.7815 | HFO | 979376184.428
| Mymensingh Zone |  |  | 0 | 0 | 4.8934 | 0 | 0 | 0.39311 | 0 | 0 | 5.2865 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.2828 | 0 | 0 | 0 | 0 | 0.07007 | 0 | 0 | 23.3529 | Hydro | 1.94 | Hydro | 194000
| Khulna Zone |  |  | 0 | 24.2545 | 0.23525 | 0 | 0 | 0.42192 | 22.5767 | 0 | 47.4884 | Solar | 4.2952 | Solar | 69202339.754
| Barishal Zone |  |  | 8.1529 | 43.7775 | 0.83846 | 0 | 0 | 0.003651 | 0 | 0 | 52.7725 | Import | 60.6818 | Import | 385505825.43
| Rajshahi Zone |  |  | 10.1802 | 0 | 3.5834 | 0 | 0 | 1.1255 | 34.9592 | 0 | 49.8482 | Wind | 0.23808 | Wind | 3502156.8
| Rangpur Zone |  |  | 0 | 2.086 | 3.7556 | 0 | 0 | 1.5498 | 0 | 0 | 7.3914
| Total |  |  | 91.3879 | 112.1598 | 53.7815 | 0 | 1.94 | 4.2952 | 60.6818 | 0.23808 | 324.4842
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 319330126.4512 |  | Hydro | 194000
|  |  |  | Coal | 757574790.1242 |  | Solar | 69202339.754
|  |  |  | HFO | 979376184.428 |  | Import | 385505825.43
|  |  |  | HSD | 0 |  | Wind | 3502156.8
[5 empty] | Total: | 251,46,85,422 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6647 | Peak Hr Flow | 898.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 49881781.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 34.9592 | Peak Hr Flow | 1453.54 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2202 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.1459 | Peak Hr Flow | 138.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2724 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 59.7698 | Peak Hr Flow | 2489.54 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 4 |  | 5363
|  |  |  | Chattogram |  | 0 |  | 1416
|  |  |  | Cumilla |  | 288 |  | 1583
|  |  |  | Mymensingh |  | 165 |  | 1325
|  |  |  | Sylhet |  | 89 |  | 667
|  |  |  | Khulna |  | 362 |  | 1967
|  |  |  | Barishal |  | 82 |  | 491
|  |  |  | Rajshahi |  | 287 |  | 1618
|  |  |  | Rangpur |  | 239 |  | 1185
|  |  |  | Total |  | 1516 |  | 15615
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 89
|  |  |  | Total Unavailable Capacity |  |  |  | 389
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:02 | 17:17 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-1 Project Work S/D Due to Tower
crossing
| 08:03 | 17:18 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-2 Project Work S/D Due to Tower
crossing
| 08:03 | 17:19 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 Project Work S/D Due to ,Project work
| 08:04 | 17:20 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 Project Work S/D Due to Project work
| 08:18 | 14:15 | Halishahar-Khulshi 132kV Ckt-1 Scheduled S/D from Halishahar 132/33kV end Due to Due to
OPGW Cable fault inspection in 4-Ckt Tower 1&11 CEpz area.
| 08:32 | 14:14 | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 Scheduled S/D Due to Due to OPGW Cable
fault inspection in 4-Ckt Tower 1 &11 CEpz area
| 08:48 | 18:07 | Bhulta-Ghorasal 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230/132kV end.
| 09:01 | 11:59 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to DCRM Test for CB.
|  | 09:11 | Sreepur 230/132/33kV S/S 132 kV BUS-2 is restored.
|  | 09:18 | Kulaura 132/33kV S/S TR-1 AB HT is restored.
|  | 09:21 | Kulaura 132/33kV S/S TR-1 AB LT is restored.
| 09:44 | 18:50 | Meghnaghat 400/230kV S/S ATR -03 HT Project Work S/D Due to For fire fighting work
| 09:44 | 18:50 | Meghnaghat 400/230kV S/S ATR -03 LT Project Work S/D
| 09:58 | 17:30 | Baghabari-Roppur 230kV Ckt-1 Project Work S/D from Baghabari 230/132kV end Due to SCADA
Integration & Commissioning এর Live CRP side Cable Termination কাজের জন্য।
|  | 09:59 | Mymensingh 132/33kV S/S Bus A is restored.
| 10:05 | 11:53 | Sitakunda 132/33kV S/S TRAFO-1 LT Forced S/D Due to PDB End Isolator and ACR Maintenance
| 10:22 |  | Barapukuria 275 MW TPP Unit-3 Tripped
| 10:45 | 14:37 | Mymensingh 132/33kV S/S Bus B Project Work S/D
|  | 10:51 | Barapukuria-Rangpur 132 kV Ckt-1 is restored.
| 11:05 | 11:53 | Sitakunda 132/33kV S/S TRAFO-1 HT Forced S/D Due to PDB End Isolator and ACR Maintenance
|  | 12:36 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 HT is restored.
|  | 12:38 | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 LT is restored.
| 14:28 | 15:29 | Palashbari 132/33kV S/S TR1-414T LT Forced S/D Due to red hot maintenance | [7 empty] | 20.0MW load
interrup.
| 14:28 | 15:29 | Palashbari 132/33kV S/S TR1-414T HT Forced S/D Due to red hot maintenance | [7 empty] | 20.0MW load
interrup.
|  | 16:15 | Chattak-Sylhet 132 kV Ckt-1 is restored.
| 16:35 |  | Barapukuria 275 MW TPP Unit-3 Synchronized
| 17:23 |  | Barapukuria 275 MW TPP Unit-3 Tripped
| 21:00 |  | Evening Peak Generation: 14703 MW.
| 01:35 |  | Barapukuria TPP Unit-1 Synchronized
| 03:41 |  | Barapukuria 275 MW TPP Unit-3 Synchronized
| 03:55 |  | Niamatpur 132/33kV S/S Transformer-1(407T) LT Forced S/D Due to 33 kV side Red Hot.
| 03:56 |  | Niamatpur 132/33kV S/S Transformer-1(407T) HT Forced S/D Due to 33 kV side Red Hot.
| 04:00 |  | Minimum Generation: 12772 MW.
| 05:50 |  | Barapukuria TPP Unit-1 Shutdown
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 31-07-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 344 | 8488800 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 140 | 3395636 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 852758 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 295 | 7193149 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 389520 | Liquid fuel shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 142 | 3191680 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 735274 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 468866 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 297000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 393840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 212755 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 81 | 1648473 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 106 | 1448640 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 663350 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 1189440 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 136628 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 431640 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 290 | 6900455 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3442800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 1926.42 | 41480704
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 110032.2 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 60480 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1174560 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 1940000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 213 | 4835240 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 91 | 2194618 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 55 | 657504 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 354255 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 463680 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 34 | 715680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 82 | 1373760 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24480 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 381382 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 430618 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2426291 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 457920 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 97 | 2278255 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 20 | 1736291 | FGMO
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 23459998 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 11 | 238080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 855 | 18581818.18 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 3216.36 | 63894942.38
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 194 | 5145000 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 355 | 7848500 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 36 | 876600 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1255669 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 3664945 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 569088 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2034425 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 182 | 3523680 | -
| Import (Tripura) |  | Import | 0 | 160 | 138 | 3145920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 732043 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 391910 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 2104440 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 31 | 184800 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 88 | 982080 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 509555 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1510.2 | 32968655
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 105732 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 154 | 2217600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1348800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 276380 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 460800 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 866160 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 281 | 5286472
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 70070 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 975000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 146 | 3391036.36 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1325760 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2430110 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 17 | 380928 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7544000 | Machine Problem
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 280 | 7236000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 986 | 23352904.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 898 | 21664727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 23 | 150720 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 84528 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 421920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1080 | 24254550 | U-2 Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2054 | 47488445
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1050 | 20203636 | AGC
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 399264 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2836000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 581 | 16613818.18 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5316940 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 439200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6960000 | Machine Problem
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3651 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2311 | 52772509.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 296328 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 409653 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 293852 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 156 | 3730182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 278 | 6450036 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 538901 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 529552 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 90 | 1119360 | Fuel shortage due to BPDB's payment delay
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 57 | 692064 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 27000 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1453.54 | 34959163 | Coal shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 309744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 492390 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2197.54 | 49848225
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 2086000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 1140278 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 43411.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2615302 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 201023 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1305360 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 220 | 7391374.8
Eastern Grid Total |  |  |  |  | 17440.562 | 7919.98 | 166983677.74
Western Grid Total |  |  |  |  | 11731.125 | 6782.54 | 157500553.98
National Grid Total |  |  |  |  | 29171.687 | 14702.52 | 324484231.72
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 31-07-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9864.14 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4291 | MW
i) Dhaka area |  |  | 5358.94 |  | MW | i) Khulna area |  |  |  | 1605 | MW
ii) Chattogram area |  |  | 1472.2 |  | MW | ii) Barishal area |  |  |  | 408.6 | MW
iii) Cumilla area |  |  | 1295 |  | MW | iii) Rajshahi area |  |  |  | 1331.4 | MW
iv) Mymensingh area |  |  | 1160 |  | MW | iv) Rangpur area |  |  |  | 946 | MW
v) Sylhet area |  |  | 578 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14155.14 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 21 | 18:30 | 67 | HaripurSBU | 140 | 08:00 | 133 | Narshingdi | 190 | 00:00 | 199 | Uttara | 88 | 20:00
2 | AKSML | 112.1 | 04:00 | 68 | Hasnabad | 84 | 22:00 | 134 | Natore | 126 | 19:30 | 200 | UttaraNew | 55 | 13:00
3 | Aftabnagar | 42 | 12:00 | 69 | Hathazari | 90 | 19:30 | 135 | Nawabganj | 66 | 22:00 | 201 | Zigatola | 90 | 13:00
4 | Agargaon | 108 | 13:00 | 70 | Hatirjheel | 65 | 15:00 | 136 | Netrakona | 136 | 18:30
5 | Agrabad | 60 | 12:00 | 71 | Ishurdi | 71 | 13:00 | 137 | New | 71.8 | 00:00
6 | Amnura | 30 | 22:00 | 72 | Jaldhaka | 74 | 06:00 | 138 | Niamatpur | 71 | 23:00
7 | Ashuganj | 102 | 01:00 | 73 | Jamalpur | 132 | 22:00 | 139 | Noapara | 40 | 19:00
8 | BSRM | 177 | 16:00 | 74 | Jashore | 147 | 20:00 | 140 | PHP | 10 | 18:00
9 | Bagerhat | 81 | 00:00 | 75 | Jhenaidah | 86 | 22:00 | 141 | Pabna | 92 | 00:00
10 | Bajitpur | 90 | 19:30 | 76 | Joydebpur | 148 | 20:00 | 142 | Palashbari | 126 | 00:00
11 | Bakerganj | 15.4 | 11:00 | 77 | Joypurhat | 56 | 13:00 | 143 | Panchagarh | 60 | 21:00
12 | Bakulia | 85 | 19:30 | 78 | Juldah | 16 | 08:00 | 144 | Patiya | 11 | 19:30
13 | Banani | 48.8 | 19:00 | 79 | KSRM | 32 | 08:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 4 | 10:00 | 80 | Kabirpur | 234 | 21:00 | 146 | Patuakhali | 67.2 | 19:00
15 | Barapukuria | 65 | 13:00 | 81 | Kachua | 98 | 19:00 | 147 | Payra | 32 | 03:00
16 | Barguna | 20 | 19:00 | 82 | Kaliganj | 38 | 13:00 | 148 | Postogola | 56 | 00:00
17 | Barishal | 101 | 12:00 | 83 | Kallyanpur | 126 | 13:00 | 149 | Pubail | 46 | 12:00
18 | Barishal-230 | 90 | 19:30 | 84 | Kalurghat | 33 | 23:00 | 150 | Purbachal | 28 | 19:00
19 | Baroaulia | 55 | 11:00 | 85 | Kamrangirchar | 72 | 00:00 | 151 | Purbasadipur | 133 | 22:00
20 | Baroirhat | 61 | 20:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 36 | 19:30
21 | Bashundhara | 194 | 12:00 | 87 | Kasba | 40 | 19:00 | 153 | Rahim | 53 | 02:00
22 | BashundharaCement | 6 | 00:00 | 88 | Kazla | 112 | 12:00 | 154 | Rajbari | 84 | 19:00
23 | Beanibazar | 84 | 18:30 | 89 | Keranigonj | 78 | 22:00 | 155 | Rajendrapur | 122 | 22:00
24 | Benapole | 70 | 13:00 | 90 | Khagrachori | 34 | 19:30 | 156 | Rajshahi | 112 | 13:00
25 | Bhaluka | 158 | 16:00 | 91 | Khulna | 49 | 19:30 | 157 | Rajshahi-230 | 89 | 23:00
26 | Bhandaria | 52 | 19:00 | 92 | Khulshi | 174 | 21:00 | 158 | Ramganj | 116 | 19:30
27 | Bhangura | 40 | 19:00 | 93 | Kishoreganj | 133 | 22:00 | 159 | Rampur | 42 | 22:00
28 | Bheramara(GK) | 62 | 13:00 | 94 | Kodda | 283 | 20:00 | 160 | Rangamati | 20 | 21:00
29 | Bhulta | 216 | 00:00 | 95 | Kulaura | 54 | 19:00 | 161 | Rangpur | 126 | 13:00
30 | Bog-Sherpur | 78 | 03:00 | 96 | Kurigram | 62 | 20:00 | 162 | Ruppur | 4.2 | 09:00
31 | Bogura | 184 | 23:00 | 97 | Kushtia | 130 | 19:30 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 64 | 21:00 | 98 | Laksam | 28 | 23:00 | 164 | Saidpur | 94 | 13:00
33 | Brahmanbaria | 144 | 19:30 | 99 | Lakshmipur | 51 | 19:30 | 165 | Santhia | 36 | 19:30
34 | Cantonment | 123 | 13:00 | 100 | Lalbag | 68 | 00:00 | 166 | Satkhira | 129 | 23:00
35 | Chandina | 40 | 10:00 | 101 | Lalmonirhat | 76 | 19:00 | 167 | Satmasjid | 100 | 13:00
36 | Chandpur | 90 | 19:30 | 102 | MI_Cement | 12 | 12:00 | 168 | Savar | 193 | 00:00
37 | Chandraghona | 34 | 12:00 | 103 | Madanganj | 41 | 08:00 | 169 | SevenRings | 15.83 | 01:00
38 | Chapai | 70 | 06:00 | 104 | Madaripur | 97 | 21:00 | 170 | ShahCement | 35 | 12:00
39 | Charfasson | 30 | 22:00 | 105 | Madartek | 81 | 23:00 | 171 | Shahjadpur | 72 | 19:30
40 | Charsaidpur | 45 | 02:00 | 106 | Madunaghat | 51 | 19:00 | 172 | Shahjibazar | 132 | 19:30
41 | Chauddagram | 75 | 19:00 | 107 | Magura | 62 | 13:00 | 173 | Shahmirpur | 46 | 21:00
42 | Chhatak | 33 | 19:00 | 108 | Mahasthangarh | 72 | 04:00 | 174 | Shariatpur | 79 | 00:00
43 | Chowmuhani | 139 | 21:00 | 109 | Maijdee | 44 | 19:30 | 175 | Sherpur | 154 | 20:00
44 | Chuadanga | 107 | 14:00 | 110 | Manikganj | 145 | 21:00 | 176 | Shikalbaha | 29 | 00:00
45 | Coxsbazar | 136 | 20:00 | 111 | Maniknagar | 72 | 13:00 | 177 | Shitalakhya | 56.6 | 13:00
46 | Cumilla(N) | 124 | 20:00 | 112 | Matarbari | 61 | 19:30 | 178 | Sholosohor | 43 | 12:00
47 | Cumilla(S) | 148 | 13:00 | 113 | Matuail | 74 | 00:00 | 179 | Shomvuganj | 50 | 19:00
48 | Daganbhuiyan | 39 | 19:00 | 114 | Metrorail_Motijheel | 15 | 16:00 | 180 | Shyampur | 146 | 00:00
49 | Daudkandi | 132 | 12:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 119 | 12:00
50 | DhakaUniversity | 46 | 00:00 | 116 | Millgate | 84 | 11:00 | 182 | Sirajganj | 112 | 00:00
51 | Dhamrai | 106 | 21:00 | 117 | Mirpur | 143 | 12:00 | 183 | Sitakunda | 34 | 22:00
52 | Dhanmondi | 89 | 12:00 | 118 | Mirsorai | 37 | 03:00 | 184 | Sonargaon | 131 | 06:00
53 | Dohazari | 112 | 19:30 | 119 | Mirzapur | 41 | 19:00 | 185 | Sreemongol | 91 | 19:30
54 | Faridpur | 154 | 22:00 | 120 | Mithapukur | 76 | 07:00 | 186 | Sreepur | 104 | 20:00
55 | Fatullah | 92 | 00:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 52.57 | 22:00
56 | Fenchuganj | 46 | 19:00 | 122 | Mogbazar | 40.1 | 13:00 | 188 | Sunamganj | 64 | 19:00
57 | Feni | 93 | 19:00 | 123 | Mongla | 39 | 00:00 | 189 | Sylhet | 126 | 19:00
58 | GPH | 1 | 00:00 | 124 | Motijheel | 38 | 13:00 | 190 | Sylhet_(South) | 67 | 12:00
59 | Ghatail | 100 | 19:00 | 125 | Muktagacha | 40 | 15:00 | 191 | TK | 26 | 19:30
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 110 | 22:00 | 192 | Tangail | 172 | 21:00
61 | Ghorashal-230 | 102 | 19:30 | 127 | Muradnagar | 52 | 19:00 | 193 | Taraganj | 35 | 19:00
62 | Goalpara | 36 | 13:00 | 128 | Mymensingh | 150 | 00:00 | 194 | Tasnim | 38 | 00:00
63 | Gollamari | 96 | 13:00 | 129 | Nabinagar | 104 | 00:00 | 195 | Thakurgaon | 108 | 00:00
64 | Gopalganj | 97 | 21:00 | 130 | Naogaon | 137 | 19:30 | 196 | Tongi | 122 | 11:00
65 | Gulshan | 84 | 15:00 | 131 | Narail | 61 | 19:00 | 197 | Ullahpara | 39 | 19:30
66 | Halishahar | 75 | 15:00 | 132 | Narinda | 55 | 13:00 | 198 | Ullon | 57 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 31-07-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14027.63 | 2238 |  | 16366.34
1:00 | 13662.17 | 2161 |  | 15920.17
2:00 | 13629.24 | 2072 |  | 15794.24
3:00 | 13458.03 | 2054 |  | 15604.03
4:00 | 13382.92 | 1951 |  | 15421.92
5:00 | 13336.05 | 1918 |  | 15340.05
6:00 | 13097.48 | 579 |  | 13702.48
7:00 | 12957.01 | 325 |  | 13297.01
8:00 | 12911.39 | 206 |  | 13126.39
9:00 | 12836.33 | 223 |  | 13069.33
10:00 | 12814.01 | 172 |  | 12994.01
11:00 | 13023.16 | 44 |  | 13069.16
12:00 | 13543.01 | 364 |  | 13923.01
13:00 | 13709.18 | 660 |  | 14399.18
14:00 | 13565.38 | 527 |  | 14116.1
15:00 | 13153.63 | 1066 |  | 14267.6
16:00 | 13079.16 | 632 |  | 13739.6
17:00 | 12968.29 | 0 |  | 12968.29
18:00 | 12755.01 | 0 |  | 12755.01
19:00 | 13873.32 | 117 |  | 13995.32
19:30 | 14575.19 | 1013 |  | 15634.19
20:00 | 14446.94 | 1303 |  | 15808.94
21:00 | 14702.52 | 1516 |  | 16286.52
22:00 | 14775.74 | 1249 |  | 16080.74
23:00 | 14769.57 | 1688 |  | 16533.57
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 31-07-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7501.62 | 6526.01 | 14027.63 | DAILY GENERATION CURVE
00:30 | 7425.62 | 6419.28 | 13844.9
01:00 | 7349.62 | 6312.55 | 13662.17 | 31-07-2026
01:30 | 7247.62 | 6398.085 | 13645.705
02:00 | 7145.62 | 6483.62 | 13629.24
02:30 | 7072.12 | 6471.515 | 13543.635
03:00 | 6998.62 | 6459.41 | 13458.03
03:30 | 6942.62 | 6477.855 | 13420.475
04:00 | 6886.62 | 6496.3 | 13382.92
04:30 | 6860.02 | 6499.465 | 13359.485
05:00 | 6833.42 | 6502.63 | 13336.05
05:30 | 6726.215 | 6490.55 | 13216.765
06:00 | 6619.01 | 6478.47 | 13097.48
06:30 | 6527.45 | 6499.795 | 13027.245
07:00 | 6435.89 | 6521.12 | 12957.01
07:30 | 6391.295 | 6542.905 | 12934.2
08:00 | 6346.7 | 6564.69 | 12911.39
08:30 | 6395.73 | 6478.13 | 12873.86
09:00 | 6444.76 | 6391.57 | 12836.33
09:30 | 6468.145 | 6357.025 | 12825.17
10:00 | 6491.53 | 6322.48 | 12814.01
10:30 | 6581.82 | 6336.765 | 12918.585
11:00 | 6672.11 | 6351.05 | 13023.16
11:30 | 6755.17 | 6527.915 | 13283.085
12:00 | 6838.23 | 6704.78 | 13543.01
12:30 | 6905.215 | 6720.88 | 13626.095
13:00 | 6972.2 | 6736.98 | 13709.18
13:30 | 6971.575 | 6665.705 | 13637.28
14:00 | 6970.95 | 6594.43 | 13565.38
14:30 | 6965.385 | 6394.12 | 13359.505
15:00 | 6959.82 | 6193.81 | 13153.63
15:30 | 6921.665 | 6194.73 | 13116.395
16:00 | 6883.51 | 6195.65 | 13079.16
16:30 | 6823.41 | 6200.315 | 13023.725
17:00 | 6763.31 | 6204.98 | 12968.29
17:30 | 6692.735 | 6168.915 | 12861.65
18:00 | 6622.16 | 6132.85 | 12755.01
18:30 | 6967.79 | 6346.375 | 13314.165
19:00 | 7313.42 | 6559.9 | 13873.32
19:30 | 7861.12 | 6714.07 | 14575.19
20:00 | 7695.12 | 6751.82 | 14446.94
20:30 | 7807.55 | 6767.18 | 14574.73 |  | Executive Engineer
21:00 | 7919.98 | 6782.54 | 14702.52 |  | Network Operation Division
21:30 | 7958.98 | 6780.15 | 14739.13
22:00 | 7997.98 | 6777.76 | 14775.74
22:30 | 7979.8 | 6792.855 | 14772.655
23:00 | 7961.62 | 6807.95 | 14769.57

## En-Curve
QF-LDC-12
Date | 31-07-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2443 | 1271 | 897 | 38 | 146 | 1480.01 | 222 | 4627 | 0 | 651.42 | 2244.2 | 0 | 0 | 8 | 2238 | DAILY ENERGY CURVE
00:30 | 2442.5 | 1273.5 | 897.5 | 38 | 144 | 1465.68 | 222 | 4623.5 | 0 | 592.42 | 2137.8 | 0 | 0 | 8 | 2199.5 | 31-07-2026
01:00 | 2442 | 1276 | 898 | 38 | 142 | 1451.35 | 222 | 4620 | 0 | 533.42 | 2031.4 | 0 | 0 | 8 | 2161
01:30 | 2449.5 | 1277.5 | 898 | 38 | 141 | 1465.385 | 221 | 4659.5 | 0 | 484.42 | 2003.9 | 0 | 0 | 7.5 | 2116.5 | Energy Generated | 324.4842 |  | MKWHr
02:00 | 2457 | 1279 | 898 | 38 | 140 | 1479.42 | 220 | 4699 | 0 | 435.42 | 1976.4 | 0 | 0 | 7 | 2072 | Energy not Served | 23.065 |  | MKWHr
02:30 | 2453 | 1291.5 | 898 | 38 | 140 | 1478.815 | 217.5 | 4664.5 | 0 | 434.92 | 1920.9 | 0 | 0 | 6.5 | 2063 | Total Energy Requirement | 347.5492 |  | MKWHr
03:00 | 2449 | 1304 | 898 | 38 | 140 | 1478.21 | 215 | 4630 | 0 | 434.42 | 1865.4 | 0 | 0 | 6 | 2054
03:30 | 2468 | 1317.5 | 898 | 38 | 134 | 1477.155 | 214.5 | 4641 | 0 | 430.92 | 1792.9 | 0 | 0 | 8.5 | 2002.5
04:00 | 2487 | 1331 | 898 | 38 | 128 | 1476.1 | 214 | 4652 | 0 | 427.42 | 1720.4 | 0 | 0 | 11 | 1951
04:30 | 2486 | 1328 | 898 | 38 | 132 | 1473.765 | 214.5 | 4654.5 | 0 | 427.42 | 1696.8 | 0 | 0 | 10.5 | 1934.5
05:00 | 2485 | 1325 | 898 | 38 | 136 | 1471.43 | 215 | 4657 | 0 | 427.42 | 1673.2 | 0 | 0 | 10 | 1918
05:30 | 2482.5 | 1268 | 898 | 38 | 131 | 1471.07 | 215.5 | 4654.5 | 8.575 | 418.92 | 1618.2 | 0 | 0 | 12.5 | 1248.5
06:00 | 2480 | 1211 | 898 | 38 | 126 | 1470.71 | 216 | 4652 | 17.15 | 410.42 | 1563.2 | 0 | 0 | 15 | 579
06:30 | 2485 | 1253.5 | 898 | 38 | 121 | 1474.535 | 218.5 | 4639.5 | 73.59 | 352.42 | 1462.2 | 0 | 0 | 11 | 452
07:00 | 2490 | 1296 | 898 | 38 | 116 | 1478.36 | 221 | 4627 | 130.03 | 294.42 | 1361.2 | 0 | 0 | 7 | 325
07:30 | 2490.5 | 1290 | 897.5 | 38 | 117 | 1473.845 | 221.5 | 4604.5 | 189.735 | 294.42 | 1313.7 | 0 | 0 | 3.5 | 265.5
08:00 | 2491 | 1284 | 897 | 38 | 118 | 1469.33 | 222 | 4582 | 249.44 | 294.42 | 1266.2 | 0 | 0 | 0 | 206
08:30 | 2452 | 1268.5 | 897.5 | 38 | 116 | 1465.47 | 222 | 4520 | 344.87 | 294.42 | 1251.1 | 0 | 0 | 4 | 214.5
09:00 | 2413 | 1253 | 898 | 38 | 114 | 1461.61 | 222 | 4458 | 440.3 | 294.42 | 1236 | 0 | 0 | 8 | 223
09:30 | 2387.5 | 1245.75 | 898 | 38 | 112 | 1434.425 | 222 | 4390.5 | 476.075 | 306.42 | 1310.5 | 0 | 0 | 4 | 197.5
10:00 | 2362 | 1238.5 | 898 | 38 | 110 | 1407.24 | 222 | 4323 | 511.85 | 318.42 | 1385 | 0 | 0 | 0 | 172
10:30 | 2395 | 1259.75 | 898.5 | 38 | 118 | 1426.125 | 222 | 4283 | 547.79 | 317.92 | 1412.5 | 0 | 0 | 0 | 108
11:00 | 2428 | 1281 | 899 | 38 | 126 | 1445.01 | 222 | 4243 | 583.73 | 317.42 | 1440 | 0 | 0 | 0 | 44
11:30 | 2430 | 1284.5 | 898 | 38 | 135 | 1448.94 | 222 | 4392.5 | 597.725 | 337.42 | 1499 | 0 | 0 | 0 | 204
12:00 | 2432 | 1288 | 897 | 38 | 144 | 1452.87 | 222 | 4542 | 611.72 | 357.42 | 1558 | 0 | 0 | 0 | 364
12:30 | 2431 | 1293.5 | 897.5 | 38 | 146 | 1448.34 | 222 | 4625 | 584.335 | 356.92 | 1583.5 | 0 | 0 | 0 | 512
13:00 | 2430 | 1299 | 898 | 38 | 148 | 1443.81 | 222 | 4708 | 556.95 | 356.42 | 1609 | 0 | 0 | 0 | 660
13:30 | 2398 | 1262 | 898 | 38 | 145 | 1447.22 | 222 | 4670 | 529.64 | 356.42 | 1665 | 0 | 0 | 6 | 593.5
14:00 | 2366 | 1225 | 898 | 38 | 142 | 1450.63 | 222 | 4632 | 502.33 | 356.42 | 1721 | 0 | 0 | 12 | 527
14:30 | 2401 | 1262.5 | 898 | 38 | 143 | 1450.16 | 219 | 4417.5 | 438.925 | 347.42 | 1730 | 0 | 0 | 14 | 796.5
15:00 | 2436 | 1300 | 898 | 38 | 144 | 1449.69 | 216 | 4203 | 375.52 | 338.42 | 1739 | 0 | 0 | 16 | 1066
15:30 | 2455.5 | 1282.5 | 897.5 | 38 | 138 | 1441.605 | 216 | 4225.5 | 295.98 | 330.71 | 1772.6 | 0 | 0 | 22.5 | 849
16:00 | 2475 | 1265 | 897 | 38 | 132 | 1433.52 | 216 | 4248 | 216.44 | 323 | 1806.2 | 0 | 0 | 29 | 632
16:30 | 2484.5 | 1261.5 | 897.5 | 38 | 133 | 1433.23 | 216 | 4263.5 | 173.395 | 329 | 1770.1 | 0 | 0 | 24 | 316
17:00 | 2494 | 1258 | 898 | 38 | 134 | 1432.94 | 216 | 4279 | 130.35 | 335 | 1734 | 0 | 0 | 19 | 0
17:30 | 2491.5 | 1257 | 898 | 38 | 128 | 1422.565 | 217 | 4304 | 80.085 | 351.5 | 1656 | 0 | 0 | 18 | 0
18:00 | 2489 | 1256 | 898 | 38 | 122 | 1412.19 | 218 | 4329 | 29.82 | 368 | 1578 | 0 | 0 | 17 | 0
18:30 | 2511.5 | 1267 | 897.5 | 38 | 131 | 1422.045 | 219 | 4533 | 14.91 | 526.71 | 1740 | 0 | 0 | 13.5 | 58.5
19:00 | 2534 | 1278 | 897 | 38 | 140 | 1431.9 | 220 | 4737 | 0 | 685.42 | 1902 | 0 | 0 | 10 | 117
19:30 | 2534 | 1362 | 898 | 38 | 144 | 1480.07 | 220 | 4968 | 0 | 687.42 | 2233.7 | 0 | 0 | 10 | 1013
20:00 | 2421 | 1277 | 898 | 38 | 140 | 1475.82 | 220 | 5027 | 0 | 726.42 | 2214.7 | 0 | 0 | 9 | 1303
20:30 | 2459.5 | 1315 | 898 | 38 | 139 | 1464.68 | 221 | 5062 | 0 | 726.92 | 2240.63 | 0 | 0 | 10 | 1409.5
21:00 | 2498 | 1353 | 898 | 38 | 138 | 1453.54 | 222 | 5097 | 0 | 727.42 | 2266.56 | 0 | 0 | 11 | 1516
21:30 | 2502.5 | 1326 | 898 | 38 | 136 | 1455.65 | 222 | 5129 | 0 | 723.42 | 2295.06 | 0 | 0 | 13.5 | 1382.5
22:00 | 2507 | 1299 | 898 | 38 | 134 | 1457.76 | 222 | 5161 | 0 | 719.42 | 2323.56 | 0 | 0 | 16 | 1249
22:30 | 2534.5 | 1311 | 898 | 38 | 134 | 1459.855 | 222 | 5162 | 0 | 673.42 | 2327.38 | 0 | 0 | 12.5 | 1468.5
23:00 | 2562 | 1323 | 898 | 38 | 134 | 1461.95 | 222 | 5163 | 0 | 627.42 | 2331.2 | 0 | 0 | 9 | 1688
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 31-07-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 158 | 47 | 470 | 180 | 1500 | 604 | Ishurdi-Ghorashal Ckt-1 | Export | 3895781.82
1:00 | 148 | 43 | 420 | 140 | 1524 | 568
2:00 | 151 | 46 | 440 | 148 | 1600 | 568 |  | Import | 0
3:00 | 154 | 44 | 460 | 146 | 1650 | 568
4:00 | 152 | 43 | 450 | 146 | 1632 | 582 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 154 | 44 | 460 | 144 | 1618 | 566
6:00 | 157 | 36 | 490 | 142 | 1658 | 552 |  | Import | 0
7:00 | 157 | 34 | 490 | 124 | 1644 | 574
8:00 | 157 | 33 | 480 | 120 | 1660 | 610 | Sirajganj-Sreepur Ckt-1 | Export | 2848000
9:00 | 186 | 46 | 520 | 136 | 1658 | 652
10:00 | 186 | 43 | 530 | 120 | 1700 | 628 |  | Import | 0
11:00 | 203 | 55 | 540 | 160 | 1800 | 684
12:00 | 200 | 55 | 580 | 178 | 1944 | 718 | Sirajganj-Sreepur Ckt-2 | Export | 2858000
13:00 | 160 | 26 | 510 | 154 | 1736 | 586
14:00 | 157 | 37 | 460 | 142 | 1620 | 266 |  | Import | 0
15:00 | 181 | 54 | 510 | 160 | 1724 | 624
16:00 | 186 | 54 | 530 | 186 | 1740 | 650 | Gopalganj-Aminbazar Ckt-1 | Export | 20110000
17:00 | 181 | 44 | 510 | 160 | 1668 | 586
18:00 | 165 | 31 | 470 | 134 | 1658 | 548 |  | Import | 0
18:30 | 167 | 33 | 490 | 136 | 1640 | 538
19:00 | 171 | 33 | 530 | 204 | 1740 | 610 | Gopalganj-Aminbazar Ckt-2 | Export | 20170000
19:30 | 131 | 11 | 420 | 144 | 1638 | 536
20:00 | 139 | 15 | 440 | 132 | 1634 | 582 |  | Import | 0
21:00 | 146 | 20 | 450 | 162 | 1606 | 594
22:00 | 137 | 19 | 420 | 180 | 1550 | 598 |  | Total Export | 49881781.82
23:00 | 147 | 29 | 420 | 172 | 1608 | 618 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 31-07-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 378 | 18:00 | 361 | 12:00 | Madunaghat | 400 | 02:00 | 393 | 13:00
Amtali | 412 | 04:00 | 405 | 10:00 | Meghnaghat | 384 | 18:30 | 367 | 12:00
Ashuganj | 398 | 18:00 | 381 | 13:00 | Mirsorai | 398 | 18:00 | 384 | 7:00
Bhulta | 392 | 18:00 | 373 | 12:00 | Payra | 413 | 03:00 | 407 | 12:00
Bibiana | 380 | 18:30 | 372 | 12:00 | Rahanpur | 401 | 18:30 | 390 | 19:30
BIPTC | 401 | 06:00 | 393 | 12:00 | Rampal | 397 | 18:00 | 384 | 13:00
Bogura | 385 | 18:30 | 370 | 23:00
Gopalganj | 392 | 18:30 | 380 | 12:00
Kaliakoir | 369 | 18:30 | 349 | 12:00
Korerhat | 398 | 18:00 | 388 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 18:00 | 218 | 12:00 | Ishurdi | 237 | 15:00 | 225 | 13:00
AKSML | 238.9 | 01:00 | 231 | 12:00 | Jhenaidah | 229 | 15:00 | 214 | 22:00
Aminbazar | 232 | 18:00 | 219 | 12:00 | Kachua | 230 | 05:00 | 224 | 08:00
Ashuganj | 226 | 18:00 | 215 | 00:00 | Kaliakoir | 230 | 18:30 | 215 | 12:00
Ashuganj-400 | 226 | 18:00 | 215 | 00:00 | Keranigonj | 228 | 18:30 | 216 | 12:00
Baghabari | 232 | 15:00 | 224 | 22:00 | Khulna(S) | 227 | 18:00 | 217 | 13:00
Barapukuria | 225 | 17:00 | 210 | 13:00 | Korerhat | 228 | 18:30 | 222 | 12:00
Barapukuria-230 | 225 | 17:00 | 210 | 13:00 | Madunaghat | 239 | 00:00 | 234 | 22:00
Barishal | 226 | 18:00 | 220 | 22:00 | Madunaghat-400 | 241 | 02:00 | 236 | 13:00
Bheramara | 235 | 15:00 | 222 | 13:00 | Maniknagar | 223 | 05:00 | 212 | 12:00
Bhulta | 225 | 18:00 | 214 | 12:00 | Meghnaghat | 232 | 18:00 | 213 | 00:00
Bibiana | 220 | 10:00 | 210 | 16:00 | Meghnaghat-400 | 228 | 18:30 | 217 | 12:00
BIPTC | 237 | 15:00 | 222 | 13:00 | Mirsorai | 233 | 06:00 | 226 | 12:00
Bogura | 241 | 18:00 | 231 | 13:00 | Naogaon | 228 | 18:30 | 209 | 23:00
Bogura-400 | 242 | 18:30 | 232 | 23:00 | Purbasadipur | 223 | 17:00 | 208 | 19:30
Borhanuddin | 230 | 18:00 | 226 | 02:00 | Rajshahi | 233 | 18:00 | 220 | 13:00
BSRM | 229 | 18:30 | 223 | 12:00 | Rampal | 228 | 18:30 | 216 | 13:00
Charfasson | 230 | 05:00 | 226 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 01:00 | 223 | 12:00 | Rampura | 224 | 18:30 | 212 | 12:00
Cumilla(N) | 224 | 18:00 | 216 | 12:00 | Shikalbaha | 239 | 00:00 | 235 | 12:00
Faridpur | 223 | 18:30 | 208 | 14:00 | Shyampur | 228 | 18:30 | 216 | 12:00
Fenchuganj | 221 | 05:00 | 217 | 00:00 | Siddhirganj | 227 | 18:00 | 215 | 12:00
Feni | 226 | 18:00 | 220 | 12:00 | Sirajgonj | 238 | 18:00 | 230 | 05:00
Ghorashal | 217 | 18:00 | 202 | 12:00 | Sreepur | 225 | 18:30 | 215 | 22:00
Ghorashal-230 | 217 | 18:00 | 202 | 12:00 | Tongi | 223 | 18:00 | 206 | 11:00
Gopalganj | 223 | 18:00 | 216 | 12:00
GPH | 235 | 01:00 | 229 | 23:00
Haripur | 225 | 18:00 | 215 | 12:00
Hasnabad | 227 | 17:00 | 216 | 11:00
Hathazari | 237 | 04:00 | 230 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 06:00 | 130 | 12:00 | Madartek | 137 | 01:00 | 125 | 00:00
Agargaon | 135 | 18:00 | 127 | 12:00 | Madunaghat | 139 | 00:00 | 135 | 12:00
Agrabad | 138 | 00:00 | 134 | 11:00 | Magura | 138 | 15:00 | 126 | 22:00
AKS | 135 | 00:00 | 132 | 11:00 | Mahasthangarh | 137 | 16:00 | 130 | 01:00
Aminbazar | 133 | 18:00 | 122 | 12:00 | Maijdee | 128 | 01:00 | 125 | 08:00
Amnura | 139 | 18:30 | 126 | 13:00 | Manikganj | 130 | 18:30 | 123 | 08:00
Ashuganj | 133 | 18:00 | 128 | 00:00 | Maniknagar | 131 | 04:00 | 124 | 12:00
Ashuganj-230 | 133 | 18:00 | 128 | 00:00 | Matarbari | 133 | 19:00 | 116 | 19:30
Bagerhat | 129 | 16:00 | 123 | 00:00 | Matuail | 134 | 18:00 | 128.4 | 13:00
Bajitpur | 125 | 09:00 | 118 | 00:00 | Metrorail_Motijheel | 131 | 04:00 | 124 | 12:00
Bakerganj | 132 | 08:00 | 128 | 13:00 | Metrorail_Uttara | 133 | 18:00 | 123 | 12:00
Bakulia | 139 | 05:00 | 136 | 09:00 | Millgate | 133 | 17:00 | 124 | 12:00
Banani | 138 | 06:00 | 129 | 12:00 | Mirpur | 132 | 03:00 | 121 | 12:00
Bangabhaban | 131 | 06:00 | 124 | 13:00 | Mirzapur | 130 | 15:00 | 122 | 12:00
Barapukuria | 137 | 17:00 | 125 | 13:00 | Mithapukur | 134 | 16:00 | 124 | 02:00
Barguna | 131 | 09:00 | 128 | 02:00 | MI_Cement | 135 | 18:00 | 125 | 00:00
Barishal | 132 | 18:00 | 128 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barishal-230 | 132 | 18:00 | 127 | 23:00 | Mogbazar | 140 | 18:00 | 131 | 12:00
Baroaulia | 138 | 05:00 | 134 | 12:00 | Mongla | 128 | 10:00 | 121 | 00:00
Baroirhat | 132 | 01:00 | 129 | 12:00 | Motijheel | 131 | 06:00 | 124 | 13:00
Bashundhara | 137 | 04:00 | 123 | 12:00 | Muktagacha | 128 | 18:00 | 116 | 12:00
BashundharaCement | 133 | 18:00 | 128 | 00:00 | Munshiganj | 132 | 18:00 | 126 | 13:00
Beanibazar | 123 | 20:00 | 118 | 18:30 | Muradnagar | 128 | 01:00 | 122 | 12:00
Benapole | 137 | 15:00 | 116 | 13:00 | Mymensingh | 127 | 18:00 | 108 | 22:00
Bhaluka | 128 | 10:00 | 119 | 22:00 | Nabinagar | 129 | 18:00 | 120 | 12:00
Bhandaria | 129 | 18:00 | 125 | 01:00 | Naogaon | 137 | 18:00 | 126 | 22:00
Bhangura | 135 | 15:00 | 129 | 13:00 | Narail | 138 | 15:00 | 125 | 13:00
Bheramara | 138 | 15:00 | 130 | 22:00 | Narinda | 131 | 04:00 | 124 | 12:00
Bheramara(GK) | 137 | 05:00 | 130 | 00:00 | Narshingdi | 127 | 18:00 | 118 | 00:00
Bhulta | 128 | 18:30 | 121 | 00:00 | Natore | 136 | 18:00 | 128 | 19:30
Bhulta-400 | 130 | 18:00 | 124 | 12:00 | Nawabganj | 138 | 18:30 | 130 | 12:00
Bog-Sherpur | 138 | 18:30 | 131 | 13:00 | Netrakona | 121 | 10:00 | 107 | 18:30
Bogura | 140 | 17:00 | 134 | 01:00 | New | 134 | 18:30 | 124 | 00:00
Bogura-230 | 140 | 18:00 | 133 | 13:00 | Niamatpur | 133 | 16:00 | 127 | 22:00
Brahmanbaria | 127 | 18:00 | 121 | 00:00 | Noapara | 133 | 18:00 | 124 | 13:00
Cantonment | 135 | 18:30 | 127 | 12:00 | Pabna | 136 | 18:00 | 129 | 13:00
Chandina | 130 | 18:00 | 125 | 12:00 | Palashbari | 133 | 16:00 | 124 | 06:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandpur | 134 | 01:00 | 128 | 08:00 | Panchagarh | 137 | 17:00 | 126 | 13:00
Chandraghona | 139 | 01:00 | 136 | 12:00 | Patiya | 139 | 00:00 | 133 | 19:30
Chapai | 133 | 19:00 | 126 | 22:00 | Patnitala | 134 | 18:30 | 126 | 13:00
Charsaidpur | 133 | 05:00 | 127 | 12:00 | Patuakhali | 131 | 01:00 | 128 | 13:00
Chauddagram | 130 | 01:00 | 126 | 12:00 | Payra | 135 | 10:00 | 131 | 13:00
Chhatak | 122 | 22:00 | 113 | 19:00 | PHP | 132 | 01:00 | 129 | 12:00
Chowmuhani | 128 | 01:00 | 125 | 09:00 | Postogola | 136 | 18:00 | 127 | 12:00
Chuadanga | 137 | 16:00 | 125 | 22:00 | Pubail | 130 | 19:00 | 118 | 00:00
Coxsbazar | 131 | 00:00 | 119 | 20:00 | Purbachal | 138 | 05:00 | 129 | 13:00
Cumilla(N) | 130 | 18:00 | 125 | 12:00 | Purbasadipur | 135 | 17:00 | 125 | 19:30
Cumilla(S) | 130 | 18:30 | 124 | 12:00 | Rahanpur | 134 | 18:00 | 129 | 22:00
Daganbhuiyan | 130 | 01:00 | 127 | 22:00 | Rahanpur-400 | 135 | 18:30 | 130 | 22:00
Daudkandi | 127 | 06:00 | 120 | 12:00 | Rahim | 134 | 18:00 | 128 | 13:00
DhakaUniversity | 137 | 18:00 | 130 | 12:00 | Rajbari | 126 | 18:00 | 119 | 14:00
Dhamrai | 130 | 18:30 | 123 | 00:00 | Rajendrapur | 127 | 10:00 | 118 | 22:00
Dhanmondi | 138 | 04:00 | 130 | 12:00 | Rajshahi | 134 | 18:00 | 125 | 13:00
Dohazari | 136 | 01:00 | 129 | 19:30 | Rajshahi-230 | 135 | 18:00 | 126 | 13:00
Faridpur | 128 | 18:00 | 121 | 14:00 | Ramganj | 129 | 01:00 | 124 | 07:00
Fatullah | 137 | 18:00 | 127 | 12:00 | Rampur | 139 | 01:00 | 134 | 12:00
Fenchuganj | 130 | 01:00 | 126 | 19:00 | Rampura | 138 | 06:00 | 129 | 12:00
Feni | 131 | 01:00 | 127 | 22:00 | Rangamati | 138 | 02:00 | 135 | 11:00
Feni-230 | 132 | 14:00 | 128 | 11:00 | Rangpur | 133 | 17:00 | 122 | 13:00
Ghatail | 126 | 15:00 | 115 | 23:00 | Ruppur | 138 | 06:00 | 131 | 13:00
Ghorashal | 131 | 16:00 | 121 | 12:00 | Saidpur | 135 | 19:00 | 124 | 13:00
Goalpara | 137 | 18:30 | 129 | 22:00 | Santhia | 136 | 15:00 | 130 | 20:00
Gollamari | 136 | 18:00 | 129 | 13:00 | Satkhira | 132 | 18:00 | 123 | 23:00
Gopalganj | 131 | 18:30 | 124 | 13:00 | Satmasjid | 135 | 18:30 | 127 | 12:00
Gopalganj-400 | 132 | 18:00 | 127 | 13:00 | Savar | 132 | 01:00 | 118 | 12:00
Gulshan | 137 | 06:00 | 129 | 13:00 | SevenRings | 130 | 19:30 | 121 | 00:00
Halishahar | 139 | 00:00 | 135 | 22:00 | ShahCement | 133 | 02:00 | 127 | 12:00
Haripur | 135 | 18:30 | 128 | 12:00 | Shahjadpur | 136 | 14:00 | 133 | 13:00
HaripurSBU | 134 | 18:00 | 127 | 00:00 | Shahjibazar | 127 | 20:00 | 121 | 00:00
Hasnabad | 134 | 02:00 | 128 | 12:00 | Shahmirpur | 140 | 00:00 | 135 | 22:00
Hathazari | 139 | 04:00 | 135 | 00:00 | Shariatpur | 130 | 18:00 | 126 | 00:00
Hatirjheel | 138 | 01:00 | 130 | 12:00 | Sherpur | 126 | 15:00 | 110 | 02:00
Ishurdi | 139 | 15:00 | 132 | 22:00 | Shikalbaha | 129 | 00:00 | 124 | 12:00
Jaldhaka | 132 | 15:00 | 122 | 13:00 | Shikalbaha-230 | 140 | 00:00 | 136 | 12:00
Jamalpur | 129 | 15:00 | 114 | 02:00 | Shitalakhya | 135 | 18:00 | 125 | 00:00
Jashore | 139 | 15:00 | 119 | 13:00 | Sholosohor | 138 | 00:00 | 135 | 11:00
Jhenaidah | 140 | 15:00 | 123 | 13:00 | Shomvuganj | 120 | 10:00 | 113 | 00:00
Jhenaidah-230 | 141 | 15:00 | 130 | 22:00 | Shyampur | 136 | 18:00 | 129 | 12:00
Joydebpur | 128 | 19:30 | 116 | 00:00 | Shyampur-230 | 137 | 18:00 | 128 | 12:00
Joypurhat | 134 | 18:00 | 126 | 13:00 | Siddhirganj | 135 | 18:00 | 129 | 12:00
Juldah | 139 | 00:00 | 135 | 19:30 | Sirajganj | 135 | 15:00 | 127 | 19:30
Kabirpur | 134 | 18:00 | 121 | 00:00 | Sitakunda | 138 | 00:00 | 134 | 22:00
Kachua | 131 | 01:00 | 128 | 07:00 | Sonargaon | 132 | 18:30 | 123 | 00:00
Kaliakoir | 136 | 18:30 | 127 | 12:00 | Sreemongol | 127 | 20:00 | 121 | 00:00
Kaliganj | 140 | 16:00 | 127 | 22:00 | Sreepur | 131 | 10:00 | 122 | 22:00
Kallyanpur | 131 | 18:00 | 122 | 12:00 | Srinagar | 138 | 18:00 | 130 | 12:00
Kalurghat | 139 | 02:00 | 136 | 09:00 | SSM | 140 | 01:00 | 138 | 12:00
Kamrangirchar | 138 | 04:00 | 120 | 12:00 | Sunamganj | 120 | 23:00 | 109 | 19:00
Kaptai | 140 | 5:00 | 138 | 12:00 | Sylhet | 124 | 06:00 | 120 | 19:00
Kasba | 128 | 18:00 | 121 | 12:00 | Sylhet_(South) | 124 | 06:00 | 119 | 19:00
Kazla | 131 | 06:00 | 123 | 12:00 | Tangail | 127 | 15:00 | 117 | 23:00
Keranigonj | 138 | 18:00 | 131 | 12:00 | Taraganj | 133 | 16:00 | 125 | 02:00
Khagrachori | 137 | 00:00 | 133 | 12:00 | Tasnim | 132 | 18:30 | 124 | 00:00
Khulna | 135 | 18:00 | 127 | 13:00 | Thakurgaon | 138 | 17:00 | 127 | 13:00
Khulna(S) | 136 | 18:00 | 129 | 13:00 | TK | 138 | 06:00 | 135 | 00:00
Khulshi | 137 | 04:00 | 132 | 13:00 | Tongi | 136 | 18:00 | 128 | 11:00
Kishoreganj | 125 | 10:00 | 115 | 22:00 | Ullahpara | 135 | 15:00 | 128 | 19:30
Kodda | 133 | 19:30 | 117 | 09:00 | Ullon | 137 | 05:00 | 130 | 12:00
Korerhat | 134 | 01:00 | 131 | 12:00 | Uttara | 132 | 18:00 | 125 | 00:00
KSRM | 138 | 00:00 | 135 | 10:00 | UttaraNew | 133 | 18:00 | 123 | 12:00
Kulaura | 129 | 08:00 | 124 | 19:00 | Zigatola | 139 | 18:30 | 130 | 13:00
Kurigram | 130 | 15:00 | 119 | 13:00
Kushtia | 133 | 15:00 | 125 | 13:00
Laksam | 131 | 07:00 | 126 | 00:00
Lakshmipur | 127 | 18:00 | 123 | 12:00
Lalbag | 138 | 18:30 | 130 | 12:00
Lalmonirhat | 130 | 16:00 | 120 | 13:00
Madanganj | 133 | 18:30 | 128 | 00:00
Madaripur | 131 | 18:00 | 128 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division