## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 03-08-2026 | [28 empty] | Date: | 03-08-2026 | [28 empty] | Date: | 03-08-2026 | [28 empty] | Date: | 03-08-2026 | [28 empty] | Date: | 03-08-2026 | [18 empty] | Date: | 03-08-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 32 | 35 | 34 | 15 | 80 | 0 | 35 | 35 | 0 | 0 | 135 | 280 | 0 | 55 | 300 | 0 | 0 | 0 | 17 | 12.5 | 21 | 0 | 0 | 101 | 16 | 11 | 0 | 14 | 50 | 15 | 17 | 12 | 12 | 0 | 222 | 94 | 2 | 1130 | 143 | 0 | 50 | 0 | 105 | 208 | 0 | 0 | 0 | 1224 | 0 | 13 | 8 | 0 | 350 | 0 | 51 | 10 | 215 | 39 | 51 | 58 | 184 | 7 | 19 | 105 | 174 | 52.2 | 0 | 23 | 320 | 0 | 293 | 40 | 0 | 154 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 18 | 7383.7 | 898 | 0 | 0 | 24 | 37 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1163 | 0 | 0 | 0 | 1474.68 | 0 | 0 | 0 | 37 | 35 | 0 | 93 | 0 | 52.2 | 0 | 0 | 14 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 145 | 0 | 113 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 800 | 565 | 17 | 6593.88 | 13977.58 | 101.63
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 17 | 17 | 34 | 15 | 50 | 0 | 35 | 17 | 0 | 0 | 129 | 280 | 0 | 35 | 290 | 0 | 0 | 0 | 17 | 12.5 | 21 | 0 | 0 | 100 | 16 | 18 | 0 | 5 | 50 | 15 | 0 | 12 | 12 | 0 | 222 | 94 | 2 | 1130 | 17 | 0 | 50 | 0 | 101 | 207 | 0 | 0 | 0 | 1224 | 0 | 13 | 8 | 0 | 350 | 0 | 51 | 10 | 214 | 39 | 51 | 58 | 42 | 0 | 19 | 105 | 176 | 52.2 | 0 | 23 | 320 | 0 | 292 | 40 | 0 | 153 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6927.7 | 898 | 0 | 0 | 24 | 37 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1161 | 0 | 0 | 0 | 1473.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 14 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 145 | 0 | 112 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 700 | 568 | 17 | 6309.21 | 13236.91 | 101.62
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 17 | 17 | 34 | 15 | 48 | 0 | 35 | 0 | 0 | 0 | 135 | 280 | 0 | 35 | 300 | 0 | 0 | 0 | 17 | 12.5 | 21 | 0 | 0 | 97 | 16 | 18 | 0 | 1 | 0 | 15 | 0 | 12 | 12 | 0 | 222 | 95 | 2 | 1130 | 17 | 0 | 50 | 0 | 100 | 207 | 0 | 0 | 0 | 1224 | 0 | 13 | 8 | 0 | 350 | 0 | 51 | 10 | 213 | 39 | 51 | 58 | 34 | 0 | 19 | 105 | 168 | 52.2 | 0 | 23 | 315 | 0 | 292 | 40 | 0 | 153 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6840.7 | 898 | 0 | 0 | 0 | 37 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 1470.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 14 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 263 | 0 | 0 | 144 | 31 | 114 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 700 | 569 | 17 | 6328.73 | 13169.43 | 101.61
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 17 | 34 | 15 | 48 | 0 | 0 | 0 | 0 | 0 | 136 | 280 | 0 | 35 | 317 | 0 | 0 | 0 | 17 | 12.5 | 21 | 0 | 0 | 100 | 16 | 19 | 0 | 9 | 0 | 15 | 0 | 12 | 12 | 0 | 222 | 95 | 3 | 1130 | 16 | 0 | 50 | 0 | 103 | 207 | 0 | 0 | 0 | 1224 | 0 | 13 | 8 | 0 | 350 | 0 | 51 | 10 | 214 | 39 | 39 | 58 | 34 | 0 | 19 | 103 | 162 | 52.2 | 0 | 24 | 315 | 0 | 295 | 40 | 0 | 154 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6787.7 | 898 | 0 | 0 | 0 | 37 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 1482.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 0 | 143 | 50 | 113 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 700 | 565 | 17 | 6350.16 | 13137.86 | 101.6
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 17 | 34 | 15 | 48 | 0 | 0 | 0 | 0 | 0 | 133 | 280 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 12.5 | 21 | 0 | 0 | 100 | 16 | 19 | 0 | 12 | 0 | 15 | 0 | 12 | 12 | 0 | 219 | 94 | 3 | 1130 | 16 | 0 | 50 | 0 | 102 | 207 | 0 | 0 | 0 | 1224 | 0 | 11 | 8 | 0 | 350 | 0 | 51 | 10 | 210 | 39 | 0 | 59 | 34 | 0 | 19 | 105 | 160 | 52.2 | 0 | 24 | 320 | 0 | 295 | 40 | 0 | 153 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 6673.7 | 898 | 0 | 0 | 0 | 36 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 1469.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 144 | 51 | 112 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 700 | 565 | 17 | 6342.19 | 13015.89 | 101.59
05:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 17 | 34 | 15 | 48 | 0 | 0 | 0 | 0 | 0 | 131 | 280 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 12.5 | 21 | 0 | 0 | 95 | 16 | 19 | 0 | 13 | 0 | 15 | 0 | 12 | 12 | 0 | 218 | 93 | 3 | 1130 | 18 | 0 | 50 | 0 | 97 | 207 | 0 | 0 | 0 | 1135 | 0 | 13 | 8 | 0 | 350 | 0 | 51 | 10 | 212 | 39 | 0 | 58 | 34 | 0 | 19 | 94 | 156 | 52.2 | 0 | 24 | 315 | 0 | 295 | 40 | 0 | 153 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 6567.7 | 898 | 0 | 0 | 0 | 36 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 1481.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 144 | 51 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 700 | 567 | 17 | 6328.12 | 12895.82 | 101.58
06:00 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 34 | 15 | 48 | 0 | 0 | 0 | 0 | 0 | 139 | 280 | 0 | 0 | 290 | 0 | 0 | 1 | 17 | 12.5 | 21 | 0 | 0 | 91 | 16 | 19 | 0 | 0 | 0 | 15 | 0 | 12 | 12 | 0.2 | 218 | 94 | 2 | 1130 | 16 | 0 | 50 | 0 | 95 | 207 | 0 | 0 | 0 | 870 | 0 | 13 | 8 | 0 | 354 | 0 | 51 | 10 | 215 | 39 | 0 | 57 | 34 | 0 | 19 | 105 | 152 | 17 | 1 | 22 | 305 | 0 | 295 | 40 | 0 | 145 | 0 | 8 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 48 | 0.13 | 47 | 0 | 0 | 0.54 | 12 | 6262.37 | 898 | 0 | 0 | 0 | 36 | 38 | 0 | 0 | 0 | 0 | 0 | 1.94 | 1165 | 0 | 0 | 0 | 1488.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 1.36 | 0 | 0 | 0 | 0.19 | 143 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 144 | 51 | 113 | 0 | 0 | 0 | 0 | 0 | 0.2 | 2 | 0 | 16 | 307 | 100 | 220 | 0 | 679 | 556 | 17 | 6288.97 | 12551.34 | 101.58
07:00 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 17 | 34 | 15 | 48 | 0 | 0 | 0 | 0 | 0 | 137 | 280 | 0 | 0 | 299 | 0 | 0 | 2 | 17 | 12.5 | 22 | 0 | 0 | 96 | 16 | 19 | 0 | 5 | 0 | 15 | 0 | 12 | 12 | 1.17 | 219 | 95 | 0 | 1130 | 16 | 0 | 46 | 0 | 90 | 207 | 0 | 0 | 0 | 612 | 1 | 13 | 8 | 0 | 354 | 0 | 51 | 10 | 215 | 38 | 0 | 57 | 34 | 0 | 19 | 34 | 146 | 8 | 3 | 23 | 310 | 0 | 295 | 40 | 0 | 148 | 2 | 8 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 48 | 0.1 | 47 | 0 | 0.1 | 2.02 | 12 | 5957.89 | 898 | 0 | 0 | 0 | 36 | 38 | 0 | 0 | 0 | 0 | 0 | 17.78 | 1165 | 0 | 0 | 0 | 1478.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 4.97 | 7 | 0 | 0 | 0.67 | 144 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0.07 | 147 | 52 | 114 | 0 | 0 | 0 | 0 | 0 | 0.7 | 31 | 0.04 | 16 | 307 | 100 | 220 | 0 | 678 | 563 | 17 | 6378.7 | 12336.59 | 101.56
08:00 | 0 | 17 | 52 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 34 | 15 | 48 | 0 | 0 | 0 | 0 | 0 | 144 | 280 | 0 | 0 | 321 | 0 | 0 | 5 | 17 | 12.5 | 22 | 0 | 0 | 97 | 16 | 20 | 0 | 9 | 0 | 15 | 0 | 12 | 12 | 0.74 | 220 | 94 | 0 | 1130 | 16 | 0 | 46 | 0 | 91 | 207 | 0 | 0 | 0 | 612 | 3 | 13 | 8 | 0 | 355 | 0 | 51 | 10 | 213 | 39 | 0 | 57 | 34 | 0 | 19 | 34 | 156 | 8 | 10 | 23 | 310 | 0 | 289 | 40 | 0 | 151 | 5 | 8 | 0 | 53 | 0 | 0 | 0 | 101 | 17 | 48 | 0.5 | 47 | 0 | 0 | 3.49 | 12 | 6033.23 | 873 | 0 | 0 | 0 | 35 | 38 | 0 | 0 | 0 | 0 | 0 | 30.14 | 1165 | 0 | 0 | 0 | 1477.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 6.89 | 10 | 0 | 0 | 4 | 144 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0.36 | 147 | 52 | 104 | 2 | 0 | 0 | 0 | 0 | 0.5 | 19 | 0.08 | 16 | 307 | 110 | 220 | 0 | 700 | 563 | 17 | 6340.86 | 12374.09 | 101.55
09:00 | 0 | 17 | 52 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 17 | 34 | 15 | 48 | 0 | 0 | 0 | 0 | 0 | 139 | 300 | 0 | 0 | 304 | 0 | 0 | 11 | 17 | 12 | 22 | 0 | 0 | 101 | 16 | 19 | 0 | 0 | 0 | 15 | 17 | 12 | 12 | 3.06 | 220 | 94 | 0 | 1130 | 16 | 0 | 44 | 0 | 90 | 205 | 0 | 0 | 0 | 612 | 4 | 13 | 8 | 0 | 354 | 0 | 51 | 10 | 205 | 39 | 0 | 57 | 34 | 0 | 19 | 17 | 152 | 8 | 23 | 23 | 320 | 0 | 293 | 40 | 0 | 153 | 9 | 8 | 0 | 52 | 0 | 0 | 0 | 102 | 17 | 48 | 0.66 | 47 | 0 | 0 | 9.82 | 12 | 6065.54 | 873 | 0 | 0 | 0 | 35 | 38 | 0 | 0 | 0 | 0 | 0 | 29.57 | 1165 | 0 | 0 | 0 | 1470.25 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 8 | 21.46 | 13 | 0 | 0 | 4 | 144 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0.32 | 165 | 53 | 109 | 12 | 0 | 0 | 0 | 0 | 1.6 | 60 | 0.09 | 16 | 307 | 110 | 220 | 0 | 700 | 565 | 17 | 6422.29 | 12487.83 | 101.54
10:00 | 0 | 17 | 52 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 17 | 42 | 15 | 81 | 0 | 17 | 0 | 0 | 0 | 132 | 300 | 0 | 5 | 302 | 0 | 0 | 10 | 17 | 12 | 14 | 0 | 0 | 95 | 16 | 19 | 0 | 0 | 0 | 15 | 17 | 12 | 12 | 4.53 | 221 | 95 | 0 | 1130 | 16 | 0 | 45 | 0 | 94 | 184 | 0 | 0 | 0 | 612 | 0 | 20 | 8 | 0 | 354 | 0 | 45 | 10 | 200 | 35 | 6 | 57 | 34 | 0 | 19 | 17 | 172 | 12 | 3 | 23 | 305 | 0 | 293 | 40 | 0 | 145 | 9 | 8 | 0 | 52 | 0 | 0 | 0 | 102 | 17 | 57 | 0.68 | 114 | 0 | 0.1 | 16.92 | 12 | 6171.23 | 873 | 0 | 0 | 0 | 28 | 38 | 0 | 0 | 0 | 0 | 0 | 31 | 1155 | 0 | 0 | 0 | 1477.33 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 30.85 | 30 | 0 | 0 | 6 | 145 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 0.61 | 162 | 52 | 107 | 5 | 0 | 0 | 0 | 0 | 2.2 | 54 | 0.04 | 16 | 307 | 110 | 220 | 0 | 1050 | 560 | 17 | 6793.03 | 12964.26 | 101.53
11:00 | 0 | 17 | 52 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 53 | 15 | 79 | 0 | 35 | 17 | 0 | 0 | 145 | 300 | 0 | 35 | 310 | 0 | 0 | 16 | 17 | 12 | 14 | 0 | 0 | 94 | 16 | 18 | 0 | 0 | 0 | 15 | 17 | 12 | 12 | 1.54 | 176 | 94 | 0 | 1130 | 16 | 0 | 45 | 0 | 89 | 184 | 0 | 0 | 0 | 902 | 0 | 50 | 8 | 0 | 354 | 0 | 44 | 5 | 209 | 37 | 42 | 57 | 50 | 0 | 19 | 17 | 172 | 25 | 4 | 23 | 310 | 0 | 293 | 41 | 0 | 143 | 9 | 8 | 0 | 51 | 0 | 0 | 0 | 102 | 17 | 58 | 9.1 | 117 | 0 | 0.4 | 27.93 | 12 | 6630.97 | 873 | 0 | 0 | 0 | 30 | 38 | 0 | 0 | 0 | 0 | 0 | 30 | 1132 | 0 | 0 | 0 | 1473.32 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 45.06 | 64 | 0 | 0 | 19 | 148 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 156 | 52 | 105 | 5 | 0 | 0 | 0 | 0 | 3.9 | 52 | 0.05 | 16 | 280 | 110 | 220 | 0 | 1050 | 560 | 17 | 6752.33 | 13383.3 | 101.52
12:00 | 0 | 34 | 52 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 17 | 53 | 15 | 78 | 0 | 35 | 25 | 0 | 0 | 126 | 275 | 0 | 35 | 326 | 0 | 0 | 10 | 17 | 12 | 21 | 0 | 0 | 97 | 16 | 19 | 0 | 12 | 0 | 15 | 17 | 12 | 12 | 1.66 | 176 | 94 | 0 | 1130 | 16 | 0 | 44 | 5 | 93 | 184 | 0 | 0 | 0 | 992 | 8 | 53 | 8 | 0 | 354 | 0 | 51 | 5 | 207 | 37 | 51 | 57 | 70 | 0 | 19 | 17 | 178 | 25 | 19 | 22 | 310 | 0 | 293 | 41 | 0 | 147 | 12 | 8 | 0 | 33 | 0 | 0 | 0 | 102 | 17 | 58 | 15.33 | 116 | 0 | 1 | 18.5 | 12 | 6784.49 | 872 | 0 | 0 | 0 | 27 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 1144 | 0 | 0 | 0 | 1485.93 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 36.41 | 46 | 0 | 0 | 28 | 148 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 2.8 | 158 | 52 | 111 | 2 | 0 | 0 | 0 | 0 | 6.7 | 106 | 0.25 | 16 | 307 | 110 | 220 | 0 | 1050 | 560 | 17 | 6879.09 | 13663.58 | 101.52
13:00 | 0 | 34 | 52 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 17 | 49 | 15 | 93 | 0 | 35 | 54 | 0 | 0 | 115 | 250 | 0 | 35 | 326 | 0 | 0 | 9 | 143.42 | 12 | 21 | 0 | 0 | 90 | 16 | 19 | 0 | 8 | 0 | 15 | 17 | 12 | 12 | 1.23 | 176 | 94 | 0 | 1130 | 16 | 0 | 44 | 8 | 95 | 183 | 0 | 0 | 0 | 1037 | 16 | 53 | 8 | 0 | 354 | 0 | 51 | 5 | 205 | 37 | 51 | 56 | 103 | 0 | 19 | 34 | 190 | 25 | 39 | 15 | 305 | 0 | 293 | 41 | 0 | 140 | 12 | 8 | 0 | 33 | 0 | 0 | 0 | 102 | 17 | 58 | 13.2 | 116 | 0 | 1.5 | 35.04 | 12 | 7033.39 | 873 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 53 | 1147 | 0 | 0 | 0 | 1484.03 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 10.78 | 49 | 0 | 0 | 33 | 148 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 4.33 | 158 | 52 | 106 | 1 | 0 | 0 | 0 | 0 | 7.9 | 120 | 0.21 | 16 | 307 | 100 | 220 | 0 | 1045 | 555 | 17 | 6869.25 | 13902.64 | 101.51
14:00 | 0 | 105 | 52 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 12 | 17 | 34 | 15 | 80 | 0 | 35 | 54 | 0 | 0 | 125 | 250 | 0 | 35 | 321 | 0 | 0 | 4 | 143.42 | 12 | 21 | 0 | 0 | 90 | 16 | 20 | 0 | 2 | 0 | 15 | 17 | 12 | 12 | 0.59 | 176 | 94 | 0 | 1130 | 16 | 0 | 44 | 8 | 97 | 183 | 0 | 0 | 0 | 1210 | 17 | 53 | 8 | 0 | 354 | 0 | 51 | 5 | 205 | 40 | 51 | 56 | 103 | 0 | 19 | 106 | 196 | 25 | 50 | 15 | 305 | 0 | 280 | 41 | 0 | 134 | 12 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 58 | 14.1 | 116 | 0 | 1.7 | 32.76 | 12 | 7319.57 | 828 | 0 | 0 | 0 | 34 | 38 | 0 | 0 | 0 | 0 | 0 | 57 | 1155 | 0 | 0 | 0 | 1479.73 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 14.81 | 40 | 0 | 0 | 25.89 | 130 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 3.28 | 156 | 53 | 109 | 7 | 0 | 0 | 0 | 0 | 7.2 | 164 | 0.35 | 16 | 276 | 100 | 180 | 0 | 1000 | 545 | 17 | 6699.26 | 14018.83 | 101.51
15:00 | 0 | 105 | 52 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 17 | 17 | 34 | 0 | 80 | 0 | 35 | 54 | 0 | 0 | 128 | 250 | 0 | 35 | 322 | 0 | 0 | 6 | 143.42 | 12 | 21 | 0 | 0 | 92 | 16 | 20 | 0 | 0 | 0 | 15 | 17 | 12 | 12 | 2.57 | 174 | 92 | 0 | 1130 | 16 | 0 | 45 | 8 | 96 | 184 | 0 | 0 | 0 | 1160 | 16 | 53 | 8 | 0 | 351 | 0 | 44 | 5 | 209 | 37 | 52 | 56 | 137 | 0 | 19 | 114 | 198 | 37 | 39 | 15 | 310 | 0 | 305 | 41 | 0 | 141 | 3 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 58 | 7.02 | 116 | 0 | 1.1 | 22.95 | 12 | 7311.06 | 873 | 0 | 0 | 0 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 44 | 1124 | 0 | 0 | 0 | 1477.99 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 12.31 | 7 | 0 | 0 | 25.59 | 134 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 2.78 | 157 | 51 | 109 | 8 | 0 | 0 | 0 | 0 | 2.9 | 112 | 0.1 | 16 | 279 | 100 | 220 | 0 | 1024 | 555 | 17 | 6706.67 | 14017.73 | 101.5
16:00 | 0 | 105 | 52 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 17 | 17 | 34 | 1 | 80 | 0 | 35 | 54 | 0 | 0 | 115 | 250 | 0 | 35 | 322 | 0 | 0 | 1 | 143.42 | 12 | 21 | 0 | 0 | 91 | 16 | 18 | 0 | 1 | 0 | 15 | 17 | 12 | 12 | 1.39 | 172 | 95 | 0 | 1130 | 16 | 0 | 49 | 8 | 90 | 183 | 0 | 0 | 0 | 1145 | 6 | 55 | 8 | 0 | 351 | 0 | 44 | 5 | 199 | 20 | 51 | 56 | 179 | 0 | 19 | 114 | 196 | 52.2 | 37 | 23 | 305 | 0 | 368 | 41 | 0 | 149 | 2 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 58 | 6.01 | 116 | 0 | 0.2 | 21.69 | 8 | 7344.91 | 873 | 0 | 0 | 0 | 40 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 1152 | 0 | 0 | 0 | 1475.91 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 8 | 12.65 | 15 | 0 | 0 | 10.95 | 139 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 1.2 | 157 | 51 | 110 | 7 | 25 | 0 | 0 | 0 | 2.7 | 91 | 0.23 | 16 | 275 | 100 | 220 | 0 | 992 | 557 | 17 | 6717.64 | 14062.55 | 101.5
17:00 | 0 | 105 | 52 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 17 | 17 | 34 | 45 | 80 | 0 | 55 | 54 | 0 | 0 | 115 | 250 | 0 | 35 | 323 | 0 | 0 | 2 | 143.42 | 12 | 21 | 0 | 0 | 87 | 16 | 18 | 0 | 0 | 0 | 15 | 17 | 12 | 12 | 0.39 | 172 | 93 | 2 | 1130 | 16 | 0 | 50 | 8 | 102 | 183 | 0 | 0 | 0 | 1145 | 3 | 51 | 8 | 0 | 353 | 0 | 51 | 5 | 192 | 20 | 51 | 56 | 176 | 5 | 11 | 102 | 184 | 52.2 | 23 | 23 | 300 | 0 | 368 | 41 | 0 | 140 | 2 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 58 | 2.29 | 116 | 0 | 0.2 | 3.44 | 12 | 7334.94 | 873 | 0 | 0 | 0 | 43 | 38 | 0 | 0 | 0 | 0 | 0 | 22 | 1156 | 0 | 0 | 0 | 1478.02 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 8 | 5.83 | 15 | 0 | 0 | 9.16 | 139 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0.87 | 157 | 50 | 109 | 6 | 38 | 0 | 0 | 0 | 1.7 | 41 | 0.18 | 16 | 274 | 100 | 180 | 0 | 906 | 545 | 17 | 6526.76 | 13861.7 | 101.49
18:00 | 0 | 105 | 52 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 17 | 17 | 34 | 52 | 81 | 4 | 55 | 90 | 0 | 0 | 115 | 250 | 0 | 35 | 300 | 0 | 0 | 1 | 143.42 | 12 | 21 | 0 | 0 | 86 | 16 | 20 | 0 | 0 | 17 | 15 | 17 | 12 | 12 | 0.06 | 172 | 110 | 2 | 1130 | 16 | 0 | 50 | 8 | 96 | 183 | 0 | 0 | 0 | 1155 | 0 | 53 | 8 | 0 | 356 | 0 | 51 | 5 | 198 | 20 | 51 | 56 | 177 | 27 | 19 | 104 | 172 | 52.2 | 5 | 23 | 305 | 0 | 368 | 41 | 0 | 133 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 58 | 0.93 | 116 | 0 | 0.1 | 0.31 | 12 | 7400.02 | 873 | 0 | 0 | 0 | 43 | 38 | 0 | 0 | 0 | 0 | 0 | 3 | 1158 | 0 | 0 | 0 | 1472.98 | 0 | 0 | 0 | 35 | 60 | 0 | 0 | 0 | 8 | 2.37 | 5 | 0 | 0 | 2.08 | 139 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0.17 | 156 | 49 | 110 | 2 | 65 | 0 | 0 | 0 | 0.3 | 9 | 0.02 | 16 | 277 | 100 | 220 | 0 | 851 | 540 | 17 | 6479.92 | 13879.94 | 101.49
19:00 | 0 | 105 | 52 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 54 | 17 | 71 | 71 | 81 | 14 | 55 | 162 | 0 | 0 | 115 | 250 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 12 | 21 | 0 | 0 | 97 | 16 | 28 | 0 | 0 | 46 | 15 | 18 | 12 | 12 | 0 | 171 | 110 | 2 | 1130 | 60 | 0 | 50 | 8 | 102 | 183 | 0 | 0 | 0 | 1224 | 0 | 53 | 8 | 0 | 355 | 0 | 51 | 5 | 201 | 20 | 61 | 56 | 186 | 27 | 19 | 100 | 178 | 52.2 | 0 | 23 | 305 | 0 | 368 | 41 | 20 | 151 | 0 | 8 | 0 | 51 | 0 | 0 | 0 | 101 | 17 | 67 | 0 | 115 | 0 | 0 | 0 | 8 | 7829.62 | 872 | 0 | 0 | 32 | 56 | 38 | 0 | 0 | 100 | 0 | 15 | 0 | 1158 | 0 | 0 | 0 | 1477.45 | 0 | 0 | 0 | 57 | 70 | 11 | 100 | 0 | 8 | 0 | 0 | 12 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 156 | 51 | 108 | 0 | 78 | 0 | 100 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1050 | 570 | 17 | 7145.45 | 14975.07 | 101.48
19:30 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 54 | 17 | 88 | 109 | 81 | 12 | 55 | 162 | 0 | 0 | 115 | 260 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 12 | 21 | 0 | 0 | 95 | 16 | 37 | 0 | 0 | 50 | 15 | 36 | 12 | 12 | 0 | 171 | 110 | 2 | 1130 | 162 | 0 | 50 | 8 | 90 | 183 | 0 | 0 | 0 | 1224 | 0 | 53 | 8 | 0 | 354 | 0 | 51 | 5 | 185 | 20 | 89 | 56 | 167 | 27 | 8 | 104 | 154 | 52.2 | 0 | 23 | 290 | 0 | 368 | 41 | 20 | 140 | 0 | 8 | 0 | 51 | 0 | 0 | 0 | 101 | 17 | 67 | 0 | 152 | 0 | 0 | 0 | 12 | 7975.62 | 872 | 0 | 0 | 30 | 53 | 38 | 0 | 0 | 100 | 0 | 15 | 0 | 1153 | 0 | 0 | 0 | 1471.56 | 0 | 0 | 0 | 57 | 70 | 15 | 101 | 0 | 8 | 0 | 0 | 14 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 156 | 51 | 108 | 0 | 84 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1050 | 575 | 17 | 7218.56 | 15194.18
20:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 51.7 | 17 | 88 | 128 | 81 | 12 | 55 | 162 | 0 | 0 | 143 | 250 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 12 | 21 | 0 | 0 | 85 | 16 | 38 | 0 | 2 | 50 | 15 | 36 | 12 | 12 | 0 | 217 | 110 | 2 | 1130 | 158 | 0 | 50 | 8 | 93 | 184 | 0 | 0 | 0 | 1224 | 0 | 55 | 8 | 0 | 354 | 0 | 51 | 5 | 181 | 20 | 88 | 56 | 172 | 28 | 8 | 103 | 148 | 52.2 | 0 | 23 | 295 | 0 | 368 | 40 | 20 | 133 | 0 | 8 | 0 | 52 | 0 | 0 | 0 | 101 | 17 | 67 | 0 | 152 | 0 | 0 | 0 | 12 | 8045.32 | 872 | 0 | 0 | 31 | 48 | 38 | 0 | 0 | 100 | 0 | 15 | 0 | 1150 | 0 | 0 | 0 | 1473.43 | 0 | 0 | 0 | 57 | 70 | 15 | 101 | 0 | 8 | 0 | 0 | 14 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 239 | 0 | 0 | 156 | 53 | 105 | 0 | 85 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 180 | 0 | 1050 | 581 | 17 | 7185.43 | 15230.75 | 101.48
21:00 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 49.5 | 17 | 88 | 126 | 81 | 14 | 55 | 159 | 0 | 0 | 133 | 250 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 0 | 96 | 16 | 37 | 0 | 6 | 50 | 15 | 54.36 | 12 | 12 | 0 | 218 | 110 | 2 | 1130 | 152 | 0 | 50 | 8 | 92 | 186 | 0 | 0 | 0 | 1224 | 0 | 105 | 8 | 0 | 355 | 0 | 51 | 5 | 192 | 20 | 89 | 57 | 187 | 28 | 8 | 104 | 132 | 52.2 | 0 | 23 | 295 | 0 | 368 | 40 | 20 | 148 | 0 | 8 | 0 | 52 | 0 | 0 | 0 | 101 | 17 | 67 | 0 | 153 | 0 | 0 | 0 | 12 | 8080.48 | 872 | 0 | 0 | 30 | 47 | 38 | 0 | 0 | 150 | 0 | 15 | 0 | 1155 | 0 | 0 | 0 | 1475.3 | 0 | 0 | 0 | 57 | 70 | 15 | 101 | 0 | 8 | 0 | 0 | 14 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 156 | 51 | 107 | 0 | 85 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1050 | 581 | 36 | 7293.3 | 15373.78 | 101.47
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 46.7 | 17 | 86 | 141 | 81 | 12 | 55 | 144 | 0 | 0 | 131 | 250 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 0 | 89 | 16 | 38 | 0 | 5 | 50 | 15 | 54.36 | 12 | 12 | 0 | 219 | 110 | 2 | 1130 | 148 | 0 | 50 | 8 | 98 | 187 | 0 | 0 | 0 | 1224 | 0 | 150 | 8 | 0 | 320 | 0 | 51 | 5 | 188 | 20 | 74 | 49 | 190 | 28 | 8 | 102 | 136 | 52.2 | 0 | 23 | 300 | 0 | 368 | 40 | 20 | 138 | 0 | 8 | 0 | 31 | 0 | 0 | 0 | 101 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 12 | 8098.68 | 873 | 0 | 0 | 29 | 43 | 38 | 0 | 0 | 150 | 0 | 0 | 0 | 1155 | 0 | 0 | 0 | 1476.42 | 0 | 0 | 0 | 57 | 70 | 0 | 101 | 0 | 8 | 0 | 0 | 14 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 156 | 51 | 110 | 0 | 85 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 180 | 0 | 1050 | 581.53 | 17 | 7207.95 | 15306.63 | 101.47
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 46.7 | 17 | 38 | 140 | 81 | 13 | 55 | 108 | 0 | 0 | 126 | 250 | 0 | 0 | 278 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 0 | 89 | 16 | 26 | 0 | 0 | 50 | 15 | 17 | 12 | 12 | 0 | 220 | 110 | 2 | 1130 | 152 | 0 | 50 | 8 | 97 | 187 | 0 | 0 | 0 | 1224 | 0 | 100 | 8 | 0 | 310 | 0 | 51 | 5 | 179 | 20 | 58 | 50 | 186 | 27 | 8 | 103 | 148 | 52.2 | 0 | 23 | 300 | 0 | 368 | 40 | 38 | 136 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 101 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 12 | 7833.32 | 873 | 0 | 0 | 29 | 43 | 38 | 0 | 0 | 50 | 0 | 0 | 0 | 1149 | 0 | 0 | 0 | 1474.68 | 0 | 0 | 0 | 57 | 70 | 0 | 101 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 156 | 51 | 109 | 0 | 49 | 0 | 90 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 180 | 0 | 1050 | 581.53 | 17 | 6982.21 | 14815.53 | 101.46
Total KWH | 0 | 1270080 | 918240 | 0 | 0 | 0 | 0 | 0 | 8334000 | 0 | 0 | 376200 | 436680 | 1094832 | 968640 | 1644458 | 87698 | 669269 | 1179360 | 0 | 0 | 3171491 | 6537927 | 0 | 535975 | 7448449 | 0 | 0 | 80080 | 1866000 | 306000 | 500760 | 0 | 0 | 2258182 | 371345 | 533760 | 0 | 108960 | 360733 | 356112 | 386827 | 296640 | 294720 | 16559 | 4879113 | 2395345 | 22560 | 27185454.54 | 1190982 | 0 | 1165920 | 109882.8 | 2337636 | 4520774 | 0 | 0 | 0 | 25429088 | 57780 | 1080581 | 217454 | 0 | 8722400 | 0 | 1223882 | 187200 | 5049000 | 768096 | 980160 | 1318280 | 2445600 | 183120 | 374450 | 1944840 | 4039680 | 899894 | 265336 | 527072 | 7443000 | 0 | 7862000 | 958000 | 104400 | 3494536.36 | 68329 | 198000 | 0 | 995520 | 0 | 0 | 0 | 2427730 | 429840 | 1330800 | 65156 | 2227200 | 0 | 6000 | 205380 | 283680 | 170031128.7 | 21203636 | 0 | 0 | 178560 | 844672 | 912000 | 0 | 0 | 531341 | 0 | 47952 | 407520 | 27658180 | 0 | 0 | 0 | 34777818 | 0 | 0 | 0 | 400896 | 822432 | 34213 | 593056 | 0 | 480610 | 204144 | 341860 | 107720 | 0 | 176992 | 3462545 | 0 | 0 | 0 | 0 | 0 | 6043564 | 0 | 15660 | 3790000 | 1114036 | 2738975 | 67381 | 725433 | 0 | 674100 | 0 | 40138.56 | 889200 | 1804 | 419616 | 7200000 | 2452000 | 5274380 | 0 | 21607273 | 13893818.18 | 451200 | 160584725.74 | 330615854.44

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 04-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-08-2026 | during | 04-08-2026 | during | 04-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 353 | 340 | 412 | 412 | 370 | 370 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 126 | 133 | 335 | 335 | 150 | 150 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 14 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 326 | 300 | 335 | 335 | 320 | 320 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 49.5 | 53.97 | 53.97 | 0 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 126 | 149.36 | 149.36 | 125 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 12 | 33 | 33 | 13 | 13 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 52 | 0 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 78 | 81 | 300 | 300 | 81 | 81 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 53 | 88 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 88 | 105 | 105 | 17 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 25 | 159 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 10 | 0 | 22 | 0 | 22 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 275 | 250 | 583 | 583 | 583 | 583 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1484 | 1912.92 | 5797.64 | 5775.64 | 2000.42 | 2378.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 5 | 8 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 8 | 0 | 9 | 0 | 9 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 176 | 218 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 184 | 186 | 215 | 220 | 215 | 220 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 93 | 92 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 15 | 15 | 24 | 24 | 24 | 24 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 2 | 0 | 5 | 0 | 5 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 19 | 37 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.66 | 0 | 3.54 | 0 | 3.54 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 17 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 94 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 97 | 96 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 16 | 152 | 163 | 163 | 16 | 83 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 992 | 1224 | 1224 | 1224 | 900 | 900 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 12 | 6 | 12 | 8 | 12 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1130 | 1130 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 2943.66 | 3470.36 | 4091.4 | 4135.86 | 2977.54 | 3151
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 207 | 192 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 354 | 355 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 0 | 342.01 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 37 | 20 | 41.65 | 41.65 | 40 | 40 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 5 | 5 | 52.82 | 52.82 | 15 | 15 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 195 | 195 | 8 | 8 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 53 | 105 | 150 | 150 | 50 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 23 | 24 | 24 | 16 | 16 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 57 | 57 | 163 | 163 | 59 | 59 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 70 | 187 | 200 | 200 | 80 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 178 | 132 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 8 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 104 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 28 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 89 | 115 | 115 | 51 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 19 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1173 | 1416.2 | 2736.44 | 2680.44 | 1318.46 | 1516.46
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-08-2026 | during | 04-08-2026 | during | 04-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 15.33 | 0 | 15 | 0 | 15 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 153 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 67 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 18.5 | 0 | 39 | 0 | 39 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | 09:00-12:00 &17:00-23:00hrs 24MW & rest time 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 35 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 237.83 | 249 | 522.6 | 516.5 | 293.1 | 287
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 40 | 40 | 40 | 40 | 40 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 30 | 30 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 148 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 33 | 52 | 86 | 86 | 53 | 53 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 101 | 101 | 101 | 101 | 101 | plant availability zero
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 18 | 18 | 8 | 8 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 293 | 368 | 250 | 260 | 250 | 260 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 946 | 1032 | 1079 | 1089 | 906 | 916
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 872 | 872 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 30 | 30 | 30 | 30 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 27 | 47 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 40 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 150 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1144 | 1155 | 1165 | 1165 | 1165 | 1165 | AGC+FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2121 | 2307 | 3210 | 3135 | 2463 | 2388
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1050 | 1050 | 1050 | 1050 | 1050 | 1050 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 110 | 100 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 560 | 581 | 581.53 | 581.53 | 551.53 | 551.53 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 36 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.25 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3407.64 | 2280.25 | 2310 | 2549.53 | 2548.53 | 2282.53 | 2281.53
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 36.41 | 0 | 48.25 | 0 | 48.25 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 15 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 148 | 140 | 214 | 214 | 150 | 150 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 252 | 232 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 14 | 26 | 26 | 26 | 26 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 101 | 100 | 100 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 90 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 57 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 2.8 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1485.93 | 1475.3 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 28 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 46 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2042.14 | 2112.3 | 3219.87 | 3005.12 | 2486.49 | 2356.74
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 52 | 51 | 52 | 52 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 156 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 85 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.7 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 111 | 107 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 2 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 106 | 0 | 161 | 0 | 161 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 435.7 | 564 | 648 | 454 | 483 | 324
System Total |  |  |  |  | 28843.2 | 29252.637 | 13663.58 | 15373.78 | 23854.48 | 23340.09 | 15210.54 | 15599.15
Forecast Scenario (04-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13980 |  | 3237.45 |  | 17370
|  |  |  | 1:00 | 13240 |  | 3495.3 |  | 16900
|  |  |  | 2:00 | 13170 |  | 3476.2 |  | 16810
|  |  |  | 3:00 | 13140 |  | 3380.7 |  | 16680
|  |  |  | 4:00 | 13020 |  | 3294.75 |  | 16470
|  |  |  | 5:00 | 12900 |  | 3218.35 |  | 16270
|  |  |  | 6:00 | 12560 |  | 3275.65 |  | 15990
|  |  |  | 7:00 | 12340 |  | 3027.35 |  | 15510
|  |  |  | 8:00 | 12380 |  | 3017.8 |  | 15540
|  |  |  | 9:00 | 12490 |  | 2989.15 |  | 15620
|  |  |  | 10:00 | 12970 |  | 2645.35 |  | 15740
|  |  |  | 11:00 | 13390 |  | 2062.8 |  | 15550
|  |  |  | 12:00 | 13670 |  | 2702.65 |  | 16500
|  |  |  | 13:00 | 13910 |  | 2607.15 |  | 16640
|  |  |  | 14:00 | 14020 |  | 2406.6 |  | 16540
|  |  |  | 15:00 | 14020 |  | 2568.95 |  | 16710
|  |  |  | 16:00 | 14070 |  | 2196.5 |  | 16370
|  |  |  | 17:00 | 13870 |  | 2091.45 |  | 16060
|  |  |  | 18:00 | 13880 |  | 1910 |  | 15880
|  |  |  | 18:30 | 14500 |  | 1528 |  | 16100
|  |  |  | 19:00 | 14980 |  | 2330.2 |  | 17420
|  |  |  | 19:30 | 15200 |  | 2339.75 |  | 17650
|  |  |  | 20:00 | 15240 |  | 2072.35 |  | 17410
|  |  |  | 21:00 | 15380 |  | 2502.1 |  | 18000
|  |  |  | 22:00 | 15310 |  | 1995.95 |  | 17400
|  |  |  | 23:00 | 14850 |  | 2530.75 |  | 17500
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 16500.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2502
Probable Maximum Demand at Evening Peak: |  |  | 18000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15380.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 328.78 MKWHr. |  | 442 | 200 | 350 | 380 | 170 | 320 | 140 | 280 | 220 | 2502
*** This report is generated digitally from Operation Information System (OIS) at 10:37 hrs on 04-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 03-08-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13663.58 | MW | 12:00 Hr. | Energy Generated |  |  | 330.6159 |  | MKWHr.
| Day Peak Demand |  |  | 16501.58 | MW | 12:00 Hr. | Energy Unserverd |  |  | 65.145 |  | MKWHr.
| Evening Peak Generation |  |  | 15373.78 | MW | 21:00 Hr. | Energy Demand |  |  | 395.7609 |  | MKWHr.
| Evening Peak Demand |  |  | 17811.78 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.5 |  | °C
| Minimum Generation of the Day |  |  | 12336.59 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 651.22 |  | MMCFD
| Maximum Generation of the Day |  |  | 15373.78 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.3941 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.2986 | 0 | 11.0474 | 0 | 0 | 0.08008 | 0 | 0 | 37.4261 | Gas | 89.4184 | Gas | 310126058.9612
| Chattogram Zone |  |  | 4.5433 | 52.6145 | 12.0581 | 0 | 4.8791 | 0.074339 | 0 | 0.10896 | 74.2784 | Coal | 127.8778 | Coal | 870381794.465
| Cumilla Zone |  |  | 17.8608 | 0 | 8.0613 | 0 | 0 | 0.26534 | 4.0397 | 0 | 30.227 | HFO | 43.2836 | HFO | 792903979.502
| Mymensingh Zone |  |  | 0 | 0 | 4.2715 | 0 | 0 | 0.27654 | 0 | 0 | 4.5481 | HSD | 1.2054 | HSD | 31549296.2
| Sylhet Zone |  |  | 23.4832 | 0 | 0 | 0 | 0 | 0.068329 | 0 | 0 | 23.5515 | Hydro | 4.8791 | Hydro | 487911.3
| Khulna Zone |  |  | 0 | 27.6582 | 1.0712 | 0.53134 | 0 | 0.40752 | 22.1156 | 0 | 51.7839 | Solar | 2.9093 | Solar | 47339200.4648
| Barishal Zone |  |  | 7.7264 | 42.7011 | 0.87082 | 0 | 0 | 0.001804 | 0 | 0 | 51.3001 | Import | 60.9331 | Import | 390204097.14
| Rajshahi Zone |  |  | 9.5061 | 0 | 2.4389 | 0 | 0 | 0.73866 | 34.7778 | 0 | 47.4615 | Wind | 0.10896 | Wind | 1602801.6
| Rangpur Zone |  |  | 0 | 4.904 | 3.4644 | 0.6741 | 0 | 0.99672 | 0 | 0 | 10.0393
| Total |  |  | 89.4184 | 127.8778 | 43.2836 | 1.2054 | 4.8791 | 2.9093 | 60.9331 | 0.10896 | 330.6159
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 310126058.9612 |  | Hydro | 487911.3
|  |  |  | Coal | 870381794.465 |  | Solar | 47339200.4648
|  |  |  | HFO | 792903979.502 |  | Import | 390204097.14
|  |  |  | HSD | 31549296.2 |  | Wind | 1602801.6
[5 empty] | Total: | 244,45,95,139 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.2036 | Peak Hr Flow | 872.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 54289800 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 34.7778 | Peak Hr Flow | 1475.30 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2480 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 4.0397 | Peak Hr Flow | 132.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 3125 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 60.0211 | Peak Hr Flow | 2479.30 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 491 |  | 6244
|  |  |  | Chattogram |  | 164 |  | 1534
|  |  |  | Cumilla |  | 297 |  | 1673
|  |  |  | Mymensingh |  | 340 |  | 1414
|  |  |  | Sylhet |  | 171 |  | 779
|  |  |  | Khulna |  | 317 |  | 2096
|  |  |  | Barishal |  | 125 |  | 539
|  |  |  | Rajshahi |  | 283 |  | 1714
|  |  |  | Rangpur |  | 145 |  | 1097
|  |  |  | Total |  | 2333 |  | 17090
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 89
|  |  |  | Total Unavailable Capacity |  |  |  | 389
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 17:13 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 Scheduled S/D Due to Project work
| 08:01 | 17:14 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 Scheduled S/D Due to Project work
| 08:01 | 17:13 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-1 Project Work S/D
| 08:01 | 17:14 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-2 Project Work S/D
|  | 08:35 | Sylhet 132/33kV S/S T1 LT is restored.
|  | 08:35 | Sylhet 132/33kV S/S T1 LT is restored.
|  | 08:35 | Sylhet 132/33kV S/S T1 HT is restored.
| 09:41 | 18:16 | Madunaghat-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
taken by korerhat
| 09:51 | 12:40 | GPH 230/33kV S/S Transformer -2 (D07) HT Forced S/D Due to need emergency maintenance in
transformer-02
| 09:57 | 18:17 | Jhenaidah 230/132kV S/S Transformer-3 LT Project Work S/D Due to DFDR & NLDC intregation
and testing works
| 09:58 | 18:16 | Jhenaidah 230/132kV S/S Transformer-3 HT Project Work S/D Due to DFDR & NLDC intregation
and testing works
| 10:00 | 18:14 | Korerhat 400/230/132kV S/S Meghnaghat-2 Project Work S/D Due to For Project work
| 10:02 | 18:24 | Korerhat 400/230/132kV S/S ATR-3(7103T) LT Project Work S/D Due to For project work
| 10:03 | 18:22 | Korerhat 400/230/132kV S/S ATR-3(7103T) HT Project Work S/D Due to For project work
| 10:12 | 13:05 | Korerhat 400/230/132kV S/S Chowmuhani-4 Project Work S/D Due to For project work
| 10:24 | 11:11 | Bagerhat 132/33kV S/S Transformer-2 (413 T) LT Scheduled S/D Due to Pbs emergency
maintenance work
| 10:25 | 11:10 | Bagerhat 132/33kV S/S Transformer-2 (413 T) HT Scheduled S/D Due to Pbs emergency
maintenance work
| 10:38 | 17:07 | Bogura(New)-Naogaon 132 kV Ckt-1 Project Work S/D from Naogaon 132/33kV end Due to Old
bay dismantle work
| 11:38 | 13:01 | Pubail 132/33kV S/S TRX-2 LT Forced S/D Due to Pbs work
| 11:53 | 01:17 | Cumilla(S) 132/33kV S/S TR-4 HT Scheduled S/D
| 11:53 | 01:17 | Cumilla(S) 132/33kV S/S TR-4 LT Scheduled S/D Due to Redhot rectify work on 33kv balutopa | [7 empty] | 30.0MW load
|  |  | feeder by BPDB. | [7 empty] | interrup.
| 12:00 |  | Day Peak Generation: 13664 MW.
| 12:13 | 12:34 | Rangpur-Saidpur 132kV Ckt-2 Tripped from Rangpur 132/33kV end showing Distance Relay
(21) relays Due to Unknown
|  | 13:05 | Korerhat 400/230/132kV S/S Chowmuhani-4 is restored.
| 13:12 |  | Bogura West- Baropukuria North 230KV ckt-1 syn.
| 13:13 |  | Bogura West- Baropukuria North 230KV ckt-2 syn.
| 15:37 | 17:41 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Scheduled S/D Due to T-2 TR Ground Wire
Maintenance.
| 15:38 | 17:41 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Scheduled S/D Due to T-2 TR Ground Wire
Maintenance.
| 15:40 | 16:30 | Narshingdi 132/33kV S/S T-4 HT Scheduled S/D Due to T-4 BUS DS-2 (T-CLAMP) Hotspot
Maintenance Work.
| 15:40 | 16:30 | Narshingdi 132/33kV S/S T-4 LT Scheduled S/D Due to T-4 BUS DS-2 (T-CLAMP) Hotspot
Maintenance work.
|  | 16:01 | Mirsorai 400/230/33kV S/S Bus-2 (400KV) is restored.
|  | 18:14 | Korerhat 400/230/132kV S/S Meghnaghat-2 is restored.
| 19:19 | 19:40 | Mongla 132/33kV S/S T-2 LT Tripped showing Lockout Relay relays Due to A short circuit | [7 empty] | 30.0MW load
|  |  | occurred on the 33 kv rupsha oil feeder due to snake climbing onto the feeder. | [7 empty] | interrup.
| 21:00 |  | Evening Peak Generation: 15373 MW.
| 23:38 | 00:40 | Kasba 132/33kV S/S TR-1 LT Scheduled S/D Due to shutdown taken by pbs for load side ds | [7 empty] | 15.0MW load
|  |  | red hot maintenance | [7 empty] | interrup.
| 23:38 | 00:40 | Kasba 132/33kV S/S TR-1 HT Scheduled S/D Due to shutdown taken by pbs for load side ds
red hot maintenance
| 01:52 | 03:01 | Bhaluka 132/33kV S/S 03. Transformer-03 LT Tripped showing MVAJM relays Due to Earth | [7 empty] | 17.0MW load
|  |  | fault | [7 empty] | interrup.
| 06:07 | 07:32 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Scheduled S/D Due to For replacing the | [7 empty] | 25.0MW load
|  |  | damaged fuse of the auxiliary transformer. | [7 empty] | interrup.
| 06:08 | 07:31 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D Due to For replacing the | [7 empty] | 25.0MW load
|  |  | damaged fuse of the auxiliary transformer. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 03-08-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8334000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 133 | 3171491 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 14 | 87698 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7448449 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 49.5 | 376200 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 126 | 968640 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 669269 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 535975 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 12 | 306000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 500760 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 918240 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 81 | 1644458 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 88 | 1094832 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1270080 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 159 | 1179360 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 80080 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 436680 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 250 | 6537927 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 1866000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 1912.92 | 37426139
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 109882.8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 57780 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1165920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 218 | 4879113 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 186 | 4520774 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 92 | 2337636 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 15 | 356112 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 360733 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 296640 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 22560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 37 | 533760 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 16559 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 371345 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 386827 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2395345 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 294720 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 96 | 2258182 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 152 | 1190982 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 25429088 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 108960 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1130 | 27185454.54 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 3470.36 | 74278373.34
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 192 | 5049000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 355 | 8722400 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 768096 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 187200 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 217454 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1223882 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 105 | 1080581 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 527072 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 57 | 1318280 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 187 | 2445600 | -
| Import (Tripura) |  | Import | 0 | 160 | 132 | 4039680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 899894 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 8 | 374450 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 104 | 1944840 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 183120 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 980160 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 265336 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1416.2 | 30227045
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 65156 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 153 | 2227200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 67 | 1330800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 205380 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 283680 | From 00:00-16:00 hrs 12MW&17:00-24:00 hrs 24MW dis
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 429840 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 249 | 4548056
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 68329 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 958000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 104400 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 148 | 3494536.36 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 52 | 995520 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 101 | 2427730 | plant availability zero
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 198000 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7443000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 7862000 | Gas shortage
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1032 | 23551515.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 872 | 21203636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 178560 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 47 | 844672 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 47952 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 407520 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 150 | 531341 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1155 | 27658180 | AGC+FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2307 | 51783861
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1050 | 21607273 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 419616 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 100 | 2452000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 581 | 13893818.18 | U-2 Under maint.
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5274380 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 36 | 451200 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7200000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1804 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2310 | 51300091.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 204144 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 15 | 34213 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 3462545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 232 | 6043564 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 14 | 107720 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 480610 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 101 | 593056 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 822432 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 57 | 400896 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 15660 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1475.3 | 34777818 | AGC
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 176992 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 341860 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2112.3 | 47461510
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 674100 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 51 | 1114036 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 156 | 3790000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 85 | 725433 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 40138.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 107 | 2738975 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 67381 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 889200 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 564 | 10039263.56
Eastern Grid Total |  |  |  |  | 17440.562 | 8080.48 | 170031128.7
Western Grid Total |  |  |  |  | 11731.125 | 7293.3 | 160584725.74
National Grid Total |  |  |  |  | 29171.687 | 15373.78 | 330615854.44
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 03-08-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10222.56 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4575.1 | MW
i) Dhaka area |  |  | 5752.76 |  | MW | i) Khulna area |  |  |  | 1779 | MW
ii) Chattogram area |  |  | 1411.8 |  | MW | ii) Barishal area |  |  |  | 413.5 | MW
iii) Cumilla area |  |  | 1376 |  | MW | iii) Rajshahi area |  |  |  | 1430.6 | MW
iv) Mymensingh area |  |  | 1074 |  | MW | iv) Rangpur area |  |  |  | 952 | MW
v) Sylhet area |  |  | 608 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14797.66 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 17 | 20:00 | 67 | HaripurSBU | 105 | 00:00 | 133 | Narshingdi | 152 | 00:00 | 199 | Uttara | 100 | 13:00
2 | AKSML | 15 | 23:00 | 68 | Hasnabad | 102 | 21:00 | 134 | Natore | 123 | 19:00 | 200 | UttaraNew | 58 | 23:00
3 | Aftabnagar | 46 | 00:00 | 69 | Hathazari | 85 | 19:00 | 135 | Nawabganj | 59.7 | 19:30 | 201 | Zigatola | 98 | 13:00
4 | Agargaon | 132 | 13:00 | 70 | Hatirjheel | 92 | 16:00 | 136 | Netrakona | 113 | 22:00
5 | Agrabad | 70 | 12:00 | 71 | Ishurdi | 66 | 18:00 | 137 | New | 88 | 11:00
6 | Amnura | 30 | 21:00 | 72 | Jaldhaka | 77 | 20:00 | 138 | Niamatpur | 74 | 21:00
7 | Ashuganj | 94 | 00:00 | 73 | Jamalpur | 114 | 23:00 | 139 | Noapara | 44 | 15:00
8 | BSRM | 198 | 11:00 | 74 | Jashore | 171 | 19:00 | 140 | PHP | 10 | 18:00
9 | Bagerhat | 84 | 22:00 | 75 | Jhenaidah | 87 | 22:00 | 141 | Pabna | 92 | 17:00
10 | Bajitpur | 77 | 23:00 | 76 | Joydebpur | 151 | 22:00 | 142 | Palashbari | 140 | 20:00
11 | Bakerganj | 13.6 | 19:00 | 77 | Joypurhat | 54 | 19:30 | 143 | Panchagarh | 70 | 19:30
12 | Bakulia | 93 | 19:30 | 78 | Juldah | 13 | 13:00 | 144 | Patiya | 9 | 00:00
13 | Banani | 77 | 11:00 | 79 | KSRM | 41 | 12:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 18 | 10:00 | 80 | Kabirpur | 252 | 21:00 | 146 | Patuakhali | 56.5 | 20:00
15 | Barapukuria | 64 | 16:00 | 81 | Kachua | 82 | 22:00 | 147 | Payra | 32 | 11:00
16 | Barguna | 20 | 22:00 | 82 | Kaliganj | 35 | 22:00 | 148 | Postogola | 66 | 00:00
17 | Barishal | 112 | 12:00 | 83 | Kallyanpur | 132 | 19:00 | 149 | Pubail | 40 | 00:00
18 | Barishal-230 | 92 | 18:30 | 84 | Kalurghat | 39 | 12:00 | 150 | Purbachal | 34 | 13:00
19 | Baroaulia | 38 | 09:00 | 85 | Kamrangirchar | 85 | 13:00 | 151 | Purbasadipur | 136 | 19:30
20 | Baroirhat | 59 | 19:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 32 | 19:00
21 | Bashundhara | 224 | 14:00 | 87 | Kasba | 33 | 12:00 | 153 | Rahim | 57 | 04:00
22 | BashundharaCement | 6 | 10:00 | 88 | Kazla | 132 | 16:00 | 154 | Rajbari | 72 | 19:30
23 | Beanibazar | 68 | 19:00 | 89 | Keranigonj | 94 | 21:00 | 155 | Rajendrapur | 116 | 21:00
24 | Benapole | 67 | 08:00 | 90 | Khagrachori | 34 | 19:00 | 156 | Rajshahi | 106 | 22:00
25 | Bhaluka | 154 | 17:00 | 91 | Khulna | 68 | 15:00 | 157 | Rajshahi-230 | 104 | 13:00
26 | Bhandaria | 48 | 16:00 | 92 | Khulshi | 183 | 11:00 | 158 | Ramganj | 96 | 11:00
27 | Bhangura | 30 | 18:00 | 93 | Kishoreganj | 124 | 19:00 | 159 | Rampur | 46 | 19:00
28 | Bheramara(GK) | 66 | 19:30 | 94 | Kodda | 298 | 18:00 | 160 | Rangamati | 14 | 18:00
29 | Bhulta | 217 | 00:00 | 95 | Kulaura | 51 | 22:00 | 161 | Rangpur | 118 | 19:00
30 | Bog-Sherpur | 60 | 04:00 | 96 | Kurigram | 62 | 21:00 | 162 | Ruppur | 4.2 | 10:00
31 | Bogura | 192 | 19:30 | 97 | Kushtia | 146 | 22:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 66 | 20:00 | 98 | Laksam | 35 | 02:00 | 164 | Saidpur | 116 | 11:00
33 | Brahmanbaria | 127 | 21:00 | 99 | Lakshmipur | 48 | 06:00 | 165 | Santhia | 38 | 19:00
34 | Cantonment | 140 | 13:00 | 100 | Lalbag | 82 | 13:00 | 166 | Satkhira | 137 | 21:00
35 | Chandina | 47 | 22:00 | 101 | Lalmonirhat | 60 | 19:30 | 167 | Satmasjid | 111 | 14:00
36 | Chandpur | 70 | 19:30 | 102 | MI_Cement | 13.7 | 20:00 | 168 | Savar | 225 | 19:30
37 | Chandraghona | 31 | 20:00 | 103 | Madanganj | 46 | 22:00 | 169 | SevenRings | 13.01 | 04:00
38 | Chapai | 72 | 22:00 | 104 | Madaripur | 110 | 21:00 | 170 | ShahCement | 37 | 00:00
39 | Charfasson | 27 | 19:30 | 105 | Madartek | 91 | 00:00 | 171 | Shahjadpur | 72 | 18:30
40 | Charsaidpur | 37 | 00:00 | 106 | Madunaghat | 57 | 18:30 | 172 | Shahjibazar | 138 | 19:00
41 | Chauddagram | 66 | 21:00 | 107 | Magura | 60 | 22:00 | 173 | Shahmirpur | 52.5 | 22:00
42 | Chhatak | 34 | 21:00 | 108 | Mahasthangarh | 74 | 19:00 | 174 | Shariatpur | 87 | 22:00
43 | Chowmuhani | 130 | 21:00 | 109 | Maijdee | 38 | 22:00 | 175 | Sherpur | 150 | 23:00
44 | Chuadanga | 117 | 21:00 | 110 | Manikganj | 114 | 21:00 | 176 | Shikalbaha | 28 | 16:00
45 | Coxsbazar | 124 | 00:00 | 111 | Maniknagar | 85 | 14:00 | 177 | Shitalakhya | 81.1 | 13:00
46 | Cumilla(N) | 119 | 19:00 | 112 | Matarbari | 45 | 22:00 | 178 | Sholosohor | 44 | 16:00
47 | Cumilla(S) | 198 | 15:00 | 113 | Matuail | 82 | 23:00 | 179 | Shomvuganj | 35 | 21:00
48 | Daganbhuiyan | 35 | 23:00 | 114 | Metrorail_Motijheel | 31 | 13:00 | 180 | Shyampur | 170 | 00:00
49 | Daudkandi | 126 | 21:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 136 | 11:00
50 | DhakaUniversity | 102 | 13:00 | 116 | Millgate | 116 | 12:00 | 182 | Sirajganj | 126 | 20:00
51 | Dhamrai | 94 | 19:00 | 117 | Mirpur | 167 | 19:00 | 183 | Sitakunda | 37 | 19:00
52 | Dhanmondi | 125 | 13:00 | 118 | Mirsorai | 35 | 06:00 | 184 | Sonargaon | 128 | 22:00
53 | Dohazari | 96 | 19:30 | 119 | Mirzapur | 38 | 21:00 | 185 | Sreemongol | 76 | 19:00
54 | Faridpur | 164 | 21:00 | 120 | Mithapukur | 66 | 11:00 | 186 | Sreepur | 135 | 21:00
55 | Fatullah | 113 | 15:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 53.2 | 19:30
56 | Fenchuganj | 42 | 19:30 | 122 | Mogbazar | 63.8 | 16:00 | 188 | Sunamganj | 54 | 11:00
57 | Feni | 108 | 22:00 | 123 | Mongla | 49 | 19:00 | 189 | Sylhet | 122 | 20:00
58 | GPH | 3 | 13:00 | 124 | Motijheel | 52 | 13:00 | 190 | Sylhet_(South) | 70 | 00:00
59 | Ghatail | 85 | 22:00 | 125 | Muktagacha | 36 | 08:00 | 191 | TK | 23 | 00:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 108 | 21:00 | 192 | Tangail | 153 | 21:00
61 | Ghorashal-230 | 108 | 21:00 | 127 | Muradnagar | 50 | 19:00 | 193 | Taraganj | 37 | 19:00
62 | Goalpara | 36 | 12:00 | 128 | Mymensingh | 132 | 21:00 | 194 | Tasnim | 44 | 17:00
63 | Gollamari | 108 | 15:00 | 129 | Nabinagar | 100 | 20:00 | 195 | Thakurgaon | 119 | 19:30
64 | Gopalganj | 103 | 21:00 | 130 | Naogaon | 127 | 21:00 | 196 | Tongi | 155 | 00:00
65 | Gulshan | 124 | 14:00 | 131 | Narail | 61 | 21:00 | 197 | Ullahpara | 35 | 19:30
66 | Halishahar | 121 | 19:00 | 132 | Narinda | 82 | 13:00 | 198 | Ullon | 61 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 03-08-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13977.58 | 3251 |  | 17374.58
1:00 | 13236.91 | 3512 |  | 16906.91
2:00 | 13169.43 | 3484 |  | 16810.43
3:00 | 13137.86 | 3398 |  | 16688.86
4:00 | 13015.89 | 3311 |  | 16475.89
5:00 | 12895.82 | 3234 |  | 16275.82
6:00 | 12551.34 | 3294 |  | 15993.34
7:00 | 12336.59 | 3039 |  | 15512.59
8:00 | 12374.09 | 3031 |  | 15541.09
9:00 | 12487.83 | 3004 |  | 15626.83
10:00 | 12964.26 | 2656 |  | 15739.78
11:00 | 13383.3 | 2074 |  | 15550.63
12:00 | 13663.58 | 2716 |  | 16501.58
13:00 | 13902.64 | 2623 |  | 16643.64
14:00 | 14018.83 | 2412 |  | 16539.83
15:00 | 14017.73 | 2577 |  | 16710.73
16:00 | 14062.55 | 2211 |  | 16372.55
17:00 | 13861.7 | 2112 |  | 16068.7
18:00 | 13879.94 | 1916 |  | 15881.94
19:00 | 14975.07 | 2345 |  | 17426.07
19:30 | 15194.18 | 2359 |  | 17659.18
20:00 | 15230.75 | 2094 |  | 17418.75
21:00 | 15373.78 | 2333 |  | 17811.78
22:00 | 15306.63 | 1853 |  | 17242.63
23:00 | 14815.53 | 2665 |  | 17600.53
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 03-08-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7383.7 | 6593.88 | 13977.58 | DAILY GENERATION CURVE
00:30 | 7155.7 | 6451.545 | 13607.245
01:00 | 6927.7 | 6309.21 | 13236.91 | 03-08-2026
01:30 | 6884.2 | 6318.97 | 13203.17
02:00 | 6840.7 | 6328.73 | 13169.43
02:30 | 6814.2 | 6339.445 | 13153.645
03:00 | 6787.7 | 6350.16 | 13137.86
03:30 | 6730.7 | 6346.175 | 13076.875
04:00 | 6673.7 | 6342.19 | 13015.89
04:30 | 6620.7 | 6335.155 | 12955.855
05:00 | 6567.7 | 6328.12 | 12895.82
05:30 | 6415.035 | 6308.545 | 12723.58
06:00 | 6262.37 | 6288.97 | 12551.34
06:30 | 6110.13 | 6333.835 | 12443.965
07:00 | 5957.89 | 6378.7 | 12336.59
07:30 | 5995.56 | 6359.78 | 12355.34
08:00 | 6033.23 | 6340.86 | 12374.09
08:30 | 6049.385 | 6381.575 | 12430.96
09:00 | 6065.54 | 6422.29 | 12487.83
09:30 | 6118.385 | 6607.66 | 12726.045
10:00 | 6171.23 | 6793.03 | 12964.26
10:30 | 6401.1 | 6772.68 | 13173.78
11:00 | 6630.97 | 6752.33 | 13383.3
11:30 | 6707.73 | 6815.71 | 13523.44
12:00 | 6784.49 | 6879.09 | 13663.58
12:30 | 6908.94 | 6874.17 | 13783.11
13:00 | 7033.39 | 6869.25 | 13902.64
13:30 | 7176.48 | 6784.255 | 13960.735
14:00 | 7319.57 | 6699.26 | 14018.83
14:30 | 7315.315 | 6702.965 | 14018.28
15:00 | 7311.06 | 6706.67 | 14017.73
15:30 | 7327.985 | 6712.155 | 14040.14
16:00 | 7344.91 | 6717.64 | 14062.55
16:30 | 7339.925 | 6622.2 | 13962.125
17:00 | 7334.94 | 6526.76 | 13861.7
17:30 | 7367.48 | 6503.34 | 13870.82
18:00 | 7400.02 | 6479.92 | 13879.94
18:30 | 7614.82 | 6812.685 | 14427.505
19:00 | 7829.62 | 7145.45 | 14975.07
19:30 | 7975.62 | 7218.56 | 15194.18
20:00 | 8045.32 | 7185.43 | 15230.75
20:30 | 8062.9 | 7239.365 | 15302.265 |  | Executive Engineer
21:00 | 8080.48 | 7293.3 | 15373.78 |  | Network Operation Division
21:30 | 8089.58 | 7250.625 | 15340.205
22:00 | 8098.68 | 7207.95 | 15306.63
22:30 | 7966 | 7095.08 | 15061.08
23:00 | 7833.32 | 6982.21 | 14815.53

## En-Curve
QF-LDC-12
Date | 03-08-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2469 | 1293.5 | 898 | 38 | 174 | 1474.68 | 222 | 5334 | 0 | 323 | 1737.4 | 0 | 0 | 14 | 3251 | DAILY ENERGY CURVE
00:30 | 2457 | 1290 | 898 | 38 | 175 | 1473.845 | 222 | 5284.5 | 0 | 267.5 | 1491.9 | 0 | 0 | 9.5 | 3381.5 | 03-08-2026
01:00 | 2445 | 1286.5 | 898 | 38 | 176 | 1473.01 | 222 | 5235 | 0 | 212 | 1246.4 | 0 | 0 | 5 | 3512
01:30 | 2452 | 1287 | 898 | 38 | 172 | 1471.77 | 222 | 5252.5 | 0 | 175 | 1231.9 | 0 | 0 | 3 | 3498 | Energy Generated | 330.6159 |  | MKWHr
02:00 | 2459 | 1287.5 | 898 | 38 | 168 | 1470.53 | 222 | 5270 | 0 | 138 | 1217.4 | 0 | 0 | 1 | 3484 | Energy not Served | 65.145 |  | MKWHr
02:30 | 2473 | 1289 | 898 | 38 | 165 | 1476.745 | 222 | 5277 | 0 | 123 | 1186.9 | 0 | 0 | 5 | 3441 | Total Energy Requirement | 395.7609 |  | MKWHr
03:00 | 2487 | 1290.5 | 898 | 38 | 162 | 1482.96 | 222 | 5284 | 0 | 108 | 1156.4 | 0 | 0 | 9 | 3398
03:30 | 2471 | 1291 | 898 | 38 | 161 | 1476.475 | 220.5 | 5285 | 0 | 107.5 | 1117.9 | 0 | 0 | 10.5 | 3354.5
04:00 | 2455 | 1291.5 | 898 | 38 | 160 | 1469.99 | 219 | 5286 | 0 | 107 | 1079.4 | 0 | 0 | 12 | 3311
04:30 | 2452.5 | 1288 | 898 | 38 | 158 | 1475.955 | 218.5 | 5242.5 | 0 | 119.5 | 1052.4 | 0 | 0 | 12.5 | 3272.5
05:00 | 2450 | 1284.5 | 898 | 38 | 156 | 1481.92 | 218 | 5199 | 0 | 132 | 1025.4 | 0 | 0 | 13 | 3234
05:30 | 2435.5 | 1279 | 898 | 38 | 154 | 1485 | 218 | 5050.5 | 4.28 | 144.5 | 1010.3 | 0 | 0 | 6.5 | 3264
06:00 | 2421 | 1273.5 | 898 | 38 | 152 | 1488.08 | 218 | 4902 | 8.56 | 157 | 995.2 | 0 | 0 | 0 | 3294
06:30 | 2448 | 1276 | 898 | 38 | 149 | 1483.175 | 218.5 | 4778 | 41.09 | 157.5 | 954.2 | 0 | 0 | 2.5 | 3166.5
07:00 | 2475 | 1278.5 | 898 | 38 | 146 | 1478.27 | 219 | 4654 | 73.62 | 158 | 913.2 | 0 | 0 | 5 | 3039
07:30 | 2487.5 | 1283.5 | 885.5 | 38 | 151 | 1478.08 | 219.5 | 4665 | 87.16 | 166 | 887.1 | 0 | 0 | 7 | 3035
08:00 | 2500 | 1288.5 | 873 | 38 | 156 | 1477.89 | 220 | 4676 | 100.7 | 174 | 861 | 0 | 0 | 9 | 3031
08:30 | 2485.5 | 1301.25 | 873 | 38 | 154 | 1474.07 | 220 | 4686.5 | 151.64 | 174 | 868.5 | 0 | 0 | 4.5 | 3017.5
09:00 | 2471 | 1314 | 873 | 38 | 152 | 1470.25 | 220 | 4697 | 202.58 | 174 | 876 | 0 | 0 | 0 | 3004
09:30 | 2465 | 1292 | 873 | 38 | 162 | 1473.79 | 220.5 | 4862.5 | 203.255 | 170.5 | 965.5 | 0 | 0 | 0 | 2830
10:00 | 2459 | 1270 | 873 | 38 | 172 | 1477.33 | 221 | 5028 | 203.93 | 167 | 1055 | 0 | 0 | 0 | 2656
10:30 | 2447.5 | 1274.5 | 873 | 38 | 172 | 1475.325 | 198.5 | 5145 | 245.455 | 168 | 1136.5 | 0 | 0 | 0 | 2365
11:00 | 2436 | 1279 | 873 | 38 | 172 | 1473.32 | 176 | 5262 | 286.98 | 169 | 1218 | 0 | 0 | 0 | 2074
11:30 | 2450 | 1257 | 872.5 | 38 | 175 | 1479.625 | 176 | 5327.5 | 320.315 | 175.5 | 1246 | 0 | 0 | 6 | 2395
12:00 | 2464 | 1235 | 872 | 38 | 178 | 1485.93 | 176 | 5393 | 353.65 | 182 | 1274 | 0 | 0 | 12 | 2716
12:30 | 2456.5 | 1211 | 872.5 | 38 | 184 | 1484.98 | 176 | 5412 | 379.92 | 242.71 | 1315.5 | 0 | 0 | 10 | 2669.5
13:00 | 2449 | 1187 | 873 | 38 | 190 | 1484.03 | 176 | 5431 | 406.19 | 303.42 | 1357 | 0 | 0 | 8 | 2623
13:30 | 2416.5 | 1163.5 | 850.5 | 38 | 193 | 1481.88 | 176 | 5478 | 428.935 | 341.42 | 1388 | 0 | 0 | 5 | 2517.5
14:00 | 2384 | 1140 | 828 | 38 | 196 | 1479.73 | 176 | 5525 | 451.68 | 379.42 | 1419 | 0 | 0 | 2 | 2412
14:30 | 2405.5 | 1164 | 850.5 | 38 | 197 | 1478.86 | 175 | 5502.5 | 382 | 374.92 | 1449 | 0 | 0 | 1 | 2494.5
15:00 | 2427 | 1188 | 873 | 38 | 198 | 1477.99 | 174 | 5480 | 312.32 | 370.42 | 1479 | 0 | 0 | 0 | 2577
15:30 | 2440.5 | 1183 | 873 | 38 | 197 | 1476.95 | 173 | 5469.5 | 278.17 | 374.92 | 1535.6 | 0 | 0 | 0.5 | 2394
16:00 | 2454 | 1178 | 873 | 38 | 196 | 1475.91 | 172 | 5459 | 244.02 | 379.42 | 1592.2 | 0 | 0 | 1 | 2211
16:30 | 2448.5 | 1151.5 | 873 | 38 | 190 | 1476.965 | 172 | 5411 | 191.04 | 402.92 | 1606.7 | 0 | 0 | 0.5 | 2161.5
17:00 | 2443 | 1125 | 873 | 38 | 184 | 1478.02 | 172 | 5363 | 138.06 | 426.42 | 1621.2 | 0 | 0 | 0 | 2112
17:30 | 2436 | 1148 | 873 | 38 | 178 | 1475.5 | 172 | 5339.5 | 84.7 | 438.42 | 1687.7 | 0 | 0 | 0 | 2014
18:00 | 2429 | 1171 | 873 | 38 | 172 | 1472.98 | 172 | 5316 | 31.34 | 450.42 | 1754.2 | 0 | 0 | 0 | 1916
18:30 | 2440 | 1194.5 | 872.5 | 38 | 175 | 1475.215 | 171.5 | 5481 | 15.67 | 565.92 | 1898.2 | 100 | 0 | 0 | 2130.5
19:00 | 2451 | 1218 | 872 | 38 | 178 | 1477.45 | 171 | 5646 | 0 | 681.42 | 2042.2 | 200 | 0 | 0 | 2345
19:30 | 2438 | 1191 | 872 | 38 | 154 | 1471.56 | 171 | 5646 | 0 | 715.42 | 2232.2 | 265 | 0 | 0 | 2359
20:00 | 2442 | 1168 | 872 | 38 | 148 | 1473.43 | 217 | 5651 | 0 | 730.42 | 2223.9 | 265 | 0 | 2 | 2094
20:30 | 2446.5 | 1191 | 872 | 38 | 140 | 1474.365 | 217.5 | 5652.5 | 0 | 698.92 | 2277.48 | 290 | 0 | 4 | 2213.5
21:00 | 2451 | 1214 | 872 | 38 | 132 | 1475.3 | 218 | 5654 | 0 | 667.42 | 2331.06 | 315 | 0 | 6 | 2333
21:30 | 2429.5 | 1180 | 872.5 | 38 | 134 | 1475.86 | 218.5 | 5654.265 | 0 | 690.92 | 2326.16 | 315 | 0 | 5.5 | 2093
22:00 | 2408 | 1146 | 873 | 38 | 136 | 1476.42 | 219 | 5654.53 | 0 | 714.42 | 2321.26 | 315 | 0 | 5 | 1853
22:30 | 2398 | 1138 | 873 | 38 | 142 | 1475.55 | 219.5 | 5651.53 | 0 | 713.92 | 2181.58 | 227.5 | 0 | 2.5 | 2259
23:00 | 2388 | 1130 | 873 | 38 | 148 | 1474.68 | 220 | 5648.53 | 0 | 713.42 | 2041.9 | 140 | 0 | 0 | 2665
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 03-08-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 185 | 64 | 528 | 222 | 1698 | 838 | Ishurdi-Ghorashal Ckt-1 | Export | 4176800
1:00 | 158 | 50 | 460 | 180 | 1584 | 768
2:00 | 160 | 51 | 488 | 196 | 1560 | 756 |  | Import | 0
3:00 | 160 | 49 | 498 | 198 | 1590 | 748
4:00 | 160 | 46 | 508 | 182 | 1620 | 754 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 158 | 41 | 526 | 184 | 1640 | 722
6:00 | 178 | 47 | 498 | 138 | 1708 | 696 |  | Import | 0
7:00 | 186 | 45 | 592 | 182 | 1820 | 706
8:00 | 187 | 50 | 592 | 200 | 1876 | 736 | Sirajganj-Sreepur Ckt-1 | Export | 3246000
9:00 | 212 | 65 | 638 | 206 | 2040 | 826
10:00 | 217 | 78 | 670 | 274 | 2238 | 1000 |  | Import | 0
11:00 | 205 | 75 | 614 | 276 | 2044 | 1020
12:00 | 208 | 74 | 660 | 286 | 2108 | 1042 | Sirajganj-Sreepur Ckt-2 | Export | 3257000
13:00 | 188 | 68 | 530 | 212 | 1960 | 1006
14:00 | 177 | 67 | 550 | 242 | 1866 | 1008 |  | Import | 0
15:00 | 160 | 47 | 500 | 212 | 1796 | 936
16:00 | 162 | 45 | 530 | 228 | 1752 | 942 | Gopalganj-Aminbazar Ckt-1 | Export | 21780000
17:00 | 159 | 44 | 520 | 230 | 1664 | 924
18:00 | 155 | 44 | 510 | 222 | 1662 | 898 |  | Import | 0
18:30 | 168 | 51 | 550 | 234 | 1798 | 810
19:00 | 168 | 50 | 540 | 214 | 1772 | 794 | Gopalganj-Aminbazar Ckt-2 | Export | 21830000
19:30 | 177 | 57 | 560 | 202 | 1878 | 812
20:00 | 169 | 54 | 430 | 204 | 1786 | 790 |  | Import | 0
21:00 | 174 | 56 | 520 | 210 | 1786 | 822
22:00 | 165 | 46 | 520 | 216 | 1726 | 770 |  | Total Export | 54289800
23:00 | 167 | 49 | 510 | 166 | 1724 | 754 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 03-08-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 367 | 05:00 | 336 | 12:00 | Madunaghat | 393 | 06:00 | 381 | 13:00
Amtali | 411 | 06:00 | 400 | 12:00 | Meghnaghat | 373 | 06:00 | 339 | 12:00
Ashuganj | 390 | 6:00 | 355 | 12:00 | Mirsorai | 391 | 07:00 | 373 | 12:00
Bhulta | 382 | 06:00 | 345 | 12:00 | Payra | 411 | 06:00 | 402 | 12:00
Bibiana | 375 | 05:00 | 360 | 12:00 | Rahanpur | 397 | 06:00 | 388 | 12:00
BIPTC | 401 | 17:00 | 392 | 00:00 | Rampal | 395 | 07:00 | 376 | 15:00
Bogura | 379 | 07:00 | 368 | 15:00
Gopalganj | 387 | 06:00 | 365 | 12:00
Kaliakoir | 358 | 06:00 | 327 | 12:00
Korerhat | 390 | 06:00 | 372 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 06:00 | 201 | 12:00 | Ishurdi | 235 | 06:00 | 218 | 15:00
AKSML | 232.5 | 09:00 | 222.5 | 12:00 | Jhenaidah | 227 | 06:00 | 210 | 15:00
Aminbazar | 224 | 05:00 | 202 | 12:00 | Kachua | 223 | 07:00 | 214 | 11:00
Ashuganj | 221 | 06:00 | 204 | 12:00 | Kaliakoir | 222 | 05:00 | 200 | 12:00
Ashuganj-400 | 221 | 06:00 | 204 | 12:00 | Keranigonj | 222 | 06:00 | 199 | 12:00
Baghabari | 230 | 06:00 | 219 | 16:00 | Khulna(S) | 225 | 01:00 | 211 | 15:00
Barapukuria | 224 | 19:30 | 219 | 11:00 | Korerhat | 222 | 06:00 | 212 | 12:00
Barapukuria-230 | 224 | 19:30 | 219 | 11:00 | Madunaghat | 235 | 07:00 | 227 | 12:00
Barishal | 225 | 06:00 | 217 | 12:00 | Madunaghat-400 | 237 | 08:00 | 229 | 13:00
Bheramara | 233 | 06:00 | 217 | 15:00 | Maniknagar | 218 | 06:00 | 194 | 12:00
Bhulta | 220 | 06:00 | 196 | 12:00 | Meghnaghat | 221 | 01:00 | 205 | 12:00
Bibiana | 219 | 07:00 | 207 | 14:00 | Meghnaghat-400 | 222 | 06:00 | 201 | 12:00
BIPTC | 236 | 06:00 | 217 | 15:00 | Mirsorai | 228 | 07:00 | 217 | 12:00
Bogura | 237 | 06:00 | 230 | 15:00 | Naogaon | 224 | 08:00 | 206 | 15:00
Bogura-400 | 238 | 07:00 | 230 | 16:00 | Purbasadipur | 223 | 19:00 | 215 | 11:00
Borhanuddin | 228 | 06:00 | 224 | 11:00 | Rajshahi | 248 | 17:00 | 214 | 16:00
BSRM | 224 | 06:00 | 213 | 14:00 | Rampal | 225 | 06:00 | 211 | 15:00
Charfasson | 229 | 6:00 | 223 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 220 | 05:00 | 212 | 12:00 | Rampura | 219 | 06:00 | 194 | 12:00
Cumilla(N) | 220 | 07:00 | 204 | 12:00 | Shikalbaha | 235 | 06:00 | 228 | 11:00
Faridpur | 221 | 07:00 | 197 | 15:00 | Shyampur | 221 | 06:00 | 198 | 12:00
Fenchuganj | 221 | 16:00 | 210 | 12:00 | Siddhirganj | 219 | 05:00 | 201 | 14:00
Feni | 221 | 06:00 | 209 | 12:00 | Sirajgonj | 235 | 06:00 | 226 | 16:00
Ghorashal | 220 | 00:00 | 208 | 16:00 | Sreepur | 222 | 06:00 | 206 | 12:00
Ghorashal-230 | 211 | 01:00 | 191 | 12:00 | Tongi | 213 | 04:00 | 193 | 11:00
Gopalganj | 221 | 06:00 | 210 | 12:00
GPH | 229 | 01:00 | 222 | 14:00
Haripur | 220 | 06:00 | 197 | 12:00
Hasnabad | 221 | 04:00 | 198 | 12:00
Hathazari | 232 | 06:00 | 224 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 06:00 | 117 | 12:00 | Madartek | 134 | 05:00 | 117 | 12:00
Agargaon | 135 | 06:00 | 119 | 12:00 | Madunaghat | 136 | 04:00 | 131 | 12:00
Agrabad | 135 | 06:00 | 129 | 12:00 | Magura | 137 | 02:00 | 124 | 12:00
AKS | 132 | 08:00 | 127 | 12:00 | Mahasthangarh | 134 | 00:00 | 129 | 15:00
Aminbazar | 127 | 05:00 | 113 | 12:00 | Maijdee | 124 | 06:00 | 119 | 11:00
Amnura | 137 | 00:00 | 124 | 15:00 | Manikganj | 126 | 02:00 | 118 | 15:00
Ashuganj | 126 | 06:00 | 118 | 12:00 | Maniknagar | 130 | 23:00 | 115 | 10:00
Ashuganj-230 | 130 | 06:00 | 124 | 12:00 | Matarbari | 130 | 09:00 | 118 | 18:30
Bagerhat | 129 | 09:00 | 118 | 15:00 | Matuail | 131 | 06:00 | 117 | 12:00
Bajitpur | 124 | 06:00 | 114 | 16:00 | Metrorail_Motijheel | 130 | 23:00 | 115 | 10:00
Bakerganj | 131 | 07:00 | 125 | 12:00 | Metrorail_Uttara | 129 | 05:00 | 111 | 12:00
Bakulia | 135 | 07:00 | 129 | 12:00 | Millgate | 131 | 05:00 | 111 | 12:00
Banani | 135 | 06:00 | 116 | 12:00 | Mirpur | 126 | 05:00 | 112 | 12:00
Bangabhaban | 130 | 23:00 | 114 | 10:00 | Mirzapur | 127 | 20:00 | 118 | 14:00
Barapukuria | 137 | 19:30 | 129 | 11:00 | Mithapukur | 133 | 00:00 | 127 | 01:00
Barguna | 131 | 06:00 | 125 | 12:00 | MI_Cement | 130.5 | 06:00 | 116 | 13:00
Barishal | 130 | 01:00 | 124 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barishal-230 | 131 | 06:00 | 124 | 12:00 | Mogbazar | 138 | 04:00 | 119 | 12:00
Baroaulia | 135 | 06:00 | 129 | 12:00 | Mongla | 128 | 09:00 | 118 | 12:00
Baroirhat | 130 | 06:00 | 122 | 12:00 | Motijheel | 130 | 23:00 | 114 | 10:00
Bashundhara | 135 | 06:00 | 112 | 12:00 | Muktagacha | 124 | 19:30 | 115 | 00:00
BashundharaCement | 130 | 00:00 | 117 | 12:00 | Munshiganj | 127 | 03:00 | 116 | 12:00
Beanibazar | 123 | 06:00 | 117 | 11:00 | Muradnagar | 125 | 06:00 | 114 | 13:00
Benapole | 134 | 06:00 | 116 | 15:00 | Mymensingh | 124 | 09:00 | 108 | 11:00
Bhaluka | 125 | 06:00 | 113 | 12:00 | Nabinagar | 128 | 05:00 | 115 | 12:00
Bhandaria | 129 | 01:00 | 120 | 12:00 | Naogaon | 135 | 09:00 | 125 | 15:00
Bhangura | 133 | 04:00 | 126 | 15:00 | Narail | 138 | 03:00 | 124 | 22:00
Bheramara | 136 | 01:00 | 127 | 15:00 | Narinda | 130 | 23:00 | 115 | 10:00
Bheramara(GK) | 136 | 06:00 | 127 | 15:00 | Narshingdi | 124 | 05:00 | 113 | 11:00
Bhulta | 125 | 08:00 | 116 | 12:00 | Natore | 135 | 00:00 | 125 | 15:00
Bhulta-400 | 127 | 06:00 | 113 | 12:00 | Nawabganj | 134 | 07:00 | 119 | 12:00
Bog-Sherpur | 135 | 07:00 | 129 | 15:00 | Netrakona | 117 | 23:00 | 105 | 22:00
Bogura | 137 | 07:00 | 132 | 15:00 | New | 131 | 05:00 | 114 | 12:00
Bogura-230 | 137 | 00:00 | 132 | 15:00 | Niamatpur | 132 | 08:00 | 127 | 22:00
Brahmanbaria | 125 | 05:00 | 117 | 12:00 | Noapara | 133 | 05:00 | 121 | 12:00
Cantonment | 134 | 05:00 | 118 | 12:00 | Pabna | 134 | 09:00 | 125 | 15:00
Chandina | 128 | 07:00 | 119 | 12:00 | Palashbari | 130 | 00:00 | 125 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandpur | 130 | 19:30 | 123 | 11:00 | Panchagarh | 135 | 09:00 | 131 | 11:00
Chandraghona | 137 | 06:00 | 132 | 12:00 | Patiya | 138 | 18:00 | 129 | 03:00
Chapai | 130 | 00:00 | 128 | 13:00 | Patnitala | 131 | 03:00 | 121 | 15:00
Charsaidpur | 130 | 06:00 | 117 | 13:00 | Patuakhali | 132 | 06:00 | 126 | 15:00
Chauddagram | 127 | 05:00 | 120 | 11:00 | Payra | 134 | 02:00 | 131 | 11:00
Chhatak | 122 | 07:00 | 112 | 11:00 | PHP | 129 | 06:00 | 123 | 11:00
Chowmuhani | 124 | 05:00 | 119 | 12:00 | Postogola | 132 | 06:00 | 117 | 12:00
Chuadanga | 135 | 01:00 | 121 | 21:00 | Pubail | 123 | 06:00 | 115 | 12:00
Coxsbazar | 131 | 08:00 | 120 | 12:00 | Purbachal | 135 | 05:00 | 116 | 12:00
Cumilla(N) | 128 | 07:00 | 118 | 14:00 | Purbasadipur | 136 | 19:00 | 130 | 11:00
Cumilla(S) | 128 | 07:00 | 119 | 12:00 | Rahanpur | 133 | 08:00 | 130 | 11:00
Daganbhuiyan | 127 | 06:00 | 120 | 12:00 | Rahanpur-400 | 133 | 04:00 | 130 | 12:00
Daudkandi | 123 | 06:00 | 114 | 11:00 | Rahim | 131 | 07:00 | 118 | 12:00
DhakaUniversity | 135 | 04:00 | 117 | 12:00 | Rajbari | 126 | 06:00 | 115 | 17:00
Dhamrai | 130 | 03:00 | 115 | 11:00 | Rajendrapur | 125 | 06:00 | 113 | 12:00
Dhanmondi | 135.5 | 06:00 | 117 | 12:00 | Rajshahi | 133 | 06:00 | 122 | 15:00
Dohazari | 133 | 09:00 | 126 | 12:00 | Rajshahi-230 | 134 | 06:00 | 124 | 12:00
Faridpur | 129 | 07:00 | 118 | 15:00 | Ramganj | 125 | 19:30 | 119 | 11:00
Fatullah | 132 | 07:00 | 115 | 12:00 | Rampur | 135 | 06:00 | 128 | 12:00
Fenchuganj | 129 | 05:00 | 124 | 01:00 | Rampura | 135 | 06:00 | 117 | 12:00
Feni | 128 | 04:00 | 122 | 15:00 | Rangamati | 135 | 04:00 | 131 | 12:00
Feni-230 | 128 | 06:00 | 121 | 12:00 | Rangpur | 133 | 19:30 | 127 | 03:00
Ghatail | 125 | 09:00 | 114 | 03:00 | Ruppur | 138 | 01:00 | 127 | 15:00
Ghorashal | 125 | 06:00 | 116 | 12:00 | Saidpur | 135 | 19:30 | 128 | 11:00
Goalpara | 135 | 09:00 | 124 | 15:00 | Santhia | 135 | 06:00 | 126 | 16:00
Gollamari | 134 | 01:00 | 124 | 15:00 | Satkhira | 132 | 09:00 | 118 | 15:00
Gopalganj | 132 | 09:00 | 122 | 12:00 | Satmasjid | 135 | 06:00 | 118 | 12:00
Gopalganj-400 | 131 | 06:00 | 123 | 15:00 | Savar | 124 | 04:00 | 113 | 10:00
Gulshan | 135 | 06:00 | 119 | 11:00 | SevenRings | 126 | 06:00 | 115 | 12:00
Halishahar | 136 | 07:00 | 129 | 12:00 | ShahCement | 130 | 06:00 | 117 | 13:00
Haripur | 131 | 06:00 | 118 | 12:00 | Shahjadpur | 135 | 01:00 | 130 | 17:00
HaripurSBU | 131 | 00:00 | 118 | 12:00 | Shahjibazar | 126 | 06:00 | 116 | 12:00
Hasnabad | 131 | 05:00 | 116 | 12:00 | Shahmirpur | 136 | 08:00 | 130 | 12:00
Hathazari | 136 | 06:00 | 131 | 12:00 | Shariatpur | 129 | 06:00 | 122 | 12:00
Hatirjheel | 136 | 06:00 | 118 | 12:00 | Sherpur | 128 | 20:00 | 111 | 03:00
Ishurdi | 139 | 06:00 | 128 | 15:00 | Shikalbaha | 127 | 02:00 | 120 | 13:00
Jaldhaka | 133 | 19:30 | 128 | 04:00 | Shikalbaha-230 | 137 | 07:00 | 132 | 11:00
Jamalpur | 129 | 19:30 | 115 | 02:00 | Shitalakhya | 130.5 | 06:00 | 114 | 12:00
Jashore | 136 | 05:00 | 118 | 12:00 | Sholosohor | 136 | 07:00 | 130 | 18:30
Jhenaidah | 138 | 05:00 | 120 | 15:00 | Shomvuganj | 120 | 06:00 | 108 | 22:00
Jhenaidah-230 | 139 | 06:00 | 127 | 21:00 | Shyampur | 130 | 04:00 | 122 | 12:00
Joydebpur | 122 | 07:00 | 113 | 12:00 | Shyampur-230 | 132 | 06:00 | 117 | 12:00
Joypurhat | 133 | 09:00 | 122 | 15:00 | Siddhirganj | 131 | 06:00 | 118 | 12:00
Juldah | 135 | 08:00 | 131 | 13:00 | Sirajganj | 132 | 00:00 | 124 | 15:00
Kabirpur | 128 | 07:00 | 109 | 12:00 | Sitakunda | 135 | 06:00 | 130 | 11:00
Kachua | 126 | 00:00 | 122 | 11:00 | Sonargaon | 128 | 06:00 | 116 | 11:00
Kaliakoir | 132 | 05:00 | 119 | 12:00 | Sreemongol | 126 | 06:00 | 117 | 16:00
Kaliganj | 138 | 01:00 | 126 | 21:00 | Sreepur | 128 | 06:00 | 116 | 12:00
Kallyanpur | 127 | 05:00 | 113 | 12:00 | Srinagar | 133 | 03:00 | 119 | 12:00
Kalurghat | 136 | 07:00 | 132 | 12:00 | SSM | 140 | 07:00 | 136 | 16:00
Kamrangirchar | 133 | 06:00 | 110 | 12:00 | Sunamganj | 119 | 03:00 | 111 | 11:00
Kaptai | 138 | 8:00 | 135 | 13:00 | Sylhet | 124 | 07:00 | 118 | 11:00
Kasba | 126 | 07:00 | 114 | 12:00 | Sylhet_(South) | 124 | 02:00 | 118 | 18:30
Kazla | 130 | 23:00 | 115 | 10:00 | Tangail | 126 | 09:00 | 115 | 13:00
Keranigonj | 135 | 06:00 | 119 | 12:00 | Taraganj | 134 | 19:30 | 127 | 11:00
Khagrachori | 135 | 06:00 | 130 | 12:00 | Tasnim | 129 | 07:00 | 116 | 11:00
Khulna | 134 | 03:00 | 123 | 15:00 | Thakurgaon | 136 | 09:00 | 132 | 11:00
Khulna(S) | 135 | 01:00 | 125 | 12:00 | TK | 135 | 04:00 | 131 | 12:00
Khulshi | 134 | 06:00 | 128 | 12:00 | Tongi | 133 | 04:00 | 118 | 11:00
Kishoreganj | 123 | 06:00 | 112 | 22:00 | Ullahpara | 133 | 06:00 | 125 | 16:00
Kodda | 128 | 06:00 | 114 | 11:00 | Ullon | 135 | 06:00 | 117 | 12:00
Korerhat | 132 | 06:00 | 124 | 16:00 | Uttara | 129 | 05:00 | 110 | 12:00
KSRM | 135 | 05:00 | 128 | 12:00 | UttaraNew | 129 | 05:00 | 111 | 12:00
Kulaura | 129 | 07:00 | 122 | 11:00 | Zigatola | 134 | 07:00 | 119 | 12:00
Kurigram | 131 | 00:00 | 120 | 11:00
Kushtia | 133 | 08:00 | 121 | 12:00
Laksam | 126 | 00:00 | 121 | 11:00
Lakshmipur | 124 | 07:00 | 118 | 12:00
Lalbag | 133 | 04:00 | 118 | 12:00
Lalmonirhat | 130 | 19:30 | 122 | 01:00
Madanganj | 129 | 01:00 | 117 | 12:00
Madaripur | 130 | 01:00 | 124 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division