## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-08-2026 | during | 05-08-2026 | during | 05-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 271 | 355 | 412 | 412 | 370 | 370 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 142 | 121 | 335 | 335 | 150 | 150 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 300 | 335 | 335 | 330 | 330 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 12 | 54 | 53.97 | 53.97 | 0 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 125 | 143 | 149.36 | 149.36 | 125 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 13 | 33 | 33 | 13 | 13 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 42 | 41 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 81 | 81 | 300 | 300 | 81 | 81 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 73 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 17 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 162 | 162 | 18 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 6 | 0 | 22 | 0 | 22 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 270 | 250 | 583 | 583 | 250 | 250 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1730.42 | 1967.42 | 5800.16 | 5778.16 | 1713.61 | 2091.61
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 5 | 8 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 11 | 0 | 12 | 0 | 12 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 220 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 193 | 200 | 180 | 180 | 180 | 180 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 104 | 99 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 15 | 23 | 24 | 24 | 24 | 24 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 0 | 5 | 0 | 5 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 19 | 47 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.39 | 0 | 1.66 | 0 | 1.66 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 17 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 104 | 107 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 101 | 94 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 16 | 140 | 163 | 163 | 16 | 83 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 4 | 7 | 11 | 13 | 11 | 13 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1130 | 1130 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 3207.39 | 3494.36 | 4056.52 | 4100.86 | 3266.66 | 3440
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 208 | 196 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 355 | 354 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 0 | 342.01 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 20 | 41.65 | 41.65 | 20 | 20 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 5 | 5 | 52.8 | 52.8 | 5 | 5 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 195 | 195 | 8 | 8 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 13 | 43 | 150 | 150 | 50 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 23 | 23 | 24 | 24 | 24 | 24 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 59 | 59 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 175 | 186 | 200 | 200 | 80 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 150 | 134 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 8 | 24.5 | 24.5 | 8 | 8 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 105 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 28 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 50 | 73 | 115 | 115 | 51 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 14 | 0 | 40 | 0 | 40 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1098 | 1286.2 | 2726.42 | 2680.42 | 1275.46 | 1483.46
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-08-2026 | during | 05-08-2026 | during | 05-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 1.88 | 0 | 16 | 0 | 16 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.2 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 155 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 57 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 8.2 | 0 | 32 | 0 | 32 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 22 | 22 | From 18:00 to 23:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 35 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 199.28 | 270 | 516.2 | 516.5 | 268.7 | 269
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 40 | 41 | 41 | 40 | 40 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 39 | 40 | 40 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 146 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 31 | 86 | 86 | 22 | 22 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 75 | 100 | 75 | 75 | 75 | 75 | plant availability zero
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 18 | 18 | 8 | 8 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 368 | 314 | 365 | 365 | 365 | 365 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 994 | 983 | 1179 | 1179 | 964 | 964
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 873 | 872 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 29 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 44.55 | 0 | 60 | 0 | 60 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 150 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1158 | 1148 | 1165 | 1165 | 1165 | 1165 | AGC+FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2142.55 | 2252 | 3477 | 3417 | 2310 | 2250
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1050 | 1051 | 900 | 1050 | 900 | 1050 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 100 | 130 | 130 | 100 | 100 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 581.53 | 560 | 581.53 | 581.53 | 551.53 | 551.53 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.11 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2291.64 | 2271 | 2399.53 | 2548.53 | 2112.53 | 2261.53
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 15.66 | 0 | 48.25 | 0 | 48.25 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 15 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 147 | 143 | 214 | 214 | 150 | 150 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 256 | 224 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 14 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 57 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 0.12 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1474.26 | 1449.2 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | FGMO
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 2.31 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 8 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1990.55 | 2080.2 | 3217.87 | 3003.12 | 2384.49 | 2326.74
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 52 | 52 | 52 | 52 | 52 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 161 | 165 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 99 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.4 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 105 | 110 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 14 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 75 | 0 | 159.69 | 0 | 159.69 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 416.4 | 591 | 652.69 | 460 | 539.69 | 382
System Total |  |  |  |  | 28843.2 | 29171.687 | 14070.23 | 15195.18 | 24025.39 | 23683.59 | 14835.14 | 15468.34
Forecast Scenario (05-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14100 |  | 2502.1 |  | 16720
|  |  |  | 1:00 | 13640 |  | 2263.35 |  | 16010
|  |  |  | 2:00 | 13600 |  | 1528 |  | 15200
|  |  |  | 3:00 | 13560 |  | 1317.9 |  | 14940
|  |  |  | 4:00 | 13520 |  | 1566.2 |  | 15160
|  |  |  | 5:00 | 13570 |  | 2015.05 |  | 15680
|  |  |  | 6:00 | 13390 |  | 1375.2 |  | 14830
|  |  |  | 7:00 | 13360 |  | 544.35 |  | 13930
|  |  |  | 8:00 | 13220 |  | 534.8 |  | 13780
|  |  |  | 9:00 | 13430 |  | 9.55 |  | 13440
|  |  |  | 10:00 | 13450 |  | 0 |  | 13450
|  |  |  | 11:00 | 13400 |  | 0 |  | 13400
|  |  |  | 12:00 | 14080 |  | 305.6 |  | 14400
|  |  |  | 13:00 | 14210 |  | 334.25 |  | 14560
|  |  |  | 14:00 | 13980 |  | 410.65 |  | 14410
|  |  |  | 15:00 | 13880 |  | 95.5 |  | 13980
|  |  |  | 16:00 | 13470 |  | 0 |  | 13470
|  |  |  | 17:00 | 12850 |  | 0 |  | 12850
|  |  |  | 18:00 | 13140 |  | 0 |  | 13140
|  |  |  | 18:30 | 13900 |  | 95.5 |  | 14000
|  |  |  | 19:00 | 14850 |  | 85.95 |  | 14940
|  |  |  | 19:30 | 15050 |  | 248.3 |  | 15310
|  |  |  | 20:00 | 15090 |  | 162.35 |  | 15260
|  |  |  | 21:00 | 15200 |  | 678.05 |  | 15910
|  |  |  | 22:00 | 15060 |  | 649.4 |  | 15740
|  |  |  | 23:00 | 15000 |  | 1451.6 |  | 16520
Probable Maximum Temperature: |  |  | 32.70°C
Probable Maximum Demand at Day Peak: |  |  | 14400.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 678
Probable Maximum Demand at Evening Peak: |  |  | 15910.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15200.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 333.05 MKWHr. |  | 110 | 70 | 60 | 135 | 40 | 90 | 25 | 80 | 68 | 678
*** This report is generated digitally from Operation Information System (OIS) at 09:46 hrs on 05-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-08-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14070.23 | MW | 12:00 Hr. | Energy Generated |  |  | 336.4635 |  | MKWHr.
| Day Peak Demand |  |  | 16182.23 | MW | 12:00 Hr. | Energy Unserverd |  |  | 49.362 |  | MKWHr.
| Evening Peak Generation |  |  | 15195.18 | MW | 21:00 Hr. | Energy Demand |  |  | 385.8255 |  | MKWHr.
| Evening Peak Demand |  |  | 17478.18 | MW | 21:00 Hr. | Maximum Temperature |  |  | 31 |  | °C
| Minimum Generation of the Day |  |  | 13216.86 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 642.96 |  | MMCFD
| Maximum Generation of the Day |  |  | 15195.18 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.4934 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 25.4885 | 0 | 15.4444 | 0 | 0 | 0.054047 | 0 | 0 | 40.9869 | Gas | 87.1256 | Gas | 301233649.4916
| Chattogram Zone |  |  | 4.4628 | 56.1236 | 12.2295 | 0 | 5.132 | 0.083864 | 0 | 0.27408 | 78.3058 | Coal | 133.8534 | Coal | 909977127.9867
| Cumilla Zone |  |  | 15.9095 | 0 | 8.6587 | 0 | 0 | 0.14281 | 3.4445 | 0 | 28.1554 | HFO | 45.8508 | HFO | 849966889.594
| Mymensingh Zone |  |  | 0 | 0 | 2.1427 | 0 | 0 | 0.13134 | 0 | 0 | 2.2741 | HSD | 1.3768 | HSD | 35596947
| Sylhet Zone |  |  | 24.2138 | 0 | 0 | 0 | 0 | 0.032029 | 0 | 0 | 24.2458 | Hydro | 5.132 | Hydro | 513195.8
| Khulna Zone |  |  | 0 | 27.5564 | 0.60523 | 0.64793 | 0 | 0.2736 | 22.024 | 0 | 51.1071 | Solar | 1.7485 | Solar | 28756827.5568
| Barishal Zone |  |  | 7.6558 | 45.027 | 0.83995 | 0 | 0 | 0.00147 | 0 | 0 | 53.5242 | Import | 61.1023 | Import | 391168806.9
| Rajshahi Zone |  |  | 9.3953 | 0 | 2.4129 | 0 | 0 | 0.3995 | 35.6338 | 0 | 47.8415 | Wind | 0.27408 | Wind | 4031716.8
| Rangpur Zone |  |  | 0 | 5.1464 | 3.5174 | 0.72891 | 0 | 0.62984 | 0 | 0 | 10.0226
| Total |  |  | 87.1256 | 133.8534 | 45.8508 | 1.3768 | 5.132 | 1.7485 | 61.1023 | 0.27408 | 336.4635
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 301233649.4916 |  | Hydro | 513195.8
|  |  |  | Coal | 909977127.9867 |  | Solar | 28756827.5568
|  |  |  | HFO | 849966889.594 |  | Import | 391168806.9
|  |  |  | HSD | 35596947 |  | Wind | 4031716.8
[5 empty] | Total: | 252,12,45,161 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.112 | Peak Hr Flow | 872.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 51644854.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 35.6338 | Peak Hr Flow | 1449.20 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2462 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.4445 | Peak Hr Flow | 134.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2655 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 60.1903 | Peak Hr Flow | 2455.20 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 381 |  | 6020
|  |  |  | Chattogram |  | 189 |  | 1622
|  |  |  | Cumilla |  | 301 |  | 1668
|  |  |  | Mymensingh |  | 239 |  | 1374
|  |  |  | Sylhet |  | 132 |  | 718
|  |  |  | Khulna |  | 352 |  | 1999
|  |  |  | Barishal |  | 108 |  | 557
|  |  |  | Rajshahi |  | 272 |  | 1773
|  |  |  | Rangpur |  | 211 |  | 1130
|  |  |  | Total |  | 2185 |  | 16861
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 89
|  |  |  | Total Unavailable Capacity |  |  |  | 389
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:19 | 18:18 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-1 Scheduled S/D
| 08:20 | 18:18 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-01 Project Work S/D Due to Project work
| 08:20 | 18:19 | Faridpur 132/33kV S/S 230kV Faridpur-Gopalganj CKT-2 Scheduled S/D
| 08:21 | 18:19 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 Project Work S/D Due to Project work
| 08:37 | 08:57 | Ashuganj-Kishoreganj 132kV Ckt-1 Tripped from Ashuganj 132/33kV end showing F21 relays. | [7 empty] | 80.0MW load
interrup. Ashuganj
132/33kV end
| 09:44 | 09:58 | Kabirpur 132/33kV S/S XFR, T-I LT Tripped showing Micom relays Due to 33kV Kabirpur | [7 empty] | 70.0MW load
|  |  | feeder faulty (breaker & CT blast) | [7 empty] | interrup.
| 09:44 | 09:58 | Kabirpur 132/33kV S/S XFR, T-2 LT Tripped showing Micom relays Due to 33kV Kabirpur | [7 empty] | 70.0MW load
|  |  | feeder faulty ( breaker &CT) blast | [7 empty] | interrup.
| 09:51 | 19:02 | Naogaon 132/33kV S/S Naogaon-SPPP Ckt-1 Project Work S/D Due to Project work.
| 09:51 | 19:04 | Bogura(New)-Naogaon 132 kV Ckt-2 Project Work S/D from Naogaon 132/33kV end Due to
Project work and from Bogura 230/132kVend.
| 10:27 | 17:45 | Korerhat 400/230/132kV S/S ATR-3(7103T) LT Project Work S/D Due to DFDR work
| 10:28 | 17:43 | Korerhat 400/230/132kV S/S ATR-3(7103T) HT Project Work S/D Due to DFDR Work
| 12:00 |  | Day Peak Generation: 14071 MW.
|  | 12:56 | Khulna(S) 230/132kV S/S Rupsha Ckt-2 is restored.
| 13:11 |  | Khulna(S) 230/132kV S/S Rupsha Ckt-1 Scheduled S/D
| 14:12 | 17:46 | Madunaghat-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Taken by korerhat
|  | 15:35 | Brahmanbaria 132/33kV S/S 403T HT is restored.
|  | 16:05 | Brahmanbaria 132/33kV S/S 403T LT is restored.
|  | 18:29 | Mirsorai 400/230/33kV S/S ATR-1 HT is restored.
|  | 18:32 | Mirsorai 400/230/33kV S/S ATR-1 LT is restored.
|  | 18:42 | Mirsorai 400/230/33kV S/S Korerhat-1 is restored.
|  | 18:42 | Korerhat 400/230/132kV S/S Mirsharai-1 is restored.
| 21:00 |  | Evening Peak Generation: 15195 MW.
| 06:00 |  | Minimum Generation: 12667 MW.
| 07:45 |  | Bogura 230/132kV S/S T-01 HT Tripped showing Backup Trip Lockout Relay (K51) relays.
| 07:45 |  | Bogura 230/132kV S/S T-01 LT Tripped showing N/A relays.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-08-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 355 | 7938000 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 121 | 3137367 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 144133 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7398267 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 392400 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 3026880 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 666111 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 533940 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 308400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 513360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 41 | 1014720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 81 | 1645713 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 73 | 739152 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2274240 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1177920 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 54047 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 518400 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 250 | 6193079 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3310800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 1967.42 | 40986929
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 106626.6 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 64665 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 998880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5131958 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 200 | 4461956 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 99 | 2398691 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 23 | 374784 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 362317 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 296640 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 47 | 634560 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 19199 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 388909 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 386279 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 107 | 2574316 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 294720 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 94 | 2236855 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 140 | 1175927 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28974543 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 7 | 274080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1130 | 27149090.91 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 3494.36 | 78305836.51
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 196 | 4916000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 354 | 8572300 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 497016 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 138240 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 217455 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1225100 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 43 | 730981 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 540752 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 156834 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 186 | 3838560 | -
| Import (Tripura) |  | Import | 0 | 160 | 134 | 3444480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 786235 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 8 | 186510 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 105 | 1602840 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 177240 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 73 | 982080 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 142809 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1286.2 | 28155432
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 32940 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 3400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 155 | 222000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1351200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 95000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 90000 | 09:00-12:00 &17:00-23:00hrs 24MW & rest time 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 479520 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 270 | 2274060
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 32029 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 956000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 936960 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 146 | 3470072.73 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 31 | 392640 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2203900 | plant availability zero
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 173232 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7402000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 314 | 8679000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 983 | 24245833.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 872 | 21112000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 180000 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 376704 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 48528 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 273600 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 150 | 647931 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1148 | 27556360 | AGC+FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2252 | 51107123
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1051 | 23709091 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 399552 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 100 | 2398000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 560 | 13986909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5257790 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 440400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7331000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1470 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2271 | 53524212.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 124240 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 15 | 29915 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 143 | 3510636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 224 | 5884654 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 14 | 80820 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 489250 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 581792 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 831360 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 57 | 399744 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 8460 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1449.2 | 35633818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 76016 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 190783 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2080.2 | 47841488
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 728910 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 52 | 1214399 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 165 | 3932000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 810700 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 40551.96 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 110 | 2706728 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 118407 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 470880 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 591 | 10022575.96
Eastern Grid Total |  |  |  |  | 17440.562 | 8000.98 | 173968091.24
Western Grid Total |  |  |  |  | 11731.125 | 7194.2 | 162495399.05
National Grid Total |  |  |  |  | 29171.687 | 15195.18 | 336463490.29
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-08-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10195.52 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4516 | MW
i) Dhaka area |  |  | 5639.32 |  | MW | i) Khulna area |  |  |  | 1647 | MW
ii) Chattogram area |  |  | 1468.2 |  | MW | ii) Barishal area |  |  |  | 448.6 | MW
iii) Cumilla area |  |  | 1367 |  | MW | iii) Rajshahi area |  |  |  | 1501.4 | MW
iv) Mymensingh area |  |  | 1135 |  | MW | iv) Rangpur area |  |  |  | 919 | MW
v) Sylhet area |  |  | 586 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14711.52 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 19 | 11:00 | 67 | HaripurSBU | 125 | 20:00 | 133 | Narshingdi | 172 | 08:00 | 199 | Uttara | 101 | 13:00
2 | AKSML | 14.6 | 00:00 | 68 | Hasnabad | 95 | 19:00 | 134 | Natore | 129 | 20:00 | 200 | UttaraNew | 57 | 00:00
3 | Aftabnagar | 44 | 00:00 | 69 | Hathazari | 94 | 19:30 | 135 | Nawabganj | 64 | 21:00 | 201 | Zigatola | 95 | 13:00
4 | Agargaon | 127 | 14:00 | 70 | Hatirjheel | 82 | 13:00 | 136 | Netrakona | 124 | 21:00
5 | Agrabad | 72 | 17:00 | 71 | Ishurdi | 74 | 21:00 | 137 | New | 86 | 12:00
6 | Amnura | 30 | 21:00 | 72 | Jaldhaka | 77 | 21:00 | 138 | Niamatpur | 85 | 22:00
7 | Ashuganj | 109 | 21:00 | 73 | Jamalpur | 110 | 19:30 | 139 | Noapara | 41 | 12:00
8 | BSRM | 204 | 09:00 | 74 | Jashore | 166 | 19:30 | 140 | PHP | 11 | 19:00
9 | Bagerhat | 91 | 21:00 | 75 | Jhenaidah | 86 | 18:30 | 141 | Pabna | 105 | 19:30
10 | Bajitpur | 75 | 05:00 | 76 | Joydebpur | 177 | 19:30 | 142 | Palashbari | 118 | 19:00
11 | Bakerganj | 14.6 | 19:00 | 77 | Joypurhat | 56 | 21:00 | 143 | Panchagarh | 67 | 00:00
12 | Bakulia | 95 | 21:00 | 78 | Juldah | 14 | 12:00 | 144 | Patiya | 11 | 19:00
13 | Banani | 77 | 13:00 | 79 | KSRM | 40 | 14:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 17 | 11:00 | 80 | Kabirpur | 225 | 21:00 | 146 | Patuakhali | 58 | 12:00
15 | Barapukuria | 66 | 10:00 | 81 | Kachua | 90 | 18:30 | 147 | Payra | 30 | 11:00
16 | Barguna | 22 | 19:00 | 82 | Kaliganj | 37 | 13:00 | 148 | Postogola | 65 | 00:00
17 | Barishal | 104 | 13:00 | 83 | Kallyanpur | 129 | 00:00 | 149 | Pubail | 40 | 21:00
18 | Barishal-230 | 98 | 22:00 | 84 | Kalurghat | 40 | 17:00 | 150 | Purbachal | 30 | 12:00
19 | Baroaulia | 40 | 15:00 | 85 | Kamrangirchar | 86 | 12:00 | 151 | Purbasadipur | 127 | 07:00
20 | Baroirhat | 57 | 18:30 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 33 | 11:00
21 | Bashundhara | 219 | 13:00 | 87 | Kasba | 32 | 19:30 | 153 | Rahim | 54 | 04:00
22 | BashundharaCement | 6 | 00:00 | 88 | Kazla | 131 | 13:00 | 154 | Rajbari | 73 | 07:00
23 | Beanibazar | 68 | 23:00 | 89 | Keranigonj | 93 | 18:30 | 155 | Rajendrapur | 120 | 08:00
24 | Benapole | 58 | 23:00 | 90 | Khagrachori | 34 | 18:30 | 156 | Rajshahi | 112 | 07:00
25 | Bhaluka | 163 | 10:00 | 91 | Khulna | 66 | 13:00 | 157 | Rajshahi-230 | 101 | 19:00
26 | Bhandaria | 46 | 12:00 | 92 | Khulshi | 171 | 19:00 | 158 | Ramganj | 98 | 19:00
27 | Bhangura | 32 | 18:30 | 93 | Kishoreganj | 130 | 21:00 | 159 | Rampur | 44 | 19:00
28 | Bheramara(GK) | 64 | 02:00 | 94 | Kodda | 304 | 20:00 | 160 | Rangamati | 17 | 18:30
29 | Bhulta | 220 | 23:00 | 95 | Kulaura | 53 | 22:00 | 161 | Rangpur | 128 | 18:30
30 | Bog-Sherpur | 64 | 22:00 | 96 | Kurigram | 62 | 18:30 | 162 | Ruppur | 4 | 09:00
31 | Bogura | 190 | 21:00 | 97 | Kushtia | 145 | 18:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 73 | 19:30 | 98 | Laksam | 36 | 23:00 | 164 | Saidpur | 110 | 10:00
33 | Brahmanbaria | 125 | 20:00 | 99 | Lakshmipur | 42 | 19:00 | 165 | Santhia | 32 | 05:00
34 | Cantonment | 132 | 13:00 | 100 | Lalbag | 75 | 13:00 | 166 | Satkhira | 133 | 00:00
35 | Chandina | 48 | 05:00 | 101 | Lalmonirhat | 58 | 23:00 | 167 | Satmasjid | 107 | 13:00
36 | Chandpur | 84 | 19:00 | 102 | MI_Cement | 13.8 | 00:00 | 168 | Savar | 209 | 14:00
37 | Chandraghona | 29 | 19:00 | 103 | Madanganj | 49 | 08:00 | 169 | SevenRings | 6.48 | 13:00
38 | Chapai | 70 | 10:00 | 104 | Madaripur | 99 | 13:00 | 170 | ShahCement | 25 | 02:00
39 | Charfasson | 31 | 22:00 | 105 | Madartek | 88 | 00:00 | 171 | Shahjadpur | 80 | 18:00
40 | Charsaidpur | 24 | 15:00 | 106 | Madunaghat | 52 | 18:30 | 172 | Shahjibazar | 131 | 22:00
41 | Chauddagram | 65 | 19:00 | 107 | Magura | 62 | 18:30 | 173 | Shahmirpur | 48 | 18:30
42 | Chhatak | 32 | 22:00 | 108 | Mahasthangarh | 72 | 04:00 | 174 | Shariatpur | 83 | 21:00
43 | Chowmuhani | 135 | 19:00 | 109 | Maijdee | 46 | 19:00 | 175 | Sherpur | 140 | 22:00
44 | Chuadanga | 107 | 06:00 | 110 | Manikganj | 131 | 22:00 | 176 | Shikalbaha | 31 | 03:00
45 | Coxsbazar | 142 | 18:30 | 111 | Maniknagar | 83 | 13:00 | 177 | Shitalakhya | 75.5 | 14:00
46 | Cumilla(N) | 114 | 19:00 | 112 | Matarbari | 47 | 18:00 | 178 | Sholosohor | 54 | 17:00
47 | Cumilla(S) | 170 | 14:00 | 113 | Matuail | 84 | 00:00 | 179 | Shomvuganj | 37 | 22:00
48 | Daganbhuiyan | 40 | 22:00 | 114 | Metrorail_Motijheel | 35 | 19:00 | 180 | Shyampur | 160 | 00:00
49 | Daudkandi | 127 | 21:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 135 | 12:00
50 | DhakaUniversity | 94 | 13:00 | 116 | Millgate | 115 | 12:00 | 182 | Sirajganj | 128 | 21:00
51 | Dhamrai | 94 | 22:00 | 117 | Mirpur | 157 | 19:00 | 183 | Sitakunda | 35 | 19:00
52 | Dhanmondi | 104.6 | 13:00 | 118 | Mirsorai | 49 | 06:00 | 184 | Sonargaon | 126 | 04:00
53 | Dohazari | 96 | 18:30 | 119 | Mirzapur | 37 | 21:00 | 185 | Sreemongol | 71 | 03:00
54 | Faridpur | 156 | 22:00 | 120 | Mithapukur | 72 | 22:00 | 186 | Sreepur | 127 | 08:00
55 | Fatullah | 111 | 12:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 49.57 | 22:00
56 | Fenchuganj | 40 | 23:00 | 122 | Mogbazar | 63.7 | 13:00 | 188 | Sunamganj | 50 | 21:00
57 | Feni | 103 | 23:00 | 123 | Mongla | 49 | 11:00 | 189 | Sylhet | 108 | 18:00
58 | GPH | 2 | 10:00 | 124 | Motijheel | 53 | 13:00 | 190 | Sylhet_(South) | 72 | 18:30
59 | Ghatail | 88 | 19:30 | 125 | Muktagacha | 36 | 18:30 | 191 | TK | 24 | 19:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 118 | 21:00 | 192 | Tangail | 172 | 23:00
61 | Ghorashal-230 | 103 | 23:00 | 127 | Muradnagar | 47 | 00:00 | 193 | Taraganj | 35 | 10:00
62 | Goalpara | 39 | 13:00 | 128 | Mymensingh | 138 | 19:30 | 194 | Tasnim | 48 | 15:00
63 | Gollamari | 108 | 13:00 | 129 | Nabinagar | 106 | 20:00 | 195 | Thakurgaon | 113 | 19:30
64 | Gopalganj | 103 | 19:00 | 130 | Naogaon | 138 | 22:00 | 196 | Tongi | 145 | 12:00
65 | Gulshan | 122 | 12:00 | 131 | Narail | 62 | 19:00 | 197 | Ullahpara | 34 | 19:00
66 | Halishahar | 117 | 10:00 | 132 | Narinda | 81 | 13:00 | 198 | Ullon | 46 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-08-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14098.59 | 3232 |  | 17475.59
1:00 | 13635.92 | 3006 |  | 16776.92
2:00 | 13594.18 | 2799 |  | 16519.18
3:00 | 13553.47 | 2684 |  | 16358.47
4:00 | 13513.33 | 2563 |  | 16191.33
5:00 | 13564.99 | 2306 |  | 15974.99
6:00 | 13381.67 | 2083 |  | 15558.67
7:00 | 13355.79 | 1887 |  | 15327.79
8:00 | 13216.86 | 1762 |  | 15058.15
9:00 | 13428.7 | 1839 |  | 15350.46
10:00 | 13731.41 | 1226 |  | 15012.58
11:00 | 13917.12 | 1347 |  | 15324.74
12:00 | 14070.23 | 2021 |  | 16182.23
13:00 | 14207.3 | 1843 |  | 16133.3
14:00 | 13975.21 | 2020 |  | 16086.21
15:00 | 13873.97 | 2284 |  | 16260.97
16:00 | 13808.8 | 1995 |  | 15893.8
17:00 | 13612.54 | 1508 |  | 15188.54
18:00 | 13810.03 | 1194 |  | 15058.03
19:00 | 14842.03 | 1880 |  | 16807.03
19:30 | 15048.96 | 1955 |  | 17091.96
20:00 | 15085.64 | 1928 |  | 17100.64
21:00 | 15195.18 | 2185 |  | 17478.18
22:00 | 15052.78 | 1809 |  | 16942.78
23:00 | 14925.51 | 1961 |  | 16974.51
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 04-08-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 160 | 43 | 460 | 142 | 1590 | 748 | Ishurdi-Ghorashal Ckt-1 | Export | 3823854.54
1:00 | 159 | 50 | 476 | 148 | 1654 | 752
2:00 | 144 | 41 | 450 | 138 | 1608 | 710 |  | Import | 0
3:00 | 135 | 32 | 426 | 124 | 1590 | 690
4:00 | 135 | 33 | 440 | 130 | 1560 | 676 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 131 | 32 | 420 | 126 | 1546 | 676
6:00 | 129 | 27 | 420 | 112 | 1548 | 646 |  | Import | 0
7:00 | 125 | 22 | 420 | 106 | 1600 | 648
8:00 | 142 | 31 | 480 | 142 | 1704 | 724 | Sirajganj-Sreepur Ckt-1 | Export | 2975000
9:00 | 184 | 59 | 530 | 142 | 1876 | 814
10:00 | 155 | 38 | 490 | 136 | 1878 | 742 |  | Import | 0
11:00 | 175 | 58 | 570 | 212 | 1902 | 842
12:00 | 179 | 60 | 562 | 216 | 1892 | 882 | Sirajganj-Sreepur Ckt-2 | Export | 2986000
13:00 | 168 | 53 | 542 | 210 | 1782 | 812
14:00 | 177 | 58 | 560 | 216 | 1896 | 828 |  | Import | 0
15:00 | 181 | 65 | 540 | 216 | 1934 | 954
16:00 | 183 | 70 | 540 | 230 | 1846 | 966 | Gopalganj-Aminbazar Ckt-1 | Export | 20900000
17:00 | 170 | 59 | 526 | 226 | 1860 | 926
18:00 | 144 | 37 | 476 | 178 | 1760 | 758 |  | Import | 0
18:30 | 146 | 38 | 500 | 200 | 1774 | 786
19:00 | 173 | 54 | 536 | 220 | 1756 | 796 | Gopalganj-Aminbazar Ckt-2 | Export | 20960000
19:30 | 181 | 60 | 542 | 216 | 1784 | 810
20:00 | 175 | 57 | 526 | 210 | 1720 | 784 |  | Import | 0
21:00 | 174 | 54 | 540 | 226 | 1748 | 784
22:00 | 175 | 55 | 538 | 224 | 1714 | 760 |  | Total Export | 51644854.54
23:00 | 163 | 43 | 532 | 214 | 1730 | 744 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-08-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7457.52 | 6641.07 | 14098.59 | DAILY GENERATION CURVE
00:30 | 7326.07 | 6541.185 | 13867.255
01:00 | 7194.62 | 6441.3 | 13635.92 | 04-08-2026
01:30 | 7156.62 | 6458.43 | 13615.05
02:00 | 7118.62 | 6475.56 | 13594.18
02:30 | 7095.37 | 6478.455 | 13573.825
03:00 | 7072.12 | 6481.35 | 13553.47
03:30 | 7049.62 | 6483.78 | 13533.4
04:00 | 7027.12 | 6486.21 | 13513.33
04:30 | 7071.62 | 6467.54 | 13539.16
05:00 | 7116.12 | 6448.87 | 13564.99
05:30 | 7038.095 | 6435.235 | 13473.33
06:00 | 6960.07 | 6421.6 | 13381.67
06:30 | 6927.595 | 6441.135 | 13368.73
07:00 | 6895.12 | 6460.67 | 13355.79
07:30 | 6840.825 | 6445.5 | 13286.325
08:00 | 6786.53 | 6430.33 | 13216.86
08:30 | 6837.625 | 6485.155 | 13322.78
09:00 | 6888.72 | 6539.98 | 13428.7
09:30 | 6911.935 | 6668.12 | 13580.055
10:00 | 6935.15 | 6796.26 | 13731.41
10:30 | 7008.59 | 6815.675 | 13824.265
11:00 | 7082.03 | 6835.09 | 13917.12
11:30 | 7155.56 | 6838.115 | 13993.675
12:00 | 7229.09 | 6841.14 | 14070.23
12:30 | 7300.01 | 6838.755 | 14138.765
13:00 | 7370.93 | 6836.37 | 14207.3
13:30 | 7302.515 | 6788.74 | 14091.255
14:00 | 7234.1 | 6741.11 | 13975.21
14:30 | 7182.78 | 6741.81 | 13924.59
15:00 | 7131.46 | 6742.51 | 13873.97
15:30 | 7130.53 | 6710.855 | 13841.385
16:00 | 7129.6 | 6679.2 | 13808.8
16:30 | 7093.45 | 6617.22 | 13710.67
17:00 | 7057.3 | 6555.24 | 13612.54
17:30 | 7175.22 | 6536.065 | 13711.285
18:00 | 7293.14 | 6516.89 | 13810.03
18:30 | 7580.88 | 6745.15 | 14326.03
19:00 | 7868.62 | 6973.41 | 14842.03
19:30 | 7962.62 | 7086.34 | 15048.96
20:00 | 7994.62 | 7091.02 | 15085.64
20:30 | 7997.8 | 7142.61 | 15140.41 |  | Executive Engineer
21:00 | 8000.98 | 7194.2 | 15195.18 |  | Network Operation Division
21:30 | 7952.48 | 7171.5 | 15123.98
22:00 | 7903.98 | 7148.8 | 15052.78
22:30 | 7808.59 | 7180.555 | 14989.145
23:00 | 7713.2 | 7212.31 | 14925.51

## En-Curve
QF-LDC-12
Date | 04-08-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2362 | 1150 | 873 | 38 | 116 | 1469.54 | 222 | 5504.53 | 0 | 708.42 | 1655.1 | 0 | 0 | 0 | 3232 | DAILY ENERGY CURVE
00:30 | 2362 | 1142.5 | 872.5 | 38 | 114 | 1474.155 | 222 | 5504.03 | 0 | 643.92 | 1493.65 | 0 | 0 | 0.5 | 3119 | 04-08-2026
01:00 | 2362 | 1135 | 872 | 38 | 112 | 1478.77 | 222 | 5503.53 | 0 | 579.42 | 1332.2 | 0 | 0 | 1 | 3006
01:30 | 2364.5 | 1158 | 872 | 38 | 128 | 1475.665 | 222 | 5503.765 | 0 | 549.92 | 1300.7 | 0 | 0 | 2.5 | 2902.5 | Energy Generated | 336.4635 |  | MKWHr
02:00 | 2367 | 1181 | 872 | 38 | 144 | 1472.56 | 222 | 5504 | 0 | 520.42 | 1269.2 | 0 | 0 | 4 | 2799 | Energy not Served | 49.362 |  | MKWHr
02:30 | 2368.5 | 1187.25 | 872.5 | 38 | 146 | 1472.455 | 216.5 | 5503.5 | 0 | 520.42 | 1243.2 | 0 | 0 | 5.5 | 2741.5 | Total Energy Requirement | 385.8255 |  | MKWHr
03:00 | 2370 | 1193.5 | 873 | 38 | 148 | 1472.35 | 211 | 5503 | 0 | 520.42 | 1217.2 | 0 | 0 | 7 | 2684
03:30 | 2373 | 1200 | 872.5 | 38 | 144 | 1474.78 | 210 | 5503.5 | 0 | 506.42 | 1200.2 | 0 | 0 | 11 | 2623.5
04:00 | 2376 | 1206.5 | 872 | 38 | 140 | 1477.21 | 209 | 5504 | 0 | 492.42 | 1183.2 | 0 | 0 | 15 | 2563
04:30 | 2406.5 | 1208.5 | 872.5 | 38 | 141 | 1471.54 | 208.5 | 5504.5 | 0 | 492.42 | 1181.2 | 0 | 0 | 14.5 | 2434.5
05:00 | 2437 | 1210.5 | 873 | 38 | 142 | 1465.87 | 208 | 5505 | 0 | 492.42 | 1179.2 | 0 | 0 | 14 | 2306
05:30 | 2443.5 | 1174 | 873 | 38 | 135 | 1467.02 | 207.5 | 5484.5 | 2.29 | 491.92 | 1144.1 | 0 | 0 | 12.5 | 2194.5
06:00 | 2450 | 1137.5 | 873 | 38 | 128 | 1468.17 | 207 | 5464 | 4.58 | 491.42 | 1109 | 0 | 0 | 11 | 2083
06:30 | 2423.5 | 1137.75 | 873 | 38 | 125 | 1472.245 | 207 | 5455 | 22.815 | 498.92 | 1103.5 | 0 | 0 | 12 | 1985
07:00 | 2397 | 1138 | 873 | 38 | 122 | 1476.32 | 207 | 5446 | 41.05 | 506.42 | 1098 | 0 | 0 | 13 | 1887
07:30 | 2396.5 | 1129 | 873 | 38 | 123 | 1478.605 | 207.5 | 5423.5 | 52.8 | 502.42 | 1050 | 0 | 0 | 12 | 1824.5
08:00 | 2396 | 1120 | 873 | 38 | 124 | 1480.89 | 208 | 5401 | 64.55 | 498.42 | 1002 | 0 | 0 | 11 | 1762
08:30 | 2396.5 | 1158.75 | 873 | 38 | 127 | 1482.42 | 215 | 5404.5 | 79.59 | 502.42 | 1034.1 | 0 | 0 | 11.5 | 1800.5
09:00 | 2397 | 1197.5 | 873 | 38 | 130 | 1483.95 | 222 | 5408 | 94.63 | 506.42 | 1066.2 | 0 | 0 | 12 | 1839
09:30 | 2374 | 1189.75 | 872.5 | 38 | 134 | 1479.555 | 222 | 5476.5 | 136.63 | 506.42 | 1141.7 | 0 | 0 | 9 | 1532.5
10:00 | 2351 | 1182 | 872 | 38 | 138 | 1475.16 | 222 | 5545 | 178.63 | 506.42 | 1217.2 | 0 | 0 | 6 | 1226
10:30 | 2354 | 1199.5 | 872 | 38 | 150 | 1478.145 | 222 | 5581.265 | 184.735 | 506.42 | 1232.7 | 0 | 0 | 5.5 | 1286.5
11:00 | 2357 | 1217 | 872 | 38 | 162 | 1481.13 | 222 | 5617.53 | 190.84 | 506.42 | 1248.2 | 0 | 0 | 5 | 1347
11:30 | 2377.5 | 1209 | 872.5 | 38 | 156 | 1477.695 | 222 | 5641.53 | 201.33 | 494.42 | 1299.2 | 0 | 0 | 4.5 | 1684
12:00 | 2398 | 1201 | 873 | 38 | 150 | 1474.26 | 222 | 5665.53 | 211.82 | 482.42 | 1350.2 | 0 | 0 | 4 | 2021
12:30 | 2428 | 1183 | 873 | 38 | 153 | 1471.16 | 222 | 5667.03 | 231.455 | 494.42 | 1369.2 | 0 | 0 | 8.5 | 1932
13:00 | 2458 | 1165 | 873 | 38 | 156 | 1468.06 | 222 | 5668.53 | 251.09 | 506.42 | 1388.2 | 0 | 0 | 13 | 1843
13:30 | 2459.5 | 1166.5 | 873 | 38 | 164 | 1470.18 | 222 | 5652.53 | 231.425 | 453.92 | 1342.2 | 0 | 0 | 18 | 1931.5
14:00 | 2461 | 1168 | 873 | 38 | 172 | 1472.3 | 222 | 5636.53 | 211.76 | 401.42 | 1296.2 | 0 | 0 | 23 | 2020
14:30 | 2450 | 1165.5 | 872.5 | 38 | 169 | 1474.095 | 222 | 5645.53 | 212.845 | 364.92 | 1291.2 | 0 | 0 | 19 | 2152
15:00 | 2439 | 1163 | 872 | 38 | 166 | 1475.89 | 222 | 5654.53 | 213.93 | 328.42 | 1286.2 | 0 | 0 | 15 | 2284
15:30 | 2420.5 | 1162.5 | 872 | 38 | 166 | 1464.91 | 222 | 5638.265 | 187.59 | 328.42 | 1327.2 | 0 | 0 | 14 | 2139.5
16:00 | 2402 | 1162 | 872 | 38 | 166 | 1453.93 | 222 | 5622 | 161.25 | 328.42 | 1368.2 | 0 | 0 | 13 | 1995
16:30 | 2413 | 1136.5 | 872.5 | 38 | 159 | 1432.995 | 174 | 5605 | 137.055 | 327.42 | 1404.2 | 0 | 0 | 11 | 1751.5
17:00 | 2424 | 1111 | 873 | 38 | 152 | 1412.06 | 126 | 5588 | 112.86 | 326.42 | 1440.2 | 0 | 0 | 9 | 1508
17:30 | 2378.5 | 1133 | 873 | 38 | 153 | 1410.58 | 149 | 5534.5 | 71.585 | 356.92 | 1598.2 | 0 | 0 | 15 | 1351
18:00 | 2333 | 1155 | 873 | 38 | 154 | 1409.1 | 172 | 5481 | 30.31 | 387.42 | 1756.2 | 0 | 0 | 21 | 1194
18:30 | 2361 | 1167.5 | 872.5 | 38 | 162 | 1431.255 | 172 | 5547.5 | 15.155 | 526.42 | 1925.2 | 90 | 0 | 17.5 | 1537
19:00 | 2389 | 1180 | 872 | 38 | 170 | 1453.41 | 172 | 5614 | 0 | 665.42 | 2094.2 | 180 | 0 | 14 | 1880
19:30 | 2371 | 1199 | 873 | 38 | 130 | 1424.34 | 172 | 5575 | 0 | 692.42 | 2225.2 | 315 | 0 | 34 | 1955
20:00 | 2377 | 1146 | 872 | 38 | 128 | 1434.02 | 221 | 5608 | 0 | 690.42 | 2237.2 | 315 | 0 | 19 | 1928
20:30 | 2381 | 1166.5 | 872 | 38 | 131 | 1441.61 | 220.5 | 5622.5 | 0 | 696.42 | 2242.88 | 315 | 0 | 13 | 2056.5
21:00 | 2385 | 1187 | 872 | 38 | 134 | 1449.2 | 220 | 5637 | 0 | 702.42 | 2248.56 | 315 | 0 | 7 | 2185
21:30 | 2390 | 1179.5 | 872.5 | 38 | 134 | 1443.5 | 220 | 5634 | 0 | 691.92 | 2199.06 | 315 | 0 | 6.5 | 1997
22:00 | 2395 | 1172 | 873 | 38 | 134 | 1437.8 | 220 | 5631 | 0 | 681.42 | 2149.56 | 315 | 0 | 6 | 1809
22:30 | 2395.5 | 1177 | 872.5 | 38 | 136 | 1449.055 | 220 | 5645.5 | 0 | 618.21 | 2117.38 | 315 | 0 | 5 | 1885
23:00 | 2396 | 1182 | 872 | 38 | 138 | 1460.31 | 220 | 5660 | 0 | 555 | 2085.2 | 315 | 0 | 4 | 1961
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-08-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 365 | 06:00 | 340 | 12:00 | Madunaghat | 391 | 07:00 | 380 | 16:00
Amtali | 408 | 06:00 | 402 | 15:00 | Meghnaghat | 370 | 06:00 | 340 | 15:00
Ashuganj | 362 | 01:00 | 335 | 15:00 | Mirsorai | 387 | 07:00 | 371 | 15:00
Bhulta | 384 | 07:00 | 354 | 15:00 | Payra | 410 | 19:30 | 404 | 12:00
Bibiana | 373 | 06:00 | 360 | 15:00 | Rahanpur | 396 | 19:30 | 389 | 13:00
BIPTC | 401 | 05:00 | 394 | 12:00 | Rampal | 390 | 01:00 | 378 | 15:00
Bogura | 379 | 19:30 | 368 | 15:00
Gopalganj | 383 | 06:00 | 370 | 15:00
Kaliakoir | 362 | 01:00 | 335 | 15:00
Korerhat | 386 | 06:00 | 365 | 03:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 07:00 | 206 | 15:00 | Ishurdi | 231 | 01:00 | 222 | 11:00
AKSML | 232.6 | 07:00 | 222.2 | 14:00 | Jhenaidah | 222 | 01:00 | 213 | 13:00
Aminbazar | 223 | 07:00 | 207 | 15:00 | Kachua | 222 | 01:00 | 211 | 15:00
Ashuganj | 220 | 06:00 | 206 | 14:00 | Kaliakoir | 220 | 04:00 | 205 | 15:00
Ashuganj-400 | 220 | 06:00 | 206 | 14:00 | Keranigonj | 220 | 06:00 | 203 | 15:00
Baghabari | 226 | 19:00 | 220 | 11:00 | Khulna(S) | 222 | 01:00 | 214 | 13:00
Barapukuria | 227 | 19:30 | 219 | 10:00 | Korerhat | 221 | 03:00 | 211 | 15:00
Barapukuria-230 | 227 | 19:30 | 219 | 10:00 | Madunaghat | 233 | 07:00 | 227 | 12:00
Barishal | 224 | 07:00 | 218 | 15:00 | Madunaghat-400 | 235 | 07:00 | 228 | 15:00
Bheramara | 230 | 01:00 | 220 | 12:00 | Maniknagar | 219 | 05:00 | 200 | 15:00
Bhulta | 221 | 06:00 | 202 | 15:00 | Meghnaghat | 225 | 07:00 | 209 | 16:00
Bibiana | 217 | 03:00 | 207 | 15:00 | Meghnaghat-400 | 222 | 06:00 | 200 | 15:00
BIPTC | 232 | 01:00 | 221 | 11:00 | Mirsorai | 226 | 00:00 | 216 | 12:00
Bogura | 237 | 19:30 | 231 | 11:00 | Naogaon | 221 | 00:00 | 208 | 15:00
Bogura-400 | 238 | 19:30 | 231 | 15:00 | Purbasadipur | 224 | 19:30 | 216 | 10:00
Borhanuddin | 229 | 08:00 | 224 | 13:00 | Rajshahi | 228 | 19:30 | 219 | 11:00
BSRM | 222 | 07:00 | 211 | 15:00 | Rampal | 222 | 01:00 | 214 | 12:00
Charfasson | 229 | 03:00 | 223 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 222 | 07:00 | 212 | 15:00 | Rampura | 221 | 07:00 | 200 | 15:00
Cumilla(N) | 218 | 07:00 | 204 | 14:00 | Shikalbaha | 236 | 23:00 | 227 | 14:00
Faridpur | 217 | 03:00 | 200 | 13:00 | Shyampur | 220 | 06:00 | 203 | 15:00
Fenchuganj | 218 | 04:00 | 211 | 15:00 | Siddhirganj | 217 | 02:00 | 201 | 15:00
Feni | 220 | 06:00 | 208 | 15:00 | Sirajgonj | 231 | 01:00 | 227 | 11:00
Ghorashal | 220 | 01:00 | 210 | 11:00 | Sreepur | 219 | 03:00 | 209 | 15:00
Ghorashal-230 | 210 | 03:00 | 192 | 15:00 | Tongi | 212 | 04:00 | 195 | 15:00
Gopalganj | 218 | 03:00 | 212 | 12:00
GPH | 229 | 06:00 | 220 | 15:00
Haripur | 221 | 07:00 | 202 | 15:00
Hasnabad | 220 | 04:00 | 201 | 15:00
Hathazari | 230 | 03:00 | 223 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 07:00 | 123 | 15:00 | Madartek | 137 | 07:00 | 122 | 16:00
Agargaon | 134 | 06:00 | 123 | 15:00 | Madunaghat | 135 | 04:00 | 131 | 11:00
Agrabad | 134 | 20:00 | 128 | 15:00 | Magura | 134 | 01:00 | 127 | 23:00
AKS | 131 | 00:00 | 126 | 11:00 | Mahasthangarh | 135 | 19:30 | 129 | 07:00
Aminbazar | 126 | 07:00 | 117 | 11:00 | Maijdee | 124 | 01:00 | 117 | 15:00
Amnura | 138 | 19:30 | 126 | 11:00 | Manikganj | 125 | 00:00 | 120 | 12:00
Ashuganj | 127 | 06:00 | 117 | 15:00 | Maniknagar | 137 | 07:00 | 122 | 16:00
Ashuganj-230 | 130 | 03:00 | 124 | 15:00 | Matarbari | 127 | 19:00 | 116 | 11:00
Bagerhat | 124 | 01:00 | 119 | 22:00 | Matuail | 131 | 05:00 | 121 | 15:00
Bajitpur | 123 | 09:00 | 116 | 11:00 | Metrorail_Motijheel | 137 | 07:00 | 122 | 16:00
Bakerganj | 129 | 07:00 | 126 | 13:00 | Metrorail_Uttara | 127 | 05:00 | 113 | 15:00
Bakulia | 134 | 00:00 | 129 | 11:00 | Millgate | 128 | 03:00 | 115 | 11:00
Banani | 138 | 04:00 | 122 | 13:00 | Mirpur | 125 | 05:00 | 115 | 11:00
Bangabhaban | 136 | 03:00 | 122 | 15:00 | Mirzapur | 125 | 04:00 | 119 | 09:00
Barapukuria | 138 | 19:30 | 129 | 10:00 | Mithapukur | 134 | 19:30 | 126 | 10:00
Barguna | 130 | 07:00 | 126 | 12:00 | MI_Cement | 130 | 07:00 | 118 | 15:00
Barishal | 130 | 07:00 | 125 | 12:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal-230 | 130 | 07:00 | 126 | 11:00 | Mogbazar | 138 | 07:00 | 124 | 15:00
Baroaulia | 133 | 20:00 | 129 | 10:00 | Mongla | 124 | 18:00 | 118 | 23:00
Baroirhat | 130 | 13:00 | 122 | 15:00 | Motijheel | 136 | 03:00 | 122 | 15:00
Bashundhara | 137 | 06:00 | 115 | 11:00 | Muktagacha | 127 | 09:00 | 114 | 00:00
BashundharaCement | 131 | 07:00 | 121 | 17:00 | Munshiganj | 129 | 06:00 | 120 | 16:00
Beanibazar | 123 | 06:00 | 118 | 11:00 | Muradnagar | 124 | 06:00 | 116 | 15:00
Benapole | 131 | 01:00 | 121 | 13:00 | Mymensingh | 126 | 10:00 | 108 | 21:00
Bhaluka | 127 | 09:00 | 116 | 21:00 | Nabinagar | 124 | 03:00 | 117 | 11:00
Bhandaria | 127 | 18:30 | 120 | 12:00 | Naogaon | 133 | 00:00 | 125 | 12:00
Bhangura | 131 | 19:30 | 127 | 11:00 | Narail | 134 | 09:00 | 127 | 23:00
Bheramara | 135 | 01:00 | 129 | 11:00 | Narinda | 137 | 07:00 | 122 | 16:00
Bheramara(GK) | 133 | 09:00 | 128 | 11:00 | Narshingdi | 123 | 10:00 | 113 | 15:00
Bhulta | 125 | 08:00 | 118 | 16:00 | Natore | 133 | 09:00 | 128 | 11:00
Bhulta-400 | 128 | 07:00 | 117 | 15:00 | Nawabganj | 132 | 04:00 | 122 | 15:00
Bog-Sherpur | 134 | 19:30 | 129 | 11:00 | Netrakona | 120 | 00:00 | 106 | 22:00
Bogura | 137 | 19:30 | 132 | 11:00 | New | 130 | 06:00 | 115 | 15:00
Bogura-230 | 137 | 19:30 | 132 | 11:00 | Niamatpur | 132 | 06:00 | 128 | 11:00
Brahmanbaria | 124 | 07:00 | 116 | 15:00 | Noapara | 131 | 01:00 | 124 | 13:00
Cantonment | 134 | 07:00 | 122 | 13:00 | Pabna | 132 | 01:00 | 127 | 11:00
Chandina | 126 | 03:00 | 118 | 15:00 | Palashbari | 132 | 19:30 | 126 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandpur | 131 | 18:00 | 120 | 15:00 | Panchagarh | 136 | 09:00 | 131 | 12:00
Chandraghona | 136 | 06:00 | 132 | 11:00 | Patiya | 133 | 18:30 | 128 | 12:00
Chapai | 131 | 09:00 | 129 | 10:00 | Patnitala | 130 | 00:00 | 122 | 13:00
Charsaidpur | 131 | 06:00 | 120 | 15:00 | Patuakhali | 129 | 02:00 | 126 | 13:00
Chauddagram | 126 | 00:00 | 119 | 15:00 | Payra | 133 | 00:00 | 131 | 11:00
Chhatak | 121 | 06:00 | 115 | 11:00 | PHP | 128 | 04:00 | 122 | 15:00
Chowmuhani | 125 | 05:00 | 118 | 15:00 | Postogola | 131 | 05:00 | 120 | 15:00
Chuadanga | 132 | 01:00 | 126 | 23:00 | Pubail | 128 | 05:00 | 114 | 15:00
Coxsbazar | 127 | 19:00 | 118 | 18:00 | Purbachal | 137 | 06:00 | 121 | 15:00
Cumilla(N) | 126 | 18:00 | 118 | 14:00 | Purbasadipur | 136 | 19:30 | 130 | 10:00
Cumilla(S) | 130 | 01:00 | 119 | 15:00 | Rahanpur | 132 | 00:00 | 129 | 13:00
Daganbhuiyan | 127 | 07:00 | 120 | 15:00 | Rahanpur-400 | 133 | 19:30 | 130 | 12:00
Daudkandi | 124 | 05:00 | 115 | 15:00 | Rahim | 131 | 06:00 | 121 | 15:00
DhakaUniversity | 137 | 06:00 | 122 | 15:00 | Rajbari | 129 | 07:00 | 113 | 13:00
Dhamrai | 126 | 06:00 | 118 | 11:00 | Rajendrapur | 124 | 10:00 | 116 | 13:00
Dhanmondi | 137 | 06:00 | 121 | 15:00 | Rajshahi | 130 | 01:00 | 124 | 11:00
Dohazari | 131 | 08:00 | 124 | 11:00 | Rajshahi-230 | 131 | 01:00 | 126 | 11:00
Faridpur | 126 | 08:00 | 118 | 11:00 | Ramganj | 126 | 01:00 | 118 | 14:00
Fatullah | 131 | 06:00 | 118 | 16:00 | Rampur | 134 | 20:00 | 128 | 11:00
Fenchuganj | 129 | 07:00 | 124 | 13:00 | Rampura | 138 | 07:00 | 122 | 12:00
Feni | 128 | 04:00 | 121 | 16:00 | Rangamati | 135 | 04:00 | 130 | 15:00
Feni-230 | 128 | 07:00 | 120 | 15:00 | Rangpur | 134 | 19:30 | 124 | 08:00
Ghatail | 123 | 19:00 | 112 | 09:00 | Ruppur | 134 | 09:00 | 130 | 10:00
Ghorashal | 126 | 02:00 | 118 | 14:00 | Saidpur | 136 | 19:30 | 129 | 10:00
Goalpara | 133 | 01:00 | 127 | 13:00 | Santhia | 133 | 01:00 | 127 | 11:00
Gollamari | 132 | 01:00 | 127 | 11:00 | Satkhira | 128 | 01:00 | 122 | 23:00
Gopalganj | 127 | 01:00 | 122 | 13:00 | Satmasjid | 133 | 06:00 | 121 | 16:00
Gopalganj-400 | 129 | 01:00 | 124 | 13:00 | Savar | 125 | 19:00 | 114 | 11:00
Gulshan | 136 | 06:00 | 122 | 15:00 | SevenRings | 127 | 02:00 | 117 | 15:00
Halishahar | 135 | 07:00 | 128 | 14:00 | ShahCement | 131 | 06:00 | 120 | 15:00
Haripur | 132 | 07:00 | 121 | 15:00 | Shahjadpur | 135 | 19:00 | 131 | 01:00
HaripurSBU | 131 | 07:00 | 121 | 15:00 | Shahjibazar | 122 | 01:00 | 115 | 15:00
Hasnabad | 132 | 06:00 | 119 | 15:00 | Shahmirpur | 135 | 07:00 | 129 | 17:00
Hathazari | 135 | 01:00 | 130 | 15:00 | Shariatpur | 128 | 07:00 | 122 | 11:00
Hatirjheel | 138 | 07:00 | 122 | 15:00 | Sherpur | 127 | 10:00 | 108 | 02:00
Ishurdi | 135 | 02:00 | 131 | 11:00 | Shikalbaha | 123 | 18:30 | 119 | 15:00
Jaldhaka | 134 | 19:30 | 125 | 10:00 | Shikalbaha-230 | 137 | 23:00 | 130 | 14:00
Jamalpur | 126 | 14:00 | 112 | 02:00 | Shitalakhya | 130 | 07:00 | 118 | 15:00
Jashore | 132 | 06:00 | 121 | 13:00 | Sholosohor | 135 | 07:00 | 128 | 15:00
Jhenaidah | 135 | 05:00 | 122 | 11:00 | Shomvuganj | 119 | 07:00 | 110 | 23:00
Jhenaidah-230 | 136 | 01:00 | 129 | 13:00 | Shyampur | 130 | 05:00 | 122 | 12:00
Joydebpur | 126 | 03:00 | 114 | 16:00 | Shyampur-230 | 132 | 06:00 | 122 | 15:00
Joypurhat | 131 | 19:30 | 124 | 12:00 | Siddhirganj | 131 | 05:00 | 121 | 16:00
Juldah | 134 | 18:30 | 130 | 11:00 | Sirajganj | 132 | 04:00 | 126 | 07:00
Kabirpur | 129 | 07:00 | 111 | 15:00 | Sitakunda | 134 | 04:00 | 129 | 12:00
Kachua | 127 | 00:00 | 120 | 15:00 | Sonargaon | 128 | 03:00 | 117 | 16:00
Kaliakoir | 130 | 03:00 | 122 | 12:00 | Sreemongol | 123 | 01:00 | 117 | 22:00
Kaliganj | 136 | 03:00 | 128 | 11:00 | Sreepur | 127 | 09:00 | 120 | 12:00
Kallyanpur | 125 | 01:00 | 115 | 15:00 | Srinagar | 133 | 06:00 | 123 | 15:00
Kalurghat | 135 | 03:00 | 131 | 15:00 | SSM | 138 | 00:00 | 133 | 11:00
Kamrangirchar | 133 | 06:00 | 113 | 15:00 | Sunamganj | 119 | 04:00 | 113 | 15:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 123 | 03:00 | 119 | 11:00
Kasba | 124 | 06:00 | 116 | 15:00 | Sylhet_(South) | 124 | 07:00 | 119 | 15:00
Kazla | 136 | 06:00 | 121 | 16:00 | Tangail | 122 | 10:00 | 114 | 23:00
Keranigonj | 134 | 07:00 | 123 | 15:00 | Taraganj | 135 | 19:30 | 127 | 10:00
Khagrachori | 133 | 04:00 | 130 | 11:00 | Tasnim | 128 | 06:00 | 117 | 15:00
Khulna | 131 | 04:00 | 126 | 11:00 | Thakurgaon | 137 | 09:00 | 132 | 10:00
Khulna(S) | 133 | 01:00 | 127 | 13:00 | TK | 135 | 04:00 | 131 | 14:00
Khulshi | 133 | 03:00 | 127 | 12:00 | Tongi | 131 | 07:00 | 118 | 15:00
Kishoreganj | 122 | 04:00 | 112 | 21:00 | Ullahpara | 131 | 19:00 | 126 | 11:00
Kodda | 127 | 04:00 | 115 | 14:00 | Ullon | 137 | 06:00 | 122 | 15:00
Korerhat | 130 | 02:00 | 125 | 14:00 | Uttara | 127 | 03:00 | 113 | 11:00
KSRM | 136 | 19:30 | 129 | 11:00 | UttaraNew | 127 | 05:00 | 113 | 15:00
Kulaura | 127 | 01:00 | 123 | 13:00 | Zigatola | 134 | 06:00 | 122 | 16:00
Kurigram | 132 | 19:30 | 123 | 10:00
Kushtia | 131 | 01:00 | 122 | 11:00
Laksam | 127 | 18:00 | 119 | 15:00
Lakshmipur | 124 | 07:00 | 117 | 15:00
Lalbag | 133 | 06:00 | 120 | 15:00
Lalmonirhat | 131 | 09:00 | 123 | 07:00
Madanganj | 131 | 07:00 | 121 | 15:00
Madaripur | 129 | 05:00 | 125 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-08-2026 | [28 empty] | Date: | 04-08-2026 | [28 empty] | Date: | 04-08-2026 | [28 empty] | Date: | 04-08-2026 | [28 empty] | Date: | 04-08-2026 | [18 empty] | Date: | 04-08-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [18 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 48.9 | 17 | 19 | 140 | 80 | 14 | 35 | 35 | 0 | 0 | 140 | 250 | 0 | 0 | 287 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 0 | 91 | 16 | 19 | 0 | 0 | 50 | 15 | 17 | 12 | 12 | 0 | 222 | 110 | 2 | 1130 | 152 | 0 | 50 | 8 | 95 | 187 | 0 | 0 | 0 | 1224 | 0 | 53 | 8 | 0 | 290 | 0 | 51 | 5 | 192 | 20 | 50 | 38 | 173 | 0 | 8 | 105 | 116 | 52.2 | 0 | 23 | 300 | 0 | 368 | 40 | 38 | 142 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 7457.52 | 873 | 0 | 0 | 29 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1155 | 0 | 0 | 0 | 1469.54 | 0 | 0 | 0 | 37 | 35 | 0 | 101 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 238 | 0 | 0 | 155 | 52 | 112 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 180 | 0 | 900 | 581.53 | 17 | 6641.07 | 14098.59 | 101.46
01:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 17 | 0 | 17 | 141 | 48 | 14 | 35 | 17 | 0 | 0 | 128 | 250 | 0 | 0 | 285 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 0 | 95 | 16 | 18 | 0 | 1 | 50 | 15 | 0 | 12 | 12 | 0 | 222 | 109 | 2 | 1130 | 50 | 0 | 50 | 0 | 100 | 187 | 0 | 0 | 0 | 1224 | 0 | 55 | 8 | 0 | 290 | 0 | 51 | 5 | 181 | 20 | 51 | 39 | 170 | 0 | 8 | 102 | 112 | 52.2 | 0 | 23 | 295 | 0 | 367 | 40 | 39 | 144 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 101 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7194.62 | 872 | 0 | 0 | 0 | 38 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1154 | 0 | 0 | 0 | 1478.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 247 | 0 | 0 | 156 | 51 | 111 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 180 | 0 | 900 | 581.53 | 17 | 6441.3 | 13635.92 | 101.45
02:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 17 | 0 | 17 | 141 | 48 | 13 | 35 | 0 | 0 | 0 | 131 | 250 | 0 | 0 | 292 | 0 | 0 | 0 | 143.42 | 12 | 22 | 0 | 0 | 87 | 16 | 18 | 0 | 4 | 0 | 15 | 0 | 12 | 12 | 0 | 222 | 105 | 2 | 1130 | 18 | 0 | 50 | 0 | 95 | 187 | 0 | 0 | 0 | 1224 | 0 | 53 | 8 | 0 | 290 | 0 | 51 | 5 | 190 | 20 | 51 | 40 | 172 | 0 | 8 | 105 | 144 | 52.2 | 0 | 23 | 300 | 0 | 367 | 40 | 39 | 142 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 101 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7118.62 | 872 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1157 | 0 | 0 | 0 | 1472.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 155 | 51 | 112 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 900 | 580 | 17 | 6475.56 | 13594.18 | 101.45
03:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 17 | 141 | 48 | 14 | 0 | 0 | 0 | 0 | 132 | 250 | 0 | 0 | 288 | 0 | 0 | 0 | 143.42 | 12.5 | 22 | 0 | 0 | 91 | 16 | 17 | 0 | 7 | 0 | 15 | 0 | 12 | 12 | 0 | 211 | 106 | 2 | 1130 | 16 | 0 | 50 | 0 | 98 | 187 | 0 | 0 | 0 | 1224 | 0 | 55 | 8 | 0 | 290 | 0 | 51 | 5 | 193 | 20 | 38 | 36 | 182 | 0 | 8 | 102 | 148 | 52.2 | 0 | 23 | 305 | 0 | 367 | 40 | 39 | 148 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7072.12 | 873 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1156 | 0 | 0 | 0 | 1472.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 263 | 0 | 0 | 155 | 51 | 111 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 900 | 580 | 17 | 6481.35 | 13553.47 | 101.44
04:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 17 | 127 | 48 | 14 | 0 | 0 | 0 | 0 | 139 | 250 | 0 | 0 | 303 | 0 | 0 | 0 | 143.42 | 12.5 | 22 | 0 | 0 | 91 | 16 | 18 | 0 | 15 | 0 | 15 | 0 | 12 | 12 | 0 | 209 | 104 | 2 | 1130 | 18 | 0 | 50 | 0 | 97 | 184 | 0 | 0 | 0 | 1224 | 0 | 53 | 8 | 0 | 290 | 0 | 51 | 5 | 203 | 20 | 0 | 16 | 181 | 0 | 8 | 100 | 140 | 52.2 | 0 | 23 | 310 | 0 | 367 | 40 | 39 | 149 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 101 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7027.12 | 872 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1155 | 0 | 0 | 0 | 1477.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 269 | 0 | 0 | 155 | 53 | 112 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 900 | 580 | 17 | 6486.21 | 13513.33 | 101.44
05:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 17 | 127 | 48 | 15 | 0 | 0 | 0 | 0 | 139 | 250 | 0 | 0 | 303 | 0 | 0 | 0 | 143.42 | 12.5 | 22 | 0 | 0 | 101 | 16 | 18 | 0 | 14 | 0 | 15 | 0 | 12 | 12 | 0 | 208 | 103 | 2 | 1130 | 16 | 0 | 50 | 0 | 104 | 167 | 0 | 0 | 0 | 1224 | 0 | 55 | 8 | 0 | 355 | 0 | 51 | 5 | 202 | 20 | 0 | 0 | 190 | 0 | 8 | 104 | 142 | 52.2 | 0 | 23 | 310 | 0 | 367 | 40 | 39 | 153 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 101 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 7116.12 | 873 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1157 | 0 | 0 | 0 | 1465.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 156 | 54 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 900 | 577 | 17 | 6448.87 | 13564.99 | 101.43
06:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 17 | 126 | 48 | 13 | 0 | 0 | 0 | 0 | 137 | 250 | 0 | 0 | 301 | 0 | 0 | 0 | 143.42 | 12.5 | 22 | 0 | 0 | 87 | 16 | 19 | 0 | 11 | 0 | 15 | 0 | 12 | 12 | 0.15 | 207 | 104 | 2 | 1130 | 18 | 0 | 50 | 0 | 95 | 167 | 0 | 0 | 0 | 1180 | 1 | 53 | 8 | 0 | 355 | 0 | 51 | 5 | 198 | 20 | 0 | 0 | 179 | 0 | 8 | 106 | 128 | 16 | 0 | 23 | 305 | 0 | 367 | 40 | 39 | 135 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 101 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 6960.07 | 873 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 1468.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0.38 | 0 | 0 | 0 | 0.04 | 145 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0.01 | 157 | 54 | 110 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 16 | 307 | 100 | 180 | 0 | 900 | 574 | 17 | 6421.6 | 13381.67 | 101.43
07:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 17 | 141 | 48 | 13 | 0 | 0 | 0 | 0 | 130 | 250 | 0 | 0 | 286 | 0 | 0 | 1 | 143.42 | 13 | 22 | 0 | 0 | 91 | 16 | 18 | 0 | 13 | 0 | 15 | 0 | 12 | 12 | 0.64 | 207 | 106 | 0 | 1130 | 16 | 0 | 50 | 0 | 98 | 167 | 0 | 0 | 0 | 1160 | 3 | 55 | 8 | 0 | 354 | 0 | 51 | 5 | 185 | 20 | 0 | 0 | 179 | 0 | 8 | 94 | 122 | 8 | 6 | 23 | 305 | 0 | 367 | 40 | 39 | 144 | 1 | 0 | 0 | 22 | 0 | 0 | 0 | 101 | 17 | 48 | 0.06 | 48 | 0 | 0 | 0 | 0 | 6895.12 | 873 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 0.34 | 1162 | 0 | 0 | 0 | 1476.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 5.32 | 4 | 0 | 0 | 1.26 | 147 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0.13 | 158 | 54 | 111 | 4 | 0 | 0 | 0 | 0 | 0.2 | 14 | 0.1 | 16 | 307 | 100 | 180 | 0 | 900 | 575 | 17 | 6460.67 | 13355.79 | 101.4
08:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0 | 17 | 141 | 48 | 14 | 0 | 0 | 0 | 0 | 132 | 250 | 0 | 0 | 298 | 0 | 0 | 2 | 143.42 | 13 | 22 | 0 | 0 | 84 | 16 | 19 | 0 | 11 | 0 | 15 | 0 | 12 | 12 | 1.32 | 208 | 104 | 0 | 1130 | 16 | 0 | 50 | 0 | 94 | 170 | 0 | 0 | 0 | 1160 | 4 | 53 | 8 | 0 | 354 | 0 | 51 | 5 | 194 | 20 | 0 | 0 | 177 | 0 | 8 | 17 | 124 | 8 | 5 | 23 | 300 | 0 | 367 | 40 | 39 | 129 | 3 | 0 | 0 | 22 | 0 | 0 | 0 | 101 | 17 | 48 | 0.43 | 48 | 0 | 0 | 0.36 | 0 | 6786.53 | 873 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 1.86 | 1119 | 0 | 0 | 0 | 1480.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8.9 | 13 | 0 | 0 | 1.88 | 148 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 0.31 | 156 | 54 | 107 | 4 | 0 | 0 | 0 | 0 | 1.4 | 17 | 0.09 | 16 | 307 | 100 | 180 | 0 | 900 | 575 | 17 | 6430.33 | 13216.86 | 101.42
09:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 17 | 141 | 48 | 12 | 0 | 0 | 0 | 0 | 134 | 250 | 0 | 17 | 298 | 0 | 0 | 3 | 143.42 | 12.5 | 22 | 0 | 0 | 97 | 16 | 19 | 0 | 12 | 0 | 15 | 17 | 12 | 12 | 2.8 | 222 | 107 | 0 | 1130 | 16 | 0 | 50 | 0 | 102 | 185 | 0 | 0 | 0 | 1160 | 9 | 18 | 8 | 0 | 354 | 0 | 51 | 5 | 198 | 20 | 0 | 0 | 173 | 0 | 8 | 17 | 130 | 8 | 13 | 23 | 310 | 0 | 367 | 40 | 39 | 147 | 6 | 8 | 0 | 22 | 0 | 0 | 0 | 102 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 0 | 6888.72 | 873 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 5.66 | 1130 | 0 | 0 | 0 | 1483.95 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 52.2 | 8.35 | 23 | 0 | 0 | 5.12 | 148 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 0.77 | 152 | 54 | 109 | 5 | 0 | 0 | 0 | 0 | 2.9 | 10 | 0.03 | 16 | 307 | 100 | 220 | 0 | 900 | 575 | 17 | 6539.98 | 13428.7 | 101.4
10:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 9 | 17 | 141 | 81 | 12 | 0 | 0 | 0 | 0 | 134 | 265 | 0 | 35 | 330 | 0 | 0 | 5 | 143.42 | 12 | 22 | 0 | 0 | 90 | 16 | 19 | 0 | 6 | 0 | 15 | 17 | 12 | 12 | 2.63 | 222 | 106 | 0 | 1130 | 16 | 0 | 50 | 0 | 96 | 185 | 0 | 0 | 0 | 1139 | 10 | 13 | 8 | 0 | 353 | 0 | 51 | 5 | 194 | 20 | 1 | 0 | 172 | 0 | 8 | 17 | 138 | 8 | 4 | 23 | 305 | 0 | 367 | 41 | 39 | 139 | 7 | 8 | 0 | 5 | 0 | 0 | 0 | 75 | 17 | 67 | 0.19 | 104 | 0 | 0 | 0.91 | 0 | 6935.15 | 872 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 33.07 | 1132 | 0 | 0 | 0 | 1475.16 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 8.65 | 37 | 0 | 0 | 6.8 | 147 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 1.12 | 159 | 53 | 110 | 11 | 0 | 0 | 0 | 0 | 6.9 | 44 | 0.36 | 16 | 307 | 100 | 220 | 0 | 1050 | 575 | 17 | 6796.26 | 13731.41 | 101.4
11:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 237 | 0 | 0 | 0 | 35 | 21 | 141 | 81 | 0 | 0 | 17 | 0 | 0 | 144 | 280 | 0 | 35 | 325 | 0 | 0 | 6 | 143.42 | 12 | 22 | 0 | 0 | 94 | 16 | 19 | 0 | 5 | 0 | 15 | 17 | 12 | 12 | 1.8 | 222 | 94 | 0 | 1130 | 16 | 0 | 0 | 1 | 100 | 185 | 0 | 0 | 0 | 1182 | 5 | 11 | 8 | 0 | 354 | 0 | 51 | 5 | 210 | 20 | 45 | 0 | 173 | 0 | 8 | 17 | 162 | 8 | 5 | 23 | 310 | 0 | 369 | 41 | 39 | 144 | 4 | 8 | 0 | 5 | 0 | 0 | 0 | 75 | 17 | 67 | 0.7 | 117 | 0 | 0.2 | 3.91 | 0 | 7082.03 | 872 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 30.99 | 1152 | 0 | 0 | 0 | 1481.13 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 8.66 | 18 | 0 | 0 | 6.24 | 147 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0.83 | 161 | 54 | 103 | 11 | 0 | 0 | 0 | 0 | 7.4 | 81 | 0.11 | 16 | 307 | 100 | 220 | 0 | 1050 | 581.53 | 17 | 6835.09 | 13917.12 | 101.4
12:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 12 | 35 | 34 | 125 | 81 | 0 | 35 | 35 | 0 | 0 | 142 | 270 | 0 | 35 | 325 | 0 | 0 | 6 | 143.42 | 12 | 22 | 0 | 0 | 101 | 16 | 19 | 0 | 4 | 0 | 15 | 17 | 12 | 12 | 2.39 | 222 | 104 | 0 | 1130 | 16 | 0 | 0 | 5 | 104 | 193 | 0 | 0 | 0 | 1224 | 11 | 13 | 8 | 0 | 355 | 0 | 44 | 5 | 208 | 20 | 50 | 0 | 175 | 0 | 8 | 17 | 150 | 8 | 14 | 23 | 305 | 0 | 368 | 41 | 39 | 152 | 1 | 8 | 0 | 5 | 0 | 0 | 0 | 75 | 17 | 57 | 1.88 | 115 | 0 | 0.2 | 8.2 | 0 | 7229.09 | 873 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 44.55 | 1158 | 0 | 0 | 0 | 1474.26 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 15.66 | 8 | 0 | 0 | 2.31 | 147 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 0.12 | 161 | 54 | 105 | 14 | 0 | 0 | 0 | 0 | 7.4 | 75 | 0.11 | 16 | 307 | 100 | 220 | 0 | 1050 | 581.53 | 17 | 6841.14 | 14070.23 | 101.4
13:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 17 | 35 | 41 | 141 | 81 | 0 | 35 | 54 | 0 | 0 | 120 | 250 | 0 | 35 | 328 | 0 | 0 | 9 | 143.42 | 12 | 22 | 0 | 0 | 97 | 16 | 19 | 0 | 13 | 0 | 15 | 17 | 12 | 12 | 2.16 | 222 | 106 | 0 | 1130 | 16 | 0 | 0 | 8 | 100 | 196 | 0 | 0 | 0 | 1224 | 11 | 13 | 8 | 0 | 354 | 0 | 51 | 5 | 195 | 20 | 51 | 0 | 184 | 0 | 8 | 17 | 156 | 8 | 23 | 23 | 305 | 0 | 368 | 40 | 39 | 151 | 1 | 8 | 0 | 5 | 0 | 0 | 0 | 74 | 17 | 58 | 4.15 | 116 | 0 | 0.2 | 14 | 0 | 7370.93 | 873 | 0 | 0 | 0 | 29 | 38 | 0 | 0 | 0 | 0 | 0 | 49.59 | 1158 | 0 | 0 | 0 | 1468.06 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 10.62 | 8 | 0 | 0 | 0.91 | 146 | 0 | 0 | 0 | 0 | 0 | 238 | 0 | 0.43 | 164 | 54 | 103 | 14 | 0 | 0 | 0 | 0 | 7.9 | 95 | 0.13 | 16 | 307 | 100 | 220 | 0 | 1050 | 581.53 | 17 | 6836.37 | 14207.3 | 101.39
14:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 17 | 35 | 34 | 143 | 81 | 0 | 55 | 54 | 0 | 0 | 120 | 250 | 0 | 35 | 326 | 0 | 0 | 9 | 143.42 | 12 | 21 | 0 | 0 | 99 | 16 | 19 | 0 | 23 | 0 | 15 | 17 | 12 | 12 | 2.83 | 222 | 109 | 0 | 1130 | 16 | 0 | 1 | 8 | 101 | 193 | 0 | 0 | 0 | 1224 | 4 | 13 | 8 | 0 | 354 | 0 | 51 | 5 | 190 | 20 | 51 | 0 | 67 | 0 | 8 | 17 | 172 | 8 | 16 | 23 | 310 | 0 | 368 | 40 | 39 | 150 | 3 | 8 | 0 | 5 | 0 | 0 | 0 | 75 | 17 | 58 | 6 | 117 | 0 | 0.5 | 20.35 | 0 | 7234.1 | 873 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 44.49 | 1128 | 0 | 0 | 0 | 1472.3 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 19.49 | 6 | 0 | 0 | 13.64 | 145 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0.9 | 165 | 51 | 107 | 14 | 0 | 0 | 0 | 0 | 2.4 | 49 | 0.16 | 16 | 307 | 100 | 220 | 0 | 1050 | 581.53 | 17 | 6741.11 | 13975.21 | 101.39
15:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 17 | 35 | 34 | 78 | 81 | 0 | 55 | 54 | 0 | 0 | 120 | 250 | 0 | 35 | 325 | 0 | 0 | 7 | 143.42 | 12 | 21 | 0 | 0 | 92 | 16 | 19 | 0 | 15 | 0 | 7 | 17 | 12 | 12 | 0.13 | 222 | 108 | 0 | 1130 | 16 | 0 | 18 | 8 | 100 | 199 | 0 | 0 | 0 | 1224 | 7 | 13 | 8 | 0 | 354 | 0 | 51 | 5 | 194 | 20 | 52 | 0 | 50 | 0 | 8 | 17 | 166 | 8 | 18 | 23 | 305 | 0 | 368 | 40 | 39 | 150 | 3 | 8 | 0 | 5 | 0 | 0 | 0 | 75 | 17 | 58 | 8.83 | 117 | 0 | 0.8 | 19.28 | 0 | 7131.46 | 872 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28.67 | 1150 | 0 | 0 | 0 | 1475.89 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 19.23 | 20 | 0 | 0 | 24.64 | 142 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 2.4 | 161 | 51 | 105 | 19 | 0 | 0 | 0 | 0 | 4.8 | 31 | 0.15 | 16 | 307 | 100 | 220 | 0 | 1050 | 581.53 | 17 | 6742.51 | 13873.97 | 101.38
16:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 35 | 34 | 78 | 81 | 0 | 55 | 54 | 0 | 0 | 120 | 250 | 0 | 35 | 310 | 0 | 0 | 5 | 143.42 | 12 | 21 | 0 | 0 | 94 | 16 | 18 | 0 | 13 | 0 | 7 | 17 | 12 | 12 | 1.2 | 222 | 106 | 0 | 1130 | 16 | 0 | 50 | 8 | 97 | 199 | 0 | 0 | 0 | 1224 | 2 | 13 | 8 | 0 | 353 | 0 | 51 | 5 | 179 | 20 | 56 | 0 | 50 | 0 | 8 | 17 | 166 | 22 | 17 | 23 | 305 | 0 | 368 | 40 | 39 | 149 | 2 | 8 | 0 | 5 | 0 | 0 | 0 | 75 | 17 | 58 | 6.16 | 115 | 0 | 0.9 | 16.92 | 0 | 7129.6 | 872 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18.32 | 1158 | 0 | 0 | 0 | 1453.93 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 52.2 | 14.54 | 23 | 0 | 0 | 10.95 | 142 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 1.09 | 165 | 51 | 108 | 14 | 0 | 0 | 0 | 0 | 3 | 25 | 0.17 | 16 | 307 | 100 | 220 | 0 | 1012 | 575 | 17 | 6679.2 | 13808.8 | 101.38
17:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 17 | 35 | 34 | 76 | 81 | 0 | 55 | 54 | 0 | 0 | 125 | 250 | 0 | 35 | 310 | 0 | 0 | 3 | 143.42 | 12 | 21 | 0 | 0 | 85 | 16 | 19 | 0 | 9 | 0 | 7 | 17 | 12 | 12 | 0.64 | 126 | 104 | 0 | 1130 | 16 | 0 | 50 | 8 | 92 | 202 | 0 | 0 | 0 | 1224 | 1 | 12 | 8 | 0 | 353 | 0 | 51 | 5 | 198 | 20 | 69 | 0 | 69 | 5 | 5 | 17 | 152 | 52.2 | 11 | 23 | 305 | 0 | 368 | 40 | 39 | 136 | 1 | 8 | 0 | 5 | 0 | 0 | 0 | 75 | 17 | 59 | 4.38 | 115 | 0 | 0.4 | 8.26 | 3 | 7057.3 | 873 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 19.03 | 1152 | 0 | 0 | 0 | 1412.06 | 0 | 0 | 0 | 35 | 55 | 0 | 0 | 0 | 8 | 9.86 | 24 | 0 | 0 | 7 | 142 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0.7 | 160 | 51 | 109 | 2 | 40 | 0 | 0 | 0 | 0.5 | 20 | 0.09 | 16 | 307 | 100 | 180 | 0 | 1014 | 550 | 17 | 6555.24 | 13612.54 | 101.4
18:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 35 | 46 | 77 | 81 | 0 | 55 | 90 | 0 | 0 | 130 | 250 | 0 | 55 | 280 | 0 | 0 | 1 | 143.42 | 12 | 21 | 0 | 0 | 87 | 16 | 20 | 0 | 21 | 0 | 23 | 17 | 12 | 12 | 0.22 | 172 | 106 | 0 | 1100 | 16 | 0 | 50 | 8 | 96 | 199 | 0 | 0 | 0 | 1185 | 0 | 13 | 8 | 0 | 355 | 0 | 51 | 5 | 202 | 20 | 70 | 0 | 184 | 26 | 5 | 85 | 154 | 52.2 | 2 | 23 | 300 | 0 | 314 | 40 | 39 | 140 | 0 | 8 | 0 | 5 | 0 | 0 | 0 | 75 | 17 | 59 | 0.36 | 116 | 0 | 0.1 | 2.84 | 12 | 7293.14 | 873 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 4.84 | 1145 | 0 | 0 | 0 | 1409.1 | 0 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 8 | 1.05 | 4 | 0 | 0 | 3.08 | 142 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0.27 | 167 | 51 | 108 | 1 | 49 | 0 | 0 | 0 | 0.5 | 9 | 0.05 | 16 | 256 | 100 | 220 | 0 | 1027 | 550 | 17 | 6516.89 | 13810.03 | 101.4
19:00 | 0 | 105 | 41 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 35 | 52 | 143 | 81 | 0 | 55 | 162 | 0 | 0 | 131 | 250 | 0 | 55 | 300 | 0 | 0 | 0 | 143.42 | 13 | 21 | 0 | 0 | 99 | 16 | 35 | 0 | 14 | 51 | 23 | 18 | 12 | 12 | 0 | 172 | 109 | 0 | 1130 | 92 | 0 | 50 | 8 | 103 | 201 | 0 | 0 | 0 | 1224 | 0 | 26 | 8 | 0 | 355 | 0 | 51 | 5 | 212 | 20 | 68 | 0 | 192 | 27 | 5 | 106 | 170 | 52.2 | 0 | 23 | 310 | 0 | 314 | 40 | 39 | 153 | 0 | 8 | 0 | 5 | 0 | 0 | 0 | 100 | 28 | 59 | 0 | 115 | 0 | 0 | 0 | 12 | 7868.62 | 872 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 100 | 0 | 15 | 0 | 1148 | 0 | 0 | 0 | 1453.41 | 0 | 0 | 0 | 57 | 70 | 4 | 88 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 163 | 52 | 110 | 0 | 83 | 0 | 80 | 0 | 0 | 0 | 0 | 16 | 277 | 100 | 220 | 0 | 1050 | 570 | 17 | 6973.41 | 14842.03 | 101.4
19:30 | 0 | 105 | 41 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 35 | 60 | 143 | 81 | 0 | 55 | 162 | 0 | 0 | 123 | 259 | 0 | 0 | 300 | 0 | 0 | 0 | 143.42 | 13 | 21 | 0 | 0 | 97 | 16 | 44 | 0 | 34 | 51 | 23 | 36 | 12 | 12 | 0 | 172 | 108 | 0 | 1130 | 143 | 0 | 50 | 8 | 98 | 200 | 0 | 0 | 0 | 1224 | 0 | 54 | 8 | 0 | 354 | 0 | 51 | 5 | 194 | 20 | 90 | 0 | 180 | 27 | 5 | 105 | 130 | 52.2 | 0 | 23 | 310 | 0 | 314 | 40 | 39 | 146 | 0 | 8 | 0 | 30 | 0 | 0 | 0 | 100 | 35 | 68 | 0 | 154 | 0 | 0 | 0 | 12 | 7962.62 | 873 | 0 | 0 | 33 | 0 | 38 | 0 | 0 | 150 | 0 | 15 | 0 | 1145 | 0 | 0 | 0 | 1424.34 | 0 | 0 | 0 | 57 | 70 | 15 | 100 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 165 | 51 | 110 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 276 | 100 | 220 | 0 | 1019 | 565 | 17 | 7086.34 | 15048.96
20:00 | 0 | 105 | 41 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 35 | 65 | 143 | 81 | 0 | 55 | 153 | 0 | 0 | 121 | 250 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 14 | 21 | 0 | 0 | 90 | 16 | 46 | 0 | 19 | 51 | 23 | 36 | 12 | 12 | 0 | 221 | 106 | 0 | 1130 | 142 | 0 | 50 | 8 | 95 | 200 | 0 | 0 | 0 | 1224 | 0 | 51 | 8 | 0 | 355 | 0 | 51 | 5 | 193 | 20 | 87 | 0 | 177 | 27 | 8 | 106 | 128 | 52.2 | 0 | 23 | 310 | 0 | 314 | 40 | 39 | 139 | 0 | 8 | 0 | 31 | 0 | 0 | 0 | 100 | 35 | 68 | 0 | 155 | 0 | 0 | 0 | 12 | 7994.62 | 872 | 0 | 0 | 31 | 0 | 38 | 0 | 0 | 150 | 0 | 15 | 0 | 1146 | 0 | 0 | 0 | 1434.02 | 0 | 0 | 0 | 57 | 70 | 15 | 100 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 155 | 52 | 109 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 180 | 0 | 1034 | 560 | 17 | 7091.02 | 15085.64 | 101.36
21:00 | 0 | 105 | 41 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 35 | 73 | 143 | 81 | 0 | 35 | 162 | 0 | 0 | 121 | 250 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 13 | 21 | 0 | 0 | 94 | 16 | 47 | 0 | 7 | 51 | 23 | 54.36 | 12 | 12 | 0 | 220 | 107 | 0 | 1130 | 140 | 0 | 50 | 8 | 99 | 200 | 0 | 0 | 0 | 1224 | 0 | 43 | 8 | 0 | 354 | 0 | 51 | 5 | 196 | 20 | 73 | 0 | 186 | 28 | 8 | 105 | 134 | 52.2 | 0 | 23 | 305 | 0 | 314 | 40 | 39 | 146 | 0 | 8 | 0 | 31 | 0 | 0 | 0 | 100 | 35 | 68 | 0 | 155 | 0 | 0 | 0 | 12 | 8000.98 | 872 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 150 | 0 | 15 | 0 | 1148 | 0 | 0 | 0 | 1449.2 | 0 | 0 | 0 | 57 | 70 | 15 | 100 | 0 | 8 | 0 | 0 | 14 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 165 | 52 | 110 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1051 | 560 | 17 | 7194.2 | 15195.18 | 101.36
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 54 | 35 | 38 | 143 | 81 | 0 | 35 | 154 | 0 | 0 | 125 | 250 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 13 | 21 | 0 | 0 | 90 | 16 | 56 | 0 | 6 | 51 | 23 | 54.36 | 12 | 12 | 0 | 220 | 105 | 0 | 1130 | 157 | 0 | 50 | 8 | 97 | 200 | 0 | 0 | 0 | 1224 | 0 | 12 | 8 | 0 | 354 | 0 | 51 | 5 | 197 | 20 | 55 | 0 | 180 | 28 | 8 | 106 | 134 | 52.2 | 0 | 23 | 305 | 0 | 314 | 40 | 39 | 136 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 68 | 0 | 155 | 0 | 0 | 0 | 12 | 7903.98 | 873 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 150 | 0 | 0 | 0 | 1158 | 0 | 0 | 0 | 1437.8 | 0 | 0 | 0 | 57 | 70 | 0 | 100 | 0 | 8 | 0 | 0 | 14 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 165 | 51 | 109 | 0 | 98 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1029 | 567 | 17 | 7148.8 | 15052.78 | 101.36
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 35 | 35 | 17 | 143 | 81 | 0 | 35 | 157 | 0 | 0 | 129 | 250 | 0 | 35 | 300 | 0 | 0 | 0 | 17 | 13 | 21 | 0 | 0 | 92 | 16 | 56 | 0 | 4 | 51 | 23 | 17 | 12 | 12 | 0 | 220 | 106 | 2 | 1130 | 160 | 0 | 50 | 8 | 98 | 184 | 0 | 0 | 0 | 1224 | 0 | 12 | 8 | 0 | 354 | 0 | 51 | 5 | 202 | 20 | 51 | 0 | 181 | 28 | 8 | 104 | 138 | 52.2 | 0 | 23 | 305 | 0 | 317 | 40 | 39 | 140 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 68 | 0 | 155 | 0 | 0 | 0 | 12 | 7713.2 | 872 | 0 | 0 | 29 | 0 | 38 | 0 | 0 | 150 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 1460.31 | 0 | 0 | 0 | 57 | 70 | 0 | 100 | 0 | 8 | 0 | 0 | 14 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 164 | 51 | 110 | 0 | 105 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1056 | 568 | 17 | 7212.31 | 14925.51 | 101.36
Total KWH | 0 | 2274240 | 1014720 | 0 | 0 | 0 | 0 | 0 | 7938000 | 0 | 0 | 392400 | 518400 | 739152 | 3026880 | 1645713 | 144133 | 666111 | 1177920 | 0 | 0 | 3137367 | 6193079 | 0 | 533940 | 7398267 | 0 | 0 | 54047 | 3310800 | 308400 | 513360 | 0 | 0 | 2236855 | 388909 | 634560 | 0 | 274080 | 362317 | 374784 | 386279 | 296640 | 294720 | 19199 | 5131958 | 2574316 | 840 | 27149090.91 | 1175927 | 0 | 998880 | 106626.6 | 2398691 | 4461956 | 0 | 0 | 0 | 28974543 | 64665 | 730981 | 217455 | 0 | 8572300 | 0 | 1225100 | 138240 | 4916000 | 497016 | 982080 | 156834 | 3838560 | 177240 | 186510 | 1602840 | 3444480 | 786235 | 142809 | 540752 | 7402000 | 0 | 8679000 | 956000 | 936960 | 3470072.73 | 32029 | 173232 | 0 | 392640 | 0 | 0 | 0 | 2203900 | 479520 | 1351200 | 32940 | 222000 | 0 | 3400 | 95000 | 90000 | 173968091.24 | 21112000 | 0 | 0 | 180000 | 376704 | 912000 | 0 | 0 | 647931 | 0 | 48528 | 273600 | 27556360 | 0 | 0 | 0 | 35633818 | 0 | 0 | 0 | 399744 | 831360 | 29915 | 581792 | 0 | 489250 | 124240 | 190783 | 80820 | 0 | 76016 | 3510636 | 0 | 0 | 0 | 0 | 0 | 5884654 | 0 | 8460 | 3932000 | 1214399 | 2706728 | 118407 | 810700 | 0 | 728910 | 0 | 40551.96 | 470880 | 1470 | 399552 | 7331000 | 2398000 | 5257790 | 0 | 23709091 | 13986909.09 | 440400 | 162495399.05 | 336463490.29