## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-08-2026 | during | 09-08-2026 | during | 09-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 325 | 330 | 412 | 412 | 300 | 300 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 120 | 125 | 335 | 335 | 120 | 120 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 0 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 294 | 266 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 0 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 125 | 143 | 149.36 | 149.36 | 125 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15.5 | 15 | 33 | 33 | 18 | 18 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 7 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 49 | 52.19 | 52.19 | 33 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 81 | 48 | 300 | 300 | 81 | 81 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 24 | 66 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 17 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 162 | 162 | 17 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 54 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 300 | 360 | 583 | 583 | 300.03 | 300.03 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 0 | 0 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1734.92 | 1997.42 | 5806.16 | 5778.16 | 1639.45 | 2029.45
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 6 | 8 | 25.5 | 25.5 | 8 | 8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 11 | 0 | 8 | 0 | 8 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 222 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 202 | 209 | 170 | 170 | 140 | 140 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 101 | 103 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 18 | 20 | 24 | 24 | 24 | 24 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 17 | 25 | 30 | 5 | 24 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 24 | 44 | 108 | 108 | 25 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.21 | 0 | 2.49 | 0 | 2.49 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 85 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 17 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 106 | 108 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 95 | 99 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 18 | 158 | 163 | 163 | 16 | 83 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 26 | 7 | 12 | 9 | 12 | 9 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 685 | 1150 | 1150 | 1150 | 1150 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 3288.21 | 3167.36 | 4069.35 | 4111.86 | 3229.49 | 3415
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 352 | 353 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 0 | 342.01 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 39 | 39 | 41.65 | 41.65 | 34 | 34 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 41 | 46 | 52.82 | 52.82 | 44 | 44 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 197 | 195 | 195 | 195 | 110 | 110 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 40 | 140 | 150 | 150 | 50 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 23 | 31 | 32 | 32 | 24 | 24 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 51 | 163 | 163 | 0 | 0 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 183 | 190 | 200 | 200 | 80 | 180 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 170 | 176 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 8 | 8 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 104 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 26 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 26 | 90 | 115 | 115 | 51 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 44 | 0 | 40 | 0 | 40 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1295 | 1563.2 | 2513.19 | 2467.19 | 1166.21 | 1374.21
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-08-2026 | during | 09-08-2026 | during | 09-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 10.6 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.7 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 154 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 69 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 53.08 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 7 | 0 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 263.38 | 240 | 537.6 | 516.5 | 280.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 41 | 41 | 41 | 41 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 39 | 40 | 40 | 40 | 40 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 149 | 150 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 22 | 86 | 86 | 86 | 22.04 | 22.04 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 70 | 127 | 120 | 120 | 102 | 102 | plant availability zero
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 230 | 230 | 250 | 260 | 250 | 260 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 885 | 995 | 1079 | 1089 | 917.04 | 927.04
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 901 | 901 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 28 | 30 | 30 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 9.22 | 0 | 57 | 0 | 57 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 237 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1162 | 1163 | 1165 | 1165 | 1165 | 1165 | AGC+FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2110.22 | 2382 | 3472 | 3415 | 2307 | 2250
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 600 | 1050 | 600 | 600 | 600 | 600 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 60 | 60 | 60 | 60 | 100 | 100 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 565 | 558 | 581.53 | 941.53 | 551.53 | 551.53 | AGC+U-2 Under Maintenance
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.17 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 1785.17 | 2228 | 2029.53 | 2388.53 | 1812.53 | 1811.53
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 45.58 | 0 | 48.25 | 0 | 48.25 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 200 | 177 | 214 | 214 | 170 | 170 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 384 | 348 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 14 | 14 | 14 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 92 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 90 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 57 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 2.96 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 753.62 | 1123.64 | 1469.13 | 1469.13 | 1100 | 1100 | Problem with coal feeding system
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 50.62 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 104 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1548.78 | 1947.64 | 3207.87 | 2993.12 | 2035.36 | 1977.61
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 46 | 46 | 50 | 50 | 52 | 52 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 162 | 162 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 78 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.2 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 108 | 105 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 189 | 0 | 177.67 | 0 | 177.67 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 525.2 | 556 | 682.67 | 472 | 571.67 | 396
System Total |  |  |  |  | 28843.2 | 29171.687 | 13435.88 | 15076.62 | 23397.37 | 23231.36 | 13958.85 | 14439.84
Forecast Scenario (09-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13480 |  | 3514.4 |  | 17160
|  |  |  | 1:00 | 12910 |  | 3810.45 |  | 16900
|  |  |  | 2:00 | 12830 |  | 3485.75 |  | 16480
|  |  |  | 3:00 | 12760 |  | 3161.05 |  | 16070
|  |  |  | 4:00 | 12710 |  | 2989.15 |  | 15840
|  |  |  | 5:00 | 12700 |  | 2740.85 |  | 15570
|  |  |  | 6:00 | 12480 |  | 2549.85 |  | 15150
|  |  |  | 7:00 | 12420 |  | 2368.4 |  | 14900
|  |  |  | 8:00 | 12750 |  | 2053.25 |  | 14900
|  |  |  | 9:00 | 12810 |  | 2129.65 |  | 15040
|  |  |  | 10:00 | 13220 |  | 1881.35 |  | 15190
|  |  |  | 11:00 | 13330 |  | 2043.7 |  | 15470
|  |  |  | 12:00 | 13440 |  | 2358.85 |  | 15910
|  |  |  | 13:00 | 13570 |  | 2387.5 |  | 16070
|  |  |  | 14:00 | 13380 |  | 2540.3 |  | 16040
|  |  |  | 15:00 | 13080 |  | 2960.5 |  | 16180
|  |  |  | 16:00 | 12850 |  | 2922.3 |  | 15910
|  |  |  | 17:00 | 12910 |  | 2435.25 |  | 15460
|  |  |  | 18:00 | 12930 |  | 2053.25 |  | 15080
|  |  |  | 18:30 | 13500 |  | 2101 |  | 15700
|  |  |  | 19:00 | 14030 |  | 2253.8 |  | 16390
|  |  |  | 19:30 | 14510 |  | 2683.55 |  | 17320
|  |  |  | 20:00 | 14710 |  | 2416.15 |  | 17240
|  |  |  | 21:00 | 15080 |  | 2167.85 |  | 17350
|  |  |  | 22:00 | 14670 |  | 2397.05 |  | 17180
|  |  |  | 23:00 | 13230 |  | 3896.4 |  | 17310
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 15910.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2168
Probable Maximum Demand at Evening Peak: |  |  | 17350.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15080.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 318.28 MKWHr. |  | 550 | 180 | 218 | 320 | 120 | 300 | 100 | 210 | 170 | 2168
*** This report is generated digitally from Operation Information System (OIS) at 08:57 hrs on 09-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-08-2026 | [28 empty] | Date: | 08-08-2026 | [28 empty] | Date: | 08-08-2026 | [28 empty] | Date: | 08-08-2026 | [28 empty] | Date: | 08-08-2026 | [18 empty] | Date: | 08-08-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [18 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 38 | 142 | 81 | 0 | 35 | 54 | 0 | 0 | 120 | 320 | 0 | 0 | 282 | 0 | 0 | 0 | 143.42 | 13 | 22 | 0 | 0 | 92 | 16 | 45 | 0 | 28 | 50 | 23 | 17 | 12 | 12 | 0 | 221 | 106 | 34 | 1125 | 35 | 0 | 50 | 8 | 97 | 187 | 0 | 0 | 0 | 1192 | 0 | 50 | 185 | 0 | 330 | 0 | 51 | 44 | 0 | 33 | 51 | 50 | 182 | 5 | 19 | 102 | 156 | 52.2 | 0 | 15 | 305 | 0 | 305 | 40 | 39 | 139 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 49 | 0 | 47 | 0 | 0 | 0 | 12 | 7471.62 | 840 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 792.95 | 0 | 0 | 0 | 55 | 113 | 0 | 100 | 21 | 52.2 | 0 | 0 | 14 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 158 | 47 | 110 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 180 | 0 | 800 | 550 | 35 | 6008.15 | 13479.77 | 102.74
01:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 18 | 142 | 48 | 0 | 35 | 17 | 0 | 0 | 120 | 315 | 0 | 0 | 270 | 0 | 0 | 0 | 143.42 | 13 | 22 | 0 | 0 | 89 | 16 | 20 | 0 | 19 | 50 | 23 | 0 | 12 | 12 | 0 | 222 | 105 | 37 | 1125 | 16 | 0 | 50 | 0 | 100 | 187 | 0 | 0 | 0 | 1193 | 0 | 50 | 190 | 0 | 359 | 0 | 51 | 45 | 0 | 33 | 38 | 50 | 185 | 0 | 18 | 106 | 152 | 52.2 | 0 | 15 | 315 | 0 | 305 | 40 | 39 | 147 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 46 | 0 | 48 | 0 | 0 | 0 | 12 | 7254.62 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 0 | 0 | 0 | 787.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 52.2 | 0 | 0 | 14 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 158 | 48 | 109 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 600 | 550 | 17 | 5654.89 | 12909.51 | 102.75
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 17 | 142 | 48 | 0 | 35 | 0 | 0 | 0 | 120 | 300 | 0 | 0 | 282 | 0 | 0 | 0 | 143.42 | 13 | 22 | 0 | 0 | 91 | 16 | 19 | 0 | 9 | 0 | 23 | 0 | 12 | 12 | 0 | 222 | 104 | 40 | 1125 | 16 | 0 | 50 | 0 | 97 | 187 | 0 | 0 | 0 | 1202 | 0 | 50 | 192 | 0 | 356 | 0 | 51 | 44 | 0 | 33 | 34 | 50 | 187 | 0 | 18 | 100 | 152 | 43 | 0 | 15 | 315 | 0 | 305 | 40 | 39 | 149 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 46 | 0 | 48 | 0 | 0 | 0 | 12 | 7165.42 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 790.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 14 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 156 | 48 | 110 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 600 | 555 | 17 | 5655.35 | 12820.77 | 102.76
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 17 | 142 | 48 | 0 | 35 | 0 | 0 | 0 | 120 | 310 | 0 | 0 | 272 | 0 | 0 | 0 | 143.42 | 13 | 22 | 0 | 0 | 89 | 16 | 19 | 0 | 11 | 0 | 23 | 0 | 12 | 12 | 0 | 222 | 106 | 40 | 1125 | 18 | 0 | 50 | 0 | 101 | 187 | 0 | 0 | 0 | 1192 | 0 | 20 | 192 | 0 | 359 | 0 | 51 | 44 | 0 | 33 | 0 | 50 | 181 | 0 | 18 | 105 | 148 | 43 | 0 | 16 | 315 | 0 | 305 | 40 | 39 | 153 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 9 | 0 | 85 | 0 | 0 | 0 | 12 | 7102.42 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1166 | 0 | 0 | 0 | 790.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 47 | 107 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 600 | 560 | 17 | 5653.46 | 12755.88 | 102.77
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 17 | 142 | 48 | 0 | 0 | 0 | 0 | 0 | 120 | 300 | 0 | 0 | 285 | 0 | 0 | 0 | 143.42 | 13 | 22 | 0 | 0 | 92 | 16 | 19 | 0 | 32 | 0 | 23 | 0 | 12 | 12 | 0 | 222 | 105 | 40 | 1125 | 18 | 0 | 50 | 0 | 97 | 187 | 0 | 0 | 0 | 1187 | 0 | 20 | 192 | 0 | 359 | 0 | 51 | 44 | 0 | 33 | 0 | 51 | 182 | 0 | 18 | 102 | 148 | 43 | 0 | 16 | 310 | 0 | 305 | 40 | 39 | 147 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 9 | 0 | 86 | 0 | 0 | 0 | 12 | 7073.42 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1166 | 0 | 0 | 0 | 762.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 48 | 109 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 600 | 560 | 17 | 5629.04 | 12702.46 | 102.78
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 17 | 143 | 48 | 0 | 0 | 0 | 0 | 0 | 120 | 310 | 0 | 0 | 295 | 0 | 0 | 0 | 143.42 | 13 | 22 | 0 | 0 | 87 | 16 | 19 | 0 | 22 | 0 | 23 | 0 | 12 | 12 | 0 | 222 | 106 | 40 | 1125 | 18 | 0 | 50 | 0 | 102 | 187 | 0 | 0 | 0 | 1192 | 0 | 20 | 192 | 0 | 358 | 0 | 51 | 44 | 0 | 33 | 0 | 50 | 186 | 0 | 18 | 106 | 146 | 43 | 0 | 16 | 315 | 0 | 305 | 40 | 39 | 153 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 100 | 17 | 9 | 0 | 87 | 0 | 0 | 0 | 12 | 7106.42 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1165 | 0 | 0 | 0 | 750.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 48 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 600 | 565 | 17 | 5591.44 | 12697.86 | 102.79
06:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 17 | 143 | 48 | 0 | 0 | 0 | 0 | 0 | 120 | 300 | 0 | 0 | 276 | 0 | 0 | 0 | 143.42 | 13 | 22 | 0 | 0 | 90 | 16 | 18 | 0 | 9 | 0 | 23 | 0 | 12 | 12 | 0.26 | 222 | 105 | 38 | 1125 | 17 | 0 | 50 | 0 | 97 | 187 | 0 | 0 | 0 | 1192 | 0 | 20 | 194 | 0 | 359 | 0 | 51 | 45 | 0 | 33 | 0 | 50 | 183 | 0 | 18 | 104 | 122 | 43 | 4 | 16 | 315 | 0 | 293 | 40 | 39 | 148 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 25 | 17 | 9 | 0.1 | 87 | 20 | 0 | 0.8 | 12 | 6957.58 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.7 | 1165 | 0 | 0 | 0 | 752.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0.31 | 2 | 0 | 0 | 0.43 | 150 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.03 | 159 | 48 | 109 | 1 | 0 | 0 | 0 | 0 | 0.4 | 6 | 0 | 16 | 307 | 60 | 220 | 0 | 600 | 560 | 17 | 5516.97 | 12474.55 | 102.8
07:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 17 | 142 | 48 | 0 | 0 | 0 | 0 | 0 | 120 | 295 | 0 | 0 | 270 | 0 | 0 | 1 | 143.42 | 13 | 22 | 0 | 0 | 91 | 16 | 18 | 0 | 19 | 0 | 15 | 0 | 12 | 12 | 1.06 | 221 | 106 | 30 | 1125 | 16 | 0 | 50 | 0 | 96 | 187 | 0 | 0 | 0 | 1192 | 2 | 20 | 194 | 0 | 300 | 0 | 51 | 44 | 0 | 33 | 0 | 50 | 181 | 0 | 19 | 103 | 120 | 43 | 13 | 16 | 305 | 0 | 293 | 40 | 39 | 134 | 2 | 8 | 0 | 22 | 0 | 0 | 0 | 23 | 17 | 9 | 1.2 | 87 | 10 | 0.1 | 4.08 | 12 | 6865.86 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18.2 | 1165 | 0 | 0 | 0 | 752.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 14.04 | 10 | 0 | 0 | 6.92 | 150 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.43 | 158 | 48 | 111 | 5 | 0 | 0 | 0 | 0 | 1 | 49 | 0.02 | 16 | 307 | 60 | 220 | 0 | 600 | 545 | 17 | 5545.37 | 12411.23 | 102.81
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 17 | 126 | 48 | 0 | 0 | 0 | 0 | 0 | 120 | 300 | 0 | 0 | 290 | 0 | 0 | 5 | 143.42 | 12.5 | 22 | 0 | 0 | 89 | 16 | 18 | 0 | 9 | 0 | 15 | 17 | 12 | 12 | 1.42 | 220 | 107 | 10 | 1125 | 17 | 0 | 50 | 0 | 98 | 187 | 0 | 0 | 0 | 1190 | 3 | 20 | 194 | 0 | 354 | 0 | 51 | 45 | 0 | 33 | 0 | 50 | 183 | 0 | 19 | 101 | 130 | 43 | 19 | 16 | 310 | 0 | 293 | 40 | 39 | 144 | 3 | 8 | 0 | 22 | 0 | 0 | 0 | 23 | 17 | 47 | 8.1 | 47 | 8 | 0.4 | 25.18 | 12 | 6977.02 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 25.07 | 1165 | 0 | 0 | 0 | 751.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 7.99 | 41 | 0 | 0 | 22.37 | 183 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.73 | 163 | 48 | 110 | 16 | 0 | 0 | 0 | 0 | 1.7 | 100 | 0.07 | 16 | 307 | 60 | 180 | 0 | 600 | 550 | 17 | 5771.22 | 12748.24 | 102.82
09:00 | 0 | 36 | 30 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 17 | 126 | 48 | 3 | 0 | 0 | 0 | 0 | 120 | 295 | 0 | 0 | 270 | 0 | 0 | 10 | 143.42 | 16.5 | 0 | 0 | 0 | 91 | 16 | 19 | 0 | 10 | 0 | 15 | 17 | 12 | 12 | 1.55 | 220 | 106 | 4 | 1125 | 17 | 0 | 50 | 0 | 97 | 187 | 0 | 0 | 0 | 1150 | 6 | 40 | 195 | 0 | 354 | 0 | 51 | 44 | 0 | 30 | 0 | 50 | 182 | 0 | 19 | 99 | 136 | 43 | 45 | 16 | 305 | 0 | 287 | 40 | 39 | 142 | 5 | 8 | 0 | 22 | 0 | 0 | 0 | 23 | 17 | 48 | 15 | 47 | 0 | 1.7 | 44.18 | 12 | 6972.35 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 48.33 | 1162 | 0 | 0 | 0 | 743.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 35.39 | 40 | 0 | 0 | 25.73 | 200 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.83 | 160 | 47 | 108 | 5 | 0 | 0 | 0 | 0 | 2.6 | 159 | 0.23 | 16 | 307 | 60 | 180 | 0 | 600 | 550 | 17 | 5829.92 | 12802.27 | 102.84
10:00 | 0 | 88 | 51 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 17 | 126 | 81 | 0 | 12 | 0 | 0 | 0 | 120 | 295 | 0 | 17 | 280 | 0 | 0 | 16 | 143.42 | 16 | 0 | 0 | 0 | 87 | 16 | 19 | 0 | 13 | 0 | 15 | 17 | 12 | 12 | 3.91 | 220 | 105 | 5 | 1125 | 17 | 0 | 50 | 0 | 95 | 188 | 0 | 0 | 0 | 1224 | 15 | 40 | 195 | 0 | 353 | 0 | 51 | 43 | 0 | 39 | 0 | 50 | 181 | 0 | 19 | 104 | 134 | 43 | 60 | 16 | 300 | 0 | 287 | 42 | 39 | 136 | 6 | 8 | 0 | 22 | 0 | 0 | 0 | 54 | 17 | 59 | 13.1 | 115 | 0 | 1.6 | 28.21 | 12 | 7311.24 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 79 | 1159 | 0 | 0 | 0 | 747.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 31.54 | 70 | 0 | 0 | 21.53 | 200 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.07 | 163 | 49 | 110 | 25 | 0 | 0 | 0 | 0 | 1.6 | 139 | 0.35 | 16 | 293 | 60 | 220 | 0 | 600 | 535 | 17 | 5899.39 | 13210.63 | 102.86
11:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 17 | 125 | 81 | 8 | 35 | 0 | 0 | 0 | 120 | 320 | 0 | 35 | 284 | 0 | 0 | 6 | 143.42 | 16 | 0 | 0 | 0 | 96 | 16 | 24 | 0 | 17 | 0 | 15 | 17 | 12 | 12 | 2.74 | 219 | 108 | 2 | 1125 | 16 | 0 | 50 | 0 | 102 | 201 | 0 | 0 | 0 | 1224 | 15 | 40 | 195 | 0 | 354 | 0 | 51 | 41 | 0 | 38 | 0 | 51 | 186 | 0 | 19 | 17 | 154 | 43 | 41 | 15 | 315 | 0 | 230 | 40 | 39 | 151 | 11 | 8 | 0 | 22 | 0 | 0 | 0 | 56 | 17 | 59 | 16.2 | 115 | 0 | 1.1 | 40.29 | 12 | 7338.75 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 20 | 1157 | 0 | 0 | 0 | 747.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 48.63 | 87 | 0 | 0 | 51.02 | 200 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 5.32 | 163 | 48 | 110 | 34 | 0 | 0 | 0 | 0 | 1.1 | 201 | 0.12 | 16 | 307 | 60 | 220 | 0 | 600 | 555 | 17 | 5990.83 | 13329.58 | 102.9
12:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 24 | 125 | 81 | 15 | 35 | 17 | 0 | 0 | 120 | 300 | 0 | 35 | 294 | 0 | 0 | 33 | 143.42 | 15.5 | 0 | 0 | 0 | 95 | 16 | 24 | 0 | 26 | 0 | 18 | 17 | 12 | 12 | 4.21 | 219 | 106 | 2 | 1125 | 18 | 0 | 50 | 6 | 101 | 202 | 0 | 0 | 0 | 1224 | 11 | 40 | 197 | 0 | 352 | 0 | 51 | 41 | 0 | 39 | 26 | 50 | 183 | 0 | 19 | 17 | 170 | 43 | 44 | 23 | 315 | 0 | 230 | 40 | 39 | 149 | 12 | 8 | 0 | 22 | 0 | 0 | 0 | 70 | 17 | 59 | 10.6 | 116 | 0 | 0.7 | 53.08 | 7 | 7466.51 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9.22 | 1162 | 0 | 0 | 0 | 753.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 45.58 | 104 | 0 | 0 | 50.62 | 200 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 2.96 | 162 | 46 | 108 | 16 | 0 | 0 | 0 | 0 | 4.2 | 189 | 0.17 | 16 | 307 | 60 | 220 | 0 | 600 | 565 | 17 | 5969.37 | 13435.88 | 102.94
13:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 17 | 34 | 139 | 81 | 15 | 35 | 35 | 0 | 0 | 120 | 310 | 0 | 35 | 270 | 0 | 0 | 28 | 143.42 | 15.5 | 0 | 0 | 0 | 97 | 16 | 24 | 0 | 36 | 0 | 22 | 17 | 12 | 12 | 4.53 | 220 | 92 | 3 | 1125 | 16 | 0 | 50 | 8 | 90 | 207 | 0 | 0 | 0 | 1224 | 10 | 40 | 195 | 0 | 355 | 0 | 51 | 41 | 0 | 38 | 34 | 50 | 186 | 0 | 19 | 17 | 178 | 43 | 59 | 30 | 320 | 0 | 230 | 40 | 39 | 151 | 6 | 8 | 0 | 58 | 0 | 0 | 0 | 71 | 17 | 59 | 6.22 | 116 | 0 | 0.4 | 16.62 | 6 | 7540.69 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2.2 | 1158 | 0 | 0 | 0 | 756.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 63.82 | 107 | 0 | 0 | 62.13 | 195 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 3.36 | 160 | 47 | 107 | 37 | 0 | 0 | 0 | 0 | 4.7 | 212 | 0.13 | 16 | 307 | 60 | 220 | 0 | 600 | 569 | 17 | 6028.8 | 13569.49 | 102.98
14:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 17 | 24 | 138 | 48 | 15 | 35 | 54 | 0 | 0 | 120 | 305 | 0 | 35 | 293 | 0 | 0 | 31 | 143.42 | 15.5 | 0 | 0 | 0 | 97 | 16 | 24 | 0 | 23 | 0 | 22 | 17 | 12 | 12 | 3.58 | 222 | 93 | 2 | 1125 | 18 | 0 | 50 | 8 | 91 | 208 | 0 | 0 | 0 | 1224 | 11 | 40 | 197 | 0 | 352 | 0 | 51 | 43 | 0 | 38 | 34 | 51 | 184 | 0 | 19 | 17 | 186 | 52.2 | 40 | 30 | 315 | 0 | 230 | 40 | 39 | 147 | 1 | 8 | 0 | 63 | 0 | 0 | 0 | 73 | 17 | 59 | 5.6 | 115 | 0 | 0 | 49.96 | 6 | 7474.26 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3.75 | 1160 | 0 | 0 | 0 | 756.77 | 0 | 0 | 0 | 0 | 21 | 0 | 7 | 0 | 8 | 34.88 | 58 | 0 | 0 | 13.11 | 192 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 3.63 | 160 | 47 | 108 | 29 | 0 | 0 | 0 | 0 | 6 | 210 | 0.02 | 16 | 307 | 60 | 220 | 0 | 600 | 560 | 17 | 5901.16 | 13375.42 | 103.05
15:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 17 | 17 | 138 | 48 | 15 | 35 | 54 | 0 | 0 | 120 | 305 | 0 | 35 | 270 | 0 | 0 | 4 | 143.42 | 15.5 | 0 | 0 | 0 | 90 | 16 | 25 | 0 | 4 | 0 | 20 | 17 | 12 | 12 | 3.11 | 222 | 101 | 0 | 1075 | 18 | 0 | 50 | 8 | 102 | 204 | 0 | 0 | 0 | 1224 | 14 | 36 | 197 | 0 | 354 | 0 | 51 | 42 | 0 | 35 | 35 | 51 | 184 | 0 | 19 | 17 | 182 | 52.2 | 44 | 23 | 315 | 0 | 229 | 40 | 39 | 150 | 2 | 8 | 0 | 63 | 0 | 0 | 0 | 73 | 17 | 59 | 21.81 | 115 | 0 | 0 | 13.01 | 6 | 7325.05 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 9.89 | 1162 | 0 | 0 | 0 | 759.15 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 8 | 8.44 | 22 | 0 | 0 | 47.08 | 190 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 4.35 | 162 | 46 | 108 | 18 | 0 | 0 | 0 | 0 | 5.5 | 171 | 0.02 | 16 | 307 | 60 | 220 | 0 | 500 | 565 | 17 | 5753.43 | 13078.48 | 103.06
16:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 17 | 17 | 137 | 48 | 15 | 35 | 54 | 0 | 0 | 120 | 310 | 0 | 35 | 278 | 0 | 0 | 17 | 143.42 | 15.5 | 0 | 0 | 0 | 91 | 16 | 24 | 0 | 29 | 32 | 20 | 54.36 | 12 | 12 | 2.2 | 222 | 109 | 4 | 920 | 16 | 0 | 50 | 8 | 93 | 204 | 0 | 0 | 0 | 1224 | 6 | 35 | 195 | 0 | 349 | 0 | 51 | 42 | 0 | 35 | 50 | 51 | 189 | 0 | 19 | 30 | 176 | 52.2 | 27 | 25 | 320 | 0 | 230 | 39 | 39 | 149 | 7 | 8 | 0 | 85 | 0 | 0 | 0 | 73 | 17 | 59 | 3.2 | 117 | 0 | 0.4 | 3.37 | 6 | 7290.65 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 12.42 | 1161 | 0 | 0 | 0 | 755.78 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 8 | 11.73 | 8 | 0 | 0 | 31.66 | 191 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 3.06 | 162 | 46 | 106 | 11 | 13 | 0 | 0 | 0 | 0.4 | 89 | 0.07 | 16 | 307 | 60 | 220 | 0 | 416 | 560 | 17 | 5557.12 | 12847.77 | 103.08
17:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 17 | 17 | 137 | 48 | 15 | 35 | 54 | 0 | 0 | 120 | 300 | 0 | 35 | 275 | 0 | 0 | 6 | 143.42 | 15 | 0 | 0 | 0 | 91 | 49 | 24 | 0 | 13 | 50 | 20 | 54.36 | 12 | 12 | 0.21 | 222 | 105 | 12 | 920 | 18 | 0 | 50 | 8 | 95 | 203 | 0 | 0 | 0 | 1224 | 4 | 43 | 197 | 0 | 353 | 0 | 51 | 43 | 0 | 38 | 51 | 50 | 181 | 5 | 19 | 105 | 176 | 52.2 | 11 | 31 | 305 | 0 | 230 | 39 | 39 | 146 | 0 | 8 | 0 | 86 | 0 | 0 | 0 | 88 | 17 | 59 | 1.11 | 117 | 0 | 0.2 | 3.2 | 6 | 7372.7 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 6.93 | 1161 | 0 | 0 | 0 | 777.85 | 0 | 0 | 0 | 35 | 38 | 0 | 17 | 0 | 8 | 5.36 | 6 | 0 | 0 | 8.25 | 189 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 2.1 | 158 | 46 | 105 | 11 | 24 | 0 | 0 | 0 | 0.6 | 61 | 0.08 | 16 | 307 | 60 | 220 | 0 | 410 | 545 | 17 | 5532.17 | 12904.87 | 103.1
18:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 17 | 36 | 138 | 48 | 15 | 0 | 54 | 0 | 0 | 120 | 295 | 0 | 35 | 282 | 0 | 0 | 1 | 143.42 | 15 | 0 | 0 | 0 | 87 | 49 | 24 | 0 | 17 | 50 | 20 | 54.36 | 12 | 12 | 0.19 | 222 | 104 | 5 | 880 | 18 | 0 | 50 | 8 | 92 | 206 | 0 | 0 | 0 | 1190 | 1 | 50 | 197 | 0 | 351 | 0 | 51 | 45 | 0 | 39 | 57 | 51 | 181 | 26 | 19 | 106 | 150 | 52.2 | 2 | 31 | 305 | 0 | 230 | 40 | 39 | 136 | 1 | 8 | 0 | 86 | 0 | 0 | 0 | 91 | 17 | 59 | 0.44 | 115 | 0 | 0.1 | 4.38 | 6 | 7343.09 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 3.54 | 1162 | 0 | 0 | 0 | 766.22 | 0 | 0 | 0 | 57 | 87 | 0 | 25 | 0 | 8 | 1.69 | 3 | 0 | 0 | 1.93 | 179 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0.19 | 160 | 46 | 107 | 4 | 90 | 0 | 0 | 0 | 0.6 | 15 | 0.03 | 16 | 307 | 60 | 220 | 0 | 406 | 545 | 17 | 5583.2 | 12926.29 | 103.12
19:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 54 | 17 | 71 | 140 | 48 | 0 | 35 | 162 | 0 | 0 | 125 | 335 | 0 | 35 | 285 | 0 | 0 | 0 | 143.42 | 15 | 8 | 0 | 0 | 101 | 49 | 29 | 0 | 10 | 50 | 20 | 54.36 | 12 | 12 | 0 | 222 | 109 | 14 | 795 | 90 | 0 | 50 | 8 | 105 | 206 | 0 | 0 | 0 | 1224 | 0 | 67 | 195 | 0 | 353 | 0 | 51 | 47 | 0 | 39 | 79 | 50 | 190 | 26 | 19 | 104 | 178 | 52.2 | 0 | 31 | 310 | 0 | 230 | 42 | 39 | 154 | 0 | 8 | 0 | 86 | 0 | 0 | 0 | 127 | 17 | 59 | 0 | 115 | 0 | 0 | 0 | 0 | 7781.98 | 901 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 151 | 0 | 15 | 0 | 1164 | 0 | 0 | 0 | 887.21 | 0 | 0 | 0 | 57 | 90 | 0 | 100 | 22 | 8 | 0 | 0 | 12 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 161 | 46 | 109 | 0 | 92 | 0 | 130 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 540 | 545 | 17 | 6243.21 | 14025.19 | 103.14
19:30 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 54 | 54 | 71 | 125 | 48 | 0 | 35 | 162 | 0 | 0 | 119 | 311 | 0 | 35 | 265 | 0 | 0 | 0 | 143.42 | 15 | 7 | 0 | 0 | 92 | 70 | 37 | 0 | 26 | 34 | 20 | 54.36 | 12 | 12 | 0 | 222 | 101 | 5 | 720 | 160 | 0 | 50 | 8 | 88 | 207 | 0 | 0 | 0 | 1224 | 0 | 100 | 187 | 0 | 355 | 0 | 51 | 47 | 0 | 39 | 90 | 50 | 180 | 26 | 19 | 106 | 174 | 52.2 | 0 | 31 | 300 | 0 | 230 | 42 | 39 | 152 | 0 | 8 | 0 | 86 | 0 | 0 | 0 | 128 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 0 | 7799.98 | 901 | 0 | 0 | 31 | 0 | 38 | 0 | 0 | 175 | 0 | 15 | 0 | 1165 | 0 | 0 | 0 | 1064.58 | 0 | 0 | 0 | 57 | 90 | 0 | 100 | 26 | 8 | 0 | 0 | 12 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 160 | 45 | 105 | 0 | 91 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 750 | 560 | 17 | 6706.58 | 14506.56
20:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 54 | 54 | 72 | 143 | 48 | 0 | 35 | 162 | 0 | 0 | 127 | 315 | 0 | 35 | 277 | 0 | 0 | 0 | 143.42 | 15 | 7 | 0 | 0 | 89 | 85 | 38 | 0 | 26 | 34 | 20 | 54.36 | 12 | 12 | 0 | 222 | 105 | 21 | 700 | 160 | 0 | 50 | 8 | 93 | 209 | 0 | 0 | 0 | 1224 | 0 | 98 | 195 | 0 | 355 | 0 | 51 | 46 | 0 | 39 | 90 | 51 | 179 | 26 | 19 | 103 | 180 | 52.2 | 0 | 31 | 300 | 0 | 230 | 42 | 39 | 139 | 0 | 8 | 0 | 86 | 0 | 0 | 0 | 127 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 0 | 7857.98 | 901 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 175 | 0 | 15 | 0 | 1163 | 0 | 0 | 0 | 1126.98 | 0 | 0 | 0 | 57 | 90 | 0 | 100 | 30 | 8 | 0 | 0 | 14 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 160 | 47 | 102 | 0 | 92 | 0 | 100 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 180 | 0 | 1000 | 555 | 17 | 6843.98 | 14701.96 | 103.16
21:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 54 | 54 | 66 | 143 | 48 | 0 | 35 | 162 | 0 | 0 | 125 | 360 | 0 | 35 | 266 | 0 | 0 | 0 | 143.42 | 15 | 7 | 0 | 0 | 99 | 85 | 44 | 0 | 7 | 50 | 20 | 54.36 | 12 | 12 | 0 | 222 | 108 | 17 | 685 | 158 | 0 | 50 | 8 | 103 | 209 | 0 | 0 | 0 | 1224 | 0 | 140 | 195 | 0 | 353 | 0 | 51 | 46 | 0 | 39 | 90 | 51 | 190 | 26 | 19 | 104 | 176 | 52.2 | 0 | 31 | 315 | 0 | 230 | 40 | 39 | 150 | 0 | 8 | 0 | 86 | 0 | 0 | 0 | 127 | 17 | 69 | 0 | 154 | 0 | 0 | 0 | 0 | 7962.98 | 901 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 237 | 0 | 15 | 0 | 1163 | 0 | 0 | 0 | 1123.64 | 0 | 0 | 0 | 57 | 90 | 0 | 100 | 30 | 8 | 0 | 0 | 14 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 162 | 46 | 105 | 0 | 78 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 1050 | 558 | 17 | 7113.64 | 15076.62 | 103.17
22:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 54 | 17 | 62 | 143 | 48 | 0 | 35 | 108 | 0 | 0 | 136 | 320 | 0 | 35 | 280 | 0 | 0 | 0 | 143.42 | 15 | 7 | 0 | 0 | 91 | 88 | 44 | 0 | 13 | 50 | 21 | 54.36 | 12 | 12 | 0 | 220 | 106 | 27 | 685 | 35 | 0 | 50 | 8 | 98 | 210 | 0 | 0 | 0 | 1224 | 0 | 150 | 197 | 0 | 237 | 0 | 51 | 45 | 0 | 39 | 80 | 50 | 184 | 26 | 19 | 103 | 176 | 52.2 | 0 | 31 | 315 | 0 | 264 | 40 | 39 | 141 | 0 | 8 | 0 | 86 | 0 | 0 | 0 | 127 | 17 | 69 | 0 | 155 | 0 | 0 | 0 | 1 | 7637.98 | 901 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 150 | 0 | 15 | 0 | 1164 | 0 | 0 | 0 | 1128.35 | 0 | 0 | 0 | 57 | 90 | 0 | 100 | 30 | 8 | 0 | 0 | 14 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 160 | 46 | 103 | 0 | 78 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 1050 | 560 | 17 | 7027.35 | 14665.33 | 103.2
23:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 17 | 17 | 43 | 143 | 48 | 0 | 35 | 54 | 0 | 0 | 138 | 310 | 0 | 0 | 300 | 0 | 0 | 0 | 143.42 | 13 | 21 | 0 | 0 | 95 | 88 | 45 | 0 | 5 | 50 | 21 | 54.36 | 12 | 12 | 0 | 220 | 108 | 31 | 685 | 16 | 0 | 50 | 8 | 100 | 209 | 0 | 0 | 0 | 1224 | 0 | 65 | 197 | 0 | 234 | 0 | 51 | 46 | 0 | 39 | 68 | 51 | 187 | 27 | 19 | 106 | 176 | 52.2 | 0 | 31 | 310 | 0 | 292 | 40 | 39 | 147 | 0 | 8 | 0 | 62 | 0 | 0 | 0 | 128 | 17 | 69 | 0 | 155 | 0 | 0 | 0 | 5 | 7420.98 | 901 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1165 | 0 | 0 | 0 | 1127.42 | 0 | 0 | 0 | 57 | 90 | 0 | 100 | 28 | 8 | 0 | 0 | 14 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 162 | 48 | 109 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 1050 | 560 | 17 | 6730.42 | 14151.4 | 103.2
Total KWH | 0 | 1642560 | 767040 | 0 | 0 | 0 | 0 | 0 | 7923600 | 0 | 0 | 327960 | 502560 | 736416 | 3286080 | 1315767 | 127252 | 588062 | 989280 | 0 | 0 | 3041018 | 7551818 | 0 | 468802 | 6899376 | 0 | 0 | 147725 | 3484800 | 350400 | 285120 | 0 | 0 | 2224309 | 810436 | 641280 | 0 | 381600 | 451862 | 455068 | 595403 | 294720 | 295680 | 25078 | 5340762 | 2583500 | 443520 | 24000000 | 812945 | 0 | 1218240 | 106367.4 | 2384473 | 4799014 | 0 | 0 | 0 | 28963633 | 95175 | 1196000 | 4666909 | 0 | 8474100 | 0 | 1249083 | 1054560 | 0 | 868176 | 840960 | 1169778 | 4433280 | 172200 | 458670 | 2026920 | 3816960 | 1140946 | 434700 | 532256 | 7534000 | 0 | 6531000 | 958000 | 935400 | 3524645.46 | 54521 | 193728 | 0 | 1132800 | 0 | 0 | 0 | 1935100 | 429840 | 1149600 | 108208 | 2438400 | 34560 | 7800 | 249810 | 190320 | 177301931.86 | 21695273 | 0 | 0 | 155040 | 0 | 912000 | 0 | 0 | 719942 | 0 | 92160 | 238320 | 27912730 | 0 | 0 | 0 | 20075925 | 0 | 0 | 0 | 391584 | 808512 | 0 | 661568 | 151736 | 519518 | 328432 | 635110 | 103000 | 0 | 357040 | 4470364 | 0 | 0 | 0 | 0 | 0 | 9037491 | 0 | 27900 | 3943000 | 1114036 | 2716741 | 213434 | 756681 | 0 | 610312.5 | 0 | 41427.6 | 1457280 | 1486 | 397344 | 7375000 | 1441000 | 5326080 | 0 | 15861818 | 13751272.73 | 434400 | 144734957.83 | 322036889.69

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-08-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13435.88 | MW | 12:00 Hr. | Energy Generated |  |  | 322.0369 |  | MKWHr.
| Day Peak Demand |  |  | 15326.88 | MW | 12:00 Hr. | Energy Unserverd |  |  | 51.5 |  | MKWHr.
| Evening Peak Generation |  |  | 15076.62 | MW | 21:00 Hr. | Energy Demand |  |  | 373.5369 |  | MKWHr.
| Evening Peak Demand |  |  | 17850.62 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.5 |  | °C
| Minimum Generation of the Day |  |  | 12411.23 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 666.63 |  | MMCFD
| Maximum Generation of the Day |  |  | 15076.62 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.6304 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 26.0513 | 0 | 14.2366 | 0 | 0 | 0.14772 | 0 | 0 | 40.4356 | Gas | 92.2893 | Gas | 327369810.0732
| Chattogram Zone |  |  | 5.2425 | 52.9636 | 12.8743 | 0 | 5.3408 | 0.12025 | 0 | 0.3816 | 76.9231 | Coal | 122.9215 | Coal | 840029418.9968
| Cumilla Zone |  |  | 17.9413 | 0 | 10.3426 | 0 | 0 | 0.4347 | 3.817 | 0 | 32.5355 | HFO | 48.8499 | HFO | 901260047.856
| Mymensingh Zone |  |  | 0.03456 | 0 | 4.2082 | 0 | 0 | 0.36582 | 0 | 0 | 4.6085 | HSD | 1.3303 | HSD | 33389278.4
| Sylhet Zone |  |  | 22.7447 | 0 | 0 | 0 | 0 | 0.054521 | 0 | 0 | 22.7992 | Hydro | 5.3408 | Hydro | 534076.2
| Khulna Zone |  |  | 0 | 27.9127 | 0.2472 | 0.71994 | 0 | 0.23832 | 22.6073 | 0 | 51.7255 | Solar | 4.4234 | Solar | 71398338.218
| Barishal Zone |  |  | 6.7671 | 36.9881 | 0.83174 | 0 | 0 | 0.001486 | 0 | 0 | 44.5884 | Import | 46.5002 | Import | 277664792.97
| Rajshahi Zone |  |  | 13.5079 | 0 | 2.6359 | 0 | 0 | 1.3485 | 20.0759 | 0 | 37.5682 | Wind | 0.3816 | Wind | 5613336
| Rangpur Zone |  |  | 0 | 5.057 | 3.4734 | 0.61031 | 0 | 1.7121 | 0 | 0 | 10.8529
| Total |  |  | 92.2893 | 122.9215 | 48.8499 | 1.3303 | 5.3408 | 4.4234 | 46.5002 | 0.3816 | 322.0369
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 327369810.0732 |  | Hydro | 534076.2
|  |  |  | Coal | 840029418.9968 |  | Solar | 71398338.218
|  |  |  | HFO | 901260047.856 |  | Import | 277664792.97
|  |  |  | HSD | 33389278.4 |  | Wind | 5613336
[5 empty] | Total: | 245,72,59,098 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6953 | Peak Hr Flow | 901.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43742218.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 20.0759 | Peak Hr Flow | 1123.64 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2515 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.817 | Peak Hr Flow | 176.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2547 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.5882 | Peak Hr Flow | 2200.64 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 537 |  | 5982
|  |  |  | Chattogram |  | 31 |  | 1599
|  |  |  | Cumilla |  | 286 |  | 1652
|  |  |  | Mymensingh |  | 486 |  | 1553
|  |  |  | Sylhet |  | 195 |  | 762
|  |  |  | Khulna |  | 366 |  | 1990
|  |  |  | Barishal |  | 132 |  | 531
|  |  |  | Rajshahi |  | 334 |  | 1735
|  |  |  | Rangpur |  | 288 |  | 1197
|  |  |  | Total |  | 2655 |  | 17001
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 89
|  |  |  | Total Unavailable Capacity |  |  |  | 389
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:14 | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) HT is restored.
|  | 08:15 | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) LT is restored.
| 08:20 | 13:27 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to 33 kV Bus Section-2 | [7 empty] | 10.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 08:20 | 13:26 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to 33 kV Bus Section-2 | [7 empty] | 10.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 08:26 | 09:37 | Ishurdi 230/132kV S/S 230/132 kV T-02 LT Tripped showing 1.MCB FAULYT DC SUPPLY CONTROL
PANEL.2.TRIP CIRCUIT FAILURE.3.PRIMARY PROTECTION DISTRUBED.4.PRIMARY PROTECTION
OPERATED.5.MCB FAULTY MOTOR DRIVE MARSH. KIOSK relays.
| 08:26 | 09:34 | Ishurdi 230/132kV S/S 230/132 kV T-02 HT Tripped showing 1.MCB FAULYT DC SUPPLY CONTROL
PANEL.2.TRIP CIRCUIT FAILURE.3.PRIMARY PROTECTION DISTRUBED.4.PRIMARY PROTECTION
OPERATED.5.MCB FAULTY MOTOR DRIVE MARSH. KIOSK relays Due to UNKNOWN
|  | 08:42 | Ashuganj-Sreepur 230 kV Ckt-2 is restored.
|  | 09:00 | Faridpur 132/33kV S/S Transformer-1 LT is restored.
|  | 09:00 | Faridpur 132/33kV S/S Transformer-1 HT is restored.
|  | 09:40 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-2 is restored.
|  | 09:40 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 is restored.
|  | 09:41 | Sirajganj-Sreepur 230 kV Ckt-1 is restored.
| 09:57 | 12:13 | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Hot spot
| 09:57 | 12:13 | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Hot spot
|  | 10:12 | Barishal 230/132kV S/S T-4 HT is restored.
|  | 10:15 | Barishal 230/132kV S/S T-4 LT is restored.
| 12:00 |  | Day Peak Generation: 13435 MW.
|  | 13:46 | Halishahar-Khulshi 132kV Ckt-1 is restored.
|  | 14:07 | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 is restored.
| 17:30 | 18:51 | Niamatpur 132/33kV S/S Transformer-1(407T) HT Scheduled S/D Due to Red Hot Maintenance | [7 empty] | 20.0MW load
interrup.
| 17:30 | 18:52 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Scheduled S/D Due to Red Hot Maintenance | [7 empty] | 20.0MW load
interrup.
| 21:00 |  | Evening Peak Generation: 15077 MW.
| 21:20 |  | Ashuganj North ST tripped
| 06:15 | 06:27 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Tripped showing Over Current relay relays Due | [7 empty] | 27.0MW load
|  |  | to Due to 33KV Aganagar feeder CT explode | [7 empty] | interrup.
| 06:15 | 06:27 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Tripped showing Over current realy relays Due | [7 empty] | 27.0MW load
|  |  | to Due to 33 kv Aganagar feeder CT explode. | [7 empty] | interrup.
| 06:43 |  | Ghorasal- Ishwardi 230 kV Ckt-1 Scheduled S/D from Ishurdi 230/132kV end.
| 06:59 |  | Ghorasal- Ishwardi 230 kV Ckt-1 Project Work S/D from Ghorashal 230kV end Due to
Shutdown requisition from STGE Project
| 07:43 |  | Munshiganj 132/33kV S/S Transformer-1 LT Scheduled S/D Due to 33 KV XLPE cable
termination
| 07:43 |  | Munshiganj 132/33kV S/S Transformer-1 HT Scheduled S/D Due to 33 KV XLPE cable
termination
| 07:54 |  | Ashuganj CCPP 225 MW Synchronized with remarks:- GT
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-08-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 330 | 7923600 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 125 | 3041018 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 127252 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 266 | 6899376 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 327960 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 3286080 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 588062 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 468802 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 350400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 285120 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 49 | 767040 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 48 | 1315767 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 66 | 736416 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1642560 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 989280 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 147725 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 502560 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 360 | 7551818 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3484800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 1997.42 | 40435636
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 106367.4 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 95175 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1218240 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5340762 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 209 | 4799014 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 103 | 2384473 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 20 | 455068 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 451862 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 294720 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 443520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 44 | 641280 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25078 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 85 | 810436 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 595403 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 108 | 2583500 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 295680 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 99 | 2224309 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 158 | 812945 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28963633 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 7 | 381600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 685 | 24000000 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 3167.36 | 76923065.4
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 0 | 0 | Under Maintenance
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 353 | 8474100 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 39 | 868176 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 46 | 1054560 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 195 | 4666909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1249083 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 140 | 1196000 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 532256 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 51 | 1169778 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 190 | 4433280 | -
| Import (Tripura) |  | Import | 0 | 160 | 176 | 3816960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1140946 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 458670 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 104 | 2026920 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 172200 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 840960 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 434700 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1563.2 | 32535498
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 108208 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 34560 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 154 | 2438400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 1149600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 249810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 190320 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 429840 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 240 | 4608538
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 54521 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 958000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 935400 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 150 | 3524645.46 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1132800 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 127 | 1935100 | plant availability zero
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 193728 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7534000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 230 | 6531000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 995 | 22799194.46
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 901 | 21695273 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 28 | 155040 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 92160 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 238320 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 237 | 719942 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1163 | 27912730 | AGC+FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2382 | 51725465
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1050 | 15861818 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 397344 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 60 | 1441000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 558 | 13751272.73 | Coal shortage
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5326080 | -
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 434400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7375000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1486 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2228 | 44588400.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 328432 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 151736 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 177 | 4470364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 348 | 9037491 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 14 | 103000 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 519518 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 661568 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 90 | 808512 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 57 | 391584 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 27900 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1123.64 | 20075925 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 357040 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 635110 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1947.64 | 37568180
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 610312.5 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1114036 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 162 | 3943000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 78 | 756681 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 41427.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 105 | 2716741 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 213434 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1457280 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 556 | 10852912.1
Eastern Grid Total |  |  |  |  | 17440.562 | 7962.98 | 177301931.86
Western Grid Total |  |  |  |  | 11731.125 | 7113.64 | 144734957.83
National Grid Total |  |  |  |  | 29171.687 | 15076.62 | 322036889.69
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-08-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10069.05 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4333.6 | MW
i) Dhaka area |  |  | 5445.05 |  | MW | i) Khulna area |  |  |  | 1624 | MW
ii) Chattogram area |  |  | 1624 |  | MW | ii) Barishal area |  |  |  | 399.2 | MW
iii) Cumilla area |  |  | 1366 |  | MW | iii) Rajshahi area |  |  |  | 1401.4 | MW
iv) Mymensingh area |  |  | 1067 |  | MW | iv) Rangpur area |  |  |  | 909 | MW
v) Sylhet area |  |  | 567 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14402.65 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 19 | 11:00 | 67 | HaripurSBU | 130 | 00:00 | 133 | Narshingdi | 170 | 21:00 | 199 | Uttara | 95 | 19:30
2 | AKSML | 139 | 02:00 | 68 | Hasnabad | 105 | 20:00 | 134 | Natore | 122 | 19:30 | 200 | UttaraNew | 56 | 23:00
3 | Aftabnagar | 42 | 13:00 | 69 | Hathazari | 90 | 22:00 | 135 | Nawabganj | 68.1 | 20:00 | 201 | Zigatola | 108 | 13:00
4 | Agargaon | 115 | 19:30 | 70 | Hatirjheel | 77 | 15:00 | 136 | Netrakona | 112 | 21:00
5 | Agrabad | 74 | 20:00 | 71 | Ishurdi | 68 | 08:00 | 137 | New | 85.2 | 12:00
6 | Amnura | 28 | 02:00 | 72 | Jaldhaka | 76 | 06:00 | 138 | Niamatpur | 82 | 20:00
7 | Ashuganj | 92 | 23:00 | 73 | Jamalpur | 105 | 20:00 | 139 | Noapara | 35 | 11:00
8 | BSRM | 199 | 04:00 | 74 | Jashore | 160 | 19:30 | 140 | PHP | 11 | 14:00
9 | Bagerhat | 79 | 21:00 | 75 | Jhenaidah | 82 | 20:00 | 141 | Pabna | 86 | 08:00
10 | Bajitpur | 76 | 22:00 | 76 | Joydebpur | 160 | 10:00 | 142 | Palashbari | 121 | 19:30
11 | Bakerganj | 14.2 | 21:00 | 77 | Joypurhat | 50 | 04:00 | 143 | Panchagarh | 66 | 20:00
12 | Bakulia | 103 | 20:00 | 78 | Juldah | 14 | 10:00 | 144 | Patiya | 12 | 21:00
13 | Banani | 60 | 13:00 | 79 | KSRM | 22 | 07:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 6 | 11:00 | 80 | Kabirpur | 246 | 20:00 | 146 | Patuakhali | 55 | 19:00
15 | Barapukuria | 62 | 10:00 | 81 | Kachua | 84 | 21:00 | 147 | Payra | 28 | 07:00
16 | Barguna | 20 | 21:00 | 82 | Kaliganj | 35 | 21:00 | 148 | Postogola | 61 | 23:00
17 | Barishal | 93 | 11:00 | 83 | Kallyanpur | 126 | 19:00 | 149 | Pubail | 38 | 11:00
18 | Barishal-230 | 86 | 21:00 | 84 | Kalurghat | 39 | 20:00 | 150 | Purbachal | 28 | 19:00
19 | Baroaulia | 73 | 19:00 | 85 | Kamrangirchar | 81 | 13:00 | 151 | Purbasadipur | 124 | 00:00
20 | Baroirhat | 67 | 21:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 37 | 19:00
21 | Bashundhara | 207 | 19:00 | 87 | Kasba | 37 | 22:00 | 153 | Rahim | 54 | 23:00
22 | BashundharaCement | 8 | 17:00 | 88 | Kazla | 116 | 11:00 | 154 | Rajbari | 71 | 08:00
23 | Beanibazar | 66 | 19:00 | 89 | Keranigonj | 90 | 20:00 | 155 | Rajendrapur | 112 | 10:00
24 | Benapole | 59 | 21:00 | 90 | Khagrachori | 40 | 21:00 | 156 | Rajshahi | 114 | 07:00
25 | Bhaluka | 139 | 21:00 | 91 | Khulna | 57 | 19:00 | 157 | Rajshahi-230 | 83 | 19:00
26 | Bhandaria | 45 | 07:00 | 92 | Khulshi | 170 | 21:00 | 158 | Ramganj | 96 | 22:00
27 | Bhangura | 35 | 19:00 | 93 | Kishoreganj | 124 | 01:00 | 159 | Rampur | 48 | 00:00
28 | Bheramara(GK) | 65 | 07:00 | 94 | Kodda | 291 | 18:00 | 160 | Rangamati | 17 | 21:00
29 | Bhulta | 194 | 00:00 | 95 | Kulaura | 50 | 02:00 | 161 | Rangpur | 118 | 10:00
30 | Bog-Sherpur | 58 | 00:00 | 96 | Kurigram | 72 | 07:00 | 162 | Ruppur | 2.8 | 10:00
31 | Bogura | 191 | 19:30 | 97 | Kushtia | 130 | 21:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 66 | 20:00 | 98 | Laksam | 31 | 18:30 | 164 | Saidpur | 103 | 11:00
33 | Brahmanbaria | 120 | 21:00 | 99 | Lakshmipur | 43 | 01:00 | 165 | Santhia | 36 | 21:00
34 | Cantonment | 128 | 13:00 | 100 | Lalbag | 76 | 13:00 | 166 | Satkhira | 120 | 21:00
35 | Chandina | 31 | 06:00 | 101 | Lalmonirhat | 56 | 02:00 | 167 | Satmasjid | 104 | 14:00
36 | Chandpur | 72 | 21:00 | 102 | MI_Cement | 15.8 | 16:00 | 168 | Savar | 210 | 20:00
37 | Chandraghona | 32 | 18:30 | 103 | Madanganj | 48 | 20:00 | 169 | SevenRings | 12.9 | 13:00
38 | Chapai | 60 | 21:00 | 104 | Madaripur | 91 | 22:00 | 170 | ShahCement | 28 | 18:30
39 | Charfasson | 29 | 22:00 | 105 | Madartek | 83 | 21:00 | 171 | Shahjadpur | 72 | 22:00
40 | Charsaidpur | 38 | 01:00 | 106 | Madunaghat | 56 | 20:00 | 172 | Shahjibazar | 121 | 20:00
41 | Chauddagram | 64 | 21:00 | 107 | Magura | 54 | 07:00 | 173 | Shahmirpur | 55 | 21:00
42 | Chhatak | 35 | 05:00 | 108 | Mahasthangarh | 73 | 03:00 | 174 | Shariatpur | 72 | 21:00
43 | Chowmuhani | 135 | 23:00 | 109 | Maijdee | 36 | 19:00 | 175 | Sherpur | 130 | 19:00
44 | Chuadanga | 97 | 04:00 | 110 | Manikganj | 118 | 21:00 | 176 | Shikalbaha | 24 | 19:30
45 | Coxsbazar | 146 | 21:00 | 111 | Maniknagar | 70 | 23:00 | 177 | Shitalakhya | 77.7 | 15:00
46 | Cumilla(N) | 124 | 22:00 | 112 | Matarbari | 60 | 19:30 | 178 | Sholosohor | 52 | 20:00
47 | Cumilla(S) | 184 | 14:00 | 113 | Matuail | 72 | 15:00 | 179 | Shomvuganj | 36 | 20:00
48 | Daganbhuiyan | 33 | 19:00 | 114 | Metrorail_Motijheel | 27 | 15:00 | 180 | Shyampur | 150 | 08:00
49 | Daudkandi | 122 | 21:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 135 | 12:00
50 | DhakaUniversity | 80 | 13:00 | 116 | Millgate | 110 | 15:00 | 182 | Sirajganj | 122 | 19:30
51 | Dhamrai | 96 | 00:00 | 117 | Mirpur | 155 | 19:00 | 183 | Sitakunda | 28 | 10:00
52 | Dhanmondi | 104 | 16:00 | 118 | Mirsorai | 53 | 14:00 | 184 | Sonargaon | 135 | 21:00
53 | Dohazari | 110 | 21:00 | 119 | Mirzapur | 38 | 19:00 | 185 | Sreemongol | 67 | 00:00
54 | Faridpur | 148 | 20:00 | 120 | Mithapukur | 78 | 07:00 | 186 | Sreepur | 135 | 20:00
55 | Fatullah | 106 | 15:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 47.9 | 19:30
56 | Fenchuganj | 45 | 21:00 | 122 | Mogbazar | 47.2 | 00:00 | 188 | Sunamganj | 48 | 21:00
57 | Feni | 113 | 22:00 | 123 | Mongla | 32 | 11:00 | 189 | Sylhet | 98 | 21:00
58 | GPH | 2 | 17:00 | 124 | Motijheel | 45 | 13:00 | 190 | Sylhet_(South) | 71 | 01:00
59 | Ghatail | 83 | 11:00 | 125 | Muktagacha | 40 | 15:00 | 191 | TK | 24 | 21:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 120 | 20:00 | 192 | Tangail | 162 | 19:00
61 | Ghorashal-230 | 95 | 20:00 | 127 | Muradnagar | 44 | 21:00 | 193 | Taraganj | 34 | 10:00
62 | Goalpara | 36 | 19:00 | 128 | Mymensingh | 152 | 20:00 | 194 | Tasnim | 43 | 06:00
63 | Gollamari | 96 | 12:00 | 129 | Nabinagar | 108 | 10:00 | 195 | Thakurgaon | 111 | 19:30
64 | Gopalganj | 95 | 07:00 | 130 | Naogaon | 123 | 21:00 | 196 | Tongi | 153 | 11:00
65 | Gulshan | 102 | 13:00 | 131 | Narail | 59 | 22:00 | 197 | Ullahpara | 33 | 07:00
66 | Halishahar | 110 | 20:00 | 132 | Narinda | 72 | 13:00 | 198 | Ullon | 45 | 22:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-08-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13479.77 | 2370 |  | 15956.77
1:00 | 12909.51 | 2632 |  | 15659.95
2:00 | 12820.77 | 2531 |  | 15465.67
3:00 | 12755.88 | 2432 |  | 15297.32
4:00 | 12702.46 | 2180 |  | 14980.56
5:00 | 12697.86 | 2021 |  | 14809.81
6:00 | 12474.55 | 1734 |  | 14286.58
7:00 | 12411.23 | 1566 |  | 14047.7
8:00 | 12748.24 | 1427 |  | 14239.46
9:00 | 12802.27 | 1505 |  | 14375
10:00 | 13210.63 | 911 |  | 14162.63
11:00 | 13329.58 | 1272 |  | 14658.58
12:00 | 13435.88 | 1810 |  | 15326.88
13:00 | 13569.49 | 2003 |  | 15662.49
14:00 | 13375.42 | 2127 |  | 15598.42
15:00 | 13078.48 | 2958 |  | 16169.48
16:00 | 12847.77 | 2778 |  | 15750.77
17:00 | 12904.87 | 2534 |  | 15552.9
18:00 | 12926.29 | 2190 |  | 15215.29
19:00 | 14025.19 | 2575 |  | 16716.19
19:30 | 14506.56 | 2681 |  | 17308.56
20:00 | 14701.96 | 1969 |  | 16759.96
21:00 | 15076.62 | 2655 |  | 17850.62
22:00 | 14665.33 | 2442 |  | 17217.33
23:00 | 14151.4 | 2878 |  | 17159.4
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-08-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7471.62 | 6008.15 | 13479.77 | DAILY GENERATION CURVE
00:30 | 7363.12 | 5831.52 | 13194.64
01:00 | 7254.62 | 5654.89 | 12909.51 | 08-08-2026
01:30 | 7210.02 | 5655.12 | 12865.14
02:00 | 7165.42 | 5655.35 | 12820.77
02:30 | 7133.92 | 5654.405 | 12788.325
03:00 | 7102.42 | 5653.46 | 12755.88
03:30 | 7087.92 | 5641.25 | 12729.17
04:00 | 7073.42 | 5629.04 | 12702.46
04:30 | 7089.92 | 5610.24 | 12700.16
05:00 | 7106.42 | 5591.44 | 12697.86
05:30 | 7032 | 5554.205 | 12586.205
06:00 | 6957.58 | 5516.97 | 12474.55
06:30 | 6911.72 | 5531.17 | 12442.89
07:00 | 6865.86 | 5545.37 | 12411.23
07:30 | 6921.44 | 5658.295 | 12579.735
08:00 | 6977.02 | 5771.22 | 12748.24
08:30 | 6974.685 | 5800.57 | 12775.255
09:00 | 6972.35 | 5829.92 | 12802.27
09:30 | 7141.795 | 5864.655 | 13006.45
10:00 | 7311.24 | 5899.39 | 13210.63
10:30 | 7324.995 | 5945.11 | 13270.105
11:00 | 7338.75 | 5990.83 | 13329.58
11:30 | 7402.63 | 5980.1 | 13382.73
12:00 | 7466.51 | 5969.37 | 13435.88
12:30 | 7503.6 | 5999.085 | 13502.685
13:00 | 7540.69 | 6028.8 | 13569.49
13:30 | 7507.475 | 5964.98 | 13472.455
14:00 | 7474.26 | 5901.16 | 13375.42
14:30 | 7399.655 | 5827.295 | 13226.95
15:00 | 7325.05 | 5753.43 | 13078.48
15:30 | 7307.85 | 5655.275 | 12963.125
16:00 | 7290.65 | 5557.12 | 12847.77
16:30 | 7331.675 | 5544.645 | 12876.32
17:00 | 7372.7 | 5532.17 | 12904.87
17:30 | 7357.895 | 5557.685 | 12915.58
18:00 | 7343.09 | 5583.2 | 12926.29
18:30 | 7562.535 | 5913.205 | 13475.74
19:00 | 7781.98 | 6243.21 | 14025.19
19:30 | 7799.98 | 6706.58 | 14506.56
20:00 | 7857.98 | 6843.98 | 14701.96
20:30 | 7910.48 | 6978.81 | 14889.29 |  | Executive Engineer
21:00 | 7962.98 | 7113.64 | 15076.62 |  | Network Operation Division
21:30 | 7800.48 | 7070.495 | 14870.975
22:00 | 7637.98 | 7027.35 | 14665.33
22:30 | 7529.48 | 6878.885 | 14408.365
23:00 | 7420.98 | 6730.42 | 14151.4

## En-Curve
QF-LDC-12
Date | 08-08-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2248 | 1462 | 840 | 38 | 156 | 792.95 | 221 | 5339 | 0 | 657.42 | 1697.4 | 0 | 0 | 28 | 2370 | DAILY ENERGY CURVE
00:30 | 2289 | 1492.5 | 870.5 | 38 | 154 | 790.32 | 221.5 | 5240 | 0 | 557.92 | 1517.4 | 0 | 0 | 23.5 | 2501 | 08-08-2026
01:00 | 2330 | 1523 | 901 | 38 | 152 | 787.69 | 222 | 5141 | 0 | 458.42 | 1337.4 | 0 | 0 | 19 | 2632
01:30 | 2339.5 | 1518.5 | 901 | 38 | 152 | 788.92 | 222 | 5149.5 | 0 | 422.92 | 1318.8 | 0 | 0 | 14 | 2581.5 | Energy Generated | 322.0369 |  | MKWHr
02:00 | 2349 | 1514 | 901 | 38 | 152 | 790.15 | 222 | 5158 | 0 | 387.42 | 1300.2 | 0 | 0 | 9 | 2531 | Energy not Served | 51.5 |  | MKWHr
02:30 | 2355.5 | 1521 | 901 | 38 | 150 | 790.305 | 222 | 5155 | 0 | 380.92 | 1264.6 | 0 | 0 | 10 | 2481.5 | Total Energy Requirement | 373.5369 |  | MKWHr
03:00 | 2362 | 1528 | 901 | 38 | 148 | 790.46 | 222 | 5152 | 0 | 374.42 | 1229 | 0 | 0 | 11 | 2432
03:30 | 2369.5 | 1517.5 | 901 | 38 | 148 | 776.25 | 222 | 5150 | 0 | 374.42 | 1211 | 0 | 0 | 21.5 | 2306
04:00 | 2377 | 1507 | 901 | 38 | 148 | 762.04 | 222 | 5148 | 0 | 374.42 | 1193 | 0 | 0 | 32 | 2180
04:30 | 2381.5 | 1517.5 | 901 | 38 | 147 | 756.24 | 222 | 5153.5 | 0 | 374.92 | 1181.5 | 0 | 0 | 27 | 2100.5
05:00 | 2386 | 1528 | 901 | 38 | 146 | 750.44 | 222 | 5159 | 0 | 375.42 | 1170 | 0 | 0 | 22 | 2021
05:30 | 2296.5 | 1517 | 901 | 38 | 134 | 751.67 | 222 | 5157.5 | 8.515 | 375.42 | 1169.1 | 0 | 0 | 15.5 | 1877.5
06:00 | 2207 | 1506 | 901 | 38 | 122 | 752.9 | 222 | 5156 | 17.03 | 375.42 | 1168.2 | 0 | 0 | 9 | 1734
06:30 | 2143.5 | 1491.5 | 901 | 38 | 121 | 752.73 | 221.5 | 5148 | 73.04 | 370.92 | 1167.7 | 0 | 0 | 14 | 1650
07:00 | 2080 | 1477 | 901 | 38 | 120 | 752.56 | 221 | 5140 | 129.05 | 366.42 | 1167.2 | 0 | 0 | 19 | 1566
07:30 | 2189.5 | 1457.25 | 901 | 38 | 125 | 751.825 | 220.5 | 5144 | 205.04 | 358.42 | 1175.2 | 0 | 0 | 14 | 1496.5
08:00 | 2299 | 1437.5 | 901 | 38 | 130 | 751.09 | 220 | 5148 | 281.03 | 350.42 | 1183.2 | 0 | 0 | 9 | 1427
08:30 | 2289 | 1419.5 | 901 | 38 | 133 | 747.45 | 220 | 5124.5 | 363.785 | 358.42 | 1171.1 | 0 | 0 | 9.5 | 1466
09:00 | 2279 | 1401.5 | 901 | 38 | 136 | 743.81 | 220 | 5101 | 446.54 | 366.42 | 1159 | 0 | 0 | 10 | 1505
09:30 | 2305 | 1415.75 | 901 | 38 | 135 | 745.555 | 220 | 5124.5 | 479.725 | 402.92 | 1227.5 | 0 | 0 | 11.5 | 1208
10:00 | 2331 | 1430 | 901 | 38 | 134 | 747.3 | 220 | 5148 | 512.91 | 439.42 | 1296 | 0 | 0 | 13 | 911
10:30 | 2302 | 1455 | 901 | 38 | 144 | 747.47 | 219.5 | 5163.5 | 547.215 | 446.42 | 1291 | 0 | 0 | 15 | 1091.5
11:00 | 2273 | 1480 | 901 | 38 | 154 | 747.64 | 219 | 5179 | 581.52 | 453.42 | 1286 | 0 | 0 | 17 | 1272
11:30 | 2279 | 1469.75 | 901 | 38 | 162 | 750.63 | 219 | 5185 | 585.93 | 458.92 | 1312 | 0 | 0 | 21.5 | 1541
12:00 | 2285 | 1459.5 | 901 | 38 | 170 | 753.62 | 219 | 5191 | 590.34 | 464.42 | 1338 | 0 | 0 | 26 | 1810
12:30 | 2271 | 1485.5 | 901 | 38 | 174 | 755.04 | 219.5 | 5190.5 | 606.725 | 476.92 | 1353.5 | 0 | 0 | 31 | 1906.5
13:00 | 2257 | 1511.5 | 901 | 38 | 178 | 756.46 | 220 | 5190 | 623.11 | 489.42 | 1369 | 0 | 0 | 36 | 2003
13:30 | 2261 | 1508.5 | 901 | 38 | 182 | 756.615 | 221 | 5186.5 | 561.82 | 453.42 | 1373.1 | 0 | 0 | 29.5 | 2065
14:00 | 2265 | 1505.5 | 901 | 38 | 186 | 756.77 | 222 | 5183 | 500.53 | 417.42 | 1377.2 | 0 | 0 | 23 | 2127
14:30 | 2246 | 1505.5 | 900.5 | 38 | 184 | 757.96 | 222 | 5112 | 444.37 | 417.42 | 1385.7 | 0 | 0 | 13.5 | 2542.5
15:00 | 2227 | 1505.5 | 900 | 38 | 182 | 759.15 | 222 | 5041 | 388.21 | 417.42 | 1394.2 | 0 | 0 | 4 | 2958
15:30 | 2230.5 | 1522 | 900.5 | 38 | 179 | 757.465 | 222 | 4918.5 | 310.86 | 433.92 | 1433.88 | 0 | 0 | 16.5 | 2868
16:00 | 2234 | 1538.5 | 901 | 38 | 176 | 755.78 | 222 | 4796 | 233.51 | 450.42 | 1473.56 | 0 | 0 | 29 | 2778
16:30 | 2240.5 | 1530.25 | 901 | 38 | 176 | 766.815 | 222 | 4783.5 | 180.275 | 462.42 | 1554.56 | 0 | 0 | 21 | 2656
17:00 | 2247 | 1522 | 901 | 38 | 176 | 777.85 | 222 | 4771 | 127.04 | 474.42 | 1635.56 | 0 | 0 | 13 | 2534
17:30 | 2248.5 | 1512 | 900.5 | 38 | 163 | 772.035 | 222 | 4733.5 | 83.565 | 517.92 | 1709.56 | 0 | 0 | 15 | 2362
18:00 | 2250 | 1502 | 900 | 38 | 150 | 766.22 | 222 | 4696 | 40.09 | 561.42 | 1783.56 | 0 | 0 | 17 | 2190
18:30 | 2267 | 1544.5 | 900.5 | 38 | 164 | 826.715 | 222 | 4739 | 20.045 | 638.42 | 1961.56 | 140.5 | 0 | 13.5 | 2382.5
19:00 | 2284 | 1587 | 901 | 38 | 178 | 887.21 | 222 | 4782 | 0 | 715.42 | 2139.56 | 281 | 0 | 10 | 2575
19:30 | 2271 | 1527 | 901 | 38 | 174 | 1064.58 | 222 | 4931 | 0 | 691.42 | 2320.56 | 340 | 0 | 26 | 2681
20:00 | 2221 | 1509 | 901 | 38 | 180 | 1126.98 | 222 | 5156 | 0 | 712.42 | 2334.56 | 275 | 0 | 26 | 1969
20:30 | 2245 | 1561.5 | 901 | 38 | 178 | 1125.31 | 222 | 5175.5 | 0 | 720.42 | 2367.56 | 338.5 | 0 | 16.5 | 2312
21:00 | 2269 | 1614 | 901 | 38 | 176 | 1123.64 | 222 | 5195 | 0 | 728.42 | 2400.56 | 402 | 0 | 7 | 2655
21:30 | 2233.5 | 1600.5 | 901 | 38 | 176 | 1125.995 | 221 | 5195.5 | 0 | 728.92 | 2282.06 | 358.5 | 0 | 10 | 2548.5
22:00 | 2198 | 1587 | 901 | 38 | 176 | 1128.35 | 220 | 5196 | 0 | 729.42 | 2163.56 | 315 | 0 | 13 | 2442
22:30 | 2219 | 1580 | 901 | 38 | 176 | 1127.885 | 220 | 5198.5 | 0 | 728.42 | 2053.06 | 157.5 | 0 | 9 | 2660
23:00 | 2240 | 1573 | 901 | 38 | 176 | 1127.42 | 220 | 5201 | 0 | 727.42 | 1942.56 | 0 | 0 | 5 | 2878
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 08-08-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 177 | 55 | 260 | 166 | 1244 | 580 | Ishurdi-Ghorashal Ckt-1 | Export | 4384218.18
1:00 | 161 | 40 | 266 | 144 | 1134 | 528
2:00 | 164 | 44 | 282 | 152 | 1158 | 534 |  | Import | 0
3:00 | 174 | 60 | 274 | 152 | 1108 | 518
4:00 | 179 | 65 | 260 | 156 | 1098 | 532 | Ishurdi-Ghorashal Ckt-2 | Export | 0
5:00 | 174 | 64 | 256 | 154 | 1096 | 538
6:00 | 178 | 61 | 224 | 134 | 1128 | 534 |  | Import | 0
7:00 | 187 | 72 | 0 | 0 | 1302 | 600
8:00 | 189 | 74 | 0 | 0 | 1608 | 728 | Sirajganj-Sreepur Ckt-1 | Export | 1962000
9:00 | 199 | 87 | 0 | 0 | 1844 | 800
10:00 | 173 | 70 | 380 | 148 | 1540 | 750 |  | Import | 0
11:00 | 196 | 51 | 430 | 164 | 1490 | 768
12:00 | 182 | 40 | 404 | 160 | 1464 | 766 | Sirajganj-Sreepur Ckt-2 | Export | 1966000
13:00 | 191 | 41 | 464 | 192 | 1540 | 772
14:00 | 188 | 42 | 442 | 184 | 1580 | 806 |  | Import | 0
15:00 | 185 | 41 | 424 | 144 | 1552 | 752
16:00 | 187 | 44 | 380 | 130 | 1500 | 754 | Gopalganj-Aminbazar Ckt-1 | Export | 17690000
17:00 | 183 | 44 | 390 | 156 | 1426 | 734
18:00 | 175 | 36 | 360 | 136 | 1322 | 700 |  | Import | 0
18:30 | 184 | 41 | 386 | 150 | 1520 | 688
19:00 | 189 | 39 | 432 | 164 | 1532 | 672 | Gopalganj-Aminbazar Ckt-2 | Export | 17740000
19:30 | 191 | 32 | 452 | 154 | 1688 | 656
20:00 | 194 | 43 | 464 | 168 | 1766 | 710 |  | Import | 0
21:00 | 189 | 51 | 470 | 144 | 1856 | 620
22:00 | 195 | 48 | 500 | 148 | 1852 | 622 |  | Total Export | 43742218.18
23:00 | 181 | 40 | 470 | 160 | 1804 | 638 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-08-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 380 | 01:00 | 362 | 10:00 | Madunaghat | 402 | 19:00 | 393 | 11:00
Amtali | 415 | 17:00 | 408 | 22:00 | Meghnaghat | 384 | 01:00 | 364 | 08:00
Ashuganj | 403 | 6:00 | 384 | 9:00 | Mirsorai | 402 | 19:30 | 385 | 12:00
Bhulta | 397 | 06:00 | 377 | 13:00 | Payra | 415 | 06:00 | 410 | 20:00
Bibiana | 382 | 01:00 | 372 | 11:00 | Rahanpur | 414 | 00:00 | 406 | 20:00
BIPTC | 402 | 05:00 | 393 | 20:00 | Rampal | 399 | 01:00 | 389 | 11:00
Bogura | 401 | 09:00 | 393 | 05:00
Gopalganj | 394 | 01:00 | 385 | 20:00
Kaliakoir | 370 | 05:00 | 352 | 10:00
Korerhat | 400 | 19:30 | 386 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 01:00 | 220 | 12:00 | Ishurdi | 236 | 00:00 | 226 | 12:00
AKSML | 236 | 18:30 | 230 | 13:00 | Jhenaidah | 226 | 00:00 | 216 | 12:00
Aminbazar | 233 | 01:00 | 219 | 10:00 | Kachua | 233 | 19:30 | 224 | 13:00
Ashuganj | 227 | 01:00 | 213 | 08:00 | Kaliakoir | 232 | 01:00 | 218 | 10:00
Ashuganj-400 | 227 | 1:00 | 213 | 8:00 | Keranigonj | 230 | 01:00 | 218 | 11:00
Baghabari | 234 | 07:00 | 227 | 20:00 | Khulna(S) | 227 | 00:00 | 221 | 12:00
Barapukuria | 228 | 18:30 | 221 | 04:00 | Korerhat | 229 | 18:30 | 221 | 13:00
Barapukuria-230 | 228 | 18:00 | 222 | 4:00 | Madunaghat | 240 | 18:30 | 234 | 13:00
Barishal | 228 | 01:00 | 223 | 23:00 | Madunaghat-400 | 241 | 19:00 | 236 | 11:00
Bheramara | 234 | 00:00 | 223 | 12:00 | Maniknagar | 225 | 01:00 | 214 | 14:00
Bhulta | 228 | 01:00 | 216 | 12:00 | Meghnaghat | 234 | 03:00 | 225 | 11:00
Bibiana | 223 | 18:00 | 215 | 11:00 | Meghnaghat-400 | 230 | 01:00 | 217 | 12:00
BIPTC | 236 | 00:00 | 224 | 12:00 | Mirsorai | 236 | 19:00 | 225 | 11:00
Bogura | 242 | 18:00 | 237 | 05:00 | Naogaon | 228 | 19:00 | 219 | 04:00
Bogura-400 | 242 | 18:30 | 236 | 05:00 | Purbasadipur | 227 | 07:00 | 219 | 05:00
Borhanuddin | 231 | 16:00 | 226 | 20:00 | Rajshahi | 232 | 23:00 | 221 | 10:00
BSRM | 229 | 18:30 | 222 | 12:00 | Rampal | 227 | 07:00 | 220 | 12:00
Charfasson | 232 | 09:00 | 226 | 20:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 231 | 18:30 | 222 | 13:00 | Rampura | 227 | 01:00 | 215 | 12:00
Cumilla(N) | 234 | 00:00 | 217 | 09:00 | Shikalbaha | 240 | 18:30 | 235 | 10:00
Faridpur | 224 | 00:00 | 219 | 21:00 | Shyampur | 230 | 03:00 | 217 | 12:00
Fenchuganj | 224 | 18:00 | 217 | 08:00 | Siddhirganj | 228 | 01:00 | 217 | 13:00
Feni | 227 | 01:00 | 219 | 13:00 | Sirajgonj | 238 | 17:00 | 233 | 21:00
Ghorashal | 230 | 00:00 | 220 | 11:00 | Sreepur | 230 | 02:00 | 200 | 08:00
Ghorashal-230 | 214 | 01:00 | 195 | 10:00 | Tongi | 224 | 04:00 | 207 | 11:00
Gopalganj | 224 | 00:00 | 219 | 20:00
GPH | 236 | 18:30 | 227 | 08:00
Haripur | 228 | 06:00 | 216 | 13:00
Hasnabad | 230 | 01:00 | 217 | 10:00
Hathazari | 236 | 18:30 | 230 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 05:00 | 129 | 13:00 | Madartek | 138 | 06:00 | 129 | 13:00
Agargaon | 141 | 01:00 | 132 | 11:00 | Madunaghat | 139 | 19:00 | 136 | 01:00
Agrabad | 137 | 19:00 | 133 | 11:00 | Magura | 136 | 09:00 | 129 | 12:00
AKS | 134 | 00:00 | 132 | 11:00 | Mahasthangarh | 137 | 18:30 | 131 | 04:00
Aminbazar | 133 | 00:00 | 124 | 09:00 | Maijdee | 129 | 17:00 | 125 | 12:00
Amnura | 138 | 00:00 | 129 | 10:00 | Manikganj | 130 | 01:00 | 125 | 08:00
Ashuganj | 131 | 18:00 | 123 | 08:00 | Maniknagar | 141 | 01:00 | 132 | 13:00
Ashuganj-230 | 132 | 06:00 | 126 | 08:00 | Matarbari | 127 | 16:00 | 116 | 21:00
Bagerhat | 131 | 16:00 | 126 | 12:00 | Matuail | 136 | 05:00 | 130 | 09:00
Bajitpur | 127 | 18:00 | 118 | 08:00 | Metrorail_Motijheel | 141 | 01:00 | 132 | 13:00
Bakerganj | 133 | 15:00 | 129 | 00:00 | Metrorail_Uttara | 136 | 01:00 | 122 | 11:00
Bakulia | 138 | 19:00 | 135 | 08:00 | Millgate | 138 | 02:00 | 123 | 11:00
Banani | 139 | 06:00 | 128 | 13:00 | Mirpur | 133 | 01:00 | 124 | 12:00
Bangabhaban | 141 | 04:00 | 132 | 13:00 | Mirzapur | 130 | 07:00 | 125 | 08:00
Barapukuria | 139 | 18:30 | 130 | 07:00 | Mithapukur | 136 | 19:00 | 126 | 07:00
Barguna | 133 | 15:00 | 128 | 20:00 | MI_Cement | 136 | 04:00 | 126 | 12:00
Barishal | 133 | 02:00 | 129 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal-230 | 133 | 16:00 | 129 | 23:00 | Mogbazar | 140 | 01:00 | 132 | 12:00
Baroaulia | 139 | 18:30 | 134 | 07:00 | Mongla | 130 | 16:00 | 126 | 10:00
Baroirhat | 133 | 19:30 | 128 | 11:00 | Motijheel | 141 | 04:00 | 132 | 13:00
Bashundhara | 138 | 01:00 | 122 | 12:00 | Muktagacha | 132 | 15:00 | 114 | 08:00
BashundharaCement | 135 | 01:00 | 130 | 09:00 | Munshiganj | 134 | 06:00 | 128 | 10:00
Beanibazar | 124 | 17:00 | 119 | 08:00 | Muradnagar | 129 | 01:00 | 124 | 12:00
Benapole | 133 | 07:00 | 121 | 16:00 | Mymensingh | 133 | 15:00 | 113 | 02:00
Bhaluka | 136 | 18:30 | 121 | 08:00 | Nabinagar | 136 | 01:00 | 121 | 10:00
Bhandaria | 130 | 05:00 | 125 | 23:00 | Naogaon | 137 | 19:00 | 131 | 04:00
Bhangura | 135 | 07:00 | 131 | 05:00 | Narail | 136 | 17:00 | 129 | 12:00
Bheramara | 138 | 00:00 | 132 | 05:00 | Narinda | 141 | 1:00 | 132 | 13:00
Bheramara(GK) | 137 | 00:00 | 130 | 20:00 | Narshingdi | 130 | 01:00 | 116 | 09:00
Bhulta | 130 | 01:00 | 125 | 08:00 | Natore | 136 | 00:00 | 130 | 10:00
Bhulta-400 | 132 | 01:00 | 125 | 13:00 | Nawabganj | 140 | 03:00 | 130 | 12:00
Bog-Sherpur | 137 | 09:00 | 133 | 05:00 | Netrakona | 123 | 06:00 | 109 | 08:00
Bogura | 140 | 18:30 | 134 | 10:00 | New | 138 | 01:00 | 125 | 12:00
Bogura-230 | 140 | 00:00 | 135 | 05:00 | Niamatpur | 137 | 17:00 | 133 | 20:00
Brahmanbaria | 128 | 18:00 | 119 | 08:00 | Noapara | 134 | 16:00 | 130 | 12:00
Cantonment | 140 | 01:00 | 131 | 12:00 | Pabna | 135 | 00:00 | 130 | 20:00
Chandina | 131 | 00:00 | 126 | 09:00 | Palashbari | 133 | 18:00 | 128 | 04:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandpur | 137 | 18:30 | 125 | 15:00 | Panchagarh | 137 | 19:00 | 132 | 05:00
Chandraghona | 138 | 00:00 | 130 | 19:00 | Patiya | 138 | 19:00 | 132 | 01:00
Chapai | 136 | 18:30 | 133 | 22:00 | Patnitala | 134 | 18:30 | 128 | 02:00
Charsaidpur | 135 | 01:00 | 129 | 10:00 | Patuakhali | 133 | 15:00 | 128 | 01:00
Chauddagram | 132 | 19:30 | 127 | 09:00 | Payra | 136 | 15:00 | 134 | 21:00
Chhatak | 122 | 18:00 | 117 | 08:00 | PHP | 133 | 18:30 | 128 | 11:00
Chowmuhani | 130 | 18:30 | 125 | 13:00 | Postogola | 137 | 01:00 | 128 | 12:00
Chuadanga | 135 | 16:00 | 125 | 12:00 | Pubail | 130 | 16:00 | 119 | 10:00
Coxsbazar | 129 | 19:00 | 119 | 21:00 | Purbachal | 139 | 05:00 | 128 | 13:00
Cumilla(N) | 131 | 05:00 | 127 | 09:00 | Purbasadipur | 138 | 07:00 | 132 | 05:00
Cumilla(S) | 132 | 01:00 | 120 | 15:00 | Rahanpur | 139 | 08:00 | 136 | 10:00
Daganbhuiyan | 131 | 00:00 | 126 | 13:00 | Rahanpur-400 | 139 | 00:00 | 136 | 12:00
Daudkandi | 128 | 02:00 | 123 | 12:00 | Rahim | 136 | 03:00 | 129 | 13:00
DhakaUniversity | 139 | 06:00 | 129 | 12:00 | Rajbari | 127 | 00:00 | 124 | 11:00
Dhamrai | 137 | 01:00 | 125 | 11:00 | Rajendrapur | 134 | 16:00 | 120 | 08:00
Dhanmondi | 139 | 05:00 | 130 | 12:00 | Rajshahi | 133 | 01:00 | 126 | 12:00
Dohazari | 134 | 16:00 | 128 | 21:00 | Rajshahi-230 | 134 | 00:00 | 127 | 10:00
Faridpur | 130 | 16:00 | 126 | 20:00 | Ramganj | 132 | 18:30 | 127 | 11:00
Fatullah | 137 | 01:00 | 128 | 11:00 | Rampur | 137 | 19:00 | 134 | 11:00
Fenchuganj | 131 | 17:00 | 127 | 07:00 | Rampura | 138 | 01:00 | 129 | 13:00
Feni | 131 | 00:00 | 125 | 15:00 | Rangamati | 137 | 00:00 | 134 | 12:00
Feni-230 | 133 | 19:30 | 127 | 13:00 | Rangpur | 134 | 19:30 | 125 | 07:00
Ghatail | 130 | 15:00 | 118 | 00:00 | Ruppur | 138 | 00:00 | 132 | 10:00
Ghorashal | 130 | 22:00 | 115 | 08:00 | Saidpur | 136 | 19:00 | 130 | 10:00
Goalpara | 136 | 00:00 | 132 | 12:00 | Santhia | 136 | 00:00 | 131 | 20:00
Gollamari | 136 | 06:00 | 132 | 12:00 | Satkhira | 133 | 16:00 | 125 | 20:00
Gopalganj | 132 | 16:00 | 128 | 12:00 | Satmasjid | 140 | 01:00 | 131 | 13:00
Gopalganj-400 | 133 | 00:00 | 130 | 12:00 | Savar | 132 | 00:00 | 123 | 10:00
Gulshan | 137 | 04:00 | 129 | 12:00 | SevenRings | 129 | 01:00 | 119 | 10:00
Halishahar | 138 | 00:00 | 134 | 12:00 | ShahCement | 135 | 01:00 | 129 | 10:00
Haripur | 135 | 00:00 | 129 | 13:00 | Shahjadpur | 136 | 01:00 | 134 | 10:00
HaripurSBU | 135 | 07:00 | 130 | 12:00 | Shahjibazar | 129 | 17:00 | 119 | 08:00
Hasnabad | 136 | 01:00 | 129 | 13:00 | Shahmirpur | 137 | 00:00 | 134 | 13:00
Hathazari | 138 | 18:00 | 127 | 00:00 | Shariatpur | 132 | 16:00 | 128 | 22:00
Hatirjheel | 139 | 06:00 | 129 | 13:00 | Sherpur | 133 | 15:00 | 110 | 01:00
Ishurdi | 139 | 00:00 | 133 | 12:00 | Shikalbaha | 128 | 18:30 | 124 | 11:00
Jaldhaka | 134 | 19:00 | 126 | 07:00 | Shikalbaha-230 | 140 | 19:00 | 136 | 08:00
Jamalpur | 135 | 15:00 | 115 | 08:00 | Shitalakhya | 136 | 04:00 | 126 | 12:00
Jashore | 134 | 09:00 | 124 | 12:00 | Sholosohor | 138 | 19:00 | 133 | 12:00
Jhenaidah | 138 | 16:00 | 120 | 19:30 | Shomvuganj | 124 | 00:00 | 113 | 08:00
Jhenaidah-230 | 139 | 18:00 | 130 | 12:00 | Shyampur | 136 | 22:00 | 128 | 13:00
Joydebpur | 133 | 00:00 | 124 | 20:00 | Shyampur-230 | 138 | 01:00 | 130 | 12:00
Joypurhat | 135 | 19:00 | 128 | 04:00 | Siddhirganj | 135 | 03:00 | 129 | 12:00
Juldah | 137 | 00:00 | 134 | 11:00 | Sirajganj | 133 | 00:00 | 129 | 20:00
Kabirpur | 134 | 00:00 | 118 | 20:00 | Sitakunda | 137 | 17:00 | 133 | 04:00
Kachua | 133 | 18:30 | 129 | 08:00 | Sonargaon | 131 | 00:00 | 123 | 01:00
Kaliakoir | 139 | 01:00 | 127 | 10:00 | Sreemongol | 129 | 17:00 | 121 | 08:00
Kaliganj | 137 | 03:00 | 129 | 12:00 | Sreepur | 136 | 01:00 | 121 | 08:00
Kallyanpur | 139 | 18:00 | 124 | 12:00 | Srinagar | 139 | 04:00 | 131 | 13:00
Kalurghat | 139 | 18:30 | 135 | 11:00 | SSM | 140 | 00:00 | 140 | 00:00
Kamrangirchar | 140 | 01:00 | 122 | 12:00 | Sunamganj | 120 | 23:00 | 116 | 09:00
Kaptai | 139 | 1:00 | 138 | 11:00 | Sylhet | 125 | 03:00 | 121 | 16:00
Kasba | 129 | 02:00 | 123 | 12:00 | Sylhet_(South) | 125 | 17:00 | 122 | 08:00
Kazla | 141 | 06:00 | 132 | 13:00 | Tangail | 128 | 15:00 | 119 | 08:00
Keranigonj | 140 | 01:00 | 131 | 12:00 | Taraganj | 135 | 19:00 | 127 | 07:00
Khagrachori | 136 | 00:00 | 133 | 12:00 | Tasnim | 133 | 01:00 | 127 | 10:00
Khulna | 136 | 03:00 | 131 | 12:00 | Thakurgaon | 138 | 18:30 | 133 | 05:00
Khulna(S) | 137 | 16:00 | 132 | 12:00 | TK | 137 | 01:00 | 134 | 11:00
Khulshi | 136 | 00:00 | 132 | 13:00 | Tongi | 138 | 04:00 | 126 | 11:00
Kishoreganj | 126 | 16:00 | 116 | 08:00 | Ullahpara | 135 | 00:00 | 130 | 10:00
Kodda | 135 | 00:00 | 125 | 08:00 | Ullon | 138 | 06:00 | 129 | 12:00
Korerhat | 135 | 18:30 | 130 | 13:00 | Uttara | 138 | 02:00 | 122 | 20:00
KSRM | 138 | 18:30 | 133 | 12:00 | UttaraNew | 136 | 01:00 | 122 | 11:00
Kulaura | 130 | 17:00 | 126 | 08:00 | Zigatola | 140 | 02:00 | 131 | 12:00
Kurigram | 132 | 19:00 | 121 | 07:00
Kushtia | 134 | 06:00 | 126 | 12:00
Laksam | 133 | 19:30 | 128 | 13:00
Lakshmipur | 129 | 19:30 | 124 | 13:00
Lalbag | 140 | 01:00 | 130 | 13:00
Lalmonirhat | 130 | 20:00 | 120 | 00:00
Madanganj | 135 | 01:00 | 130 | 09:00
Madaripur | 132 | 15:00 | 129 | 20:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division