## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 11-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-08-2026 | during | 11-08-2026 | during | 11-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 403 | 404 | 412 | 412 | 400 | 400 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 142 | 265 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 290 | 321 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 0 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 140 | 149.36 | 149.36 | 125 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 10.5 | 11 | 33 | 33 | 13 | 13 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 21 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 49 | 52.19 | 52.19 | 33 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 48 | 32 | 300 | 300 | 81 | 81 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 36 | 41 | 149 | 149 | 53 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 17 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 162 | 162 | 17 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 21 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 583 | 583 | 524.7 | 524.7 | FGMO
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 309 | 315 | 718 | 718 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1637.92 | 2079.42 | 5804.16 | 5778.16 | 2156.62 | 2530.62
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 17 | 25.5 | 25.5 | 25 | 25 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 11 | 0 | 12 | 0 | 12 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 44 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 222 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 205 | 194 | 170 | 170 | 170 | 170 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 90 | 105 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 30 | 29 | 24 | 24 | 24 | 24 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 46 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 2 | 37 | 2 | 37 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 18 | 50 | 108 | 108 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.73 | 0 | 3.6 | 0 | 3.6 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 35 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 94 | 110 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 109 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1197 | 1230 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 19 | 14 | 22 | 14 | 22 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 1125 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 3190.73 | 3375 | 4053.46 | 4131.86 | 3294.96 | 3405.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 199 | 189 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 354 | 359 | 350.01 | 350.01 | 350.01 | 350.01
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 0 | 342.01 | 342.01 | 342.01 | 342.01 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 34 | 42 | 41.65 | 41.65 | 40 | 40 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 14 | 43 | 52.82 | 52.82 | 38 | 38 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 45 | 45 | 195 | 195 | 108 | 108 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 150 | 150 | 150 | 50 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 37 | 31 | 32 | 32 | 24 | 24 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 86 | 85 | 163 | 163 | 86 | 86 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 179 | 188 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 136 | 146 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 106 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 27 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 25 | 89 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 59 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1283 | 1622.2 | 2361.44 | 2295.44 | 1912.47 | 2018.47
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-08-2026 | during | 11-08-2026 | during | 11-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 22.24 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.8 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 153 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 38.14 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 253.18 | 250 | 536.6 | 516.5 | 267.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 41 | 41 | 40 | 40 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 39 | 30 | 30 | 30 | 30 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 146 | 142 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 165 | 165 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 83 | 84 | 84 | 84 | 84
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 123 | 124 | 120 | 120 | 120 | 120 | plant availability zero
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 230 | 230 | 250 | 260 | 250 | 260 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 977 | 971 | 1222 | 1232 | 986 | 996
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 901 | 903 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 23 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 50 | 105 | 105 | 35 | 35 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 105 | 0 | 52 | 0 | 52 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 232 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1206 | 1095 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | AGC+FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2250 | 2341 | 3538.2 | 3486.2 | 2391.2 | 2339.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 800 | 1050 | 800 | 1050 | 800 | 1050 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 60 | 115 | 60 | 60 | 60 | 60 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 878 | 890 | 901.5 | 901.5 | 901.5 | 901.5 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.22 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2258.22 | 2615 | 2549.5 | 2798.5 | 2322.5 | 2571.5
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 22.15 | 0 | 48.25 | 0 | 48.25 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 175 | 168 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 322 | 305 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 14 | 14 | 14 | 14 | 14 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 50 | 50 | 50 | 50 | Engine Problem
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 57 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.08 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1017.09 | 1135.42 | 1469.13 | 1469.13 | 1000 | 1000 | Problem with coal feeding system
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.58 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1735.9 | 1879.42 | 3197.87 | 2983.12 | 1981.16 | 1831.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 47 | 48 | 48 | 48 | 48 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 159 | 160 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 106 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 94 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 9 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 173 | 0 | 200 | 0 | 200 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 490 | 573 | 703 | 470 | 590 | 392
System Total |  |  |  |  | 28843.2 | 29171.687 | 14075.95 | 15706.04 | 23966.23 | 23691.78 | 15902.01 | 16343.56
Forecast Scenario (11-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14160 |  | 3820 |  | 18160
|  |  |  | 1:00 | 13570 |  | 3820 |  | 17570
|  |  |  | 2:00 | 13230 |  | 3877.3 |  | 17290
|  |  |  | 3:00 | 13290 |  | 3485.75 |  | 16940
|  |  |  | 4:00 | 13130 |  | 3447.55 |  | 16740
|  |  |  | 5:00 | 13120 |  | 3161.05 |  | 16430
|  |  |  | 6:00 | 13120 |  | 2769.5 |  | 16020
|  |  |  | 7:00 | 13140 |  | 2645.35 |  | 15910
|  |  |  | 8:00 | 13220 |  | 2444.8 |  | 15780
|  |  |  | 9:00 | 13640 |  | 2158.3 |  | 15900
|  |  |  | 10:00 | 13830 |  | 2158.3 |  | 16090
|  |  |  | 11:00 | 13860 |  | 2339.75 |  | 16310
|  |  |  | 12:00 | 14080 |  | 2798.15 |  | 17010
|  |  |  | 13:00 | 14260 |  | 2721.75 |  | 17110
|  |  |  | 14:00 | 14160 |  | 2884.1 |  | 17180
|  |  |  | 15:00 | 13930 |  | 3304.3 |  | 17390
|  |  |  | 16:00 | 13860 |  | 2989.15 |  | 16990
|  |  |  | 17:00 | 13810 |  | 2683.55 |  | 16620
|  |  |  | 18:00 | 14040 |  | 2206.05 |  | 16350
|  |  |  | 18:30 | 14740 |  | 2253.8 |  | 17100
|  |  |  | 19:00 | 15400 |  | 2377.95 |  | 17890
|  |  |  | 19:30 | 15690 |  | 2597.6 |  | 18410
|  |  |  | 20:00 | 15630 |  | 2664.45 |  | 18420
|  |  |  | 21:00 | 15710 |  | 2979.6 |  | 18830
|  |  |  | 22:00 | 15310 |  | 2912.75 |  | 18360
|  |  |  | 23:00 | 14900 |  | 3447.55 |  | 18510
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 17010.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2980
Probable Maximum Demand at Evening Peak: |  |  | 18830.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15710.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 336.40 MKWHr. |  | 800 | 200 | 300 | 400 | 160 | 400 | 120 | 320 | 280 | 2980
*** This report is generated digitally from Operation Information System (OIS) at 08:57 hrs on 11-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 10-08-2026 | [28 empty] | Date: | 10-08-2026 | [28 empty] | Date: | 10-08-2026 | [28 empty] | Date: | 10-08-2026 | [28 empty] | Date: | 10-08-2026 | [18 empty] | Date: | 10-08-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 35 | 17 | 38 | 60 | 48 | 0 | 35 | 126 | 0 | 0 | 125 | 355 | 0 | 35 | 325 | 0 | 0 | 0 | 17 | 12 | 22 | 0 | 0 | 94 | 106 | 49 | 0 | 3 | 50 | 53 | 17 | 12 | 12 | 0 | 221 | 108 | 35 | 1125 | 0 | 0 | 50 | 0 | 101 | 208 | 0 | 0 | 0 | 1224 | 0 | 20 | 197 | 0 | 37 | 0 | 51 | 46 | 30 | 36 | 60 | 85 | 182 | 0 | 8 | 104 | 196 | 52.2 | 0 | 32 | 300 | 0 | 292 | 40 | 39 | 152 | 0 | 8 | 0 | 62 | 0 | 0 | 0 | 129 | 17 | 49 | 0 | 47 | 0 | 0 | 0 | 12 | 7460.2 | 901 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 35 | 0 | 1163 | 0 | 0 | 0 | 946.06 | 0 | 0 | 0 | 57 | 70 | 0 | 51 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 157 | 48 | 111 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 700 | 840 | 17 | 6296.06 | 13756.26 | 103.54
01:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 13 | 17 | 17 | 17 | 15 | 48 | 4 | 35 | 126 | 0 | 0 | 128 | 370 | 0 | 35 | 328 | 0 | 0 | 0 | 17 | 12 | 21 | 0 | 0 | 97 | 16 | 21 | 0 | 7 | 50 | 38 | 0 | 12 | 12 | 0 | 220 | 109 | 32 | 1125 | 0 | 0 | 50 | 0 | 101 | 208 | 0 | 0 | 0 | 1224 | 0 | 20 | 197 | 0 | 108 | 0 | 51 | 46 | 34 | 32 | 52 | 86 | 180 | 0 | 19 | 105 | 184 | 52.2 | 0 | 32 | 300 | 0 | 290 | 40 | 39 | 151 | 0 | 8 | 0 | 62 | 0 | 0 | 0 | 119 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7290.2 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1164 | 0 | 0 | 0 | 817.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 158 | 48 | 109 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 600 | 840 | 17 | 5871.9 | 13162.1 | 103.55
02:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 13 | 0 | 17 | 17 | 15 | 48 | 15 | 35 | 0 | 0 | 0 | 129 | 380 | 0 | 0 | 328 | 0 | 0 | 0 | 17 | 12 | 21 | 0 | 0 | 92 | 16 | 19 | 0 | 1 | 50 | 38 | 0 | 12 | 12 | 0 | 220 | 106 | 36 | 1125 | 0 | 0 | 50 | 0 | 92 | 208 | 0 | 0 | 0 | 1224 | 0 | 20 | 197 | 0 | 158 | 0 | 51 | 46 | 42 | 32 | 39 | 85 | 177 | 0 | 19 | 106 | 174 | 52.2 | 0 | 32 | 305 | 0 | 292 | 40 | 39 | 150 | 0 | 8 | 0 | 62 | 0 | 0 | 0 | 119 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7138.2 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1165 | 0 | 0 | 0 | 817.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 161 | 47 | 110 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 600 | 840 | 17 | 5882.84 | 13021.04 | 103.56
03:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 17 | 17 | 15 | 48 | 15 | 35 | 0 | 0 | 0 | 125 | 380 | 0 | 0 | 329 | 0 | 0 | 0 | 17 | 0 | 21 | 0 | 0 | 92 | 16 | 19 | 0 | 0 | 50 | 38 | 0 | 12 | 12 | 0 | 220 | 103 | 36 | 1125 | 0 | 0 | 50 | 0 | 101 | 208 | 0 | 0 | 0 | 1224 | 0 | 20 | 197 | 0 | 287 | 0 | 51 | 46 | 80 | 32 | 0 | 85 | 186 | 0 | 9 | 104 | 174 | 52.2 | 0 | 32 | 300 | 0 | 292 | 40 | 39 | 151 | 0 | 8 | 0 | 62 | 0 | 0 | 0 | 119 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7211.2 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1165 | 0 | 0 | 0 | 816.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 162 | 47 | 107 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 60 | 220 | 0 | 600 | 840 | 17 | 5870.92 | 13082.12 | 103.57
04:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 24 | 0 | 17 | 17 | 15 | 48 | 15 | 0 | 0 | 0 | 0 | 133 | 370 | 0 | 0 | 326 | 0 | 0 | 0 | 17 | 13 | 21 | 0 | 0 | 87 | 16 | 18 | 0 | 1 | 50 | 38 | 0 | 12 | 12 | 0 | 221 | 107 | 37 | 1125 | 0 | 0 | 45 | 0 | 94 | 208 | 0 | 0 | 0 | 1166 | 0 | 18 | 108 | 0 | 356 | 0 | 51 | 43 | 125 | 32 | 0 | 85 | 178 | 0 | 9 | 106 | 170 | 52.2 | 0 | 32 | 295 | 0 | 294 | 40 | 39 | 147 | 0 | 8 | 0 | 62 | 0 | 0 | 0 | 119 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7118.2 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1163 | 0 | 0 | 0 | 818.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 158 | 47 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 277 | 60 | 220 | 0 | 600 | 840 | 17 | 5808.3 | 12926.5 | 103.58
05:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 21 | 0 | 17 | 17 | 15 | 48 | 15 | 0 | 0 | 0 | 0 | 125 | 435 | 0 | 0 | 329 | 0 | 0 | 0 | 17 | 8 | 21 | 0 | 0 | 97 | 16 | 19 | 0 | 12 | 5 | 38 | 0 | 12 | 12 | 0 | 222 | 104 | 38 | 1125 | 0 | 0 | 44 | 0 | 104 | 208 | 0 | 0 | 0 | 1160 | 0 | 20 | 45 | 0 | 355 | 0 | 51 | 10 | 216 | 10 | 0 | 85 | 179 | 0 | 9 | 94 | 166 | 52.2 | 0 | 32 | 290 | 0 | 294 | 40 | 39 | 146 | 0 | 8 | 0 | 62 | 0 | 0 | 0 | 119 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7079.2 | 939 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1163 | 0 | 0 | 0 | 820.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 159 | 47 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 274 | 60 | 220 | 0 | 600 | 830 | 17 | 5839.26 | 12918.46 | 103.59
06:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 201 | 0 | 12 | 17 | 15 | 48 | 15 | 0 | 0 | 0 | 0 | 124 | 410 | 0 | 0 | 329 | 0 | 0 | 0 | 17 | 8 | 21 | 0 | 0 | 87 | 16 | 18 | 0 | 4 | 0 | 38 | 0 | 12 | 12 | 0.26 | 222 | 108 | 38 | 1125 | 0 | 0 | 44 | 0 | 91 | 208 | 0 | 0 | 0 | 1160 | 0 | 20 | 45 | 0 | 355 | 0 | 51 | 10 | 220 | 10 | 0 | 85 | 177 | 0 | 11 | 90 | 156 | 52.2 | 2 | 32 | 300 | 0 | 294 | 40 | 39 | 143 | 1 | 8 | 0 | 62 | 0 | 0 | 0 | 119 | 17 | 49 | 0.24 | 48 | 0 | 0 | 0.07 | 0 | 7182.77 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1.25 | 1165 | 0 | 0 | 0 | 822.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0.79 | 0 | 0 | 0 | 0.23 | 174 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0.04 | 158 | 47 | 109 | 1 | 0 | 0 | 0 | 0 | 0.3 | 9 | 0.02 | 16 | 276 | 60 | 220 | 0 | 600 | 830 | 17 | 5733.78 | 12916.55 | 103.6
07:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 307 | 0 | 0 | 17 | 15 | 48 | 15 | 0 | 0 | 0 | 0 | 127 | 285 | 0 | 0 | 283 | 0 | 0 | 3 | 17 | 8 | 21 | 0 | 0 | 94 | 16 | 18 | 0 | 0 | 0 | 38 | 0 | 12 | 12 | 0.44 | 222 | 102 | 33 | 1125 | 0 | 0 | 44 | 0 | 95 | 209 | 0 | 0 | 0 | 1166 | 1 | 20 | 45 | 0 | 356 | 0 | 51 | 10 | 218 | 10 | 0 | 85 | 182 | 0 | 8 | 17 | 150 | 8 | 18 | 31 | 295 | 0 | 294 | 40 | 39 | 146 | 2 | 8 | 0 | 63 | 0 | 0 | 0 | 119 | 17 | 49 | 2.2 | 48 | 0 | 0 | 5 | 0 | 7015.64 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 18 | 1165 | 0 | 0 | 0 | 847.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 4.72 | 12 | 0 | 0 | 3.72 | 175 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0.34 | 158 | 47 | 111 | 3 | 0 | 0 | 0 | 0 | 2 | 21 | 0.09 | 16 | 307 | 60 | 220 | 0 | 600 | 836 | 17 | 5918.56 | 12934.2 | 103.61
08:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 315 | 0 | 0 | 17 | 16 | 48 | 15 | 0 | 0 | 0 | 0 | 130 | 175 | 0 | 0 | 282 | 0 | 0 | 6 | 68 | 10.5 | 21 | 0 | 0 | 89 | 16 | 19 | 0 | 0 | 0 | 38 | 0 | 12 | 12 | 1.19 | 222 | 98 | 14 | 1125 | 0 | 0 | 44 | 0 | 90 | 208 | 0 | 0 | 0 | 1160 | 3 | 20 | 45 | 0 | 355 | 0 | 51 | 10 | 216 | 10 | 0 | 86 | 175 | 0 | 19 | 17 | 162 | 8 | 33 | 31 | 290 | 0 | 294 | 40 | 39 | 143 | 6 | 8 | 0 | 63 | 0 | 0 | 0 | 119 | 17 | 49 | 6.2 | 48 | 0 | 0.7 | 11.17 | 0 | 7001.76 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 36 | 1165 | 0 | 0 | 0 | 909.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 10.37 | 29 | 0 | 0 | 14.16 | 175 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 1.2 | 160 | 47 | 98 | 13 | 0 | 0 | 0 | 0 | 3.1 | 78 | 0.31 | 16 | 307 | 60 | 180 | 0 | 600 | 870 | 17 | 6016.51 | 13018.27 | 103.62
09:00 | 0 | 43 | 25 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 325 | 0 | 0 | 17 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 133 | 145 | 0 | 0 | 288 | 0 | 0 | 12 | 143.42 | 8 | 21 | 0 | 0 | 95 | 16 | 18 | 0 | 4 | 0 | 38 | 17 | 12 | 12 | 2.19 | 222 | 92 | 5 | 1125 | 0 | 0 | 44 | 0 | 89 | 208 | 0 | 0 | 0 | 1160 | 5 | 20 | 16 | 0 | 355 | 0 | 51 | 10 | 218 | 10 | 0 | 86 | 181 | 0 | 19 | 17 | 170 | 8 | 47 | 31 | 300 | 0 | 278 | 41 | 39 | 151 | 7 | 8 | 0 | 63 | 0 | 0 | 0 | 119 | 17 | 49 | 7 | 48 | 0 | 1.3 | 41.8 | 0 | 7181.71 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 41 | 1160 | 0 | 0 | 0 | 902.83 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 8 | 48.18 | 59 | 0 | 0 | 24.04 | 175 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 3.01 | 160 | 47 | 96 | 18 | 0 | 0 | 0 | 0 | 4.5 | 142 | 0.23 | 16 | 307 | 60 | 220 | 0 | 600 | 866 | 17 | 6253.79 | 13435.5 | 103.63
10:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 304 | 0 | 7 | 17 | 16 | 48 | 0 | 17 | 0 | 0 | 0 | 123 | 140 | 0 | 0 | 272 | 0 | 0 | 15 | 143.42 | 10.5 | 21 | 0 | 0 | 95 | 16 | 18 | 0 | 9 | 0 | 38 | 17 | 12 | 12 | 1.62 | 222 | 93 | 2 | 1125 | 0 | 0 | 44 | 0 | 88 | 207 | 0 | 0 | 0 | 1190 | 6 | 20 | 16 | 0 | 355 | 0 | 51 | 10 | 181 | 10 | 0 | 86 | 183 | 0 | 19 | 17 | 166 | 8 | 36 | 31 | 305 | 0 | 230 | 39 | 39 | 149 | 8 | 8 | 0 | 61 | 0 | 0 | 0 | 123 | 17 | 59 | 20 | 113 | 0 | 1.9 | 52.36 | 0 | 7236.8 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 98 | 1158 | 0 | 0 | 0 | 1011.99 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 30.32 | 73 | 0 | 0 | 37.88 | 175 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 3.94 | 164 | 46 | 96 | 12 | 0 | 0 | 0 | 0 | 6.2 | 173 | 0.77 | 16 | 307 | 60 | 220 | 0 | 600 | 875 | 17 | 6484.1 | 13720.9 | 103.64
11:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 331 | 0 | 17 | 20 | 16 | 48 | 0 | 35 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 305 | 0 | 0 | 12 | 143.42 | 10.5 | 20 | 0 | 0 | 90 | 16 | 19 | 0 | 6 | 0 | 30 | 17 | 12 | 12 | 2.8 | 220 | 94 | 2 | 1125 | 0 | 0 | 44 | 1 | 90 | 208 | 0 | 0 | 0 | 1200 | 11 | 20 | 35 | 0 | 354 | 0 | 51 | 10 | 211 | 10 | 0 | 86 | 186 | 0 | 19 | 17 | 128 | 8 | 56 | 31 | 305 | 0 | 230 | 40 | 39 | 148 | 10 | 8 | 0 | 61 | 0 | 0 | 0 | 123 | 17 | 59 | 11.6 | 116 | 0 | 1.2 | 54.61 | 0 | 7251.13 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 35 | 1176 | 0 | 0 | 0 | 1021.15 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 43.22 | 81 | 0 | 0 | 33.18 | 175 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 3.14 | 161 | 47 | 93 | 34 | 0 | 0 | 0 | 0 | 8 | 183 | 0.31 | 16 | 307 | 60 | 220 | 0 | 600 | 878 | 17 | 6499 | 13750.13 | 103.64
12:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 309 | 0 | 17 | 36 | 16 | 48 | 0 | 35 | 17 | 0 | 0 | 142 | 0 | 0 | 17 | 290 | 0 | 0 | 21 | 143.42 | 10.5 | 20 | 0 | 0 | 90 | 16 | 18 | 0 | 0 | 0 | 30 | 17 | 12 | 12 | 2.73 | 219 | 94 | 0 | 1125 | 0 | 0 | 44 | 8 | 90 | 205 | 0 | 0 | 0 | 1197 | 11 | 20 | 45 | 0 | 354 | 0 | 51 | 14 | 199 | 34 | 25 | 86 | 179 | 0 | 19 | 17 | 136 | 8 | 59 | 37 | 300 | 0 | 230 | 40 | 39 | 146 | 12 | 8 | 0 | 79 | 0 | 0 | 0 | 123 | 17 | 59 | 22.24 | 115 | 0 | 1.8 | 38.14 | 0 | 7341.83 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 105 | 1206 | 0 | 0 | 0 | 1017.09 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 22.15 | 100 | 0 | 0 | 51.58 | 175 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 5.08 | 159 | 47 | 94 | 9 | 0 | 0 | 0 | 0 | 8 | 173 | 0.22 | 16 | 307 | 60 | 180 | 0 | 800 | 878 | 17 | 6734.12 | 14075.95 | 103.64
13:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 311 | 0 | 17 | 36 | 47 | 48 | 0 | 35 | 17 | 0 | 0 | 137 | 0 | 0 | 35 | 320 | 0 | 0 | 14 | 143.42 | 11 | 20 | 0 | 0 | 91 | 16 | 18 | 0 | 12 | 0 | 23 | 17 | 12 | 12 | 3.98 | 217 | 92 | 0 | 1125 | 0 | 0 | 43 | 8 | 88 | 186 | 0 | 0 | 0 | 1170 | 8 | 21 | 108 | 0 | 356 | 0 | 51 | 38 | 199 | 36 | 34 | 86 | 177 | 0 | 19 | 17 | 138 | 8 | 77 | 37 | 305 | 0 | 230 | 40 | 39 | 146 | 12 | 8 | 0 | 79 | 0 | 0 | 0 | 124 | 17 | 59 | 22.25 | 105 | 0 | 1.8 | 12.61 | 0 | 7412.06 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 98 | 1200 | 0 | 0 | 0 | 1020.9 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 58.68 | 110 | 0 | 0 | 67.99 | 176 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 5.15 | 161 | 47 | 94 | 30 | 0 | 0 | 0 | 0 | 8 | 181 | 0.76 | 16 | 276 | 60 | 220 | 0 | 800 | 876 | 35 | 6842.48 | 14254.54 | 103.64
14:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 335 | 0 | 17 | 35 | 84 | 48 | 0 | 35 | 17 | 0 | 0 | 143 | 0 | 0 | 35 | 315 | 0 | 0 | 16 | 143.42 | 11 | 20 | 0 | 0 | 94 | 16 | 19 | 0 | 12 | 0 | 23 | 17 | 12 | 12 | 2.42 | 218 | 95 | 0 | 1125 | 0 | 0 | 43 | 8 | 89 | 185 | 0 | 0 | 0 | 1205 | 3 | 33 | 73 | 0 | 349 | 0 | 51 | 35 | 188 | 37 | 34 | 85 | 180 | 0 | 19 | 17 | 146 | 8 | 65 | 37 | 310 | 0 | 230 | 40 | 39 | 146 | 11 | 8 | 0 | 79 | 0 | 0 | 0 | 124 | 17 | 59 | 20.19 | 115 | 0 | 0.4 | 31.83 | 0 | 7486.26 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 40 | 1200 | 0 | 0 | 0 | 1018.96 | 0 | 0 | 0 | 0 | 35 | 0 | 7 | 0 | 8 | 50.13 | 21 | 0 | 0 | 45.98 | 176 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 3.14 | 159 | 47 | 94 | 23 | 0 | 0 | 0 | 0 | 7.6 | 185 | 0.63 | 16 | 307 | 60 | 220 | 0 | 800 | 875 | 17 | 6668.44 | 14154.7 | 103.65
15:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 312 | 17 | 4 | 35 | 95 | 48 | 0 | 35 | 35 | 0 | 0 | 140 | 0 | 0 | 35 | 314 | 0 | 0 | 10 | 143.42 | 11 | 20 | 0 | 0 | 96 | 16 | 18 | 0 | 11 | 0 | 21 | 17 | 12 | 12 | 3.73 | 220 | 103 | 0 | 1125 | 0 | 0 | 44 | 8 | 90 | 186 | 0 | 0 | 0 | 1203 | 10 | 33 | 73 | 0 | 349 | 0 | 51 | 20 | 182 | 38 | 34 | 86 | 184 | 0 | 19 | 17 | 140 | 8 | 51 | 37 | 315 | 0 | 230 | 40 | 38 | 146 | 9 | 8 | 0 | 82 | 0 | 0 | 0 | 124 | 17 | 59 | 16.67 | 114 | 0 | 0.4 | 26.14 | 0 | 7460.36 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 84 | 1186 | 0 | 0 | 0 | 1016.25 | 0 | 0 | 0 | 0 | 35 | 0 | 7 | 0 | 8 | 33.95 | 42 | 0 | 0 | 50.79 | 173 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 4.61 | 161 | 47 | 94 | 15 | 0 | 0 | 0 | 0 | 6.2 | 157 | 0.49 | 16 | 307 | 60 | 220 | 0 | 600 | 875 | 17 | 6464.29 | 13924.65 | 103.65
16:00 | 0 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 259 | 17 | 16 | 30 | 110 | 32 | 0 | 35 | 35 | 0 | 0 | 165 | 0 | 0 | 35 | 314 | 0 | 0 | 12 | 143.42 | 11 | 20 | 0 | 0 | 100 | 16 | 19 | 0 | 31 | 0 | 21 | 17 | 12 | 12 | 0.42 | 181 | 102 | 0 | 1125 | 0 | 0 | 44 | 8 | 88 | 188 | 0 | 0 | 0 | 1197 | 5 | 33 | 26 | 0 | 351 | 0 | 51 | 20 | 206 | 38 | 48 | 85 | 184 | 0 | 19 | 88 | 148 | 25 | 37 | 37 | 300 | 0 | 230 | 38 | 38 | 146 | 6 | 8 | 0 | 81 | 0 | 0 | 0 | 124 | 17 | 59 | 9.85 | 114 | 0 | 0.4 | 18.56 | 0 | 7451.65 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 54 | 1130 | 0 | 0 | 0 | 1016.05 | 0 | 0 | 0 | 0 | 35 | 0 | 8 | 0 | 8 | 28.67 | 61 | 0 | 0 | 29.94 | 172 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 3.1 | 163 | 47 | 93 | 19 | 66 | 0 | 0 | 0 | 5.1 | 109 | 0.43 | 0 | 307 | 90 | 220 | 0 | 600 | 875 | 17 | 6407.29 | 13858.94 | 103.65
17:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 278 | 17 | 0 | 19 | 110 | 32 | 0 | 35 | 35 | 0 | 0 | 183 | 0 | 0 | 35 | 313 | 0 | 0 | 7 | 143.42 | 0 | 20 | 0 | 0 | 94 | 16 | 18 | 0 | 53 | 0 | 21 | 17 | 12 | 12 | 0.49 | 182 | 103 | 0 | 1125 | 0 | 0 | 44 | 8 | 98 | 191 | 0 | 0 | 0 | 1214 | 1 | 33 | 26 | 0 | 345 | 0 | 51 | 20 | 208 | 37 | 51 | 85 | 180 | 5 | 19 | 100 | 140 | 25 | 11 | 37 | 305 | 0 | 230 | 39 | 38 | 144 | 3 | 8 | 0 | 81 | 0 | 0 | 0 | 124 | 17 | 58 | 5.46 | 114 | 0 | 0.5 | 12.91 | 7 | 7488.78 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 35 | 1093 | 0 | 0 | 0 | 1016.73 | 0 | 0 | 0 | 35 | 35 | 0 | 8 | 0 | 8 | 12.5 | 29 | 0 | 0 | 14.03 | 172 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 1.36 | 161 | 47 | 94 | 9 | 91 | 0 | 0 | 0 | 2 | 70 | 0.22 | 5 | 307 | 114 | 220 | 0 | 600 | 870 | 17 | 6314.84 | 13803.62 | 103.66
18:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 290 | 17 | 0 | 35 | 108 | 32 | 0 | 35 | 66 | 0 | 0 | 295 | 0 | 0 | 35 | 317 | 0 | 0 | 1 | 143.42 | 0 | 20 | 0 | 0 | 90 | 16 | 19 | 0 | 38 | 45 | 23 | 17 | 12 | 12 | 0 | 222 | 101 | 0 | 1125 | 0 | 0 | 6 | 8 | 99 | 194 | 0 | 0 | 0 | 1201 | 1 | 38 | 26 | 0 | 351 | 0 | 51 | 20 | 201 | 38 | 51 | 85 | 178 | 26 | 19 | 104 | 153 | 34 | 3 | 29 | 305 | 0 | 216 | 39 | 38 | 138 | 1 | 8 | 0 | 82 | 0 | 0 | 0 | 124 | 17 | 58 | 1.74 | 115 | 0 | 0 | 1.12 | 12 | 7741.28 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 6 | 1100 | 0 | 0 | 0 | 1012.57 | 0 | 0 | 0 | 57 | 44 | 0 | 8 | 24 | 8 | 2.21 | 4 | 0 | 0 | 1.85 | 170 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0.15 | 161 | 47 | 93 | 1 | 95 | 0 | 0 | 0 | 0.8 | 12 | 0.02 | 16 | 307 | 114 | 220 | 0 | 600 | 880 | 17 | 6298.6 | 14039.88 | 103.67
19:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 268 | 54 | 0 | 35 | 140 | 32 | 0 | 35 | 108 | 0 | 0 | 297 | 0 | 0 | 35 | 318 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 92 | 16 | 29 | 0 | 32 | 50 | 29 | 20 | 12 | 12 | 0 | 222 | 93 | 0 | 1125 | 0 | 0 | 40 | 17 | 105 | 194 | 0 | 0 | 0 | 1224 | 0 | 90 | 26 | 0 | 355 | 0 | 51 | 26 | 187 | 36 | 64 | 85 | 183 | 26 | 19 | 106 | 154 | 52.2 | 0 | 29 | 310 | 0 | 230 | 40 | 38 | 138 | 0 | 8 | 0 | 82 | 0 | 97 | 0 | 124 | 17 | 58 | 0 | 115 | 0 | 0 | 0 | 12 | 8123.62 | 902 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 150 | 0 | 50 | 0 | 1123 | 0 | 0 | 0 | 1129.11 | 0 | 0 | 0 | 57 | 70 | 0 | 51 | 30 | 8 | 0 | 0 | 20 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 161 | 46 | 95 | 0 | 106 | 0 | 130 | 0 | 0 | 0 | 0 | 16 | 307 | 114 | 220 | 0 | 1050 | 880 | 17 | 7270.11 | 15393.73 | 103.68
19:30 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 297 | 54 | 0 | 35 | 141 | 32 | 0 | 35 | 108 | 0 | 0 | 287 | 0 | 0 | 35 | 318 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 107 | 16 | 44 | 0 | 10 | 50 | 23 | 35 | 12 | 12 | 0 | 222 | 110 | 2 | 1125 | 0 | 0 | 44 | 17 | 105 | 194 | 0 | 0 | 0 | 1224 | 0 | 150 | 26 | 0 | 353 | 0 | 51 | 30 | 205 | 41 | 89 | 86 | 191 | 27 | 19 | 106 | 138 | 52.2 | 0 | 30 | 310 | 0 | 230 | 41 | 39 | 140 | 0 | 8 | 0 | 82 | 0 | 96 | 0 | 124 | 17 | 68 | 0 | 152 | 0 | 0 | 0 | 12 | 8334.62 | 902 | 0 | 0 | 26 | 0 | 38 | 0 | 0 | 151 | 0 | 50 | 0 | 1121 | 0 | 0 | 0 | 1155.55 | 0 | 0 | 0 | 57 | 70 | 0 | 51 | 30 | 8 | 0 | 0 | 20 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 161 | 47 | 95 | 0 | 106 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 1050 | 900 | 27 | 7349.55 | 15684.17
20:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 284 | 54 | 0 | 35 | 140 | 32 | 0 | 35 | 108 | 0 | 0 | 288 | 0 | 0 | 35 | 321 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 107 | 16 | 47 | 0 | 10 | 50 | 29 | 35 | 12 | 12 | 0 | 222 | 107 | 2 | 1125 | 0 | 0 | 44 | 17 | 105 | 194 | 0 | 0 | 0 | 1230 | 0 | 150 | 26 | 0 | 356 | 0 | 51 | 36 | 192 | 42 | 86 | 85 | 188 | 27 | 19 | 106 | 138 | 52.2 | 0 | 29 | 305 | 0 | 230 | 40 | 39 | 137 | 0 | 8 | 0 | 83 | 0 | 5 | 0 | 124 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 12 | 8231.62 | 902 | 0 | 0 | 28 | 0 | 38 | 0 | 0 | 150 | 0 | 50 | 0 | 1126 | 0 | 0 | 0 | 1160.27 | 0 | 27 | 0 | 57 | 70 | 0 | 51 | 31 | 8 | 0 | 0 | 20 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 162 | 47 | 95 | 0 | 106 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 1050 | 890 | 27 | 7389.27 | 15620.89 | 103.69
21:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 315 | 54 | 0 | 41 | 140 | 32 | 0 | 35 | 108 | 0 | 0 | 265 | 0 | 0 | 35 | 321 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 109 | 16 | 50 | 0 | 19 | 46 | 29 | 35 | 12 | 12 | 0 | 222 | 110 | 0 | 1125 | 0 | 0 | 44 | 17 | 105 | 194 | 0 | 0 | 0 | 1230 | 0 | 150 | 45 | 0 | 359 | 0 | 51 | 43 | 189 | 42 | 89 | 85 | 188 | 27 | 19 | 106 | 146 | 52.2 | 0 | 31 | 305 | 0 | 230 | 40 | 39 | 142 | 0 | 8 | 0 | 83 | 0 | 0 | 0 | 124 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 12 | 8297.62 | 903 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 232 | 0 | 50 | 0 | 1095 | 0 | 0 | 0 | 1135.42 | 0 | 40 | 0 | 57 | 70 | 0 | 51 | 31 | 8 | 0 | 0 | 14 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 160 | 47 | 95 | 0 | 106 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 1050 | 890 | 17 | 7408.42 | 15706.04 | 103.7
22:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 262 | 54 | 0 | 17 | 141 | 32 | 0 | 35 | 108 | 0 | 0 | 284 | 0 | 0 | 35 | 323 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 97 | 16 | 50 | 0 | 15 | 50 | 29 | 35 | 12 | 12 | 0 | 222 | 107 | 0 | 1125 | 0 | 0 | 50 | 17 | 98 | 193 | 0 | 0 | 0 | 1232 | 0 | 150 | 71 | 0 | 360 | 0 | 51 | 43 | 217 | 42 | 70 | 85 | 188 | 27 | 11 | 99 | 142 | 52.2 | 0 | 31 | 300 | 0 | 227 | 40 | 39 | 141 | 0 | 8 | 0 | 83 | 0 | 0 | 0 | 124 | 17 | 69 | 0 | 154 | 0 | 0 | 0 | 12 | 8240.62 | 902 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 150 | 0 | 50 | 0 | 979 | 0 | 0 | 0 | 1018.28 | 0 | 39 | 0 | 57 | 70 | 0 | 51 | 22 | 52.2 | 0 | 0 | 14 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 160 | 46 | 95 | 0 | 107 | 0 | 100 | 0 | 0 | 0 | 0 | 16 | 307 | 116 | 220 | 0 | 1050 | 890 | 17 | 7064.48 | 15305.1 | 103.71
23:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 286 | 35 | 0 | 17 | 141 | 32 | 0 | 35 | 108 | 0 | 0 | 279 | 0 | 0 | 35 | 327 | 0 | 0 | 0 | 143.42 | 11 | 0 | 0 | 0 | 91 | 16 | 39 | 0 | 10 | 50 | 29 | 17 | 12 | 12 | 0 | 222 | 108 | 2 | 1125 | 0 | 0 | 50 | 17 | 103 | 195 | 0 | 0 | 0 | 1231 | 0 | 75 | 72 | 0 | 361 | 0 | 51 | 43 | 220 | 39 | 69 | 85 | 184 | 27 | 19 | 104 | 156 | 52.2 | 0 | 31 | 300 | 0 | 227 | 40 | 39 | 139 | 0 | 8 | 0 | 83 | 5 | 25 | 0 | 124 | 17 | 69 | 0 | 154 | 0 | 0 | 0 | 12 | 8170.62 | 903 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 100 | 0 | 50 | 0 | 897 | 0 | 0 | 0 | 1006.36 | 0 | 39 | 0 | 57 | 70 | 0 | 51 | 22 | 52.2 | 0 | 0 | 14 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 155 | 46 | 95 | 0 | 107 | 0 | 50 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 180 | 0 | 1050 | 890 | 17 | 6769.56 | 14940.18 | 103.71
Total KWH | 0 | 1550400 | 637440 | 0 | 0 | 0 | 0 | 0 | 9122400 | 0 | 5782280 | 325440 | 214200 | 592416 | 1533120 | 1028727 | 116840 | 604631 | 986400 | 0 | 0 | 4308945 | 3197359 | 0 | 467153 | 7512431 | 0 | 0 | 137947 | 2438400 | 218400 | 458640 | 0 | 0 | 2273236 | 383891 | 593280 | 0 | 306240 | 543303 | 742920 | 346275 | 289920 | 295680 | 25391 | 5239842 | 2479818 | 328320 | 27018181.82 | 0 | 0 | 1064160 | 157402.8 | 2327600 | 4553800 | 0 | 0 | 0 | 28827270 | 72630 | 1098981 | 1739636 | 0 | 8137000 | 0 | 1229820 | 661440 | 4417000 | 697608 | 839040 | 2042522 | 4371360 | 170520 | 392110 | 1665540 | 3664320 | 765922 | 479445 | 775696 | 7327000 | 0 | 6261000 | 944000 | 900600 | 3488890.91 | 84520 | 193104 | 0 | 1738560 | 19872 | 237000 | 0 | 2712820 | 439200 | 1347600 | 144547 | 2232000 | 0 | 13500 | 340630 | 94320 | 180769853.53 | 21794909 | 0 | 0 | 136320 | 0 | 912000 | 0 | 0 | 709152 | 0 | 510912 | 663120 | 27040000 | 0 | 0 | 0 | 23110586 | 0 | 165664 | 0 | 401952 | 815712 | 0 | 354944 | 195580 | 300379 | 340616 | 663630 | 78116 | 0 | 375008 | 4135818 | 0 | 0 | 0 | 0 | 0 | 7557120 | 0 | 34440 | 3962000 | 1103999 | 2460460 | 186267 | 941020 | 0 | 535657.5 | 0 | 54743.4 | 1492560 | 4392 | 371424 | 7265000 | 1884000 | 5296590 | 0 | 17607272 | 21141818.18 | 474000 | 155077181.08 | 335847034.61

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 10-08-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14075.95 | MW | 12:00 Hr. | Energy Generated |  |  | 335.847 |  | MKWHr.
| Day Peak Demand |  |  | 17139.95 | MW | 12:00 Hr. | Energy Unserverd |  |  | 69.485 |  | MKWHr.
| Evening Peak Generation |  |  | 15706.04 | MW | 21:00 Hr. | Energy Demand |  |  | 405.332 |  | MKWHr.
| Evening Peak Demand |  |  | 18519.18 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.5 |  | °C
| Minimum Generation of the Day |  |  | 12916.55 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 727.03 |  | MMCFD
| Maximum Generation of the Day |  |  | 15706.04 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.3177 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 30.6005 | 0 | 10.4952 | 0 | 0 | 0.13795 | 0 | 0 | 41.2336 | Gas | 97.4961 | Gas | 346771838.4772
| Chattogram Zone |  |  | 4.8821 | 55.8455 | 11.4975 | 0 | 5.2398 | 0.098021 | 0 | 0.30624 | 77.8692 | Coal | 133.9655 | Coal | 908069499.0934
| Cumilla Zone |  |  | 19.3171 | 0 | 9.6871 | 0 | 0 | 0.47945 | 3.6643 | 0 | 33.148 | HFO | 42.9993 | HFO | 784202341.712
| Mymensingh Zone |  |  | 0 | 0 | 4.1131 | 0 | 0 | 0.49868 | 0 | 0 | 4.6118 | HSD | 1.2448 | HSD | 30865974
| Sylhet Zone |  |  | 23.8228 | 0 | 0 | 0 | 0 | 0.08452 | 0 | 0 | 23.9074 | Hydro | 5.2398 | Hydro | 523984.2
| Khulna Zone |  |  | 0 | 27.04 | 0.64723 | 0.70915 | 0 | 0.66312 | 22.7069 | 0 | 51.7664 | Solar | 5.1134 | Solar | 82762838.952
| Barishal Zone |  |  | 7.1806 | 46.0141 | 0.84542 | 0 | 0 | 0.004392 | 0 | 0 | 54.0445 | Import | 49.4818 | Import | 299920846.26
| Rajshahi Zone |  |  | 11.6929 | 0 | 2.3123 | 0 | 0 | 1.4137 | 23.1106 | 0 | 38.5296 | Wind | 0.30624 | Wind | 4504790.4
| Rangpur Zone |  |  | 0 | 5.066 | 3.4015 | 0.53566 | 0 | 1.7336 | 0 | 0 | 10.7367
| Total |  |  | 97.4961 | 133.9655 | 42.9993 | 1.2448 | 5.2398 | 5.1134 | 49.4818 | 0.30624 | 335.847
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 346771838.4772 |  | Hydro | 523984.2
|  |  |  | Coal | 908069499.0934 |  | Solar | 82762838.952
|  |  |  | HFO | 784202341.712 |  | Import | 299920846.26
|  |  |  | HSD | 30865974 |  | Wind | 4504790.4
[5 empty] | Total: | 245,76,22,113 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7949 | Peak Hr Flow | 903.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 49069618.18 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.1106 | Peak Hr Flow | 1135.42 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2465 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.6643 | Peak Hr Flow | 146.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2727 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.5698 | Peak Hr Flow | 2184.42 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 364 |  | 6197
|  |  |  | Chattogram |  | 74 |  | 1614
|  |  |  | Cumilla |  | 385 |  | 1696
|  |  |  | Mymensingh |  | 527 |  | 1593
|  |  |  | Sylhet |  | 218 |  | 828
|  |  |  | Khulna |  | 420 |  | 2077
|  |  |  | Barishal |  | 146 |  | 549
|  |  |  | Rajshahi |  | 294 |  | 1839
|  |  |  | Rangpur |  | 264 |  | 1235
|  |  |  | Total |  | 2692 |  | 17628
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 89
|  |  |  | Total Unavailable Capacity |  |  |  | 389
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:00 | Hasnabad 230/132kV S/S AUTO TR-1 LT is restored.
|  | 08:00 | Hasnabad 230/132kV S/S AUTO TR-1 HT is restored.
|  | 08:37 | Jashore 132/33kV S/S T-3 LT is restored.
| 08:53 | 21:11 | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Project Work S/D Due to BBK Project work.
| 10:44 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- ST
| 10:51 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- GT
| 11:00 |  | Meghnaghat CCPP(Summit)-2 GT Shutdown with remarks:- None
| 11:00 |  | Meghnaghat CCPP(Summit)-2 ST Shutdown with remarks:- None
|  | 11:14 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT is restored.
| 11:19 | 17:07 | Lakshmipur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to SCADA Integration Work.
| 11:20 |  | Rajendrapur 132/33kV S/S 132 kV BUS-1 Project Work S/D Due to Sreepur Bay Extension Work
| 11:21 | 17:05 | Lakshmipur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to SCADA Integration Work.
| 11:47 | 12:42 | Ghorasal- Ishwardi 230 kV Ckt-2 Scheduled S/D from Ghorashal 230kV end Due to For
Ghorashal End Ishwardi Bay VT conncetion rectification and from Ishurdi 230/132kVend.
| 12:12 | 12:15 | Amnura 132/33kV S/S CB-408B Forced S/D Due to For 31S 33kv bus section D/S open due to | [7 empty] | 8.0MW load
|  |  | individual operation of T-01 and T-02. | [7 empty] | interrup.
| 12:12 | 12:15 | Amnura 132/33kV S/S CB-418B Forced S/D Due to For 31S 33kv bus section D/S open due to | [7 empty] | 8.0MW load
|  |  | individual operation of T-01 and T-02. | [7 empty] | interrup.
|  | 12:31 | Candpur- Kachua 132kV Ckt-2 is restored.
|  | 12:31 | Candpur- Kachua 132kV Ckt-2 is restored.
| 12:59 |  | Day Peak Generation: 14076 MW.
| 13:25 | 13:52 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to OLTC Oil Collection.
| 13:25 | 13:52 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to OLTC Oil Collection.
| 14:59 | 15:23 | Kurigram-Rangpur 132kV Ckt-1 Tripped from Rangpur 132/33kV end showing Distance relay
relays Due to Phase to Phase Fault
| 14:59 | 15:24 | Kurigram-Lalmonirhat 132kV Ckt-1 Tripped from Kurigram 132/33kV end showing Main
protection Relay(F21) Distance Relay relays Due to Distance Trip
| 16:15 |  | Payra 400/132/33kV S/S 132/33 kV Transformer-03 HT Tripped showing Differential
Protection Relay relays Due to None
| 16:21 | 17:45 | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to | [7 empty] | 90.0MW load
|  |  | 230/132kV ATR internal inspection & oil centrifuge. | [7 empty] | interrup. Kaliakoir
400/230/132kV end
| 16:21 | 16:26 | Dhamrai-Kaliakoir 132 kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to | [7 empty] | 90.0MW load
|  |  | 230/132kV ATR internal inspection & centrifuge. | [7 empty] | interrup. Kaliakoir
400/230/132kV end
| 16:43 | 18:16 | Jashore 132/33kV S/S T-1 LT Forced S/D Due to 33kv T1A side out going-1, R-phase DS red | [7 empty] | 47.0MW load
|  |  | hot maintenance(PBS) | [7 empty] | interrup.
| 16:44 | 18:15 | Jashore 132/33kV S/S T-1 HT Forced S/D Due to 33kv T1A side out going-1, R-phase DS red
hot maintenance(PBS)
| 16:56 | 18:10 | Bajitpur 132/33kV S/S Tr-1(404T) LT Scheduled S/D | [7 empty] | 40.0MW load
interrup.
| 17:35 | 19:13 | Rangpur 132/33kV S/S Rangpur-GTPS Scheduled S/D Due to Transformer sedule checkup
| 18:11 | 19:51 | BIPTC S/S 10CF26 Tripped showing 87 relays Due to Tripped by Capacitor Unbalance
|  | 18:24 | Munshiganj 132/33kV S/S Transformer-1 HT is restored.
|  | 18:24 | Munshiganj 132/33kV S/S Transformer-1 LT is restored.
|  | 18:32 | Rajendrapur 132/33kV S/S MTR-2 HT is restored.
|  | 18:33 | Rajendrapur 132/33kV S/S MTR-2 LT is restored.
| 19:21 | 19:51 | BIPTC S/S 10CF26 Scheduled S/D Due to Tripped by Capacitor Unbalance
| 21:00 |  | Evening peak generation is 15706 MW.
| 01:46 |  | Aggreko-keraniganj 132kV Ckt-1 Tripped from Keranigonj 230/132/33kV end showing Distance
relay, 11.8km relays Due to Heavy rainfall with thundering
| 02:27 |  | Nawabganj 132/33kV S/S TR-1 HT Tripped showing PRD Trip & Differential Protection P632, | [7 empty] | 12.0MW load
|  |  | Lock out relay-1,2 relays Due to 33 kV pbs bandhura feeder insulator burn. | [7 empty] | interrup.
| 05:51 |  | Haripur 412 MW CCPP Shutdown with remarks:- ST
| 06:00 |  | Minimum Generation: 13227 MW.
| 06:27 |  | Khulshi-Madunaghat 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to loop
maintenance work by khuslsi ss.
| 07:00 |  | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to Tr-06 33kv D/S Redhot Maintenance. | [7 empty] | 40.0MW load
interrup.
| 07:00 |  | Haripur 412 MW CCPP Synchronized with remarks:- false
| 07:01 |  | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to Tr-06 33kv D/S Redhot Maintenance. | [7 empty] | 40.0MW load
interrup.
| 07:15 |  | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to 33 kv bus DS maintenance work | [7 empty] | 39.0MW load
interrup.
| 07:15 |  | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to 33 kv bus DS maintenance work | [7 empty] | 39.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 10-08-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 404 | 9122400 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 265 | 4308945 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 116840 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 321 | 7512431 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 325440 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 140 | 1533120 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 604631 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 467153 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11 | 218400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 458640 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 49 | 637440 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 32 | 1028727 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 41 | 592416 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1550400 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 986400 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 137947 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 214200 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 3197359 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 315 | 5782280 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 2438400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2079.42 | 41233569
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 157402.8 | Liquid fuel shortage
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 72630 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 1064160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5239842 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 194 | 4553800 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 2327600 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 29 | 742920 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 46 | 543303 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 289920 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 328320 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 593280 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25391 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 383891 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 35 | 346275 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2479818 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 295680 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 109 | 2273236 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1230 | 28827270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 19 | 306240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 27018181.82 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 3375 | 77869160.62
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 189 | 4417000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 359 | 8137000 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 42 | 697608 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 43 | 661440 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 45 | 1739636 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1229820 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1098981 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 775696 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2042522 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 188 | 4371360 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 146 | 3664320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 765922 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 392110 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1665540 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 170520 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 839040 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 479445 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1622.2 | 33147960
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 144547 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 153 | 2232000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1347600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 340630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 94320 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 439200 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 250 | 4611797
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 84520 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 944000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 900600 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 142 | 3488890.91 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 237000 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 19872 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1738560 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 124 | 2712820 | plant availability zero
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 193104 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7327000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 230 | 6261000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 971 | 23907366.91
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 903 | 21794909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 23 | 136320 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 510912 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 663120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 232 | 709152 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1095 | 27040000 | AGC+FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2341 | 51766413
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1050 | 17607272 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 371424 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 1884000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 890 | 21141818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5296590 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 474000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7265000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4392 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2615 | 54044496.18
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 340616 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 165664 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 195580 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 168 | 4135818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 305 | 7557120 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 14 | 78116 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 300379 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 354944 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 815712 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 57 | 401952 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 34440 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1135.42 | 23110586 | Problem with coal feeding system
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 375008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 663630 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1879.42 | 38529565
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 535657.5 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1103999 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3962000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 941020 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 54743.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 2460460 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 186267 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1492560 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 573 | 10736706.9
Eastern Grid Total |  |  |  |  | 17440.562 | 8297.62 | 180769853.53
Western Grid Total |  |  |  |  | 11731.125 | 7408.42 | 155077181.08
National Grid Total |  |  |  |  | 29171.687 | 15706.04 | 335847034.61
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 10-08-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10360.14 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4575.9 | MW
i) Dhaka area |  |  | 5833.14 |  | MW | i) Khulna area |  |  |  | 1657 | MW
ii) Chattogram area |  |  | 1540 |  | MW | ii) Barishal area |  |  |  | 403.3 | MW
iii) Cumilla area |  |  | 1311 |  | MW | iii) Rajshahi area |  |  |  | 1544.6 | MW
iv) Mymensingh area |  |  | 1066 |  | MW | iv) Rangpur area |  |  |  | 971 | MW
v) Sylhet area |  |  | 610 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14936.04 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 17 | 18:30 | 67 | HaripurSBU | 150 | 21:00 | 133 | Narshingdi | 169 | 19:00 | 199 | Uttara | 103 | 13:00
2 | AKSML | 160.5 | 11:00 | 68 | Hasnabad | 96 | 19:30 | 134 | Natore | 143 | 21:00 | 200 | UttaraNew | 58 | 23:00
3 | Aftabnagar | 48 | 13:00 | 69 | Hathazari | 93 | 20:00 | 135 | Nawabganj | 63.9 | 22:00 | 201 | Zigatola | 116 | 13:00
4 | Agargaon | 130 | 13:00 | 70 | Hatirjheel | 97 | 13:00 | 136 | Netrakona | 147 | 09:00
5 | Agrabad | 76 | 19:30 | 71 | Ishurdi | 77 | 20:00 | 137 | New | 88 | 15:00
6 | Amnura | 33 | 22:00 | 72 | Jaldhaka | 70 | 18:30 | 138 | Niamatpur | 85 | 19:30
7 | Ashuganj | 91 | 21:00 | 73 | Jamalpur | 108 | 22:00 | 139 | Noapara | 36 | 19:00
8 | BSRM | 193 | 19:30 | 74 | Jashore | 180 | 19:30 | 140 | PHP | 8 | 18:00
9 | Bagerhat | 87 | 19:30 | 75 | Jhenaidah | 86 | 19:30 | 141 | Pabna | 103 | 19:00
10 | Bajitpur | 103 | 22:00 | 76 | Joydebpur | 174 | 19:30 | 142 | Palashbari | 118 | 19:00
11 | Bakerganj | 15 | 19:00 | 77 | Joypurhat | 63 | 21:00 | 143 | Panchagarh | 73 | 20:00
12 | Bakulia | 100 | 18:30 | 78 | Juldah | 16 | 00:00 | 144 | Patiya | 12 | 19:30
13 | Banani | 80.8 | 13:00 | 79 | KSRM | 21 | 03:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 18 | 10:00 | 80 | Kabirpur | 220 | 18:30 | 146 | Patuakhali | 57 | 18:30
15 | Barapukuria | 68 | 22:00 | 81 | Kachua | 82 | 19:30 | 147 | Payra | 28 | 06:00
16 | Barguna | 18 | 06:00 | 82 | Kaliganj | 40 | 07:00 | 148 | Postogola | 64 | 13:00
17 | Barishal | 93 | 18:30 | 83 | Kallyanpur | 126 | 15:00 | 149 | Pubail | 52 | 20:00
18 | Barishal-230 | 92 | 18:30 | 84 | Kalurghat | 38 | 09:00 | 150 | Purbachal | 40 | 01:00
19 | Baroaulia | 72 | 08:00 | 85 | Kamrangirchar | 81 | 17:00 | 151 | Purbasadipur | 132 | 19:00
20 | Baroirhat | 61 | 21:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 36 | 19:00
21 | Bashundhara | 224 | 19:00 | 87 | Kasba | 33 | 19:00 | 153 | Rahim | 53 | 10:00
22 | BashundharaCement | 15 | 19:00 | 88 | Kazla | 125 | 12:00 | 154 | Rajbari | 70 | 22:00
23 | Beanibazar | 64 | 21:00 | 89 | Keranigonj | 92 | 19:30 | 155 | Rajendrapur | 116 | 21:00
24 | Benapole | 60 | 19:00 | 90 | Khagrachori | 34 | 21:00 | 156 | Rajshahi | 118 | 00:00
25 | Bhaluka | 169 | 20:00 | 91 | Khulna | 58 | 09:00 | 157 | Rajshahi-230 | 108 | 22:00
26 | Bhandaria | 45 | 13:00 | 92 | Khulshi | 185 | 19:30 | 158 | Ramganj | 98 | 20:00
27 | Bhangura | 32 | 13:00 | 93 | Kishoreganj | 123 | 22:00 | 159 | Rampur | 46 | 19:30
28 | Bheramara(GK) | 58 | 20:00 | 94 | Kodda | 295 | 21:00 | 160 | Rangamati | 18 | 20:00
29 | Bhulta | 186 | 16:00 | 95 | Kulaura | 52 | 20:00 | 161 | Rangpur | 130 | 21:00
30 | Bog-Sherpur | 66 | 19:00 | 96 | Kurigram | 56 | 18:00 | 162 | Ruppur | 4.6 | 16:00
31 | Bogura | 195 | 21:00 | 97 | Kushtia | 133 | 20:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 68 | 19:30 | 98 | Laksam | 32 | 19:00 | 164 | Saidpur | 97 | 21:00
33 | Brahmanbaria | 123 | 19:00 | 99 | Lakshmipur | 45 | 20:00 | 165 | Santhia | 34 | 23:00
34 | Cantonment | 135 | 14:00 | 100 | Lalbag | 83 | 13:00 | 166 | Satkhira | 130 | 19:00
35 | Chandina | 38 | 19:00 | 101 | Lalmonirhat | 56 | 19:30 | 167 | Satmasjid | 111 | 13:00
36 | Chandpur | 72 | 21:00 | 102 | MI_Cement | 16 | 02:00 | 168 | Savar | 220 | 19:30
37 | Chandraghona | 34 | 19:30 | 103 | Madanganj | 50 | 23:00 | 169 | SevenRings | 13.44 | 03:00
38 | Chapai | 70 | 21:00 | 104 | Madaripur | 97 | 20:00 | 170 | ShahCement | 30 | 17:00
39 | Charfasson | 30 | 19:00 | 105 | Madartek | 92 | 23:00 | 171 | Shahjadpur | 77 | 19:30
40 | Charsaidpur | 36 | 01:00 | 106 | Madunaghat | 58 | 21:00 | 172 | Shahjibazar | 129 | 21:00
41 | Chauddagram | 66 | 20:00 | 107 | Magura | 57 | 21:00 | 173 | Shahmirpur | 53.5 | 00:00
42 | Chhatak | 40 | 22:00 | 108 | Mahasthangarh | 65 | 21:00 | 174 | Shariatpur | 73 | 19:30
43 | Chowmuhani | 139 | 20:00 | 109 | Maijdee | 37 | 19:00 | 175 | Sherpur | 148 | 19:00
44 | Chuadanga | 98 | 06:00 | 110 | Manikganj | 115 | 21:00 | 176 | Shikalbaha | 29 | 00:00
45 | Coxsbazar | 145 | 19:30 | 111 | Maniknagar | 84 | 14:00 | 177 | Shitalakhya | 85.1 | 15:00
46 | Cumilla(N) | 123 | 19:30 | 112 | Matarbari | 55 | 19:30 | 178 | Sholosohor | 60 | 20:00
47 | Cumilla(S) | 198 | 00:00 | 113 | Matuail | 78 | 13:00 | 179 | Shomvuganj | 35 | 18:30
48 | Daganbhuiyan | 34 | 23:00 | 114 | Metrorail_Motijheel | 22 | 15:00 | 180 | Shyampur | 158 | 00:00
49 | Daudkandi | 123 | 20:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 139 | 16:00
50 | DhakaUniversity | 104 | 13:00 | 116 | Millgate | 118 | 16:00 | 182 | Sirajganj | 134 | 22:00
51 | Dhamrai | 92 | 19:30 | 117 | Mirpur | 165 | 13:00 | 183 | Sitakunda | 15 | 15:00
52 | Dhanmondi | 126 | 13:00 | 118 | Mirsorai | 14 | 19:00 | 184 | Sonargaon | 161 | 08:00
53 | Dohazari | 113 | 19:30 | 119 | Mirzapur | 37 | 22:00 | 185 | Sreemongol | 78 | 23:00
54 | Faridpur | 162 | 21:00 | 120 | Mithapukur | 60 | 22:00 | 186 | Sreepur | 141 | 21:00
55 | Fatullah | 117 | 15:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 55.5 | 22:00
56 | Fenchuganj | 41 | 21:00 | 122 | Mogbazar | 42.5 | 14:00 | 188 | Sunamganj | 50 | 22:00
57 | Feni | 104 | 22:00 | 123 | Mongla | 41 | 19:00 | 189 | Sylhet | 105 | 19:30
58 | GPH | 73 | 18:00 | 124 | Motijheel | 54 | 13:00 | 190 | Sylhet_(South) | 79 | 19:00
59 | Ghatail | 73 | 22:00 | 125 | Muktagacha | 40 | 18:00 | 191 | TK | 24 | 19:30
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 132 | 22:00 | 192 | Tangail | 148 | 20:00
61 | Ghorashal-230 | 110 | 20:00 | 127 | Muradnagar | 43 | 19:00 | 193 | Taraganj | 29 | 19:00
62 | Goalpara | 36 | 19:00 | 128 | Mymensingh | 134 | 22:00 | 194 | Tasnim | 38 | 00:00
63 | Gollamari | 100 | 14:00 | 129 | Nabinagar | 96 | 23:00 | 195 | Thakurgaon | 116 | 21:00
64 | Gopalganj | 97 | 21:00 | 130 | Naogaon | 134 | 20:00 | 196 | Tongi | 161 | 07:00
65 | Gulshan | 132 | 15:00 | 131 | Narail | 61 | 20:00 | 197 | Ullahpara | 38 | 19:00
66 | Halishahar | 116 | 19:00 | 132 | Narinda | 81 | 13:00 | 198 | Ullon | 63 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 10-08-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 13756.26 | 3656 |  | 17576.78
1:00 | 13162.1 | 3757 |  | 17088.1
2:00 | 13021.04 | 3751 |  | 16941.04
3:00 | 13082.12 | 3639 |  | 16885.12
4:00 | 12926.5 | 3463 |  | 16545.5
5:00 | 12918.46 | 3372 |  | 16442.46
6:00 | 12916.55 | 2916 |  | 15963.55
7:00 | 12934.2 | 2703 |  | 15759.2
8:00 | 13018.27 | 2474 |  | 15603.27
9:00 | 13435.5 | 2337 |  | 15877.5
10:00 | 13720.9 | 2473 |  | 16304.9
11:00 | 13750.13 | 2579 |  | 16445.13
12:00 | 14075.95 | 2932 |  | 17139.95
13:00 | 14254.54 | 2541 |  | 16909.54
14:00 | 14154.7 | 2613 |  | 16885.29
15:00 | 13924.65 | 3408 |  | 17486.01
16:00 | 13858.94 | 3193 |  | 17195.63
17:00 | 13803.62 | 3123 |  | 17067.16
18:00 | 14039.88 | 2577 |  | 16732.85
19:00 | 15393.73 | 2599 |  | 18109.69
19:30 | 15684.17 | 2038 |  | 17813.88
20:00 | 15620.89 | 1999 |  | 17709.85
21:00 | 15706.04 | 2692 |  | 18519.18
22:00 | 15305.1 | 2217 |  | 17621.87
23:00 | 14940.18 | 2471 |  | 17522.38
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 10-08-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7460.2 | 6296.06 | 13756.26 | DAILY GENERATION CURVE
00:30 | 7375.2 | 6083.98 | 13459.18
01:00 | 7290.2 | 5871.9 | 13162.1 | 10-08-2026
01:30 | 7214.2 | 5877.37 | 13091.57
02:00 | 7138.2 | 5882.84 | 13021.04
02:30 | 7174.7 | 5876.88 | 13051.58
03:00 | 7211.2 | 5870.92 | 13082.12
03:30 | 7164.7 | 5839.61 | 13004.31
04:00 | 7118.2 | 5808.3 | 12926.5
04:30 | 7098.7 | 5823.78 | 12922.48
05:00 | 7079.2 | 5839.26 | 12918.46
05:30 | 7130.985 | 5786.52 | 12917.505
06:00 | 7182.77 | 5733.78 | 12916.55
06:30 | 7099.205 | 5826.17 | 12925.375
07:00 | 7015.64 | 5918.56 | 12934.2
07:30 | 7008.7 | 5967.535 | 12976.235
08:00 | 7001.76 | 6016.51 | 13018.27
08:30 | 7091.735 | 6135.15 | 13226.885
09:00 | 7181.71 | 6253.79 | 13435.5
09:30 | 7209.255 | 6368.945 | 13578.2
10:00 | 7236.8 | 6484.1 | 13720.9
10:30 | 7243.965 | 6491.55 | 13735.515
11:00 | 7251.13 | 6499 | 13750.13
11:30 | 7296.48 | 6616.56 | 13913.04
12:00 | 7341.83 | 6734.12 | 14075.95
12:30 | 7376.945 | 6788.3 | 14165.245
13:00 | 7412.06 | 6842.48 | 14254.54
13:30 | 7449.16 | 6755.46 | 14204.62
14:00 | 7486.26 | 6668.44 | 14154.7
14:30 | 7473.31 | 6566.365 | 14039.675
15:00 | 7460.36 | 6464.29 | 13924.65
15:30 | 7456.005 | 6435.79 | 13891.795
16:00 | 7451.65 | 6407.29 | 13858.94
16:30 | 7470.215 | 6361.065 | 13831.28
17:00 | 7488.78 | 6314.84 | 13803.62
17:30 | 7615.03 | 6306.72 | 13921.75
18:00 | 7741.28 | 6298.6 | 14039.88
18:30 | 7932.45 | 6784.355 | 14716.805
19:00 | 8123.62 | 7270.11 | 15393.73
19:30 | 8334.62 | 7349.55 | 15684.17
20:00 | 8231.62 | 7389.27 | 15620.89
20:30 | 8264.62 | 7398.845 | 15663.465 |  | Executive Engineer
21:00 | 8297.62 | 7408.42 | 15706.04 |  | Network Operation Division
21:30 | 8269.12 | 7236.45 | 15505.57
22:00 | 8240.62 | 7064.48 | 15305.1
22:30 | 8205.62 | 6917.02 | 15122.64
23:00 | 8170.62 | 6769.56 | 14940.18

## En-Curve
QF-LDC-12
Date | 10-08-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2159 | 1593 | 901 | 38 | 196 | 946.06 | 221 | 5564 | 0 | 395 | 1740.2 | 0 | 0 | 3 | 3656 | DAILY ENERGY CURVE
00:30 | 2187.5 | 1611.5 | 901 | 38 | 190 | 881.98 | 220.5 | 5515 | 0 | 326 | 1582.7 | 0 | 0 | 5 | 3706.5 | 10-08-2026
01:00 | 2216 | 1630 | 901 | 38 | 184 | 817.9 | 220 | 5466 | 0 | 257 | 1425.2 | 0 | 0 | 7 | 3757
01:30 | 2242.5 | 1639.5 | 901 | 38 | 179 | 817.87 | 220 | 5467.5 | 0 | 257 | 1325.2 | 0 | 0 | 4 | 3754 | Energy Generated | 335.847 |  | MKWHr
02:00 | 2269 | 1649 | 901 | 38 | 174 | 817.84 | 220 | 5469 | 0 | 257 | 1225.2 | 0 | 0 | 1 | 3751 | Energy not Served | 69.485 |  | MKWHr
02:30 | 2346.5 | 1627.5 | 901.5 | 38 | 174 | 817.38 | 220 | 5469.5 | 0 | 246 | 1210.7 | 0 | 0 | 0.5 | 3695 | Total Energy Requirement | 405.332 |  | MKWHr
03:00 | 2424 | 1606 | 902 | 38 | 174 | 816.92 | 220 | 5470 | 0 | 235 | 1196.2 | 0 | 0 | 0 | 3639
03:30 | 2470.5 | 1573.5 | 901.5 | 38 | 172 | 817.61 | 220.5 | 5423 | 0 | 235 | 1152.2 | 0 | 0 | 0.5 | 3551
04:00 | 2517 | 1541 | 901 | 38 | 170 | 818.3 | 221 | 5376 | 0 | 235 | 1108.2 | 0 | 0 | 1 | 3463
04:30 | 2543 | 1515 | 920 | 38 | 168 | 819.28 | 221.5 | 5367 | 0 | 212.5 | 1111.7 | 0 | 0 | 6.5 | 3417.5
05:00 | 2569 | 1489 | 939 | 38 | 166 | 820.26 | 222 | 5358 | 0 | 190 | 1115.2 | 0 | 0 | 12 | 3372
05:30 | 2538.5 | 1570.5 | 920 | 38 | 161 | 821.205 | 222 | 5359.5 | 8.1 | 171.5 | 1099.2 | 0 | 0 | 8 | 3144
06:00 | 2508 | 1652 | 901 | 38 | 156 | 822.15 | 222 | 5361 | 16.2 | 153 | 1083.2 | 0 | 0 | 4 | 2916
06:30 | 2519 | 1639.5 | 901 | 38 | 153 | 834.92 | 222 | 5382.5 | 56.355 | 152.5 | 1024.6 | 0 | 0 | 2 | 2809.5
07:00 | 2530 | 1627 | 901 | 38 | 150 | 847.69 | 222 | 5404 | 96.51 | 152 | 966 | 0 | 0 | 0 | 2703
07:30 | 2509 | 1550.75 | 901 | 38 | 156 | 878.53 | 222 | 5419 | 174.455 | 178 | 949.5 | 0 | 0 | 0 | 2588.5
08:00 | 2488 | 1474.5 | 901 | 38 | 162 | 909.37 | 222 | 5434 | 252.4 | 204 | 933 | 0 | 0 | 0 | 2474
08:30 | 2543 | 1474.75 | 901.5 | 38 | 166 | 906.1 | 222 | 5429.5 | 357.825 | 250.21 | 936 | 0 | 0 | 2 | 2405.5
09:00 | 2598 | 1475 | 902 | 38 | 170 | 902.83 | 222 | 5425 | 463.25 | 296.42 | 939 | 0 | 0 | 4 | 2337
09:30 | 2537.5 | 1457.25 | 902 | 38 | 168 | 957.41 | 222 | 5445 | 519.62 | 318.92 | 1006 | 0 | 0 | 6.5 | 2405
10:00 | 2477 | 1439.5 | 902 | 38 | 166 | 1011.99 | 222 | 5465 | 575.99 | 341.42 | 1073 | 0 | 0 | 9 | 2473
10:30 | 2515 | 1403.5 | 902 | 38 | 147 | 1016.57 | 221 | 5479.5 | 578.025 | 337.42 | 1090 | 0 | 0 | 7.5 | 2526
11:00 | 2553 | 1367.5 | 902 | 38 | 128 | 1021.15 | 220 | 5494 | 580.06 | 333.42 | 1107 | 0 | 0 | 6 | 2579
11:30 | 2556.5 | 1345.5 | 901.5 | 38 | 132 | 1019.12 | 219.5 | 5606.5 | 611 | 336.42 | 1144 | 0 | 0 | 3 | 2755.5
12:00 | 2560 | 1323.5 | 901 | 38 | 136 | 1017.09 | 219 | 5719 | 641.94 | 339.42 | 1181 | 0 | 0 | 0 | 2932
12:30 | 2565.5 | 1388.25 | 901.5 | 38 | 137 | 1018.995 | 218 | 5687 | 676.58 | 332.42 | 1196 | 0 | 0 | 6 | 2736.5
13:00 | 2571 | 1453 | 902 | 38 | 138 | 1020.9 | 217 | 5655 | 711.22 | 325.42 | 1211 | 0 | 0 | 12 | 2541
13:30 | 2555 | 1451.5 | 902.5 | 38 | 142 | 1019.93 | 217.5 | 5686.5 | 618.77 | 342.92 | 1218 | 0 | 0 | 12 | 2577
14:00 | 2539 | 1450 | 903 | 38 | 146 | 1018.96 | 218 | 5718 | 526.32 | 360.42 | 1225 | 0 | 0 | 12 | 2613
14:30 | 2531 | 1433.5 | 902.5 | 38 | 143 | 1017.605 | 219 | 5611 | 523.65 | 365.92 | 1243 | 0 | 0 | 11.5 | 3010.5
15:00 | 2523 | 1417 | 902 | 38 | 140 | 1016.25 | 220 | 5504 | 520.98 | 371.42 | 1261 | 0 | 0 | 11 | 3408
15:30 | 2551.5 | 1371.5 | 902 | 38 | 144 | 1016.15 | 200.5 | 5474 | 460.225 | 379.92 | 1333 | 0 | 0 | 21 | 3300.5
16:00 | 2580 | 1326 | 902 | 38 | 148 | 1016.05 | 181 | 5444 | 399.47 | 388.42 | 1405 | 0 | 0 | 31 | 3193
16:30 | 2590.5 | 1340.5 | 902 | 38 | 144 | 1016.39 | 181.5 | 5430.5 | 306.97 | 401.42 | 1437.5 | 0 | 0 | 42 | 3158
17:00 | 2601 | 1355 | 902 | 38 | 140 | 1016.73 | 182 | 5417 | 214.47 | 414.42 | 1470 | 0 | 0 | 53 | 3123
17:30 | 2598 | 1414.5 | 902 | 38 | 146.5 | 1014.65 | 202 | 5419 | 125.68 | 499.42 | 1516.5 | 0 | 0 | 45.5 | 2850
18:00 | 2595 | 1474 | 902 | 38 | 153 | 1012.57 | 222 | 5421 | 36.89 | 584.42 | 1563 | 0 | 0 | 38 | 2577
18:30 | 2645.5 | 1475.5 | 902 | 38 | 153.5 | 1070.84 | 222 | 5668.5 | 18.445 | 652.42 | 1695.1 | 140 | 0 | 35 | 2588
19:00 | 2696 | 1477 | 902 | 38 | 154 | 1129.11 | 222 | 5916 | 0 | 720.42 | 1827.2 | 280 | 0 | 32 | 2599
19:30 | 2701 | 1504 | 902 | 38 | 138 | 1155.55 | 222 | 5935 | 0 | 718.42 | 2044.2 | 316 | 0 | 10 | 2038
20:00 | 2616 | 1491 | 902 | 38 | 138 | 1160.27 | 222 | 5937 | 0 | 752.42 | 2039.2 | 315 | 0 | 10 | 1999
20:30 | 2615.5 | 1509.5 | 902.5 | 38 | 142 | 1147.845 | 222 | 5920.5 | 0 | 752.42 | 2042.7 | 356 | 0 | 14.5 | 2345.5
21:00 | 2615 | 1528 | 903 | 38 | 146 | 1135.42 | 222 | 5904 | 0 | 752.42 | 2046.2 | 397 | 0 | 19 | 2692
21:30 | 2631.5 | 1517 | 902.5 | 38 | 144 | 1076.85 | 222 | 5846.5 | 0 | 749.92 | 2036.8 | 323.5 | 0 | 17 | 2454.5
22:00 | 2648 | 1506 | 902 | 38 | 142 | 1018.28 | 222 | 5789 | 0 | 747.42 | 2027.4 | 250 | 0 | 15 | 2217
22:30 | 2638.5 | 1489.5 | 902.5 | 38 | 149 | 1012.32 | 222 | 5745 | 0 | 747.42 | 1965.9 | 200 | 0 | 12.5 | 2344
23:00 | 2629 | 1473 | 903 | 38 | 156 | 1006.36 | 222 | 5701 | 0 | 747.42 | 1904.4 | 150 | 0 | 10 | 2471
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 10-08-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 203 | 51 | 384 | 162 | 1566 | 644 | Ishurdi-Ghorashal Ckt-1 | Export | 2624509.09
1:00 | 166 | 34 | 318 | 148 | 1396 | 598
2:00 | 167 | 37 | 314 | 142 | 1428 | 616 |  | Import | 0
3:00 | 154 | 29 | 282 | 124 | 1370 | 568
4:00 | 140 | 23 | 280 | 136 | 1316 | 564 | Ishurdi-Ghorashal Ckt-2 | Export | 2422109.09
5:00 | 139 | 21 | 290 | 150 | 1296 | 576
6:00 | 138 | 24 | 268 | 160 | 1218 | 554 |  | Import | 0
7:00 | 149 | 24 | 324 | 164 | 1322 | 584
8:00 | 191 | 41 | 360 | 166 | 1506 | 686 | Sirajganj-Sreepur Ckt-1 | Export | 2402000
9:00 | 257 | 77 | 500 | 186 | 1688 | 772
10:00 | 282 | 86 | 500 | 186 | 1774 | 836 |  | Import | 0
11:00 | 282 | 93 | 500 | 212 | 1822 | 908
12:00 | 177 | 60 | 530 | 258 | 2020 | 994 | Sirajganj-Sreepur Ckt-2 | Export | 2411000
13:00 | 264 | 70 | 472 | 204 | 1836 | 884
14:00 | 249 | 66 | 494 | 222 | 1882 | 930 |  | Import | 0
15:00 | 285 | 95 | 492 | 208 | 1848 | 958
16:00 | 301 | 105 | 504 | 216 | 1828 | 948 | Gopalganj-Aminbazar Ckt-1 | Export | 19580000
17:00 | 253 | 81 | 400 | 172 | 1712 | 882
18:00 | 235 | 75 | 406 | 192 | 1658 | 818 |  | Import | 0
18:30 | 219 | 66 | 404 | 184 | 1638 | 790
19:00 | 208 | 42 | 422 | 190 | 1820 | 744 | Gopalganj-Aminbazar Ckt-2 | Export | 19630000
19:30 | 227 | 57 | 424 | 190 | 1888 | 788
20:00 | 230 | 53 | 432 | 198 | 1884 | 752 |  | Import | 0
21:00 | 221 | 42 | 402 | 196 | 1842 | 742
22:00 | 207 | 55 | 374 | 180 | 1682 | 694 |  | Total Export | 49069618.18
23:00 | 191 | 47 | 366 | 180 | 1620 | 660 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 10-08-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 377 | 03:00 | 348 | 12:00 | Madunaghat | 398 | 04:00 | 384 | 13:00
Amtali | 413 | 01:00 | 406 | 12:00 | Meghnaghat | 382 | 03:00 | 352 | 12:00
Ashuganj | 404 | 2:00 | 364 | 12:00 | Mirsorai | 396 | 04:00 | 375 | 12:00
Bhulta | 399 | 03:00 | 355 | 12:00 | Payra | 416 | 05:00 | 408 | 19:00
Bibiana | 380 | 00:00 | 365 | 12:00 | Rahanpur | 410 | 01:00 | 400 | 19:30
BIPTC | 399 | 04:00 | 391 | 20:00 | Rampal | 397 | 04:00 | 379 | 12:00
Bogura | 395 | 01:00 | 382 | 21:00
Gopalganj | 392 | 03:00 | 372 | 12:00
Kaliakoir | 365 | 03:00 | 335 | 12:00
Korerhat | 396 | 03:00 | 376 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 03:00 | 207 | 12:00 | Ishurdi | 234 | 01:00 | 218 | 21:00
AKSML | 237 | 01:00 | 224 | 13:00 | Jhenaidah | 226 | 01:00 | 208 | 13:00
Aminbazar | 230 | 03:00 | 210 | 12:00 | Kachua | 229 | 03:00 | 216 | 12:00
Ashuganj | 225 | 05:00 | 210 | 12:00 | Kaliakoir | 228 | 03:00 | 206 | 12:00
Ashuganj-400 | 225 | 5:00 | 210 | 12:00 | Keranigonj | 227 | 01:00 | 205 | 12:00
Baghabari | 231 | 00:00 | 221 | 13:00 | Khulna(S) | 226 | 01:00 | 214 | 13:00
Barapukuria | 223 | 00:00 | 219 | 13:00 | Korerhat | 227 | 03:00 | 215 | 12:00
Barapukuria-230 | 223 | 0:00 | 218 | 14:00 | Madunaghat | 237 | 00:00 | 229 | 12:00
Barishal | 227 | 02:00 | 220 | 12:00 | Madunaghat-400 | 239 | 01:00 | 231 | 13:00
Bheramara | 233 | 01:00 | 216 | 21:00 | Maniknagar | 227 | 03:00 | 202 | 12:00
Bhulta | 229 | 03:00 | 202 | 12:00 | Meghnaghat | 232 | 04:00 | 212 | 13:00
Bibiana | 223 | 03:00 | 212 | 12:00 | Meghnaghat-400 | 230 | 03:00 | 208 | 12:00
BIPTC | 235 | 00:00 | 217 | 19:30 | Mirsorai | 229 | 03:00 | 217 | 12:00
Bogura | 239 | 00:00 | 231 | 13:00 | Naogaon | 224 | 00:00 | 214 | 13:00
Bogura-400 | 238 | 01:00 | 231 | 14:00 | Purbasadipur | 223 | 00:00 | 216 | 13:00
Borhanuddin | 229 | 00:00 | 224 | 14:00 | Rajshahi | 232 | 00:00 | 214 | 13:00
BSRM | 228 | 01:00 | 215 | 12:00 | Rampal | 226 | 01:00 | 214 | 12:00
Charfasson | 230 | 10:00 | 225 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 224 | 00:00 | 215 | 12:00 | Rampura | 228 | 03:00 | 202 | 12:00
Cumilla(N) | 224 | 02:00 | 207 | 12:00 | Shikalbaha | 238 | 01:00 | 229 | 12:00
Faridpur | 223 | 01:00 | 213 | 13:00 | Shyampur | 228 | 03:00 | 205 | 12:00
Fenchuganj | 223 | 01:00 | 215 | 12:00 | Siddhirganj | 225 | 01:00 | 204 | 12:00
Feni | 227 | 03:00 | 212 | 12:00 | Sirajgonj | 236 | 00:00 | 229 | 12:00
Ghorashal | 230 | 01:00 | 215 | 10:00 | Sreepur | 224 | 03:00 | 212 | 12:00
Ghorashal-230 | 222 | 07:00 | 196 | 12:00 | Tongi | 222 | 04:00 | 192 | 11:00
Gopalganj | 223 | 01:00 | 214 | 12:00
GPH | 230 | 00:00 | 223 | 13:00
Haripur | 228 | 03:00 | 204 | 12:00
Hasnabad | 225 | 00:00 | 205 | 12:00
Hathazari | 235 | 03:00 | 225 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 140 | 03:00 | 121 | 12:00 | Madartek | 140 | 03:00 | 120 | 12:00
Agargaon | 139 | 03:00 | 123 | 12:00 | Madunaghat | 137 | 02:00 | 132 | 12:00
Agrabad | 136 | 00:00 | 129 | 12:00 | Magura | 134 | 00:00 | 120 | 19:00
AKS | 133 | 00:00 | 127 | 12:00 | Mahasthangarh | 135 | 00:00 | 129 | 13:00
Aminbazar | 132 | 03:00 | 118 | 11:00 | Maijdee | 128 | 01:00 | 121 | 12:00
Amnura | 137 | 00:00 | 124 | 13:00 | Manikganj | 128 | 03:00 | 120 | 12:00
Ashuganj | 131 | 03:00 | 122 | 12:00 | Maniknagar | 140 | 05:00 | 123 | 10:00
Ashuganj-230 | 133 | 01:00 | 127 | 13:00 | Matarbari | 126 | 09:00 | 114 | 19:30
Bagerhat | 129 | 01:00 | 121 | 19:00 | Matuail | 135.5 | 03:00 | 121 | 13:00
Bajitpur | 126 | 02:00 | 117 | 20:00 | Metrorail_Motijheel | 140 | 04:00 | 123 | 12:00
Bakerganj | 132 | 04:00 | 127 | 19:00 | Metrorail_Uttara | 134 | 04:00 | 125 | 06:00
Bakulia | 137 | 00:00 | 131 | 12:00 | Millgate | 135 | 03:00 | 114 | 12:00
Banani | 140 | 03:00 | 121 | 12:00 | Mirpur | 131 | 01:00 | 115 | 12:00
Bangabhaban | 140 | 03:00 | 123 | 12:00 | Mirzapur | 129 | 06:00 | 120 | 12:00
Barapukuria | 136 | 00:00 | 129 | 12:00 | Mithapukur | 133 | 16:00 | 125 | 14:00
Barguna | 131 | 00:00 | 127 | 19:00 | MI_Cement | 133 | 05:00 | 126 | 09:00
Barishal | 132 | 00:00 | 126 | 13:00 | Modern | N/A | N/A | N/A | N/A
Barishal-230 | 132 | 02:00 | 127 | 13:00 | Mogbazar | 143 | 03:00 | 124 | 12:00
Baroaulia | 136 | 01:00 | 129 | 12:00 | Mongla | 129 | 02:00 | 120 | 19:00
Baroirhat | 131 | 00:00 | 124 | 13:00 | Motijheel | 140 | 03:00 | 123 | 12:00
Bashundhara | 141 | 04:00 | 112 | 12:00 | Muktagacha | 126 | 23:00 | 117 | 19:00
BashundharaCement | 135 | 05:00 | 120 | 12:00 | Munshiganj | 134 | 02:00 | 118 | 12:00
Beanibazar | 124 | 03:00 | 120 | 13:00 | Muradnagar | 131 | 03:00 | 118 | 12:00
Benapole | 130 | 02:00 | 109 | 19:00 | Mymensingh | 126 | 23:00 | 111 | 09:00
Bhaluka | 129 | 18:00 | 122 | 20:00 | Nabinagar | 131 | 01:00 | 114 | 12:00
Bhandaria | 130 | 01:00 | 122 | 13:00 | Naogaon | 135 | 00:00 | 129 | 13:00
Bhangura | 133 | 00:00 | 125 | 13:00 | Narail | 135 | 01:00 | 121 | 13:00
Bheramara | 137 | 00:00 | 126 | 21:00 | Narinda | 140 | 5:00 | 123 | 10:00
Bheramara(GK) | 137 | 00:00 | 126 | 20:00 | Narshingdi | 130 | 01:00 | 114 | 20:00
Bhulta | 128 | 07:00 | 115 | 12:00 | Natore | 135 | 00:00 | 126 | 13:00
Bhulta-400 | 133 | 03:00 | 117 | 12:00 | Nawabganj | 137 | 03:00 | 122 | 12:00
Bog-Sherpur | 135 | 00:00 | 129 | 13:00 | Netrakona | 121 | 02:00 | 107 | 09:00
Bogura | 137 | 18:00 | 132 | 13:00 | New | 134 | 04:00 | 116 | 12:00
Bogura-230 | 138 | 00:00 | 132 | 13:00 | Niamatpur | 136 | 01:00 | 131 | 19:00
Brahmanbaria | 129 | 04:00 | 120 | 20:00 | Noapara | 133 | 01:00 | 125 | 13:00
Cantonment | 138 | 03:00 | 122 | 12:00 | Pabna | 135 | 00:00 | 125 | 20:00
Chandina | 132 | 03:00 | 120 | 12:00 | Palashbari | 131 | 00:00 | 126 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandpur | 135 | 01:00 | 128 | 13:00 | Panchagarh | 135 | 00:00 | 129 | 14:00
Chandraghona | 138 | 00:00 | 133 | 12:00 | Patiya | 136 | 01:00 | 129 | 15:00
Chapai | 136 | 01:00 | 130 | 21:00 | Patnitala | 130 | 05:00 | 123 | 00:00
Charsaidpur | 136 | 03:00 | 121 | 13:00 | Patuakhali | 132 | 00:00 | 128 | 18:30
Chauddagram | 130 | 00:00 | 121 | 12:00 | Payra | 135 | 00:00 | 132 | 19:00
Chhatak | 124 | 01:00 | 118 | 19:00 | PHP | 132 | 01:00 | 124 | 13:00
Chowmuhani | 126 | 00:00 | 121 | 12:00 | Postogola | 135 | 04:00 | 120 | 12:00
Chuadanga | 133 | 00:00 | 117 | 19:00 | Pubail | 131 | 02:00 | 120 | 13:00
Coxsbazar | 128 | 00:00 | 118 | 20:00 | Purbachal | 140 | 03:00 | 121 | 12:00
Cumilla(N) | 130 | 02:00 | 120 | 12:00 | Purbasadipur | 135 | 16:00 | 129 | 13:00
Cumilla(S) | 132 | 05:00 | 121 | 00:00 | Rahanpur | 137 | 00:00 | 133 | 19:00
Daganbhuiyan | 131 | 01:00 | 122 | 12:00 | Rahanpur-400 | 137 | 00:00 | 134 | 12:00
Daudkandi | 129 | 01:00 | 116 | 12:00 | Rahim | 135 | 04:00 | 121 | 12:00
DhakaUniversity | 139 | 03:00 | 120 | 12:00 | Rajbari | 127 | 04:00 | 120 | 13:00
Dhamrai | 130 | 07:00 | 117 | 12:00 | Rajendrapur | 132 | 02:00 | 124 | 14:00
Dhanmondi | 140 | 05:00 | 121 | 12:00 | Rajshahi | 132 | 01:00 | 122 | 13:00
Dohazari | 133 | 01:00 | 124 | 19:30 | Rajshahi-230 | 134 | 01:00 | 123 | 13:00
Faridpur | 129 | 02:00 | 124 | 13:00 | Ramganj | 130 | 01:00 | 122 | 13:00
Fatullah | 136 | 04:00 | 118 | 12:00 | Rampur | 136 | 01:00 | 128 | 14:00
Fenchuganj | 131 | 01:00 | 127 | 12:00 | Rampura | 140 | 03:00 | 122 | 12:00
Feni | 131 | 02:00 | 121 | 12:00 | Rangamati | 137 | 01:00 | 132 | 12:00
Feni-230 | 132 | 03:00 | 123 | 12:00 | Rangpur | 131 | 00:00 | 126 | 12:00
Ghatail | 124 | 23:00 | 116 | 19:00 | Ruppur | 138 | 00:00 | 126 | 21:00
Ghorashal | 131 | 04:00 | 120 | 11:00 | Saidpur | 133 | 16:00 | 128 | 14:00
Goalpara | 136 | 01:00 | 128 | 13:00 | Santhia | 136 | 00:00 | 127 | 19:30
Gollamari | 136 | 01:00 | 127 | 13:00 | Satkhira | 131 | 02:00 | 122 | 19:00
Gopalganj | 132 | 02:00 | 124 | 12:00 | Satmasjid | 138 | 03:00 | 122 | 13:00
Gopalganj-400 | 132 | 01:00 | 126 | 12:00 | Savar | 131 | 00:00 | 115 | 12:00
Gulshan | 136 | 01:00 | 121 | 12:00 | SevenRings | 132 | 01:00 | 120 | 12:00
Halishahar | 137 | 00:00 | 127 | 01:00 | ShahCement | 136 | 03:00 | 121 | 13:00
Haripur | 137 | 03:00 | 122 | 12:00 | Shahjadpur | 136 | 00:00 | 132 | 13:00
HaripurSBU | 134 | 04:00 | 122 | 12:00 | Shahjibazar | 129 | 03:00 | 121 | 13:00
Hasnabad | 135 | 03:00 | 121 | 12:00 | Shahmirpur | 138 | 01:00 | 130 | 15:00
Hathazari | 137 | 00:00 | 131 | 15:00 | Shariatpur | 131 | 02:00 | 125 | 12:00
Hatirjheel | 140 | 03:00 | 121 | 12:00 | Sherpur | 128 | 23:00 | 114 | 02:00
Ishurdi | 138 | 01:00 | 128 | 21:00 | Shikalbaha | 125 | 01:00 | 123 | 00:00
Jaldhaka | 131 | 10:00 | 127 | 13:00 | Shikalbaha-230 | 138 | 00:00 | 132 | 12:00
Jamalpur | 131 | 23:00 | 116 | 02:00 | Shitalakhya | 133 | 05:00 | 118 | 12:00
Jashore | 132 | 08:00 | 113 | 19:00 | Sholosohor | 137 | 00:00 | 130 | 11:00
Jhenaidah | 135 | 04:00 | 120 | 20:00 | Shomvuganj | 123 | 04:00 | 115 | 09:00
Jhenaidah-230 | 138 | 02:00 | 123 | 19:00 | Shyampur | 135 | 05:00 | 122 | 13:00
Joydebpur | 128 | 23:00 | 117 | 12:00 | Shyampur-230 | 137 | 03:00 | 122 | 14:00
Joypurhat | 132 | 00:00 | 125 | 21:00 | Siddhirganj | 136 | 03:00 | 121 | 12:00
Juldah | 137 | 00:00 | 130 | 15:00 | Sirajganj | 131 | 00:00 | 124 | 19:30
Kabirpur | 130 | 03:00 | 112 | 12:00 | Sitakunda | 136 | 00:00 | 130 | 15:00
Kachua | 131 | 00:00 | 124 | 12:00 | Sonargaon | 133 | 04:00 | 119 | 12:00
Kaliakoir | 135 | 01:00 | 121 | 12:00 | Sreemongol | 127 | 01:00 | 121 | 20:00
Kaliganj | 135 | 01:00 | 122 | 19:30 | Sreepur | 135 | 02:00 | 127 | 20:00
Kallyanpur | 129 | 06:00 | 122 | 21:00 | Srinagar | 137 | 01:00 | 122 | 12:00
Kalurghat | 138 | 01:00 | 132 | 12:00 | SSM | 140 | 01:00 | 132 | 12:00
Kamrangirchar | 137 | 01:00 | 113 | 12:00 | Sunamganj | 122 | 01:00 | 116 | 13:00
Kaptai | 139 | 1:00 | 135 | 16:00 | Sylhet | 125 | 05:00 | 122 | 13:00
Kasba | 129 | 01:00 | 117 | 12:00 | Sylhet_(South) | 126 | 02:00 | 122 | 00:00
Kazla | 141 | 04:00 | 122 | 13:00 | Tangail | 126 | 07:00 | 118 | 21:00
Keranigonj | 138 | 03:00 | 124 | 12:00 | Taraganj | 133 | 16:00 | 126 | 00:00
Khagrachori | 137 | 04:00 | 130 | 15:00 | Tasnim | 134 | 03:00 | 118 | 11:00
Khulna | 134 | 00:00 | 126 | 13:00 | Thakurgaon | 136 | 00:00 | 130 | 14:00
Khulna(S) | 136 | 01:00 | 128 | 13:00 | TK | 137 | 00:00 | 132 | 14:00
Khulshi | 136 | 00:00 | 128 | 12:00 | Tongi | 137 | 04:00 | 117 | 11:00
Kishoreganj | 127 | 05:00 | 116 | 20:00 | Ullahpara | 133 | 01:00 | 126 | 13:00
Kodda | 128 | 07:00 | 117 | 12:00 | Ullon | 137 | 01:00 | 120 | 12:00
Korerhat | 134 | 03:00 | 126 | 13:00 | Uttara | 135 | 04:00 | 114 | 12:00
KSRM | 136 | 04:00 | 130 | 12:00 | UttaraNew | 134 | 03:00 | 114 | 12:00
Kulaura | 130 | 01:00 | 126 | 12:00 | Zigatola | 137 | 04:00 | 121 | 13:00
Kurigram | 129 | 00:00 | 123 | 12:00
Kushtia | 134 | 01:00 | 121 | 19:30
Laksam | 132 | 01:00 | 123 | 12:00
Lakshmipur | 127 | 01:00 | 121 | 15:00
Lalbag | 137 | 02:00 | 122 | 13:00
Lalmonirhat | 130 | 01:00 | 123 | 12:00
Madanganj | 135 | 05:00 | 120 | 12:00
Madaripur | 132 | 01:00 | 126 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division