## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-08-2026 | [28 empty] | Date: | 11-08-2026 | [28 empty] | Date: | 11-08-2026 | [28 empty] | Date: | 11-08-2026 | [28 empty] | Date: | 11-08-2026 | [18 empty] | Date: | 11-08-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [18 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 237 | 17 | 0 | 17 | 141 | 32 | 0 | 35 | 108 | 0 | 0 | 299 | 0 | 0 | 35 | 335 | 0 | 0 | 0 | 143.42 | 11 | 0 | 0 | 0 | 95 | 16 | 36 | 0 | 16 | 50 | 21 | 17 | 12 | 12 | 0 | 220 | 107 | 2 | 1125 | 0 | 0 | 50 | 17 | 100 | 194 | 0 | 0 | 0 | 1226 | 0 | 40 | 73 | 0 | 361 | 0 | 51 | 43 | 222 | 39 | 60 | 85 | 183 | 0 | 19 | 105 | 160 | 52.2 | 0 | 31 | 305 | 0 | 228 | 40 | 39 | 143 | 0 | 8 | 0 | 83 | 30 | 95 | 0 | 124 | 17 | 49 | 0 | 47 | 0 | 0 | 0 | 12 | 7929.62 | 868 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 923 | 0 | 0 | 0 | 996.31 | 0 | 39 | 0 | 57 | 70 | 0 | 51 | 22 | 52.2 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 159 | 47 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 180 | 0 | 800 | 890 | 17 | 6248.51 | 14178.13 | 103.73
01:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 308 | 17 | 0 | 17 | 141 | 32 | 0 | 35 | 108 | 0 | 0 | 295 | 0 | 0 | 35 | 329 | 0 | 0 | 0 | 143.42 | 11 | 3 | 0 | 0 | 90 | 16 | 20 | 0 | 9 | 50 | 21 | 0 | 12 | 12 | 0 | 218 | 103 | 2 | 1125 | 0 | 0 | 50 | 0 | 93 | 194 | 0 | 0 | 0 | 1230 | 0 | 40 | 73 | 0 | 360 | 0 | 51 | 44 | 221 | 39 | 52 | 85 | 174 | 0 | 19 | 104 | 160 | 8 | 0 | 31 | 300 | 0 | 227 | 40 | 39 | 133 | 0 | 8 | 0 | 55 | 28 | 95 | 0 | 124 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7777.42 | 902 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 991 | 0 | 0 | 0 | 908.35 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 22 | 52.2 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 157 | 46 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 799 | 880 | 17 | 6081.55 | 13858.97 | 103.74
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 308 | 0 | 0 | 17 | 141 | 32 | 0 | 35 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 143.42 | 11 | 22 | 0 | 0 | 94 | 16 | 19 | 0 | 16 | 50 | 21 | 0 | 12 | 12 | 0 | 219 | 92 | 2 | 1125 | 0 | 0 | 50 | 0 | 89 | 195 | 0 | 0 | 0 | 1229 | 0 | 38 | 73 | 0 | 361 | 0 | 51 | 45 | 203 | 39 | 43 | 85 | 180 | 0 | 19 | 103 | 162 | 8 | 0 | 31 | 310 | 0 | 266 | 40 | 39 | 141 | 0 | 8 | 0 | 55 | 25 | 95 | 0 | 124 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7594.42 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1024 | 0 | 0 | 0 | 914.43 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 15 | 52.2 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 160 | 47 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 800 | 880 | 17 | 6162.63 | 13757.05 | 103.75
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 303 | 0 | 31 | 17 | 142 | 32 | 0 | 35 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 97 | 16 | 19 | 0 | 22 | 0 | 21 | 0 | 12 | 12 | 0 | 219 | 94 | 0 | 1125 | 0 | 0 | 50 | 0 | 90 | 195 | 0 | 0 | 0 | 1227 | 0 | 40 | 73 | 0 | 360 | 0 | 51 | 46 | 196 | 39 | 0 | 85 | 185 | 0 | 19 | 105 | 162 | 8 | 0 | 31 | 305 | 0 | 292 | 40 | 39 | 142 | 0 | 8 | 0 | 55 | 25 | 93 | 0 | 124 | 17 | 49 | 0 | 47 | 0 | 0 | 0 | 0 | 7547.42 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1022 | 0 | 0 | 0 | 910.01 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 15 | 52.2 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 160 | 47 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 797 | 880 | 17 | 6139.21 | 13686.63 | 103.76
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 308 | 0 | 35 | 17 | 142 | 32 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 89 | 16 | 19 | 0 | 9 | 0 | 21 | 0 | 12 | 12 | 0 | 221 | 93 | 2 | 1125 | 0 | 0 | 50 | 0 | 89 | 195 | 0 | 0 | 0 | 1226 | 0 | 40 | 73 | 0 | 360 | 0 | 51 | 46 | 202 | 39 | 0 | 85 | 180 | 0 | 19 | 104 | 160 | 8 | 0 | 31 | 300 | 0 | 299 | 40 | 39 | 132 | 0 | 8 | 0 | 55 | 25 | 93 | 0 | 124 | 17 | 49 | 0 | 47 | 0 | 0 | 0 | 0 | 7479.42 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1024 | 0 | 0 | 0 | 913.01 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 15 | 52.2 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 158 | 47 | 95 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 764 | 880 | 17 | 6113.21 | 13592.63 | 103.77
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 313 | 0 | 35 | 17 | 142 | 32 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 143.42 | 11 | 21 | 0 | 0 | 90 | 16 | 18 | 0 | 15 | 0 | 21 | 0 | 12 | 12 | 0 | 222 | 94 | 2 | 1125 | 0 | 0 | 50 | 0 | 90 | 195 | 0 | 0 | 0 | 1227 | 0 | 40 | 73 | 0 | 359 | 0 | 51 | 46 | 208 | 39 | 0 | 85 | 180 | 0 | 19 | 104 | 154 | 8 | 0 | 31 | 305 | 0 | 305 | 40 | 39 | 136 | 0 | 8 | 0 | 55 | 28 | 93 | 0 | 121 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 0 | 7499.42 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1026 | 0 | 0 | 0 | 831.57 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 158 | 47 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 115 | 220 | 0 | 800 | 880 | 17 | 6019.77 | 13519.19 | 103.78
06:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 267 | 0 | 35 | 17 | 142 | 32 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 143.42 | 10.5 | 21 | 0 | 0 | 95 | 16 | 19 | 0 | 23 | 0 | 21 | 0 | 12 | 12 | 0.06 | 222 | 92 | 9 | 1125 | 0 | 0 | 50 | 0 | 89 | 195 | 0 | 0 | 0 | 1227 | 0 | 40 | 73 | 0 | 360 | 0 | 51 | 46 | 205 | 39 | 0 | 85 | 183 | 0 | 19 | 93 | 150 | 8 | 3 | 31 | 305 | 0 | 305 | 40 | 39 | 138 | 0 | 8 | 0 | 55 | 28 | 95 | 0 | 121 | 17 | 49 | 0.1 | 48 | 0 | 0 | 0.21 | 0 | 7274.29 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 2 | 1028 | 0 | 0 | 0 | 838.81 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 0.01 | 0 | 0 | 0 | 0.64 | 169 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.07 | 158 | 46 | 95 | 0 | 0 | 0 | 0 | 0 | 0.2 | 1 | 0.01 | 0 | 307 | 115 | 180 | 0 | 783 | 880 | 17 | 5951.94 | 13226.23 | 103.79
07:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 334 | 0 | 35 | 17 | 142 | 32 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 326 | 0 | 0 | 3 | 143.42 | 10 | 0 | 0 | 0 | 95 | 16 | 19 | 0 | 17 | 0 | 21 | 0 | 12 | 12 | 0.65 | 222 | 93 | 0 | 1125 | 0 | 0 | 50 | 0 | 90 | 196 | 0 | 0 | 0 | 1224 | 4 | 40 | 73 | 0 | 360 | 0 | 51 | 45 | 215 | 39 | 0 | 85 | 186 | 0 | 19 | 34 | 150 | 8 | 16 | 31 | 315 | 0 | 250 | 40 | 39 | 142 | 2 | 8 | 0 | 55 | 25 | 95 | 0 | 121 | 17 | 49 | 4 | 48 | 0 | 0.1 | 3.79 | 0 | 7325.96 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 34 | 1029 | 0 | 0 | 0 | 828.47 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 52.2 | 2.76 | 4 | 0 | 0 | 5.65 | 169 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0.63 | 159 | 46 | 95 | 6 | 0 | 0 | 0 | 0 | 1.8 | 16 | 0.22 | 0 | 307 | 115 | 220 | 0 | 800 | 880 | 17 | 6086.73 | 13412.69 | 103.8
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 329 | 0 | 35 | 17 | 143 | 32 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 322 | 0 | 0 | 9 | 143.42 | 10 | 21 | 0 | 0 | 91 | 16 | 18 | 0 | 16 | 0 | 21 | 0 | 12 | 12 | 2.49 | 222 | 93 | 0 | 1125 | 0 | 0 | 46 | 0 | 88 | 195 | 0 | 0 | 0 | 1224 | 10 | 40 | 73 | 0 | 358 | 0 | 51 | 46 | 211 | 36 | 0 | 85 | 183 | 0 | 19 | 17 | 148 | 8 | 38 | 31 | 305 | 0 | 305 | 40 | 39 | 136 | 6 | 8 | 0 | 57 | 30 | 0 | 0 | 122 | 17 | 49 | 6.3 | 48 | 0 | 0.6 | 14.22 | 0 | 7344.03 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 30 | 1029 | 0 | 0 | 0 | 831.15 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11.07 | 20 | 0 | 0 | 13.67 | 150 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0.68 | 159 | 47 | 95 | 14 | 0 | 0 | 0 | 0 | 3.8 | 39 | 0.28 | 0 | 307 | 115 | 180 | 0 | 787 | 880 | 17 | 5992.65 | 13336.68 | 103.81
09:00 | 0 | 45 | 25 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 224 | 0 | 35 | 17 | 143 | 32 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 326 | 0 | 0 | 13 | 143.42 | 10 | 21 | 0 | 0 | 94 | 16 | 19 | 0 | 28 | 0 | 21 | 0 | 12 | 12 | 3.17 | 222 | 92 | 0 | 1125 | 0 | 0 | 44 | 0 | 89 | 210 | 0 | 0 | 0 | 1160 | 15 | 38 | 71 | 0 | 360 | 0 | 51 | 45 | 192 | 39 | 0 | 85 | 185 | 0 | 19 | 17 | 158 | 8 | 53 | 31 | 300 | 0 | 305 | 40 | 39 | 143 | 11 | 8 | 0 | 74 | 30 | 0 | 0 | 122 | 17 | 49 | 11 | 48 | 0 | 1 | 32.77 | 0 | 7334.36 | 893 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 81 | 1026 | 0 | 0 | 0 | 825.58 | 0 | 40 | 0 | 0 | 2 | 0 | 0 | 0 | 8 | 23.69 | 48 | 0 | 0 | 35.84 | 168 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 2.04 | 157 | 47 | 95 | 7 | 0 | 0 | 0 | 0 | 5.5 | 78 | 0.59 | 0 | 307 | 115 | 220 | 0 | 765 | 880 | 17 | 6191.24 | 13525.6 | 103.83
10:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 281 | 0 | 35 | 17 | 142 | 32 | 0 | 17 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 320 | 0 | 0 | 25 | 143.42 | 10 | 21 | 0 | 0 | 89 | 16 | 18 | 0 | 22 | 0 | 21 | 0 | 12 | 12 | 3.78 | 222 | 98 | 0 | 1125 | 0 | 0 | 41 | 0 | 90 | 218 | 0 | 0 | 0 | 1150 | 19 | 31 | 71 | 0 | 320 | 0 | 43 | 45 | 196 | 30 | 0 | 85 | 180 | 0 | 19 | 17 | 160 | 8 | 65 | 23 | 305 | 0 | 281 | 40 | 39 | 140 | 9 | 8 | 0 | 80 | 30 | 0 | 0 | 122 | 17 | 77 | 15.64 | 95 | 0 | 1 | 47.93 | 0 | 7482.77 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 24.21 | 1024 | 0 | 0 | 0 | 931.82 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 46.1 | 50 | 0 | 0 | 54.17 | 168 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 4.94 | 156 | 47 | 95 | 10 | 0 | 0 | 0 | 0 | 6.9 | 91 | 0.56 | 0 | 274 | 115 | 180 | 0 | 792 | 870 | 17 | 6229.7 | 13712.47 | 103.85
11:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 331 | 0 | 35 | 17 | 141 | 32 | 0 | 35 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 320 | 0 | 0 | 28 | 143.42 | 10 | 21 | 0 | 0 | 90 | 16 | 19 | 0 | 17 | 0 | 15 | 0 | 12 | 12 | 4.52 | 221 | 93 | 0 | 1125 | 0 | 0 | 44 | 0 | 89 | 214 | 0 | 0 | 0 | 1160 | 20 | 23 | 71 | 0 | 344 | 0 | 51 | 44 | 209 | 36 | 12 | 86 | 184 | 0 | 17 | 17 | 170 | 8 | 71 | 23 | 310 | 0 | 266 | 39 | 39 | 148 | 12 | 8 | 0 | 80 | 30 | 0 | 0 | 122 | 17 | 78 | 15 | 97 | 0 | 2.4 | 49.98 | 0 | 7632.32 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 100 | 955 | 0 | 0 | 0 | 926.05 | 0 | 39 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 44.58 | 104 | 0 | 0 | 59.19 | 161 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 3.34 | 160 | 47 | 95 | 16 | 0 | 0 | 0 | 0 | 7.2 | 109 | 0.51 | 0 | 279 | 115 | 220 | 0 | 800 | 860 | 17 | 6390.87 | 14023.19 | 103.87
12:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 295 | 0 | 35 | 17 | 140 | 32 | 0 | 35 | 17 | 0 | 0 | 296 | 0 | 0 | 17 | 320 | 0 | 0 | 29 | 143.42 | 10 | 21 | 0 | 0 | 90 | 16 | 19 | 0 | 32 | 0 | 22 | 17 | 12 | 12 | 5.12 | 219 | 92 | 0 | 1125 | 0 | 0 | 44 | 5 | 88 | 215 | 0 | 0 | 0 | 1140 | 9 | 18 | 118 | 0 | 354 | 0 | 51 | 44 | 194 | 32 | 34 | 86 | 184 | 0 | 19 | 45 | 178 | 8 | 73 | 31 | 310 | 0 | 236 | 41 | 39 | 152 | 12 | 8 | 0 | 82 | 30 | 0 | 0 | 122 | 17 | 77 | 22.25 | 94 | 0 | 2.5 | 53.88 | 0 | 7725.17 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 103 | 926 | 0 | 0 | 0 | 934.71 | 0 | 38 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 39.97 | 66 | 0 | 0 | 36.04 | 157 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 5.48 | 159 | 47 | 95 | 34 | 0 | 0 | 0 | 0 | 4.4 | 189 | 0.21 | 0 | 272 | 115 | 220 | 0 | 795 | 872 | 17 | 6389.81 | 14114.98 | 103.89
13:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 230 | 17 | 35 | 17 | 140 | 32 | 0 | 35 | 17 | 0 | 0 | 297 | 0 | 0 | 35 | 320 | 96 | 0 | 25 | 143.42 | 10 | 21 | 0 | 0 | 90 | 16 | 19 | 0 | 24 | 0 | 22 | 17 | 12 | 12 | 3.1 | 218 | 92 | 0 | 1125 | 0 | 0 | 44 | 8 | 100 | 200 | 0 | 0 | 0 | 1160 | 0 | 16 | 177 | 0 | 354 | 0 | 51 | 42 | 200 | 37 | 34 | 86 | 181 | 0 | 14 | 106 | 190 | 8 | 70 | 31 | 315 | 0 | 236 | 41 | 39 | 141 | 11 | 8 | 0 | 82 | 30 | 0 | 0 | 122 | 17 | 68 | 20 | 105 | 0 | 2.2 | 50.56 | 0 | 7819.28 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 101 | 925 | 0 | 0 | 0 | 934.05 | 0 | 38 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 57.36 | 91 | 0 | 0 | 60.8 | 152 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 5.55 | 159 | 47 | 95 | 34 | 0 | 0 | 0 | 0 | 5.1 | 205 | 0.78 | 0 | 307 | 115 | 220 | 0 | 755 | 876 | 17 | 6432.64 | 14251.92 | 103.9
14:00 | 0 | 18 | 8 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 265 | 17 | 35 | 17 | 142 | 32 | 0 | 35 | 17 | 0 | 0 | 301 | 0 | 0 | 35 | 312 | 133 | 0 | 25 | 143.42 | 10 | 21 | 0 | 0 | 91 | 16 | 19 | 0 | 16 | 0 | 22 | 17 | 12 | 12 | 3.85 | 218 | 91 | 0 | 1125 | 0 | 0 | 44 | 8 | 94 | 201 | 0 | 0 | 0 | 1180 | 18 | 20 | 187 | 0 | 351 | 0 | 51 | 41 | 185 | 37 | 34 | 85 | 181 | 0 | 19 | 106 | 182 | 16 | 63 | 35 | 305 | 0 | 236 | 40 | 38 | 145 | 11 | 8 | 0 | 82 | 30 | 0 | 0 | 122 | 17 | 58 | 20.17 | 114 | 0 | 2.1 | 41.98 | 0 | 7740.52 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 95 | 925 | 0 | 0 | 0 | 942.13 | 0 | 38 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 51.91 | 97 | 0 | 0 | 54.56 | 151 | 0 | 0 | 0 | 0 | 0 | 264 | 0 | 4.99 | 160 | 47 | 95 | 27 | 0 | 12 | 0 | 0 | 7.9 | 165 | 0.73 | 0 | 307 | 115 | 220 | 0 | 758 | 875 | 17 | 6412.22 | 14152.74 | 103.91
15:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 290 | 17 | 35 | 17 | 140 | 32 | 0 | 35 | 17 | 0 | 0 | 299 | 0 | 0 | 35 | 314 | 134 | 0 | 21 | 143.42 | 10 | 21 | 0 | 0 | 89 | 16 | 18 | 0 | 36 | 0 | 22 | 17 | 12 | 12 | 3.4 | 218 | 92 | 0 | 1125 | 0 | 0 | 44 | 8 | 95 | 205 | 0 | 0 | 0 | 1190 | 16 | 20 | 187 | 0 | 342 | 0 | 51 | 40 | 156 | 37 | 33 | 85 | 183 | 0 | 19 | 104 | 186 | 16 | 51 | 36 | 310 | 0 | 230 | 40 | 38 | 146 | 9 | 8 | 0 | 82 | 30 | 0 | 0 | 122 | 17 | 58 | 10.25 | 114 | 0 | 1.7 | 32.36 | 0 | 7666.13 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 77 | 925 | 0 | 0 | 0 | 943.03 | 0 | 38 | 0 | 0 | 35 | 0 | 8.5 | 0 | 8 | 42.46 | 85 | 0 | 0 | 43.54 | 151 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 2.83 | 160 | 46 | 95 | 26 | 0 | 0 | 0 | 0 | 6.4 | 105 | 0.57 | 0 | 307 | 113 | 220 | 0 | 800 | 875 | 17 | 6323.33 | 13989.46 | 103.92
16:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 300 | 17 | 35 | 17 | 141 | 32 | 0 | 35 | 17 | 0 | 0 | 280 | 0 | 0 | 35 | 315 | 75 | 0 | 15 | 143.42 | 9 | 21 | 0 | 0 | 90 | 16 | 19 | 0 | 33 | 0 | 22 | 17 | 12 | 12 | 2.22 | 218 | 97 | 0 | 1125 | 0 | 0 | 44 | 8 | 94 | 210 | 0 | 0 | 0 | 1160 | 0 | 20 | 155 | 0 | 355 | 0 | 51 | 27 | 215 | 30 | 44 | 85 | 179 | 0 | 14 | 104 | 192 | 16 | 35 | 44 | 310 | 0 | 265 | 40 | 38 | 139 | 6 | 8 | 0 | 82 | 30 | 40 | 18 | 123 | 17 | 58 | 11 | 114 | 0 | 1 | 22.35 | 0 | 7702.99 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 56 | 925 | 0 | 0 | 0 | 898.15 | 0 | 38 | 0 | 0 | 35 | 0 | 8.5 | 0 | 8 | 28.87 | 61 | 0 | 0 | 30.65 | 151 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 1.59 | 160 | 45 | 95 | 18 | 12 | 0 | 0 | 0 | 4.5 | 55 | 0.4 | 0 | 307 | 110 | 220 | 0 | 746 | 885 | 35 | 6113.66 | 13816.65 | 103.93
17:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 275 | 17 | 35 | 19 | 141 | 32 | 0 | 35 | 35 | 0 | 0 | 282 | 0 | 0 | 35 | 315 | 37 | 0 | 8 | 143.42 | 9 | 21 | 0 | 0 | 87 | 16 | 19 | 0 | 40 | 0 | 22 | 17 | 12 | 12 | 0.33 | 218 | 92 | 0 | 1080 | 0 | 0 | 44 | 8 | 92 | 210 | 0 | 0 | 0 | 1140 | 1 | 22 | 110 | 0 | 320 | 80 | 51 | 20 | 127 | 30 | 48 | 85 | 172 | 7 | 19 | 103 | 184 | 16 | 18 | 44 | 300 | 0 | 350 | 40 | 38 | 125 | 3 | 8 | 0 | 82 | 30 | 95 | 16 | 123 | 17 | 58 | 6.33 | 114 | 0 | 0.5 | 10.69 | 8 | 7773.27 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 31 | 925 | 0 | 0 | 0 | 934.73 | 0 | 38 | 0 | 35 | 35 | 0 | 8.5 | 0 | 8 | 12.59 | 29 | 0 | 0 | 12.48 | 151 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 1.26 | 159 | 45 | 75 | 9 | 78 | 0 | 0 | 0 | 2.5 | 72 | 0.12 | 8 | 274 | 110 | 180 | 0 | 744 | 885 | 35 | 6045.18 | 13818.45 | 103.94
18:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 310 | 17 | 35 | 28 | 140 | 32 | 0 | 35 | 35 | 0 | 0 | 300 | 0 | 0 | 35 | 314 | 0 | 0 | 1 | 143.42 | 9 | 21 | 0 | 0 | 92 | 16 | 37 | 0 | 38 | 0 | 22 | 17 | 12 | 12 | 0.05 | 219 | 91 | 0 | 1040 | 0 | 0 | 44 | 8 | 91 | 207 | 0 | 0 | 0 | 1160 | 1 | 35 | 8 | 0 | 290 | 80 | 51 | 11 | 212 | 30 | 69 | 85 | 180 | 26 | 19 | 104 | 174 | 16 | 2 | 37 | 310 | 0 | 350 | 40 | 37 | 137 | 0 | 8 | 0 | 79 | 30 | 96 | 0 | 123 | 17 | 58 | 0.69 | 114 | 0 | 0.1 | 1.69 | 12 | 7807.95 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 60 | 6 | 925 | 0 | 0 | 0 | 1137.16 | 0 | 38 | 0 | 54 | 47 | 0 | 17 | 0 | 8 | 2.2 | 5 | 0 | 0 | 1.8 | 150 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0.1 | 159 | 46 | 75 | 2 | 90 | 0 | 0 | 0 | 0.6 | 12 | 0 | 16 | 273 | 110 | 220 | 0 | 799 | 880 | 17 | 6297.86 | 14105.81 | 103.95
19:00 | 0 | 105 | 41 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 317 | 20 | 35 | 17 | 140 | 32 | 0 | 35 | 108 | 0 | 0 | 301 | 0 | 0 | 35 | 314 | 0 | 0 | 0 | 143.42 | 9 | 21 | 0 | 0 | 96 | 16 | 49 | 0 | 40 | 50 | 22 | 17 | 12 | 12 | 0 | 220 | 105 | 0 | 1125 | 35 | 0 | 49 | 17 | 94 | 159 | 0 | 0 | 0 | 1161 | 0 | 78 | 8 | 0 | 351 | 80 | 51 | 5 | 213 | 30 | 72 | 85 | 184 | 26 | 19 | 104 | 134 | 16 | 0 | 37 | 305 | 0 | 350 | 40 | 39 | 144 | 0 | 8 | 0 | 80 | 30 | 94 | 0 | 123 | 17 | 58 | 0 | 123 | 0 | 0 | 0 | 12 | 8218.42 | 874 | 0 | 0 | 21 | 0 | 38 | 0 | 0 | 50 | 0 | 67 | 0 | 925 | 0 | 0 | 0 | 1283.58 | 0 | 38 | 0 | 57 | 70 | 0 | 50 | 20 | 8 | 0 | 0 | 20 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 159 | 46 | 75 | 0 | 92 | 0 | 130 | 0 | 0 | 0 | 0 | 16 | 307 | 113 | 220 | 0 | 1050 | 880 | 17 | 7005.58 | 15224 | 103.96
19:30 | 0 | 105 | 41 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 221 | 54 | 35 | 17 | 140 | 32 | 0 | 35 | 162 | 0 | 0 | 281 | 0 | 0 | 35 | 317 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 0 | 90 | 16 | 45 | 0 | 46 | 50 | 22 | 17 | 12 | 12 | 0 | 222 | 101 | 0 | 1125 | 150 | 0 | 50 | 17 | 92 | 154 | 0 | 0 | 0 | 1160 | 0 | 100 | 8 | 0 | 320 | 80 | 51 | 5 | 215 | 30 | 85 | 85 | 176 | 27 | 19 | 105 | 130 | 25 | 0 | 37 | 305 | 0 | 304 | 40 | 38 | 136 | 0 | 8 | 0 | 82 | 30 | 95 | 0 | 123 | 17 | 68 | 0 | 152 | 0 | 0 | 0 | 12 | 8280.42 | 873 | 0 | 0 | 27 | 0 | 38 | 0 | 0 | 154 | 0 | 67 | 0 | 918 | 0 | 0 | 0 | 1276.78 | 0 | 38 | 0 | 57 | 70 | 0 | 50 | 29 | 8 | 0 | 0 | 20 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 156 | 46 | 75 | 0 | 92 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 180 | 0 | 1048 | 870 | 17 | 7076.78 | 15357.2
20:00 | 0 | 105 | 41 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 312 | 54 | 35 | 17 | 142 | 32 | 0 | 17 | 150 | 0 | 0 | 303 | 0 | 0 | 35 | 318 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 0 | 87 | 16 | 47 | 0 | 49 | 50 | 22 | 24 | 12 | 12 | 0 | 222 | 103 | 0 | 1125 | 150 | 0 | 50 | 17 | 94 | 155 | 0 | 0 | 0 | 1160 | 0 | 122 | 8 | 0 | 320 | 80 | 51 | 5 | 215 | 30 | 84 | 85 | 175 | 26 | 19 | 87 | 96 | 43 | 0 | 29 | 305 | 0 | 350 | 40 | 38 | 131 | 0 | 8 | 0 | 80 | 30 | 95 | 0 | 124 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 16 | 8409.42 | 874 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 150 | 0 | 67 | 0 | 916 | 0 | 0 | 0 | 1272.9 | 0 | 38 | 0 | 57 | 70 | 0 | 70 | 31 | 8 | 0 | 0 | 20 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 156 | 46 | 75 | 0 | 92 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 180 | 0 | 1022 | 860 | 17 | 7047.9 | 15457.32 | 103.97
21:00 | 0 | 105 | 41 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 308 | 54 | 35 | 17 | 142 | 32 | 0 | 17 | 159 | 0 | 0 | 301 | 0 | 0 | 35 | 319 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 0 | 95 | 16 | 45 | 0 | 30 | 36 | 22 | 54.36 | 12 | 12 | 0 | 222 | 101 | 0 | 1125 | 150 | 0 | 50 | 17 | 93 | 155 | 0 | 0 | 0 | 1224 | 0 | 150 | 8 | 0 | 354 | 100 | 51 | 5 | 216 | 30 | 88 | 85 | 181 | 27 | 19 | 105 | 100 | 43 | 0 | 29 | 310 | 0 | 348 | 40 | 38 | 143 | 0 | 8 | 0 | 81 | 28 | 95 | 0 | 123 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 24 | 8603.78 | 874 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 233 | 0 | 67 | 0 | 920 | 0 | 0 | 0 | 1280.59 | 0 | 38 | 0 | 57 | 70 | 0 | 100 | 28 | 8 | 0 | 0 | 20 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 159 | 46 | 75 | 0 | 92 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 115 | 220 | 0 | 1025 | 860 | 17 | 7229.59 | 15833.37 | 103.98
22:00 | 0 | 105 | 41 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 306 | 35 | 35 | 17 | 142 | 32 | 0 | 35 | 149 | 0 | 0 | 301 | 0 | 0 | 17 | 323 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 0 | 89 | 16 | 47 | 0 | 53 | 50 | 22 | 54.36 | 12 | 12 | 0 | 222 | 101 | 2 | 1125 | 142 | 0 | 50 | 17 | 94 | 153 | 0 | 0 | 0 | 1224 | 0 | 135 | 8 | 0 | 355 | 120 | 51 | 5 | 199 | 30 | 71 | 85 | 178 | 27 | 19 | 105 | 114 | 52.2 | 0 | 29 | 300 | 0 | 348 | 40 | 38 | 132 | 0 | 8 | 0 | 81 | 28 | 96 | 0 | 123 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 24 | 8567.98 | 874 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 234 | 0 | 67 | 0 | 925 | 0 | 0 | 0 | 1283.04 | 0 | 38 | 0 | 57 | 70 | 0 | 100 | 28 | 8 | 0 | 0 | 20 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 159 | 45 | 95 | 0 | 92 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1050 | 860 | 17 | 7265.04 | 15833.02 | 103.99
23:00 | 0 | 105 | 41 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 309 | 17 | 35 | 17 | 142 | 32 | 0 | 35 | 154 | 0 | 0 | 301 | 0 | 0 | 17 | 318 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 0 | 92 | 16 | 44 | 0 | 27 | 50 | 22 | 17 | 12 | 12 | 0 | 222 | 102 | 3 | 1125 | 16 | 0 | 50 | 17 | 93 | 153 | 0 | 0 | 0 | 1224 | 0 | 45 | 8 | 0 | 355 | 120 | 51 | 5 | 194 | 30 | 56 | 85 | 182 | 26 | 19 | 106 | 114 | 52.2 | 0 | 29 | 310 | 0 | 348 | 40 | 39 | 143 | 0 | 0 | 0 | 81 | 28 | 94 | 0 | 124 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 24 | 8274.62 | 874 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 234 | 0 | 67 | 0 | 925 | 0 | 0 | 0 | 1282.57 | 0 | 39 | 0 | 57 | 70 | 0 | 100 | 28 | 8 | 0 | 0 | 12 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 158 | 45 | 95 | 0 | 92 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1050 | 865 | 17 | 7261.57 | 15536.19 | 104
Total KWH | 0 | 1359360 | 511200 | 0 | 0 | 0 | 0 | 0 | 6436800 | 0 | 7357890 | 327240 | 789840 | 438336 | 3384480 | 779575 | 0 | 540182 | 1104480 | 0 | 0 | 7181353 | 0 | 0 | 400732 | 7722358 | 502000 | 0 | 192556 | 3489600 | 241200 | 448200 | 0 | 0 | 2206745 | 363818 | 640320 | 0 | 615360 | 378555 | 610216 | 335515 | 294720 | 290880 | 28320 | 5301765 | 2328400 | 22560 | 26887272.73 | 563709 | 0 | 1142880 | 154436.4 | 2245636 | 4632974 | 0 | 0 | 0 | 28669088 | 108945 | 1105672 | 1856727 | 0 | 8678000 | 730000 | 1167623 | 755520 | 4914000 | 844344 | 841920 | 2046346 | 4355520 | 170520 | 439410 | 2012100 | 3710400 | 435278 | 557018 | 764416 | 7419000 | 0 | 7178000 | 926000 | 913800 | 3364690.91 | 86998 | 183792 | 0 | 1713600 | 674880 | 1492000 | 31000 | 2733000 | 432000 | 1404000 | 134697 | 2172000 | 0 | 13800 | 328560 | 148800 | 187764929.04 | 21564364 | 0 | 0 | 142080 | 0 | 912000 | 0 | 0 | 825491 | 0 | 453456 | 735120 | 23120000 | 0 | 0 | 0 | 23819273 | 0 | 936254 | 0 | 398400 | 821280 | 0 | 539536 | 199617 | 510053 | 376448 | 682430 | 78035 | 0 | 396000 | 3822182 | 0 | 0 | 0 | 0 | 0 | 6513600 | 0 | 33660 | 3927000 | 1073890 | 2189836 | 199869 | 835411 | 0 | 740565 | 0 | 52055.52 | 1172160 | 4887 | 150624 | 7200000 | 2693000 | 5277770 | 0 | 20276364 | 21472000 | 450000 | 154594710.52 | 342359639.56

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-08-2026 | during | 12-08-2026 | during | 12-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 275 | 338 | 412 | 412 | 400 | 400 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 296 | 301 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 319 | 335 | 335 | 330 | 330 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 0 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 140 | 142 | 149.36 | 149.36 | 125 | 125 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 17 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 10 | 10 | 33 | 33 | 12 | 12 | Gas shortage
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 22 | 22 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 41 | 52.19 | 52.19 | 33 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 32 | 300 | 300 | 81 | 81 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 17 | 149 | 149 | 17 | 17 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 88 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 159 | 162 | 162 | 17 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 400 | 400 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 295 | 308 | 718 | 718 | 334 | 334 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1795.42 | 2077.42 | 5625.16 | 5595.16 | 2402.92 | 2605.92
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 5 | 17 | 25.5 | 25.5 | 25 | 25 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 222 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 155 | 140 | 140 | 140 | 140 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 88 | 93 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 22 | 22 | 24 | 24 | 24 | 24 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 36 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 25 | 32 | 25 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 19 | 45 | 108 | 108 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 5.12 | 0 | 4.58 | 0 | 4.58 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 92 | 101 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 95 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 0 | 150 | 163 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1140 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 32 | 30 | 25 | 32 | 25 | 32 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 1125 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4898.863 | 3162.12 | 3459.36 | 4065.44 | 4106.86 | 3286.58 | 3380
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 194 | 216 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 354 | 354 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 100 | 342.01 | 342.01 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 32 | 30 | 41.65 | 41.65 | 40 | 40 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 44 | 5 | 52.82 | 52.82 | 46 | 46 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 118 | 8 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 18 | 150 | 150 | 150 | 50 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 31 | 29 | 40 | 40 | 40 | 40 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 86 | 85 | 163 | 163 | 86 | 86 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 184 | 181 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 178 | 100 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 45 | 105 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 27 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 88 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 73 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1469 | 1591 | 2762.44 | 2696.44 | 1681.46 | 1787.46
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-08-2026 | during | 12-08-2026 | during | 12-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 22.25 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.5 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 94 | 153 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 77 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 53.88 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 266.63 | 262 | 536.6 | 516.5 | 267.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 40 | 41 | 41 | 40 | 40 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 38 | 40 | 40 | 40 | 40 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 143 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 95 | 165 | 165 | 0 | 0 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 28 | 30 | 30 | 0 | 0 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 81 | 84 | 86 | 84 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 122 | 123 | 120 | 120 | 120 | 120 | plant availability zero
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 236 | 348 | 250 | 260 | 250 | 260 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1032 | 1214 | 1242 | 1254 | 996 | 1008
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 901 | 874 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 23 | 30 | 30 | 30 | 30 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 67 | 105 | 105 | 35 | 35 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 103 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 233 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 926 | 920 | 925 | 925 | 1234.2 | 1234.2 | AGC+FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1968 | 2155 | 3240 | 3175 | 2402.2 | 2337.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 795 | 1025 | 1000 | 1050 | 800 | 1050 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 130 | 130 | 115 | 115 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 872 | 860 | 916.5 | 916.5 | 916.5 | 916.5 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 272 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.21 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2291.21 | 2560 | 2834.5 | 2883.5 | 2392.5 | 2641.5
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 39.97 | 0 | 48.25 | 0 | 48.25 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 38 | 38 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 157 | 146 | 214 | 214 | 170 | 170 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 282 | 230 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 14 | 14 | 14 | 14 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 50 | 50 | Engine Problem
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 57 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.48 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 934.71 | 1280.59 | 1469.13 | 1469.13 | 950 | 950 | Problem with coal feeding system
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 36.04 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 66 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1602.2 | 1977.59 | 3247.87 | 3033.12 | 1921.16 | 1771.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 47 | 46 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 159 | 159 | 165 | 165 | 165 | 165 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 92 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.4 | 0 | 3 | 0 | 3 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 75 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 189 | 0 | 158.51 | 0 | 158.51 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 528.4 | 537 | 668.51 | 477 | 555.51 | 399
System Total |  |  |  |  | 28843.2 | 29171.687 | 14114.98 | 15833.37 | 24222.52 | 23737.58 | 15905.43 | 16189.49
Forecast Scenario (12-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14380 |  | 4221.1 |  | 18800
|  |  |  | 1:00 | 14060 |  | 4049.2 |  | 18300
|  |  |  | 2:00 | 13960 |  | 3915.5 |  | 18060
|  |  |  | 3:00 | 13890 |  | 3781.8 |  | 17850
|  |  |  | 4:00 | 13800 |  | 3705.4 |  | 17680
|  |  |  | 5:00 | 13720 |  | 3629 |  | 17520
|  |  |  | 6:00 | 13330 |  | 3466.65 |  | 16960
|  |  |  | 7:00 | 13520 |  | 3199.25 |  | 16870
|  |  |  | 8:00 | 13440 |  | 3342.5 |  | 16940
|  |  |  | 9:00 | 13630 |  | 3180.15 |  | 16960
|  |  |  | 10:00 | 13820 |  | 3141.95 |  | 17110
|  |  |  | 11:00 | 14130 |  | 2769.5 |  | 17030
|  |  |  | 12:00 | 14220 |  | 3313.85 |  | 17690
|  |  |  | 13:00 | 14360 |  | 3227.9 |  | 17740
|  |  |  | 14:00 | 14260 |  | 3247 |  | 17660
|  |  |  | 15:00 | 14090 |  | 3600.35 |  | 17860
|  |  |  | 16:00 | 13920 |  | 3600.35 |  | 17690
|  |  |  | 17:00 | 13820 |  | 3342.5 |  | 17320
|  |  |  | 18:00 | 14110 |  | 2091.45 |  | 16300
|  |  |  | 18:30 | 14660 |  | 2296.775 |  | 17065
|  |  |  | 19:00 | 15230 |  | 2483 |  | 17830
|  |  |  | 19:30 | 15360 |  | 2845.9 |  | 18340
|  |  |  | 20:00 | 15460 |  | 2731.3 |  | 18320
|  |  |  | 21:00 | 15840 |  | 2645.35 |  | 18610
|  |  |  | 22:00 | 15410 |  | 2845.9 |  | 18390
|  |  |  | 23:00 | 15050 |  | 3170.6 |  | 18370
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 17690.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 18610.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15840.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 341.45 MKWHr.
*** This report is generated digitally from Operation Information System (OIS) at 11:22 hrs on 12-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 11-08-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14114.98 | MW | 12:00 Hr. | Energy Generated |  |  | 342.3596 |  | MKWHr.
| Day Peak Demand |  |  | 17308.98 | MW | 12:00 Hr. | Energy Unserverd |  |  | 57.506 |  | MKWHr.
| Evening Peak Generation |  |  | 15833.37 | MW | 21:00 Hr. | Energy Demand |  |  | 399.8656 |  | MKWHr.
| Evening Peak Demand |  |  | 18975.37 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.5 |  | °C
| Minimum Generation of the Day |  |  | 13226.23 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 764.36 |  | MMCFD
| Maximum Generation of the Day |  |  | 15833.37 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.4566 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 29.8898 | 0 | 13.125 | 0 | 0 | 0.19256 | 0 | 0 | 43.2074 | Gas | 100.9136 | Gas | 363882888.9772
| Chattogram Zone |  |  | 4.6555 | 55.5564 | 11.5558 | 0 | 5.3018 | 0.13726 | 0 | 0.61536 | 77.8221 | Coal | 132.6256 | Coal | 894061859.0069
| Cumilla Zone |  |  | 21.432 | 0 | 9.6854 | 0 | 0 | 0.55702 | 3.7104 | 0 | 35.3848 | HFO | 46.2277 | HFO | 859518306.206
| Mymensingh Zone |  |  | 0 | 0 | 4.1568 | 0 | 0 | 0.47706 | 0 | 0 | 4.6339 | HSD | 1.5661 | HSD | 39543565.4
| Sylhet Zone |  |  | 26.6298 | 0 | 0 | 0 | 0 | 0.086998 | 0 | 0 | 26.7168 | Hydro | 5.3018 | Hydro | 530176.5
| Khulna Zone |  |  | 0 | 23.12 | 0.59554 | 0.82549 | 0 | 0.73512 | 22.4764 | 0 | 47.7525 | Solar | 5.1035 | Solar | 81376884.2016
| Barishal Zone |  |  | 7.9708 | 48.9484 | 0.60062 | 0 | 0 | 0.004887 | 0 | 0 | 57.5246 | Import | 50.006 | Import | 304862052.21
| Rajshahi Zone |  |  | 10.3358 | 0 | 3.4832 | 0 | 0 | 1.4885 | 23.8193 | 0 | 39.1268 | Wind | 0.61536 | Wind | 9051945.6
| Rangpur Zone |  |  | 0 | 5.0009 | 3.0252 | 0.74057 | 0 | 1.4241 | 0 | 0 | 10.1908
| Total |  |  | 100.9136 | 132.6256 | 46.2277 | 1.5661 | 5.3018 | 5.1035 | 50.006 | 0.61536 | 342.3596
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 363882888.9772 |  | Hydro | 530176.5
|  |  |  | Coal | 894061859.0069 |  | Solar | 81376884.2016
|  |  |  | HFO | 859518306.206 |  | Import | 304862052.21
|  |  |  | HSD | 39543565.4 |  | Wind | 9051945.6
[5 empty] | Total: | 255,28,27,678 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5644 | Peak Hr Flow | 874.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 49256672.72 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.8193 | Peak Hr Flow | 1280.59 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2258 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.7104 | Peak Hr Flow | 100.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2554 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.094 | Peak Hr Flow | 2254.59 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 585 |  | 6432
|  |  |  | Chattogram |  | 208 |  | 1670
|  |  |  | Cumilla |  | 368 |  | 1743
|  |  |  | Mymensingh |  | 490 |  | 1603
|  |  |  | Sylhet |  | 191 |  | 824
|  |  |  | Khulna |  | 356 |  | 2099
|  |  |  | Barishal |  | 152 |  | 579
|  |  |  | Rajshahi |  | 361 |  | 1886
|  |  |  | Rangpur |  | 296 |  | 1272
|  |  |  | Total |  | 3007 |  | 18108
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:25 | Shahjibazar 132/33kV S/S TR-06 HT is restored.
|  | 08:26 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
|  | 09:21 | Faridpur 132/33kV S/S Transformer-2 HT is restored.
|  | 09:22 | Faridpur 132/33kV S/S Transformer-2 LT is restored.
| 09:25 | 11:10 | Bajitpur 132/33kV S/S 132 kV Bus-2 Scheduled S/D Due to High temperature maintenance
| 09:37 | 11:21 | Bajitpur 132/33kV S/S Tr-1(404T) LT Scheduled S/D
| 09:41 | 13:15 | Madunaghat 400/230kV S/S Madunaghat-Meghnaghat 400kV Ckt.-2 Project Work S/D
| 09:46 | 13:19 | Korerhat 400/230/132kV S/S Madunaghat-2 Project Work S/D Due to DFDR WORK
| 10:07 | 14:01 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Project Work S/D Due to SAS signal
Interlock and operations Check at Barapukuria North SS
| 10:07 | 13:57 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Project Work S/D Due to SAS signal
Interlock and operations Check at Barapukuria North SS
| 10:22 | 19:04 | Bogura 230/132kV S/S T-02 HT Scheduled S/D
| 10:22 | 19:04 | Bogura 230/132kV S/S T-02 LT Scheduled S/D
| 11:02 | 12:45 | Kaliakoir 400/230/132kV S/S 230kV Bus 2 Scheduled S/D Due to Dismantle jumper between
230kV bus2 and DS.
|  | 12:56 | Aggreko-keraniganj 132kV Ckt-1 is restored.
|  | 12:56 | Aggreko-keraniganj 132kV Ckt-1 is restored.
| 12:56 | 14:01 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to 132
KVBagerhat Bhandaria Line tree trimming works.
| 13:57 | 14:02 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Shut down
by ALDC
| 14:30 | 15:40 | Saidpur 132/33kV S/S TR-01 HT Scheduled S/D Due to Power Plant internal work.
| 15:09 | 19:22 | Madanganj 132/33kV S/S Madanganj -DPDC Char sayedpur 132k Ckt-2 Forced S/D Due to Purpose
of tree trimming
| 15:09 | 15:18 | Benapole 132/33kV S/S Transformer-1(406T) LT Tripped showing O/C, E/F trip, 50DMT STG1, | [7 empty] | 22.0MW load
|  |  | 51N DMT STG1 relays Due to 33 kv Benapole feeder trip | [7 empty] | interrup.
| 15:30 |  | Haripur 412 MW CCPP Synchronized with remarks:- ST
|  | 16:29 | Nawabganj 132/33kV S/S TR-1 HT is restored.
| 00:03 | 02:54 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Tripped from Brahmanbaria 132/33kV end showing
Distance relay relays. and from Shahjibazar 132/33kV end showing Distance Realy relays
Due to N/A
| 02:08 | 02:34 | Bhaluka-Mymensingh 132 kV Ckt-2 Tripped from Bhaluka 132/33kV end showing P40 Agile | [7 empty] | 110.0MW load
|  |  | (P141) relays. | [7 empty] | interrup. Bhaluka
132/33kV end
| 02:10 | 02:36 | Bhaluka-Mymensingh 132 kV Ckt-1 Tripped from Mymensingh 132/33kV end showing Distance.
relays Due to Bajitpur - Kishorganj both ckt tripped.
| 02:10 | 02:40 | Ashuganj-Kishoreganj 132kV Ckt-2 Tripped from Kishoreganj 132/33kV end showing Dist Relay | [7 empty] | 40.0MW load
|  |  | relays Due to Extreme lightning | [7 empty] | interrup.
Kishoreganj
132/33kV end
| 02:10 | 02:36 | Ashuganj-Kishoreganj 132kV Ckt-1 Tripped from Kishoreganj 132/33kV end showing Dist Relay | [7 empty] | 40.0MW load
|  |  | relays Due to Extremely lightning. | [7 empty] | interrup.
Kishoreganj
132/33kV end
| 05:52 |  | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
NLDC.
| 05:52 |  | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
NLDC.
| 06:04 |  | Bhulta 132/33kV S/S GT1 HT Scheduled S/D Due to For Redhot work in the section of GT-01 | [7 empty] | 60.0MW load
|  |  | DS-114(R and B phase) and Bus DS-126( Y phase) | [7 empty] | interrup.
| 06:10 |  | Benapole 132/33kV S/S Transformer-1(406T) LT Forced S/D Due to TR-1 HT Bushing Red Hot
Maintenance
| 06:11 |  | Benapole 132/33kV S/S Transformer-1(406T) HT Forced S/D Due to TR-1 HT Bushing Red Hot
Maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-08-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 338 | 6436800 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 301 | 7181353 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 502000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 319 | 7722358 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 327240 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 142 | 3384480 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 540182 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 400732 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 10 | 241200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 448200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 41 | 511200 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 32 | 779575 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 17 | 438336 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1359360 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 159 | 1104480 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 192556 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 789840 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | FGMO
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 308 | 7357890 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3489600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2077.42 | 43207382
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 154436.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 108945 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1142880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5301765 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 155 | 4632974 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 93 | 2245636 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 22 | 610216 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 36 | 378555 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 294720 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 22560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 45 | 640320 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 28320 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 363818 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 335515 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 101 | 2328400 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 290880 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 95 | 2206745 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 150 | 563709 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28669088 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 30 | 615360 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 26887272.73 | -
Chattogram Area Total |  |  |  |  | 4898.863 | 3459.36 | 77822115.13
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 216 | 4914000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 354 | 8678000 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 100 | 730000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 30 | 844344 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 5 | 755520 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 1856727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1167623 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1105672 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 764416 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2046346 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 181 | 4355520 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 100 | 3710400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 435278 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 439410 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 105 | 2012100 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 170520 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 88 | 841920 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 557018 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1591 | 35384814
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 134697 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 153 | 2172000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1404000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 328560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 148800 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 432000 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 262 | 4633857
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 86998 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 926000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 913800 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 143 | 3364690.91 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 95 | 1492000 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 674880 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1713600 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 123 | 2733000 | plant availability zero
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 31000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 183792 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7419000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 348 | 7178000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1214 | 26716760.91
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 874 | 21564364 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 23 | 142080 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 453456 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 735120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 233 | 825491 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 920 | 23120000 | AGC+FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2155 | 47752511
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1025 | 20276364 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 150624 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2693000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 860 | 21472000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5277770 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 450000 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7200000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4887 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2560 | 57524645
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 376448 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 936254 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 199617 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 146 | 3822182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 230 | 6513600 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 78035 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 510053 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 539536 | Engine Problem
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 821280 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 57 | 398400 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 33660 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1280.59 | 23819273 | Problem with coal feeding system
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 396000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 682430 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1977.59 | 39126768
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 740565 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1073890 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 159 | 3927000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 835411 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 52055.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 75 | 2189836 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 199869 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1172160 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 537 | 10190786.52
Eastern Grid Total |  |  |  |  | 17440.562 | 8603.78 | 187764929.04
Western Grid Total |  |  |  |  | 11731.125 | 7229.59 | 154594710.52
National Grid Total |  |  |  |  | 29171.687 | 15833.37 | 342359639.56
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-08-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10430.14 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4671.1 | MW
i) Dhaka area |  |  | 5847.44 |  | MW | i) Khulna area |  |  |  | 1743 | MW
ii) Chattogram area |  |  | 1461.7 |  | MW | ii) Barishal area |  |  |  | 427.3 | MW
iii) Cumilla area |  |  | 1375 |  | MW | iii) Rajshahi area |  |  |  | 1524.8 | MW
iv) Mymensingh area |  |  | 1113 |  | MW | iv) Rangpur area |  |  |  | 976 | MW
v) Sylhet area |  |  | 633 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15101.24 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 15 | 12:00 | 67 | HaripurSBU | 145 | 07:00 | 133 | Narshingdi | 177 | 23:00 | 199 | Uttara | 106 | 16:00
2 | AKSML | 160.4 | 13:00 | 68 | Hasnabad | 90 | 19:00 | 134 | Natore | 113 | 00:00 | 200 | UttaraNew | 61 | 23:00
3 | Aftabnagar | 48 | 13:00 | 69 | Hathazari | 87 | 01:00 | 135 | Nawabganj | 59.7 | 18:00 | 201 | Zigatola | 118 | 22:00
4 | Agargaon | 130 | 13:00 | 70 | Hatirjheel | 87 | 13:00 | 136 | Netrakona | 122 | 00:00
5 | Agrabad | 74 | 14:00 | 71 | Ishurdi | 72 | 05:00 | 137 | New | 87.1 | 11:00
6 | Amnura | 34 | 22:00 | 72 | Jaldhaka | 76 | 21:00 | 138 | Niamatpur | 76 | 22:00
7 | Ashuganj | 93 | 22:00 | 73 | Jamalpur | 110 | 22:00 | 139 | Noapara | 38 | 19:00
8 | BSRM | 195 | 08:00 | 74 | Jashore | 174 | 19:30 | 140 | PHP | 11 | 20:00
9 | Bagerhat | 87 | 05:00 | 75 | Jhenaidah | 94 | 05:00 | 141 | Pabna | 101 | 23:00
10 | Bajitpur | 100 | 21:00 | 76 | Joydebpur | 182 | 20:00 | 142 | Palashbari | 134 | 22:00
11 | Bakerganj | 15.8 | 21:00 | 77 | Joypurhat | 56 | 21:00 | 143 | Panchagarh | 78 | 19:30
12 | Bakulia | 93 | 18:30 | 78 | Juldah | 16 | 00:00 | 144 | Patiya | 9.4 | 01:00
13 | Banani | 80.4 | 15:00 | 79 | KSRM | 21 | 07:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 18 | 11:00 | 80 | Kabirpur | 251 | 10:00 | 146 | Patuakhali | 69 | 04:00
15 | Barapukuria | 68 | 21:00 | 81 | Kachua | 84 | 21:00 | 147 | Payra | 37 | 04:00
16 | Barguna | 24 | 04:00 | 82 | Kaliganj | 35 | 12:00 | 148 | Postogola | 67 | 23:00
17 | Barishal | 95 | 18:30 | 83 | Kallyanpur | 135 | 19:00 | 149 | Pubail | 41 | 08:00
18 | Barishal-230 | 100 | 19:00 | 84 | Kalurghat | 41 | 09:00 | 150 | Purbachal | 39 | 18:30
19 | Baroaulia | 60 | 18:30 | 85 | Kamrangirchar | 84 | 13:00 | 151 | Purbasadipur | 130 | 22:00
20 | Baroirhat | 59 | 03:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 33 | 13:00
21 | Bashundhara | 225 | 15:00 | 87 | Kasba | 38 | 19:30 | 153 | Rahim | 55 | 08:00
22 | BashundharaCement | 12 | 00:00 | 88 | Kazla | 133 | 13:00 | 154 | Rajbari | 82 | 06:00
23 | Beanibazar | 72 | 02:00 | 89 | Keranigonj | 100 | 19:00 | 155 | Rajendrapur | 123 | 06:00
24 | Benapole | 60 | 22:00 | 90 | Khagrachori | 34 | 19:30 | 156 | Rajshahi | 109 | 06:00
25 | Bhaluka | 176 | 07:00 | 91 | Khulna | 56 | 02:00 | 157 | Rajshahi-230 | 102 | 21:00
26 | Bhandaria | 54 | 05:00 | 92 | Khulshi | 172 | 22:00 | 158 | Ramganj | 106 | 20:00
27 | Bhangura | 38 | 22:00 | 93 | Kishoreganj | 133 | 21:00 | 159 | Rampur | 42 | 19:30
28 | Bheramara(GK) | 67 | 05:00 | 94 | Kodda | 254 | 19:00 | 160 | Rangamati | 15 | 09:00
29 | Bhulta | 218 | 08:00 | 95 | Kulaura | 52 | 21:00 | 161 | Rangpur | 138 | 08:00
30 | Bog-Sherpur | 76 | 20:00 | 96 | Kurigram | 58 | 19:30 | 162 | Ruppur | 4.8 | 16:00
31 | Bogura | 198 | 21:00 | 97 | Kushtia | 156 | 07:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 73 | 04:00 | 98 | Laksam | 37 | 23:00 | 164 | Saidpur | 100 | 19:30
33 | Brahmanbaria | 125 | 21:00 | 99 | Lakshmipur | 41 | 03:00 | 165 | Santhia | 36 | 19:00
34 | Cantonment | 138 | 13:00 | 100 | Lalbag | 81 | 13:00 | 166 | Satkhira | 133 | 22:00
35 | Chandina | 42 | 22:00 | 101 | Lalmonirhat | 57 | 07:00 | 167 | Satmasjid | 111 | 14:00
36 | Chandpur | 74 | 19:30 | 102 | MI_Cement | 19.4 | 15:00 | 168 | Savar | 232 | 17:00
37 | Chandraghona | 32 | 22:00 | 103 | Madanganj | 52 | 22:00 | 169 | SevenRings | 15.25 | 17:00
38 | Chapai | 65 | 22:00 | 104 | Madaripur | 102 | 21:00 | 170 | ShahCement | 30 | 03:00
39 | Charfasson | 32 | 19:00 | 105 | Madartek | 94 | 23:00 | 171 | Shahjadpur | 83 | 21:00
40 | Charsaidpur | 34 | 09:00 | 106 | Madunaghat | 54 | 00:00 | 172 | Shahjibazar | 149 | 02:00
41 | Chauddagram | 70 | 22:00 | 107 | Magura | 57 | 06:00 | 173 | Shahmirpur | 55 | 18:30
42 | Chhatak | 35 | 00:00 | 108 | Mahasthangarh | 84 | 04:00 | 174 | Shariatpur | 87 | 05:00
43 | Chowmuhani | 153 | 22:00 | 109 | Maijdee | 34 | 21:00 | 175 | Sherpur | 146 | 21:00
44 | Chuadanga | 100 | 19:00 | 110 | Manikganj | 120 | 19:30 | 176 | Shikalbaha | 27.5 | 21:00
45 | Coxsbazar | 127 | 19:00 | 111 | Maniknagar | 83 | 14:00 | 177 | Shitalakhya | 87 | 16:00
46 | Cumilla(N) | 128 | 22:00 | 112 | Matarbari | 52 | 00:00 | 178 | Sholosohor | 56 | 09:00
47 | Cumilla(S) | 192 | 16:00 | 113 | Matuail | 82 | 13:00 | 179 | Shomvuganj | 44 | 04:00
48 | Daganbhuiyan | 33 | 20:00 | 114 | Metrorail_Motijheel | 35 | 16:00 | 180 | Shyampur | 176 | 11:00
49 | Daudkandi | 126 | 22:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 141 | 16:00
50 | DhakaUniversity | 100 | 12:00 | 116 | Millgate | 118 | 12:00 | 182 | Sirajganj | 136 | 20:00
51 | Dhamrai | 96 | 19:00 | 117 | Mirpur | 170 | 19:00 | 183 | Sitakunda | 15 | 15:00
52 | Dhanmondi | 110 | 13:00 | 118 | Mirsorai | 34 | 10:00 | 184 | Sonargaon | 138 | 08:00
53 | Dohazari | 96 | 19:00 | 119 | Mirzapur | 44 | 05:00 | 185 | Sreemongol | 77 | 00:00
54 | Faridpur | 179 | 21:00 | 120 | Mithapukur | 61 | 20:00 | 186 | Sreepur | 129 | 07:00
55 | Fatullah | 121 | 15:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 48.82 | 19:00
56 | Fenchuganj | 45 | 18:30 | 122 | Mogbazar | 42.2 | 16:00 | 188 | Sunamganj | 49 | 21:00
57 | Feni | 108 | 21:00 | 123 | Mongla | 52 | 19:00 | 189 | Sylhet | 112 | 21:00
58 | GPH | 66 | 01:00 | 124 | Motijheel | 54 | 13:00 | 190 | Sylhet_(South) | 88 | 22:00
59 | Ghatail | 91 | 07:00 | 125 | Muktagacha | 38 | 12:00 | 191 | TK | 23 | 03:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 101 | 00:00 | 192 | Tangail | 178 | 05:00
61 | Ghorashal-230 | 103 | 06:00 | 127 | Muradnagar | 43 | 21:00 | 193 | Taraganj | 28 | 19:30
62 | Goalpara | 39 | 19:00 | 128 | Mymensingh | 160 | 19:00 | 194 | Tasnim | 41 | 19:00
63 | Gollamari | 94 | 18:30 | 129 | Nabinagar | 104 | 19:00 | 195 | Thakurgaon | 114 | 19:30
64 | Gopalganj | 94 | 22:00 | 130 | Naogaon | 128 | 21:00 | 196 | Tongi | 141 | 18:30
65 | Gulshan | 134 | 15:00 | 131 | Narail | 64 | 21:00 | 197 | Ullahpara | 36 | 19:30
66 | Halishahar | 124 | 16:00 | 132 | Narinda | 80 | 13:00 | 198 | Ullon | 66 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-08-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14178.13 | 3537 |  | 17874.3
1:00 | 13858.97 | 2690 |  | 16670.02
2:00 | 13757.05 | 2474 |  | 16342.38
3:00 | 13686.63 | 2243 |  | 16030.57
4:00 | 13592.63 | 1827 |  | 15501.85
5:00 | 13519.19 | 1223 |  | 14797.23
6:00 | 13226.23 | 1037 |  | 14309.9
7:00 | 13412.69 | 1141 |  | 14604.69
8:00 | 13336.68 | 1100 |  | 14486.68
9:00 | 13525.6 | 1818 |  | 15425.6
10:00 | 13712.47 | 2104 |  | 15911.47
11:00 | 14023.19 | 2372 |  | 16501.93
12:00 | 14114.98 | 3056 |  | 17308.98
13:00 | 14251.92 | 2669 |  | 17040.92
14:00 | 14152.74 | 2812 |  | 17091.74
15:00 | 13989.46 | 3465 |  | 17610.46
16:00 | 13816.65 | 3270 |  | 17233.65
17:00 | 13818.45 | 3055 |  | 17010.45
18:00 | 14105.81 | 2499 |  | 16716.81
19:00 | 15224 | 2677 |  | 18021
19:30 | 15357.2 | 2489 |  | 17958.2
20:00 | 15457.32 | 2520 |  | 18090.32
21:00 | 15833.37 | 3007 |  | 18975.37
22:00 | 15833.02 | 2215 |  | 18148.02
23:00 | 15536.19 | 2695 |  | 18352.19
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-08-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7929.62 | 6248.51 | 14178.13 | DAILY GENERATION CURVE
00:30 | 7853.52 | 6165.03 | 14018.55
01:00 | 7777.42 | 6081.55 | 13858.97 | 11-08-2026
01:30 | 7685.92 | 6122.09 | 13808.01
02:00 | 7594.42 | 6162.63 | 13757.05
02:30 | 7570.92 | 6150.92 | 13721.84
03:00 | 7547.42 | 6139.21 | 13686.63
03:30 | 7513.42 | 6126.21 | 13639.63
04:00 | 7479.42 | 6113.21 | 13592.63
04:30 | 7489.42 | 6066.49 | 13555.91
05:00 | 7499.42 | 6019.77 | 13519.19
05:30 | 7386.855 | 5985.855 | 13372.71
06:00 | 7274.29 | 5951.94 | 13226.23
06:30 | 7300.125 | 6019.335 | 13319.46
07:00 | 7325.96 | 6086.73 | 13412.69
07:30 | 7334.995 | 6039.69 | 13374.685
08:00 | 7344.03 | 5992.65 | 13336.68
08:30 | 7339.195 | 6091.945 | 13431.14
09:00 | 7334.36 | 6191.24 | 13525.6
09:30 | 7408.565 | 6210.47 | 13619.035
10:00 | 7482.77 | 6229.7 | 13712.47
10:30 | 7557.545 | 6310.285 | 13867.83
11:00 | 7632.32 | 6390.87 | 14023.19
11:30 | 7678.745 | 6390.34 | 14069.085
12:00 | 7725.17 | 6389.81 | 14114.98
12:30 | 7772.225 | 6411.225 | 14183.45
13:00 | 7819.28 | 6432.64 | 14251.92
13:30 | 7779.9 | 6422.43 | 14202.33
14:00 | 7740.52 | 6412.22 | 14152.74
14:30 | 7703.325 | 6367.775 | 14071.1
15:00 | 7666.13 | 6323.33 | 13989.46
15:30 | 7684.56 | 6218.495 | 13903.055
16:00 | 7702.99 | 6113.66 | 13816.65
16:30 | 7738.13 | 6079.42 | 13817.55
17:00 | 7773.27 | 6045.18 | 13818.45
17:30 | 7790.61 | 6171.52 | 13962.13
18:00 | 7807.95 | 6297.86 | 14105.81
18:30 | 8013.185 | 6651.72 | 14664.905
19:00 | 8218.42 | 7005.58 | 15224
19:30 | 8280.42 | 7076.78 | 15357.2
20:00 | 8409.42 | 7047.9 | 15457.32
20:30 | 8506.6 | 7138.745 | 15645.345 |  | Executive Engineer
21:00 | 8603.78 | 7229.59 | 15833.37 |  | Network Operation Division
21:30 | 8585.88 | 7247.315 | 15833.195
22:00 | 8567.98 | 7265.04 | 15833.02
22:30 | 8421.3 | 7263.305 | 15684.605
23:00 | 8274.62 | 7261.57 | 15536.19

## En-Curve
QF-LDC-12
Date | 11-08-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2735 | 1454 | 868 | 38 | 160 | 996.31 | 220 | 5477 | 0 | 586.42 | 1627.4 | 0 | 0 | 16 | 3537 | DAILY ENERGY CURVE
00:30 | 2717 | 1488 | 885 | 38 | 160 | 952.33 | 219 | 5506 | 0 | 553.42 | 1487.3 | 0 | 0 | 12.5 | 3113.5 | 11-08-2026
01:00 | 2699 | 1522 | 902 | 38 | 160 | 908.35 | 218 | 5535 | 0 | 520.42 | 1347.2 | 0 | 0 | 9 | 2690
01:30 | 2713 | 1534.5 | 902 | 38 | 161 | 911.39 | 218.5 | 5553.5 | 0 | 505.42 | 1258.2 | 0 | 0 | 12.5 | 2582 | Energy Generated | 342.3596 |  | MKWHr
02:00 | 2727 | 1547 | 902 | 38 | 162 | 914.43 | 219 | 5572 | 0 | 490.42 | 1169.2 | 0 | 0 | 16 | 2474 | Energy not Served | 57.506 |  | MKWHr
02:30 | 2719 | 1554 | 902 | 38 | 162 | 912.22 | 219 | 5568.5 | 0 | 465.92 | 1162.2 | 0 | 0 | 19 | 2358.5 | Total Energy Requirement | 399.8656 |  | MKWHr
03:00 | 2711 | 1561 | 902 | 38 | 162 | 910.01 | 219 | 5565 | 0 | 441.42 | 1155.2 | 0 | 0 | 22 | 2243
03:30 | 2714 | 1556.5 | 902 | 38 | 161 | 911.51 | 220 | 5548 | 0 | 441.42 | 1131.7 | 0 | 0 | 15.5 | 2035
04:00 | 2717 | 1552 | 902 | 38 | 160 | 913.01 | 221 | 5531 | 0 | 441.42 | 1108.2 | 0 | 0 | 9 | 1827
04:30 | 2719.5 | 1557 | 902 | 38 | 157 | 872.29 | 221.5 | 5550.5 | 0 | 433.92 | 1092.2 | 0 | 0 | 12 | 1525
05:00 | 2722 | 1562 | 902 | 38 | 154 | 831.57 | 222 | 5570 | 0 | 426.42 | 1076.2 | 0 | 0 | 15 | 1223
05:30 | 2614 | 1524.75 | 902 | 38 | 152 | 835.19 | 222 | 5562 | 3.65 | 426.42 | 1073.7 | 0 | 0 | 19 | 1130
06:00 | 2506 | 1487.5 | 902 | 38 | 150 | 838.81 | 222 | 5554 | 7.3 | 426.42 | 1071.2 | 0 | 0 | 23 | 1037
06:30 | 2531.5 | 1533.25 | 902 | 38 | 150 | 833.64 | 222 | 5562 | 55.95 | 426.92 | 1044.2 | 0 | 0 | 20 | 1089
07:00 | 2557 | 1579 | 902 | 38 | 150 | 828.47 | 222 | 5570 | 104.6 | 427.42 | 1017.2 | 0 | 0 | 17 | 1141
07:30 | 2525.5 | 1558.5 | 902 | 38 | 149 | 829.81 | 222 | 5564 | 161.855 | 427.92 | 979.6 | 0 | 0 | 16.5 | 1120.5
08:00 | 2494 | 1538 | 902 | 38 | 148 | 831.15 | 222 | 5558 | 219.11 | 428.42 | 942 | 0 | 0 | 16 | 1100
08:30 | 2552 | 1503 | 897.5 | 38 | 153 | 828.365 | 222 | 5512.5 | 320.355 | 438.42 | 944 | 0 | 0 | 22 | 1459
09:00 | 2610 | 1468 | 893 | 38 | 158 | 825.58 | 222 | 5467 | 421.6 | 448.42 | 946 | 0 | 0 | 28 | 1818
09:30 | 2551 | 1481 | 897 | 38 | 159 | 878.7 | 222 | 5452.5 | 447.915 | 465.42 | 1001.5 | 0 | 0 | 25 | 1961
10:00 | 2492 | 1494 | 901 | 38 | 160 | 931.82 | 222 | 5438 | 474.23 | 482.42 | 1057 | 0 | 0 | 22 | 2104
10:30 | 2519.5 | 1552.5 | 901 | 38 | 165 | 928.935 | 221.5 | 5412 | 560.475 | 478.42 | 1071 | 0 | 0 | 19.5 | 2238
11:00 | 2547 | 1611 | 901 | 38 | 170 | 926.05 | 221 | 5386 | 646.72 | 474.42 | 1085 | 0 | 0 | 17 | 2372
11:30 | 2522.5 | 1618.5 | 901 | 38 | 174 | 930.38 | 220 | 5361 | 665.785 | 480.92 | 1132.5 | 0 | 0 | 24.5 | 2714
12:00 | 2498 | 1626 | 901 | 38 | 178 | 934.71 | 219 | 5336 | 684.85 | 487.42 | 1180 | 0 | 0 | 32 | 3056
12:30 | 2530.5 | 1617 | 888.5 | 38 | 184 | 934.38 | 218.5 | 5345 | 713.65 | 451.92 | 1234 | 0 | 0 | 28 | 2862.5
13:00 | 2563 | 1608 | 876 | 38 | 190 | 934.05 | 218 | 5354 | 742.45 | 416.42 | 1288 | 0 | 0 | 24 | 2669
13:30 | 2493 | 1631.5 | 888.5 | 38 | 186 | 938.09 | 218 | 5365.5 | 715.82 | 411.42 | 1290.5 | 6 | 0 | 20 | 2740.5
14:00 | 2423 | 1655 | 901 | 38 | 182 | 942.13 | 218 | 5377 | 689.19 | 406.42 | 1293 | 12 | 0 | 16 | 2812
14:30 | 2362 | 1669 | 901 | 38 | 184 | 942.58 | 218 | 5402.5 | 611.35 | 418.67 | 1292 | 6 | 0 | 26 | 3138.5
15:00 | 2301 | 1683 | 901 | 38 | 186 | 943.03 | 218 | 5428 | 533.51 | 430.92 | 1291 | 0 | 0 | 36 | 3465
15:30 | 2373 | 1649.5 | 901 | 38 | 189 | 920.59 | 218 | 5390.5 | 441.045 | 435.42 | 1312.5 | 0 | 0 | 34.5 | 3367.5
16:00 | 2445 | 1616 | 901 | 38 | 192 | 898.15 | 218 | 5353 | 348.58 | 439.92 | 1334 | 0 | 0 | 33 | 3270
16:30 | 2568.5 | 1549 | 887.5 | 38 | 188 | 916.44 | 218 | 5302.5 | 283.19 | 439.92 | 1390 | 0 | 0 | 36.5 | 3162.5
17:00 | 2692 | 1482 | 874 | 38 | 184 | 934.73 | 218 | 5252 | 217.8 | 439.92 | 1446 | 0 | 0 | 40 | 3055
17:30 | 2720.5 | 1482.5 | 874 | 38 | 179 | 1035.945 | 218.5 | 5267 | 127.015 | 470.17 | 1510.5 | 0 | 0 | 39 | 2777
18:00 | 2749 | 1483 | 874 | 38 | 174 | 1137.16 | 219 | 5282 | 36.23 | 500.42 | 1575 | 0 | 0 | 38 | 2499
18:30 | 2749.5 | 1485.5 | 874 | 38 | 154 | 1210.37 | 219.5 | 5467.5 | 18.115 | 627.42 | 1692 | 90 | 0 | 39 | 2588
19:00 | 2750 | 1488 | 874 | 38 | 134 | 1283.58 | 220 | 5653 | 0 | 754.42 | 1809 | 180 | 0 | 40 | 2677
19:30 | 2652 | 1327 | 873 | 38 | 130 | 1276.78 | 222 | 5630 | 0 | 769.42 | 2074 | 319 | 0 | 46 | 2489
20:00 | 2705 | 1433 | 874 | 38 | 96 | 1272.9 | 222 | 5592 | 0 | 781.42 | 2079 | 315 | 0 | 49 | 2520
20:30 | 2732.5 | 1459 | 874 | 38 | 98 | 1276.745 | 222 | 5629 | 0 | 787.92 | 2132.18 | 356.5 | 0 | 39.5 | 2763.5
21:00 | 2760 | 1485 | 874 | 38 | 100 | 1280.59 | 222 | 5666 | 0 | 794.42 | 2185.36 | 398 | 0 | 30 | 3007
21:30 | 2751.5 | 1474.5 | 874 | 38 | 107 | 1281.815 | 222 | 5680.5 | 0 | 801.42 | 2162.46 | 398.5 | 0 | 41.5 | 2611
22:00 | 2743 | 1464 | 874 | 38 | 114 | 1283.04 | 222 | 5695 | 0 | 808.42 | 2139.56 | 399 | 0 | 53 | 2215
22:30 | 2739.5 | 1472.5 | 874 | 38 | 114 | 1282.805 | 222 | 5697 | 0 | 804.92 | 2000.88 | 399 | 0 | 40 | 2455
23:00 | 2736 | 1481 | 874 | 38 | 114 | 1282.57 | 222 | 5699 | 0 | 801.42 | 1862.2 | 399 | 0 | 27 | 2695
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 11-08-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 193 | 62 | 350 | 178 | 1498 | 664 | Ishurdi-Ghorashal Ckt-1 | Export | 2678036.36
1:00 | 176 | 51 | 302 | 192 | 1466 | 658
2:00 | 170 | 43 | 316 | 182 | 1420 | 610 |  | Import | 0
3:00 | 177 | 41 | 318 | 158 | 1484 | 630
4:00 | 170 | 39 | 262 | 140 | 1408 | 618 | Ishurdi-Ghorashal Ckt-2 | Export | 2659636.36
5:00 | 132 | 13 | 210 | 140 | 1320 | 560
6:00 | 174 | 31 | 314 | 180 | 1428 | 636 |  | Import | 0
7:00 | 184 | 45 | 342 | 192 | 1494 | 674
8:00 | 211 | 72 | 336 | 186 | 1576 | 712 | Sirajganj-Sreepur Ckt-1 | Export | 2287000
9:00 | 255 | 87 | 412 | 170 | 1810 | 762
10:00 | 269 | 96 | 444 | 192 | 1756 | 860 |  | Import | 0
11:00 | 274 | 90 | 480 | 220 | 1800 | 884
12:00 | 267 | 92 | 470 | 208 | 1772 | 908 | Sirajganj-Sreepur Ckt-2 | Export | 2292000
13:00 | 265 | 88 | 450 | 184 | 1780 | 882
14:00 | 262 | 80 | 450 | 200 | 1790 | 886 |  | Import | 0
15:00 | 283 | 102 | 460 | 194 | 1778 | 896
16:00 | 263 | 90 | 380 | 152 | 1622 | 784 | Gopalganj-Aminbazar Ckt-1 | Export | 19700000
17:00 | 250 | 98 | 380 | 156 | 1564 | 806
18:00 | 241 | 85 | 400 | 164 | 1634 | 826 |  | Import | 0
18:30 | 231 | 70 | 439 | 289 | 1686 | 800
19:00 | 217 | 54 | 430 | 184 | 1726 | 708 | Gopalganj-Aminbazar Ckt-2 | Export | 19640000
19:30 | 222 | 55 | 420 | 170 | 1740 | 708
20:00 | 229 | 67 | 410 | 180 | 1656 | 740 |  | Import | 0
21:00 | 218 | 48 | 380 | 160 | 1660 | 726
22:00 | 224 | 50 | 400 | 170 | 1652 | 670 |  | Total Export | 49256672.72
23:00 | 251 | 65 | 460 | 196 | 1842 | 708 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 11-08-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 371 | 04:00 | 356 | 12:00 | Madunaghat | 395 | 20:00 | 389 | 11:00
Amtali | 411 | 01:00 | 405 | 19:00 | Meghnaghat | 375 | 03:00 | 359 | 12:00
Ashuganj | 392 | 4:00 | 375 | 11:00 | Mirsorai | 390 | 00:00 | 375 | 11:00
Bhulta | 386 | 03:00 | 368 | 12:00 | Payra | 412 | 00:00 | 408 | 21:00
Bibiana | 378 | 00:00 | 368 | 15:00 | Rahanpur | 411 | 00:00 | 400 | 21:00
BIPTC | 401 | 04:00 | 391 | 15:00 | Rampal | 395 | 00:00 | 384 | 21:00
Bogura | 395 | 00:00 | 383 | 21:00
Gopalganj | 389 | 00:00 | 378 | 21:00
Kaliakoir | 361 | 04:00 | 346 | 12:00
Korerhat | 390 | 00:00 | 375 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 00:00 | 214 | 11:00 | Ishurdi | 237 | 00:00 | 220 | 21:00
AKSML | 234 | 00:00 | 226.2 | 11:00 | Jhenaidah | 225 | 05:00 | 210 | 19:00
Aminbazar | 228 | 03:00 | 215 | 12:00 | Kachua | 226 | 00:00 | 217 | 12:00
Ashuganj | 222 | 09:00 | 216 | 11:00 | Kaliakoir | 226 | 00:00 | 213 | 12:00
Ashuganj-400 | 222 | 09:00 | 216 | 11:00 | Keranigonj | 224 | 04:00 | 211 | 13:00
Baghabari | 233 | 04:00 | 222 | 22:00 | Khulna(S) | 226 | 00:00 | 216 | 19:00
Barapukuria | 225 | 16:00 | 219 | 04:00 | Korerhat | 224 | 00:00 | 214 | 11:00
Barapukuria-230 | 225 | 16:00 | 219 | 04:00 | Madunaghat | 235 | 03:00 | 230 | 10:00
Barishal | 225 | 00:00 | 219 | 21:00 | Madunaghat-400 | 237 | 20:00 | 232 | 11:00
Bheramara | 235 | 00:00 | 219 | 21:00 | Maniknagar | 220 | 03:00 | 208 | 11:00
Bhulta | 223 | 04:00 | 210 | 12:00 | Meghnaghat | 230 | 03:00 | 218 | 11:00
Bibiana | 220 | 00:00 | 214 | 12:00 | Meghnaghat-400 | 225 | 02:00 | 214 | 11:00
BIPTC | 237 | 00:00 | 219 | 22:00 | Mirsorai | 229 | 19:30 | 217 | 12:00
Bogura | 240 | 00:00 | 232 | 21:00 | Naogaon | 226 | 09:00 | 214 | 05:00
Bogura-400 | 239 | 00:00 | 232 | 21:00 | Purbasadipur | 223 | 16:00 | 216 | 05:00
Borhanuddin | 229 | 09:00 | 225 | 18:30 | Rajshahi | 233 | 00:00 | 218 | 22:00
BSRM | 224 | 00:00 | 215 | 11:00 | Rampal | 225 | 00:00 | 215 | 21:00
Charfasson | 229 | 11:00 | 225 | 19:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 225 | 00:00 | 216 | 10:00 | Rampura | 222 | 04:00 | 209 | 12:00
Cumilla(N) | 222 | 03:00 | 213 | 11:00 | Shikalbaha | 236 | 18:00 | 231 | 10:00
Faridpur | 222 | 03:00 | 213 | 21:00 | Shyampur | 223 | 02:00 | 211 | 11:00
Fenchuganj | 223 | 00:00 | 216 | 21:00 | Siddhirganj | 222 | 02:00 | 213 | 13:00
Feni | 223 | 00:00 | 213 | 11:00 | Sirajgonj | 237 | 00:00 | 230 | 22:00
Ghorashal | 222 | 03:00 | 215 | 10:00 | Sreepur | 222 | 04:00 | 215 | 11:00
Ghorashal-230 | 218 | 00:00 | 204 | 12:00 | Tongi | 215 | 04:00 | 200 | 18:30
Gopalganj | 221 | 00:00 | 215 | 21:00
GPH | 230 | 18:30 | 223 | 11:00
Haripur | 222 | 03:00 | 211 | 11:00
Hasnabad | 223 | 00:00 | 212 | 11:00
Hathazari | 232 | 16:00 | 224 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 02:00 | 128 | 13:00 | Madartek | 135 | 00:00 | 127 | 13:00
Agargaon | 137 | 02:00 | 127 | 11:00 | Madunaghat | 136 | 08:00 | 133 | 04:00
Agrabad | 134 | 00:00 | 131 | 10:00 | Magura | 134 | 00:00 | 121 | 19:00
AKS | 132 | 01:00 | 129 | 10:00 | Mahasthangarh | 135 | 00:00 | 129 | 05:00
Aminbazar | 132 | 04:00 | 121 | 11:00 | Maijdee | 127 | 00:00 | 121 | 11:00
Amnura | 138 | 00:00 | 128 | 05:00 | Manikganj | 125 | 00:00 | 120 | 15:00
Ashuganj | 129 | 04:00 | 124 | 11:00 | Maniknagar | 138 | 03:00 | 127 | 12:00
Ashuganj-230 | 132 | 01:00 | 128 | 21:00 | Matarbari | 126 | 17:00 | 120 | 00:00
Bagerhat | 128 | 08:00 | 121 | 19:00 | Matuail | 132 | 02:00 | 125 | 11:00
Bajitpur | 126 | 03:00 | 119 | 13:00 | Metrorail_Motijheel | 138 | 04:00 | 127 | 12:00
Bakerganj | 132 | 16:00 | 127 | 19:00 | Metrorail_Uttara | 132 | 03:00 | 119 | 14:00
Bakulia | 135 | 17:00 | 132 | 10:00 | Millgate | 132 | 00:00 | 120 | 15:00
Banani | 138 | 00:00 | 127 | 11:00 | Mirpur | 128 | 00:00 | 120 | 11:00
Bangabhaban | 137 | 03:00 | 126 | 12:00 | Mirzapur | 128 | 05:00 | 120 | 21:00
Barapukuria | 137 | 16:00 | 128 | 05:00 | Mithapukur | 133 | 00:00 | 127 | 05:00
Barguna | 131 | 00:00 | 127 | 19:00 | MI_Cement | 131 | 00:00 | 121.5 | 11:00
Barishal | 131 | 00:00 | 126 | 21:00 | Modern | N/A | N/A | N/A | N/A
Barishal-230 | 130 | 00:00 | 127 | 19:00 | Mogbazar | 138 | 04:00 | 130 | 11:00
Baroaulia | 134 | 18:00 | 131 | 00:00 | Mongla | 127 | 08:00 | 120 | 21:00
Baroirhat | 130 | 00:00 | 124 | 11:00 | Motijheel | 137 | 03:00 | 126 | 12:00
Bashundhara | 138 | 00:00 | 118 | 19:00 | Muktagacha | 133 | 05:00 | 115 | 02:00
BashundharaCement | 131 | 00:00 | 125 | 10:00 | Munshiganj | 131 | 18:30 | 123 | 10:00
Beanibazar | 126 | 00:00 | 120 | 13:00 | Muradnagar | 128 | 00:00 | 119 | 15:00
Benapole | 131 | 04:00 | 115 | 19:00 | Mymensingh | 128 | 04:00 | 113 | 22:00
Bhaluka | 134 | 16:00 | 124 | 22:00 | Nabinagar | 125 | 04:00 | 118 | 15:00
Bhandaria | 127 | 01:00 | 124 | 04:00 | Naogaon | 136 | 00:00 | 128 | 05:00
Bhangura | 133 | 10:00 | 125 | 21:00 | Narail | 138 | 04:00 | 119 | 19:00
Bheramara | 138 | 00:00 | 128 | 21:00 | Narinda | 138 | 03:00 | 127 | 12:00
Bheramara(GK) | 137 | 00:00 | 128 | 21:00 | Narshingdi | 128 | 17:00 | 116 | 11:00
Bhulta | 126 | 04:00 | 123 | 08:00 | Natore | 137 | 00:00 | 127 | 21:00
Bhulta-400 | 129 | 04:00 | 123 | 10:00 | Nawabganj | 136 | 03:00 | 127 | 11:00
Bog-Sherpur | 136 | 09:00 | 130 | 21:00 | Netrakona | 127 | 04:00 | 113 | 19:30
Bogura | 138 | 09:00 | 132 | 05:00 | New | 134 | 00:00 | 123 | 11:00
Bogura-230 | 139 | 00:00 | 133 | 05:00 | Niamatpur | 137 | 09:00 | 131 | 21:00
Brahmanbaria | 126 | 00:00 | 121 | 11:00 | Noapara | 132 | 00:00 | 125 | 22:00
Cantonment | 137 | 03:00 | 126 | 12:00 | Pabna | 135 | 00:00 | 126 | 21:00
Chandina | 130 | 00:00 | 123 | 11:00 | Palashbari | 132 | 00:00 | 126 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandpur | 133 | 18:00 | 128 | 10:00 | Panchagarh | 135 | 09:00 | 130 | 05:00
Chandraghona | 136 | 00:00 | 134 | 11:00 | Patiya | 135 | 08:00 | 131 | 12:00
Chapai | 135 | 16:00 | 129 | 21:00 | Patnitala | 133 | 00:00 | 126 | 03:00
Charsaidpur | 131 | 01:00 | 125 | 10:00 | Patuakhali | 132 | 16:00 | 128 | 19:00
Chauddagram | 129 | 00:00 | 123 | 11:00 | Payra | 135 | 00:00 | 131 | 22:00
Chhatak | 125 | 02:00 | 117 | 18:30 | PHP | 130 | 00:00 | 124 | 11:00
Chowmuhani | 127 | 00:00 | 121 | 11:00 | Postogola | 133 | 00:00 | 124 | 11:00
Chuadanga | 133 | 00:00 | 120 | 22:00 | Pubail | 132 | 02:00 | 122 | 08:00
Coxsbazar | 128 | 16:00 | 123 | 01:00 | Purbachal | 137 | 03:00 | 127 | 11:00
Cumilla(N) | 129 | 00:00 | 123 | 11:00 | Purbasadipur | 135 | 09:00 | 130 | 05:00
Cumilla(S) | 132 | 21:00 | 118 | 16:00 | Rahanpur | 137 | 00:00 | 133 | 22:00
Daganbhuiyan | 129 | 00:00 | 123 | 11:00 | Rahanpur-400 | 138 | 00:00 | 134 | 19:00
Daudkandi | 127 | 00:00 | 115 | 15:00 | Rahim | 132 | 02:00 | 125 | 11:00
DhakaUniversity | 137 | 02:00 | 128 | 12:00 | Rajbari | 126 | 00:00 | 120 | 21:00
Dhamrai | 125 | 00:00 | 120 | 21:00 | Rajendrapur | 133 | 16:00 | 125 | 23:00
Dhanmondi | 137 | 03:00 | 127.6 | 12:00 | Rajshahi | 133 | 00:00 | 124 | 22:00
Dohazari | 134 | 01:00 | 126 | 10:00 | Rajshahi-230 | 135 | 00:00 | 126 | 21:00
Faridpur | 130 | 03:00 | 124 | 22:00 | Ramganj | 128 | 00:00 | 122 | 11:00
Fatullah | 133 | 04:00 | 123 | 11:00 | Rampur | 134 | 00:00 | 130 | 11:00
Fenchuganj | 131 | 00:00 | 127 | 22:00 | Rampura | 137 | 03:00 | 128 | 11:00
Feni | 129 | 00:00 | 122 | 11:00 | Rangamati | 135 | 00:00 | 133 | 10:00
Feni-230 | 130 | 00:00 | 123 | 11:00 | Rangpur | 133 | 16:00 | 125 | 06:00
Ghatail | 128 | 05:00 | 115 | 21:00 | Ruppur | 139 | 00:00 | 128 | 22:00
Ghorashal | 129 | 00:00 | 123 | 22:00 | Saidpur | 134 | 16:00 | 130 | 06:00
Goalpara | 135 | 00:00 | 129 | 21:00 | Santhia | 136 | 00:00 | 127 | 22:00
Gollamari | 135 | 09:00 | 129 | 19:00 | Satkhira | 131 | 09:00 | 122 | 22:00
Gopalganj | 131 | 00:00 | 126 | 12:00 | Satmasjid | 136 | 03:00 | 126 | 13:00
Gopalganj-400 | 131 | 00:00 | 127 | 21:00 | Savar | 128 | 00:00 | 120 | 10:00
Gulshan | 136 | 02:00 | 127 | 11:00 | SevenRings | 130 | 00:00 | 123 | 13:00
Halishahar | 134 | 00:00 | 131 | 11:00 | ShahCement | 131 | 01:00 | 125 | 10:00
Haripur | 132 | 00:00 | 126 | 11:00 | Shahjadpur | 136 | 09:00 | 130 | 22:00
HaripurSBU | 132 | 00:00 | 125 | 11:00 | Shahjibazar | 127 | 09:00 | 122 | 02:00
Hasnabad | 134 | 04:00 | 124 | 11:00 | Shahmirpur | 136 | 18:00 | 132 | 11:00
Hathazari | 136 | 19:30 | 132 | 11:00 | Shariatpur | 129 | 00:00 | 124 | 21:00
Hatirjheel | 137 | 02:00 | 128 | 11:00 | Sherpur | 134 | 23:00 | 111 | 01:00
Ishurdi | 140 | 00:00 | 130 | 21:00 | Shikalbaha | 125 | 04:00 | 133 | 14:00
Jaldhaka | 132 | 16:00 | 126 | 05:00 | Shikalbaha-230 | 136 | 02:00 | 132 | 12:00
Jamalpur | 139 | 05:00 | 115 | 03:00 | Shitalakhya | 131 | 00:00 | 121.5 | 11:00
Jashore | 131 | 07:00 | 122 | 13:00 | Sholosohor | 136 | 18:00 | 132 | 11:00
Jhenaidah | 136 | 00:00 | 120 | 22:00 | Shomvuganj | 124 | 04:00 | 115 | 22:00
Jhenaidah-230 | 136 | 00:00 | 125 | 19:00 | Shyampur | 130 | 00:00 | 126 | 09:00
Joydebpur | 126 | 09:00 | 119 | 15:00 | Shyampur-230 | 134 | 02:00 | 126 | 11:00
Joypurhat | 133 | 09:00 | 127 | 14:00 | Siddhirganj | 133 | 03:00 | 126 | 11:00
Juldah | 135 | 19:30 | 131 | 13:00 | Sirajganj | 132 | 00:00 | 124 | 21:00
Kabirpur | 130 | 04:00 | 116 | 10:00 | Sitakunda | 135 | 00:00 | 132 | 11:00
Kachua | 130 | 00:00 | 125 | 10:00 | Sonargaon | 129 | 00:00 | 110 | 16:00
Kaliakoir | 131 | 04:00 | 124 | 18:30 | Sreemongol | 126 | 00:00 | 122 | 20:00
Kaliganj | 135 | 00:00 | 123 | 19:00 | Sreepur | 136 | 16:00 | 129 | 22:00
Kallyanpur | 128 | 00:00 | 120 | 11:00 | Srinagar | 136 | 02:00 | 127 | 13:00
Kalurghat | 136 | 05:00 | 133 | 10:00 | SSM | 140 | 17:00 | 132 | 00:00
Kamrangirchar | 136 | 03:00 | 117 | 12:00 | Sunamganj | 124 | 02:00 | 115 | 21:00
Kaptai | 138 | 21:00 | 136 | 1:00 | Sylhet | 125 | 00:00 | 122 | 13:00
Kasba | 127 | 00:00 | 118 | 15:00 | Sylhet_(South) | 126 | 00:00 | 122 | 13:00
Kazla | 138 | 05:00 | 126 | 13:00 | Tangail | 125 | 23:00 | 114 | 18:30
Keranigonj | 136 | 04:00 | 127 | 13:00 | Taraganj | 133 | 00:00 | 125 | 08:00
Khagrachori | 135 | 18:00 | 132 | 10:00 | Tasnim | 130 | 00:00 | 123 | 11:00
Khulna | 134 | 00:00 | 127 | 22:00 | Thakurgaon | 137 | 16:00 | 131 | 05:00
Khulna(S) | 135 | 00:00 | 129 | 19:00 | TK | 136 | 20:00 | 133 | 12:00
Khulshi | 133 | 23:00 | 129 | 11:00 | Tongi | 132 | 04:00 | 124 | 11:00
Kishoreganj | 127 | 04:00 | 118 | 22:00 | Ullahpara | 133 | 00:00 | 127 | 21:00
Kodda | 127 | 00:00 | 117 | 12:00 | Ullon | 137 | 04:00 | 128 | 11:00
Korerhat | 132 | 00:00 | 126 | 11:00 | Uttara | 131 | 00:00 | 118 | 15:00
KSRM | 135 | 00:00 | 131 | 11:00 | UttaraNew | 132 | 03:00 | 119 | 14:00
Kulaura | 130 | 01:00 | 126 | 13:00 | Zigatola | 136 | 03:00 | 127 | 12:00
Kurigram | 132 | 19:00 | 120 | 05:00
Kushtia | 134 | 00:00 | 122 | 22:00
Laksam | 129 | 00:00 | 124 | 10:00
Lakshmipur | 126 | 00:00 | 120 | 11:00
Lalbag | 134 | 00:00 | 127 | 11:00
Lalmonirhat | 128 | 00:00 | 123 | 18:30
Madanganj | 131 | 00:00 | 125 | 10:00
Madaripur | 130 | 07:00 | 126 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division