## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 13-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-08-2026 | during | 13-08-2026 | during | 13-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 296 | 333 | 412 | 412 | 340 | 340 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 283 | 281 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 315 | 325 | 335 | 335 | 330 | 330 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 54 | 53.97 | 53.97 | 0 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 137 | 141 | 149.36 | 149.36 | 142 | 142 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 35 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 9 | 9 | 33 | 33 | 10 | 10 | Gas shortage
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 21 | 22 | 22 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 33 | 16 | 52.19 | 52.19 | 33 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 64 | 300 | 300 | 32 | 32 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 56 | 149 | 149 | 17 | 17 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 105 | 105 | 105 | 88 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 138 | 151 | 162 | 162 | 17 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 262 | 308 | 718 | 718 | 550 | 550 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1860.42 | 2132.42 | 5625.16 | 5595.16 | 2124.92 | 2327.92
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 25 | 25 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 45 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 222 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 203 | 212 | 140 | 140 | 140 | 140 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 88 | 87 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 20 | 20 | 24 | 24 | 24 | 24 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 25 | 32 | 25 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 36 | 44 | 108 | 108 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.67 | 0 | 5.25 | 0 | 5.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 93 | 107 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 91 | 97 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 88 | 160 | 163 | 163 | 0 | 0 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1168 | 1121 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 51 | 58 | 25 | 26 | 25 | 26 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 1125 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3277.67 | 3467.86 | 4053.11 | 4100.86 | 3274.25 | 3374
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 178 | 190 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 351 | 355 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 110 | 230 | 342.01 | 342.01 | 342.01 | 342.01 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 393 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 35 | 39 | 41.65 | 41.65 | 40 | 40 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 43 | 24 | 52.82 | 52.82 | 46 | 46 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 182 | 143 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 26 | 150 | 150 | 150 | 50 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 38 | 40 | 40 | 40 | 40 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 50 | 163 | 163 | 86 | 86 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 180 | 183 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 116 | 104 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 43 | 52.2 | 52.2 | 8 | 52 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 5 | 0 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 105 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 27 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 35 | 69 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 78 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1463 | 1801 | 2767.44 | 2696.44 | 1984.27 | 2129.27
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-08-2026 | during | 13-08-2026 | during | 13-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 18.5 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 155 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 53.92 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 24 | 22 | 22 | 0 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 278.62 | 264 | 536.6 | 516.5 | 267.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 38 | 30 | 39 | 39 | 39 | 39 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 143 | 147 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 140 | 94 | 165 | 165 | 144 | 144 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 25 | 0 | 30 | 30 | 25 | 25 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 86 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 102 | 102 | 102 | 102 | 102 | plant availability zero
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 8 | 8 | 8 | 8 | 8 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 356 | 387 | 360 | 360 | 360 | 360 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1135 | 1214 | 1331 | 1331 | 1255 | 1255
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 874 | 873 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 24 | 30 | 30 | 30 | 30 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 32 | 67 | 105 | 105 | 35 | 35 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 66 | 0 | 74 | 0 | 74 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 150 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 925 | 925 | 925 | 925 | 925 | 925 | FGMO
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1935 | 2077 | 3249 | 3175 | 2102 | 2028
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1000 | 1050 | 1000 | 1000 | 1000 | 1000 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 100 | 100 | 100 | 100 | 100 | 100 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 860 | 855 | 906 | 906 | 906 | 906 | AGC on unit-1
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 276 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.19 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2473.19 | 2565 | 2794 | 2793 | 2567 | 2566
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 28.3 | 0 | 48.25 | 0 | 48.25 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 40 | 40 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 15 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 15 | 22 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 150 | 139 | 214 | 214 | 205 | 205 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 234 | 241 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 20 | 20 | 20 | 20 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 43 | 8 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 50 | 50 | Engine Problem
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 113 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 95 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.87 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 931.46 | 1229.71 | 1469.13 | 1469.13 | 950 | 950 | Problem with coal feeding system
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.4 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 113 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1695.03 | 2007.71 | 3253.87 | 3039.12 | 1962.16 | 1812.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 45 | 45 | 45 | 45 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 154 | 165 | 165 | 165 | 165 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 105 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.9 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 95 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 183 | 0 | 172.17 | 0 | 172.17 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 517.9 | 564 | 680.17 | 472 | 552.17 | 379
System Total |  |  |  |  | 28843.2 | 29158.791 | 14635.83 | 16092.99 | 24290.35 | 23719.08 | 16088.87 | 16130.6
Forecast Scenario (13-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14960 |  | 3543.05 |  | 18670
|  |  |  | 1:00 | 14300 |  | 3562.15 |  | 18030
|  |  |  | 2:00 | 14050 |  | 3428.45 |  | 17640
|  |  |  | 3:00 | 13710 |  | 3504.85 |  | 17380
|  |  |  | 4:00 | 13800 |  | 2998.7 |  | 16940
|  |  |  | 5:00 | 13710 |  | 2702.65 |  | 16540
|  |  |  | 6:00 | 13510 |  | 2263.35 |  | 15880
|  |  |  | 7:00 | 13480 |  | 2320.65 |  | 15910
|  |  |  | 8:00 | 13550 |  | 2320.65 |  | 15980
|  |  |  | 9:00 | 13740 |  | 2225.15 |  | 16070
|  |  |  | 10:00 | 13910 |  | 2435.25 |  | 16460
|  |  |  | 11:00 | 14380 |  | 2463.9 |  | 16960
|  |  |  | 12:00 | 14640 |  | 2740.85 |  | 17510
|  |  |  | 13:00 | 14620 |  | 3017.8 |  | 17780
|  |  |  | 14:00 | 14550 |  | 2912.75 |  | 17600
|  |  |  | 15:00 | 14600 |  | 3056 |  | 17800
|  |  |  | 16:00 | 14180 |  | 3017.8 |  | 17340
|  |  |  | 17:00 | 14330 |  | 2435.25 |  | 16880
|  |  |  | 18:00 | 14580 |  | 1852.7 |  | 16520
|  |  |  | 18:30 | 15000 |  | 2024.6 |  | 17120
|  |  |  | 19:00 | 15490 |  | 2120.1 |  | 17710
|  |  |  | 19:30 | 15340 |  | 2998.7 |  | 18480
|  |  |  | 20:00 | 15660 |  | 2588.05 |  | 18370
|  |  |  | 21:00 | 16100 |  | 2444.8 |  | 18660
|  |  |  | 22:00 | 16180 |  | 2110.55 |  | 18390
|  |  |  | 23:00 | 15800 |  | 2473.45 |  | 18390
Probable Maximum Temperature: |  |  | 32.70°C
Probable Maximum Demand at Day Peak: |  |  | 17510.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2444.8
Probable Maximum Demand at Evening Peak: |  |  | 18660.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 347.83 MKWHr. |  | 465 | 150 | 300 | 350 | 200 | 320 | 80 | 300 | 280 | 2445
*** This report is generated digitally from Operation Information System (OIS) at 10:24 hrs on 13-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 12-08-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14635.83 | MW | 12:00 Hr. | Energy Generated |  |  | 349.6597 |  | MKWHr.
| Day Peak Demand |  |  | 17444.83 | MW | 12:00 Hr. | Energy Unserverd |  |  | 60.131 |  | MKWHr.
| Evening Peak Generation |  |  | 16092.99 | MW | 21:00 Hr. | Energy Demand |  |  | 409.7907 |  | MKWHr.
| Evening Peak Demand |  |  | 18744.99 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.5 |  | °C
| Minimum Generation of the Day |  |  | 13371.2 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 816.02 |  | MMCFD
| Maximum Generation of the Day |  |  | 16171.77 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 7.5607 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 30.4405 | 0 | 14.1775 | 0 | 0 | 0.10601 | 0 | 0 | 44.7239 | Gas | 102.5823 | Gas | 367211274.5428
| Chattogram Zone |  |  | 4.5549 | 55.0345 | 12.9535 | 0 | 5.3518 | 0.040222 | 0 | 1.1174 | 79.0524 | Coal | 135.1174 | Coal | 908402843.0903
| Cumilla Zone |  |  | 23.4166 | 0 | 10.0237 | 0 | 0 | 0.48425 | 3.0432 | 0 | 36.9677 | HFO | 51.669 | HFO | 960890038.986
| Mymensingh Zone |  |  | 0 | 0 | 4.6255 | 0 | 0 | 0.51349 | 0 | 0 | 5.139 | HSD | 0.93889 | HSD | 24538425.8
| Sylhet Zone |  |  | 27.1576 | 0 | 0 | 0 | 0 | 0.084648 | 0 | 0 | 27.2422 | Hydro | 5.3518 | Hydro | 535175.8
| Khulna Zone |  |  | 0 | 22.2036 | 1.6204 | 0.41709 | 0 | 0.47448 | 21.944 | 0 | 46.6596 | Solar | 4.4801 | Solar | 71807483.3572
| Barishal Zone |  |  | 7.7387 | 52.9265 | 0.61498 | 0 | 0 | 0.00246 | 0 | 0 | 61.2826 | Import | 48.4028 | Import | 293865263.4
| Rajshahi Zone |  |  | 9.274 | 0 | 4.4527 | 0 | 0 | 1.3529 | 23.4156 | 0 | 38.4952 | Wind | 1.1174 | Wind | 16437542.4
| Rangpur Zone |  |  | 0 | 4.9528 | 3.2007 | 0.5218 | 0 | 1.4217 | 0 | 0 | 10.097
| Total |  |  | 102.5823 | 135.1174 | 51.669 | 0.93889 | 5.3518 | 4.4801 | 48.4028 | 1.1174 | 349.6597
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 367211274.5428 |  | Hydro | 535175.8
|  |  |  | Coal | 908402843.0903 |  | Solar | 71807483.3572
|  |  |  | HFO | 960890038.986 |  | Import | 293865263.4
|  |  |  | HSD | 24538425.8 |  | Wind | 16437542.4
[5 empty] | Total: | 264,36,88,047 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.032 | Peak Hr Flow | 873.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44809400 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.4156 | Peak Hr Flow | 1229.71 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2090 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.0432 | Peak Hr Flow | 104.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2505 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.4908 | Peak Hr Flow | 2206.71 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 445 |  | 6410
|  |  |  | Chattogram |  | 5 |  | 1591
|  |  |  | Cumilla |  | 324 |  | 1724
|  |  |  | Mymensingh |  | 575 |  | 1673
|  |  |  | Sylhet |  | 256 |  | 825
|  |  |  | Khulna |  | 303 |  | 2148
|  |  |  | Barishal |  | 0 |  | 545
|  |  |  | Rajshahi |  | 337 |  | 1894
|  |  |  | Rangpur |  | 293 |  | 1296
|  |  |  | Total |  | 2538 |  | 18106
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 231
|  |  |  | Total Unavailable Capacity |  |  |  | 531
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:22 |  | Jamalpur 132/33kV S/S Bus-A Scheduled S/D Due to 132 KV CT replacement at 132 KV Bus
Coupler Bay.
| 08:49 | 11:37 | Keraniganj-Sreenagar 132kV Ckt-1 Scheduled S/D from Srinagar 132/33kV end Due to Line
maintenance by Keraniganj End. and from Keranigonj 230/132/33kV end Due to High
temperature maintenance at CSE pot at Keaniganj end.
|  | 09:04 | Bhulta 132/33kV S/S GT1 HT is restored.
|  | 09:17 | Benapole 132/33kV S/S Transformer-1(406T) HT is restored.
|  | 09:18 | Benapole 132/33kV S/S Transformer-1(406T) LT is restored.
| 09:59 | 18:19 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Project Work S/D Due to Project
work (SAS signals, interlocks and operations check) at Barapukuria North (Parbatipur)
230kV Switching Substation
| 09:59 | 18:19 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Project Work S/D Due to Project
work (SAS signals, interlocks and operations check) at Barapukuria North (Parbatipur)
230kV Switching Substation
| 10:47 |  | Bogura 230/132kV S/S T-03 LT Scheduled S/D Due to oil filling
| 10:48 |  | Bogura 230/132kV S/S T-03 HT Scheduled S/D Due to oil filling
| 10:48 | 12:12 | Chapai 132/33kV S/S T-3 (425T) LT Forced S/D Due to 132 kv ct oil leakage
| 10:50 | 12:06 | Chapai 132/33kV S/S T-3 (425T) HT Forced S/D Due to R phase CT oil leakage
| 11:19 | 11:38 | Bhulta 400/230/132kV S/S 132kV Bhulta Old Tripped showing REL 670 relays. | [7 empty] | 160.0MW load
interrup.
| 11:38 | 17:55 | Munshiganj 132/33kV S/S Transformer-1 LT Scheduled S/D Due to XLPE Cable termination and
related Maintenance works
| 11:38 | 17:55 | Munshiganj 132/33kV S/S Transformer-1 HT Scheduled S/D Due to XLPE cable termination and
related Maintenance works
| 12:00 |  | Day Peak Generation: 14636 MW.
|  | 12:07 | Payra 400/132/33kV S/S 132/33 kV Transformer-03 HT is restored.
| 15:57 |  | Shahjibazar 330 MW CCPP tripped.
| 15:59 |  | Bibiyana south 400MW CCPP GT was sync.
| 15:59 |  | Bibiyana South 400 MW Synchronized with remarks:- GT
| 17:10 |  | Shahjibazar 330 MW CCPP GT was sync.
| 19:20 |  | Bibiyana south 400MW CCPP GT was shutdown.
| 19:20 |  | Bibiyana South 400 MW Shutdown with remarks:- GT
| 20:10 |  | Sylhet 225 MW CCPP GT was sync.
| 22:15 | 22:32 | Sunamganj 132/33kV S/S Tr-1 LT Tripped showing REF 630 relays Due to During PDB Feeder | [7 empty] | 30.5MW load
|  |  | Trip . | [7 empty] | interrup.
| 22:15 | 22:35 | Sunamganj 132/33kV S/S Tr-2 HT Tripped showing REC 650 RET 650 relays Due to During PDB | [7 empty] | 30.5MW load
|  |  | Feeder trip our Tr-2 Trip | [7 empty] | interrup.
| 22:15 | 22:31 | Sunamganj 132/33kV S/S Tr-1 HT Tripped showing REC 650 RET 650 relays Due to During PDB | [7 empty] | 28.5MW load
|  |  | Feeder fault our Transformer-1 trip | [7 empty] | interrup.
| 22:22 |  | Bhulta-Ghorasal 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230/132kV end Due to None
| 22:43 | 03:22 | Kishoreganj-Mymensingh 132kV Ckt-1 Forced S/D from Kishoreganj 132/33kV end Due to
Emergency shutdown order by LDC
| 22:44 | 03:23 | Kishoreganj-Mymensingh 132kV Ckt-2 Forced S/D from Kishoreganj 132/33kV end Due to
Emergency shutdown order by NLDC
| 23:08 | 03:19 | Ashuganj 132/33kV S/S OAT-12 LT Forced S/D Due to Red hot maintenance | [7 empty] | 150.0MW load
interrup.
|  | 23:36 | Khulshi-Madunaghat 132kV Ckt-2 is restored.
| 06:15 |  | Rangpur 132/33kV S/S 33KV Bus Scheduled S/D Due to Redhot removed of 33kv burirhat nesco | [7 empty] | 25.0MW load
|  |  | feeder isolator connected to 33kv bus 1 | [7 empty] | interrup.
| 06:29 |  | Bhaluka 132/33kV S/S 01. Transformer- 01 LT Scheduled S/D Due to High temp.minimize at | [7 empty] | 70.0MW load
|  |  | 33kV bus by PBS. | [7 empty] | interrup.
| 06:30 |  | Bhaluka 132/33kV S/S 01. Transformer- 01 HT Scheduled S/D Due to High temp.minimize at | [7 empty] | 70.0MW load
|  |  | 33kV bus by PBS. | [7 empty] | interrup.
| 06:56 |  | Sylhet_(South) 132/33kV S/S Trafo-1 LT Scheduled S/D Due to DUE TO DS MAINTANENCE
| 06:57 |  | Sylhet_(South) 132/33kV S/S Trafo-1 HT Scheduled S/D Due to DUE TO DS MAINTANENCE
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 12-08-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 333 | 7671600 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 281 | 7222167 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 325 | 7587912 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 685080 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 141 | 3186240 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 564169 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 573468 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 9 | 208200 | Gas shortage
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 458640 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 603360 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 64 | 893989 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 56 | 505584 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1374720 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 151 | 1990080 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 106007 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 511560 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 308 | 7291960 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3289200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2132.42 | 44723936
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 189995.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 17820 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 1038720 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5351758 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 212 | 4516469 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 2209672 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 20 | 501984 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 468589 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 302400 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 38400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 44 | 794880 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22402 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 386400 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 400877 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 107 | 2351018 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 318720 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 97 | 2235600 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 160 | 1754691 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1121 | 27965452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 58 | 1117440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 27069090.91 | -
Chattogram Area Total |  |  |  |  | 4885.967 | 3467.86 | 79052378.31
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 190 | 4654000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 355 | 8713400 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 230 | 3748000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 39 | 816624 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 24 | 447360 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 143 | 2274909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1233000 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1078909 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 764976 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1313624 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 183 | 4344480 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 104 | 3043200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 653501 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 0 | 215710 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 105 | 1837680 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 341880 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 1002240 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 484255 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1801 | 36967748
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 143434 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13750 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 155 | 2373600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1462800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 356310 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 385200 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 403920 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 264 | 5139014
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 84648 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 971000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 824640 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3321409.09 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 94 | 1489000 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 415392 | Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1732800 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 1880310 | plant availability zero
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 116000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 165024 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7284000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 387 | 8958000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1214 | 27242223.09
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 873 | 21032000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 24 | 161280 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 1459152 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 474480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 150 | 417095 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 925 | 22203640 | AGC+FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2077 | 46659647
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1050 | 24560000 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 132576 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 100 | 2403000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 855 | 21297454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5335690 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 482400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7069000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2460 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2565 | 61282580.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 271056 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 914127 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 438590 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 139 | 3548273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 241 | 5725745 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 81467 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 564538 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 680160 | Engine Problem
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1011264 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 95 | 762528 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 35880 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1229.71 | 23415636 | Problem with coal feeding system
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 388496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 657420 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2007.71 | 38495180
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 521797.5 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 45 | 1043781 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 154 | 3909000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 929846 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 41604.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 2270857 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 200723 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1179360 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 564 | 10096969.34
Eastern Grid Total |  |  |  |  | 17427.666 | 8879.28 | 193125299.4
Western Grid Total |  |  |  |  | 11731.125 | 7213.71 | 156534376.89
National Grid Total |  |  |  |  | 29158.791 | 16092.99 | 349659676.29
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 12-08-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10618.2 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4949.4 | MW
i) Dhaka area |  |  | 5965.2 |  | MW | i) Khulna area |  |  |  | 1845 | MW
ii) Chattogram area |  |  | 1586 |  | MW | ii) Barishal area |  |  |  | 544.6 | MW
iii) Cumilla area |  |  | 1400 |  | MW | iii) Rajshahi area |  |  |  | 1556.8 | MW
iv) Mymensingh area |  |  | 1098 |  | MW | iv) Rangpur area |  |  |  | 1003 | MW
v) Sylhet area |  |  | 569 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15567.6 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 21 | 17:00 | 67 | HaripurSBU | 140 | 22:00 | 133 | Narshingdi | 182 | 00:00 | 199 | Uttara | 109 | 19:00
2 | AKSML | 173.9 | 00:00 | 68 | Hasnabad | 97 | 22:00 | 134 | Natore | 150 | 23:00 | 200 | UttaraNew | 62 | 00:00
3 | Aftabnagar | 48 | 00:00 | 69 | Hathazari | 98 | 21:00 | 135 | Nawabganj | 71.7 | 22:00 | 201 | Zigatola | 118 | 12:00
4 | Agargaon | 134 | 13:00 | 70 | Hatirjheel | 98 | 15:00 | 136 | Netrakona | 120 | 21:00
5 | Agrabad | 72 | 18:00 | 71 | Ishurdi | 86 | 18:30 | 137 | New | 88 | 12:00
6 | Amnura | 36 | 23:00 | 72 | Jaldhaka | 104 | 22:00 | 138 | Niamatpur | 83 | 22:00
7 | Ashuganj | 89 | 04:00 | 73 | Jamalpur | 106 | 23:00 | 139 | Noapara | 53 | 22:00
8 | BSRM | 195 | 02:00 | 74 | Jashore | 171 | 00:00 | 140 | PHP | 6 | 00:00
9 | Bagerhat | 94 | 23:00 | 75 | Jhenaidah | 93 | 23:00 | 141 | Pabna | 105 | 23:00
10 | Bajitpur | 89 | 18:30 | 76 | Joydebpur | 180 | 20:00 | 142 | Palashbari | 148 | 22:00
11 | Bakerganj | 16.2 | 19:30 | 77 | Joypurhat | 75 | 23:00 | 143 | Panchagarh | 78 | 20:00
12 | Bakulia | 100 | 18:30 | 78 | Juldah | 23 | 17:00 | 144 | Patiya | 10.8 | 19:30
13 | Banani | 79.4 | 14:00 | 79 | KSRM | 48.5 | 07:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 19 | 11:00 | 80 | Kabirpur | 269 | 21:00 | 146 | Patuakhali | 76 | 21:00
15 | Barapukuria | 86 | 22:00 | 81 | Kachua | 114 | 22:00 | 147 | Payra | 40 | 21:00
16 | Barguna | 24 | 21:00 | 82 | Kaliganj | 43 | 22:00 | 148 | Postogola | 67 | 00:00
17 | Barishal | 111 | 21:00 | 83 | Kallyanpur | 135 | 00:00 | 149 | Pubail | 40 | 00:00
18 | Barishal-230 | 115 | 22:00 | 84 | Kalurghat | 38 | 18:00 | 150 | Purbachal | 39 | 13:00
19 | Baroaulia | 67 | 18:30 | 85 | Kamrangirchar | 85 | 13:00 | 151 | Purbasadipur | 158 | 22:00
20 | Baroirhat | 64 | 20:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 51 | 21:00
21 | Bashundhara | 221 | 15:00 | 87 | Kasba | 43 | 22:00 | 153 | Rahim | 56 | 06:00
22 | BashundharaCement | 12 | 00:00 | 88 | Kazla | 130 | 12:00 | 154 | Rajbari | 98 | 18:30
23 | Beanibazar | 90 | 23:00 | 89 | Keranigonj | 95 | 18:30 | 155 | Rajendrapur | 119 | 18:30
24 | Benapole | 63 | 22:00 | 90 | Khagrachori | 42 | 20:00 | 156 | Rajshahi | 127 | 22:00
25 | Bhaluka | 157 | 18:30 | 91 | Khulna | 65 | 22:00 | 157 | Rajshahi-230 | 108 | 23:00
26 | Bhandaria | 58 | 21:00 | 92 | Khulshi | 180 | 19:30 | 158 | Ramganj | 116 | 23:00
27 | Bhangura | 42 | 22:00 | 93 | Kishoreganj | 134 | 20:00 | 159 | Rampur | 44 | 20:00
28 | Bheramara(GK) | 75 | 05:00 | 94 | Kodda | 274 | 19:00 | 160 | Rangamati | 15 | 20:00
29 | Bhulta | 231 | 11:00 | 95 | Kulaura | 53 | 23:00 | 161 | Rangpur | 158 | 22:00
30 | Bog-Sherpur | 88 | 22:00 | 96 | Kurigram | 76 | 22:00 | 162 | Ruppur | 4.4 | 11:00
31 | Bogura | 199 | 23:00 | 97 | Kushtia | 172 | 21:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 81 | 23:00 | 98 | Laksam | 38 | 23:00 | 164 | Saidpur | 117 | 11:00
33 | Brahmanbaria | 124 | 20:00 | 99 | Lakshmipur | 53 | 23:00 | 165 | Santhia | 40 | 22:00
34 | Cantonment | 142 | 13:00 | 100 | Lalbag | 85 | 13:00 | 166 | Satkhira | 141 | 21:00
35 | Chandina | 49 | 22:00 | 101 | Lalmonirhat | 76 | 18:30 | 167 | Satmasjid | 116 | 13:00
36 | Chandpur | 88 | 23:00 | 102 | MI_Cement | 16.6 | 09:00 | 168 | Savar | 222 | 18:00
37 | Chandraghona | 35 | 20:00 | 103 | Madanganj | 55 | 21:00 | 169 | SevenRings | 23.11 | 22:00
38 | Chapai | 86 | 23:00 | 104 | Madaripur | 116 | 14:00 | 170 | ShahCement | 29 | 21:00
39 | Charfasson | 35 | 22:00 | 105 | Madartek | 96 | 00:00 | 171 | Shahjadpur | 89 | 18:30
40 | Charsaidpur | 33 | 04:00 | 106 | Madunaghat | 55 | 19:00 | 172 | Shahjibazar | 120 | 00:00
41 | Chauddagram | 87 | 22:00 | 107 | Magura | 79 | 22:00 | 173 | Shahmirpur | 54 | 18:30
42 | Chhatak | 38 | 23:00 | 108 | Mahasthangarh | 89 | 23:00 | 174 | Shariatpur | 106 | 23:00
43 | Chowmuhani | 158 | 22:00 | 109 | Maijdee | 40 | 22:00 | 175 | Sherpur | 152 | 22:00
44 | Chuadanga | 126 | 13:00 | 110 | Manikganj | 121 | 15:00 | 176 | Shikalbaha | 33.5 | 11:00
45 | Coxsbazar | 144 | 20:00 | 111 | Maniknagar | 89 | 13:00 | 177 | Shitalakhya | 90.1 | 13:00
46 | Cumilla(N) | 112 | 21:00 | 112 | Matarbari | 48 | 22:00 | 178 | Sholosohor | 53 | 18:30
47 | Cumilla(S) | 165 | 11:00 | 113 | Matuail | 80 | 15:00 | 179 | Shomvuganj | 40 | 18:00
48 | Daganbhuiyan | 36 | 22:00 | 114 | Metrorail_Motijheel | 32 | 20:00 | 180 | Shyampur | 168 | 10:00
49 | Daudkandi | 169 | 22:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 147 | 12:00
50 | DhakaUniversity | 100 | 12:00 | 116 | Millgate | 118 | 16:00 | 182 | Sirajganj | 136 | 19:30
51 | Dhamrai | 94 | 21:00 | 117 | Mirpur | 170 | 19:00 | 183 | Sitakunda | 14 | 00:00
52 | Dhanmondi | 134 | 13:00 | 118 | Mirsorai | 52 | 11:00 | 184 | Sonargaon | 136 | 23:00
53 | Dohazari | 106 | 01:00 | 119 | Mirzapur | 38 | 21:00 | 185 | Sreemongol | 85 | 18:30
54 | Faridpur | 196 | 22:00 | 120 | Mithapukur | 84 | 23:00 | 186 | Sreepur | 145 | 23:00
55 | Fatullah | 120 | 16:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 56.5 | 22:00
56 | Fenchuganj | 59 | 22:00 | 122 | Mogbazar | 41.9 | 17:00 | 188 | Sunamganj | 61 | 22:00
57 | Feni | 124 | 22:00 | 123 | Mongla | 51 | 19:00 | 189 | Sylhet | 138 | 22:00
58 | GPH | 1 | 00:00 | 124 | Motijheel | 57 | 13:00 | 190 | Sylhet_(South) | 84 | 22:00
59 | Ghatail | 81 | 22:00 | 125 | Muktagacha | 50 | 19:00 | 191 | TK | 24 | 22:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 118 | 22:00 | 192 | Tangail | 156 | 20:00
61 | Ghorashal-230 | 106 | 23:00 | 127 | Muradnagar | 58 | 22:00 | 193 | Taraganj | 39 | 18:30
62 | Goalpara | 42 | 00:00 | 128 | Mymensingh | 148 | 21:00 | 194 | Tasnim | 41 | 00:00
63 | Gollamari | 122 | 12:00 | 129 | Nabinagar | 120 | 18:30 | 195 | Thakurgaon | 131 | 23:00
64 | Gopalganj | 120 | 22:00 | 130 | Naogaon | 150 | 23:00 | 196 | Tongi | 152 | 17:00
65 | Gulshan | 134 | 13:00 | 131 | Narail | 61 | 22:00 | 197 | Ullahpara | 38 | 18:30
66 | Halishahar | 124.5 | 18:00 | 132 | Narinda | 80 | 13:00 | 198 | Ullon | 66 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 12-08-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14654.16 | 3592 |  | 18408.16
1:00 | 13996.09 | 3194 |  | 17334.09
2:00 | 13745.2 | 3116 |  | 17001.2
3:00 | 13409.31 | 3056 |  | 16603.31
4:00 | 13598.22 | 2951 |  | 16682.22
5:00 | 13504.25 | 2873 |  | 16506.25
6:00 | 13407.97 | 2626 |  | 16151.97
7:00 | 13371.2 | 2319 |  | 15794.2
8:00 | 13440.92 | 2323 |  | 15868.92
9:00 | 13632.43 | 2589 |  | 16338.43
10:00 | 13808.23 | 2510 |  | 16431.23
11:00 | 14279.04 | 1900 |  | 16265.04
12:00 | 14635.83 | 2688 |  | 17444.83
13:00 | 14610.28 | 2438 |  | 17158.28
14:00 | 14544.35 | 2464 |  | 17119.35
15:00 | 14594.19 | 3382 |  | 18128.19
16:00 | 14174.26 | 2717 |  | 17013.26
17:00 | 14324.01 | 2664 |  | 17108.01
18:00 | 14577.29 | 1321 |  | 15957.29
19:00 | 15487.57 | 2422 |  | 18018.57
19:30 | 15332.59 | 2448 |  | 17890.75
20:00 | 15657.69 | 1941 |  | 17685.69
21:00 | 16092.99 | 2538 |  | 18744.99
22:00 | 16171.77 | 1168 |  | 17392.33
23:00 | 16099.39 | 1339 |  | 17498.65
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 12-08-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 230 | 74 | 420 | 170 | 1686 | 716 | Ishurdi-Ghorashal Ckt-1 | Export | 2273236.36
1:00 | 165 | 56 | 274 | 140 | 1576 | 702
2:00 | 139 | 48 | 210 | 130 | 1492 | 620 |  | Import | 0
3:00 | 123 | 46 | 170 | 144 | 1436 | 586
4:00 | 137 | 44 | 210 | 148 | 1420 | 600 | Ishurdi-Ghorashal Ckt-2 | Export | 2253163.64
5:00 | 143 | 48 | 220 | 148 | 1452 | 624
6:00 | 134 | 34 | 200 | 152 | 1412 | 580 |  | Import | 0
7:00 | 148 | 40 | 230 | 152 | 1448 | 602
8:00 | 189 | 57 | 290 | 180 | 1526 | 666 | Sirajganj-Sreepur Ckt-1 | Export | 1700000
9:00 | 241 | 89 | 380 | 196 | 1716 | 760
10:00 | 271 | 106 | 410 | 186 | 1824 | 800 |  | Import | 0
11:00 | 203 | 62 | 300 | 160 | 1542 | 754
12:00 | 204 | 44 | 350 | 170 | 1610 | 734 | Sirajganj-Sreepur Ckt-2 | Export | 1703000
13:00 | 256 | 72 | 370 | 176 | 1644 | 760
14:00 | 261 | 100 | 350 | 170 | 1594 | 764 |  | Import | 0
15:00 | 248 | 95 | 340 | 160 | 1708 | 790
16:00 | 236 | 87 | 350 | 184 | 1668 | 796 | Gopalganj-Aminbazar Ckt-1 | Export | 18420000
17:00 | 227 | 88 | 330 | 182 | 1660 | 812
18:00 | 216 | 94 | 320 | 180 | 1526 | 728 |  | Import | 0
18:30 | 187 | 52 | 320 | 176 | 1506 | 696
19:00 | 195 | 74 | 330 | 140 | 1596 | 686 | Gopalganj-Aminbazar Ckt-2 | Export | 18460000
19:30 | 212 | 60 | 340 | 120 | 1616 | 696
20:00 | 201 | 55 | 320 | 134 | 1492 | 642 |  | Import | 0
21:00 | 206 | 44 | 340 | 126 | 1544 | 626
22:00 | 115 | -23 | 160 | 40 | 1208 | 444 |  | Total Export | 44809400
23:00 | 108 | -7 | 150 | 54 | 1188 | 464 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 12-08-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7850.62 | 6803.54 | 14654.16 | DAILY GENERATION CURVE
00:30 | 7783.12 | 6542.005 | 14325.125
01:00 | 7715.62 | 6280.47 | 13996.09 | 12-08-2026
01:30 | 7689.12 | 6181.525 | 13870.645
02:00 | 7662.62 | 6082.58 | 13745.2
02:30 | 7496.91 | 6080.345 | 13577.255
03:00 | 7331.2 | 6078.11 | 13409.31
03:30 | 7420.7 | 6083.065 | 13503.765
04:00 | 7510.2 | 6088.02 | 13598.22
04:30 | 7474.31 | 6076.925 | 13551.235
05:00 | 7438.42 | 6065.83 | 13504.25
05:30 | 7393.065 | 6063.045 | 13456.11
06:00 | 7347.71 | 6060.26 | 13407.97
06:30 | 7305.76 | 6083.825 | 13389.585
07:00 | 7263.81 | 6107.39 | 13371.2
07:30 | 7280.21 | 6125.85 | 13406.06
08:00 | 7296.61 | 6144.31 | 13440.92
08:30 | 7350.38 | 6186.295 | 13536.675
09:00 | 7404.15 | 6228.28 | 13632.43
09:30 | 7392.215 | 6328.115 | 13720.33
10:00 | 7380.28 | 6427.95 | 13808.23
10:30 | 7604.055 | 6439.58 | 14043.635
11:00 | 7827.83 | 6451.21 | 14279.04
11:30 | 7921.27 | 6536.165 | 14457.435
12:00 | 8014.71 | 6621.12 | 14635.83
12:30 | 8046.64 | 6576.415 | 14623.055
13:00 | 8078.57 | 6531.71 | 14610.28
13:30 | 8088.505 | 6488.81 | 14577.315
14:00 | 8098.44 | 6445.91 | 14544.35
14:30 | 8144.265 | 6425.005 | 14569.27
15:00 | 8190.09 | 6404.1 | 14594.19
15:30 | 8031.115 | 6353.11 | 14384.225
16:00 | 7872.14 | 6302.12 | 14174.26
16:30 | 7959.19 | 6289.945 | 14249.135
17:00 | 8046.24 | 6277.77 | 14324.01
17:30 | 8191.59 | 6259.06 | 14450.65
18:00 | 8336.94 | 6240.35 | 14577.29
18:30 | 8438.93 | 6593.5 | 15032.43
19:00 | 8540.92 | 6946.65 | 15487.57
19:30 | 8398.92 | 6933.67 | 15332.59
20:00 | 8621.92 | 7035.77 | 15657.69
20:30 | 8750.6 | 7124.74 | 15875.34 |  | Executive Engineer
21:00 | 8879.28 | 7213.71 | 16092.99 |  | Network Operation Division
21:30 | 8982.53 | 7149.85 | 16132.38
22:00 | 9085.78 | 7085.99 | 16171.77
22:30 | 9061.78 | 7073.8 | 16135.58
23:00 | 9037.78 | 7061.61 | 16099.39

## En-Curve
QF-LDC-12
Date | 12-08-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2657 | 1367 | 874 | 38 | 112 | 1275.54 | 222 | 5699 | 0 | 720.42 | 1676.2 | 0 | 0 | 13 | 3592 | DAILY ENERGY CURVE
00:30 | 2678 | 1399.5 | 874 | 38 | 131 | 1137.505 | 220.5 | 5666.5 | 0 | 656.42 | 1497.7 | 0 | 0 | 26 | 3393 | 12-08-2026
01:00 | 2699 | 1432 | 874 | 38 | 150 | 999.47 | 219 | 5634 | 0 | 592.42 | 1319.2 | 0 | 0 | 39 | 3194
01:30 | 2696.5 | 1471 | 874 | 38 | 145 | 916.025 | 218.5 | 5645.5 | 0 | 580.92 | 1242.2 | 0 | 0 | 43 | 3155 | Energy Generated | 349.6597 |  | MKWHr
02:00 | 2694 | 1510 | 874 | 38 | 140 | 832.58 | 218 | 5657 | 0 | 569.42 | 1165.2 | 0 | 0 | 47 | 3116 | Energy not Served | 60.131 |  | MKWHr
02:30 | 2680.5 | 1490.5 | 874 | 38 | 143 | 830.845 | 218 | 5646.5 | 0 | 478.21 | 1134.2 | 0 | 0 | 43.5 | 3086 | Total Energy Requirement | 409.7907 |  | MKWHr
03:00 | 2667 | 1471 | 874 | 38 | 146 | 829.11 | 218 | 5636 | 0 | 387 | 1103.2 | 0 | 0 | 40 | 3056
03:30 | 2688.5 | 1490.5 | 873.5 | 38 | 141 | 832.565 | 218.5 | 5643.5 | 0 | 440 | 1107.7 | 0 | 0 | 30 | 3003.5
04:00 | 2710 | 1510 | 873 | 38 | 136 | 836.02 | 219 | 5651 | 0 | 493 | 1112.2 | 0 | 0 | 20 | 2951
04:30 | 2675.5 | 1510 | 873.5 | 38 | 134 | 841.425 | 219.5 | 5618.5 | 0 | 503.21 | 1100.6 | 0 | 0 | 37 | 2912
05:00 | 2641 | 1510 | 874 | 38 | 132 | 846.83 | 220 | 5586 | 0 | 513.42 | 1089 | 0 | 0 | 54 | 2873
05:30 | 2607.5 | 1508.5 | 874 | 38 | 128 | 848.41 | 221 | 5588 | 7.28 | 513.42 | 1070 | 0 | 0 | 52 | 2749.5
06:00 | 2574 | 1507 | 874 | 38 | 124 | 849.99 | 222 | 5590 | 14.56 | 513.42 | 1051 | 0 | 0 | 50 | 2626
06:30 | 2562.5 | 1498.5 | 873.5 | 38 | 120 | 865.065 | 221 | 5581 | 48.6 | 498.42 | 1031.5 | 0 | 0 | 51.5 | 2472.5
07:00 | 2551 | 1490 | 873 | 38 | 116 | 880.14 | 220 | 5572 | 82.64 | 483.42 | 1012 | 0 | 0 | 53 | 2319
07:30 | 2533 | 1470.5 | 873.5 | 38 | 124 | 859.08 | 221 | 5573.5 | 173.06 | 483.92 | 1006 | 0 | 0 | 50.5 | 2321
08:00 | 2515 | 1451 | 874 | 38 | 132 | 838.02 | 222 | 5575 | 263.48 | 484.42 | 1000 | 0 | 0 | 48 | 2323
08:30 | 2570 | 1492 | 873.5 | 38 | 139 | 836.88 | 222 | 5577 | 280.875 | 479.92 | 974 | 0 | 0 | 53.5 | 2456
09:00 | 2625 | 1533 | 873 | 38 | 146 | 835.74 | 222 | 5579 | 298.27 | 475.42 | 948 | 0 | 0 | 59 | 2589
09:30 | 2634.5 | 1422.5 | 859 | 38 | 164 | 865.19 | 222 | 5545 | 413.72 | 489.42 | 1012 | 0 | 0 | 55 | 2549.5
10:00 | 2644 | 1312 | 845 | 38 | 182 | 894.64 | 222 | 5511 | 529.17 | 503.42 | 1076 | 0 | 0 | 51 | 2510
10:30 | 2630.5 | 1460 | 859.5 | 38 | 174 | 907.575 | 222 | 5526.5 | 523.64 | 505.92 | 1148 | 0 | 0 | 48 | 2205
11:00 | 2617 | 1608 | 874 | 38 | 166 | 920.51 | 222 | 5542 | 518.11 | 508.42 | 1220 | 0 | 0 | 45 | 1900
11:30 | 2594 | 1590 | 874 | 38 | 141 | 925.985 | 221 | 5549.5 | 592.03 | 514.42 | 1369.5 | 0 | 0 | 48 | 2294
12:00 | 2571 | 1572 | 874 | 38 | 116 | 931.46 | 220 | 5557 | 665.95 | 520.42 | 1519 | 0 | 0 | 51 | 2688
12:30 | 2605.5 | 1532.5 | 874.5 | 38 | 115 | 928.215 | 219 | 5516 | 660.42 | 523.92 | 1561.5 | 0 | 0 | 48.5 | 2563
13:00 | 2640 | 1493 | 875 | 38 | 114 | 924.97 | 218 | 5475 | 654.89 | 527.42 | 1604 | 0 | 0 | 46 | 2438
13:30 | 2621.5 | 1548.5 | 874.5 | 38 | 124 | 929.485 | 218 | 5470.5 | 574.52 | 516.21 | 1625.1 | 0 | 0 | 37 | 2451
14:00 | 2603 | 1604 | 874 | 38 | 134 | 934 | 218 | 5466 | 494.15 | 505 | 1646.2 | 0 | 0 | 28 | 2464
14:30 | 2598 | 1623.5 | 874 | 38 | 129 | 935.49 | 218.5 | 5513 | 426.58 | 505 | 1668.2 | 0 | 0 | 40 | 2923
15:00 | 2593 | 1643 | 874 | 38 | 124 | 936.98 | 219 | 5560 | 359.01 | 505 | 1690.2 | 0 | 0 | 52 | 3382
15:30 | 2545.5 | 1549.5 | 873.5 | 38 | 124 | 933.215 | 220.5 | 5558 | 294.31 | 504.5 | 1687.2 | 0 | 0 | 56 | 3049.5
16:00 | 2498 | 1456 | 873 | 38 | 124 | 929.45 | 222 | 5556 | 229.61 | 504 | 1684.2 | 0 | 0 | 60 | 2717
16:30 | 2585 | 1441 | 873 | 38 | 122 | 928.165 | 222 | 5535 | 178.66 | 530.71 | 1743.1 | 0 | 0 | 52.5 | 2690.5
17:00 | 2672 | 1426 | 873 | 38 | 120 | 926.88 | 222 | 5514 | 127.71 | 557.42 | 1802 | 0 | 0 | 45 | 2664
17:30 | 2803 | 1459 | 873 | 38 | 117 | 980.29 | 222 | 5436.5 | 73.44 | 620.42 | 1783 | 0 | 0 | 45 | 1992.5
18:00 | 2934 | 1492 | 873 | 38 | 114 | 1033.7 | 222 | 5359 | 19.17 | 683.42 | 1764 | 0 | 0 | 45 | 1321
18:30 | 2850 | 1488 | 860 | 38 | 117 | 1129.675 | 222 | 5456.5 | 9.585 | 749.92 | 1940.75 | 125.5 | 0 | 45.5 | 1871.5
19:00 | 2766 | 1484 | 847 | 38 | 120 | 1225.65 | 222 | 5554 | 0 | 816.42 | 2117.5 | 251 | 0 | 46 | 2422
19:30 | 2671 | 1391 | 873 | 38 | 110 | 1205.67 | 222 | 5473 | 0 | 756.42 | 2329.5 | 201 | 0 | 62 | 2448
20:00 | 2712 | 1526 | 873 | 38 | 116 | 1195.77 | 222 | 5610 | 0 | 780.42 | 2328.5 | 201 | 0 | 55 | 1941
20:30 | 2797 | 1564.5 | 873 | 38 | 110 | 1212.74 | 222 | 5596 | 0 | 783.42 | 2364.18 | 258 | 0 | 56.5 | 2239.5
21:00 | 2882 | 1603 | 873 | 38 | 104 | 1229.71 | 222 | 5582 | 0 | 786.42 | 2399.86 | 315 | 0 | 58 | 2538
21:30 | 2939 | 1642.25 | 862.5 | 38 | 106 | 1242.35 | 222 | 5630 | 0 | 747.42 | 2420.36 | 222.5 | 0 | 60 | 1853
22:00 | 2996 | 1681.5 | 852 | 38 | 108 | 1254.99 | 222 | 5678 | 0 | 708.42 | 2440.86 | 130 | 0 | 62 | 1168
22:30 | 3017.5 | 1701.5 | 863 | 38 | 110 | 1256.8 | 222 | 5681.5 | 0 | 708.42 | 2401.36 | 90 | 0 | 45.5 | 1253.5
23:00 | 3039 | 1721.5 | 874 | 38 | 112 | 1258.61 | 222 | 5685 | 0 | 708.42 | 2361.86 | 50 | 0 | 29 | 1339
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 12-08-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 371 | 05:00 | 356 | 11:00 | Madunaghat | 396 | 02:00 | 391 | 12:00
Amtali | 410 | 02:00 | 406 | 11:00 | Meghnaghat | 376 | 06:00 | 353 | 09:00
Ashuganj | 387 | 05:00 | 376 | 11:00 | Mirsorai | 393 | 02:00 | 385 | 11:00
Bhulta | 388 | 02:00 | 370 | 11:00 | Payra | 412 | 05:00 | 408 | 11:00
Bibiana | 377 | 01:00 | 369 | 12:00 | Rahanpur | 411 | 10:00 | 392 | 23:00
BIPTC | 401 | 06:00 | 392 | 00:00 | Rampal | 393 | 01:00 | 381 | 22:00
Bogura | 396 | 10:00 | 374 | 22:00
Gopalganj | 387 | 05:00 | 376 | 11:00
Kaliakoir | 361 | 05:00 | 343 | 13:00
Korerhat | 391 | 04:00 | 383 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 06:00 | 213 | 11:00 | Ishurdi | 235 | 10:00 | 209 | 22:00
AKSML | 235 | 05:00 | 226 | 22:00 | Jhenaidah | 226 | 10:00 | 195 | 22:00
Aminbazar | 226 | 05:00 | 214 | 11:00 | Kachua | 227 | 01:00 | 221 | 08:00
Ashuganj | 227 | 23:00 | 217 | 00:00 | Kaliakoir | 226 | 05:00 | 210 | 13:00
Ashuganj-400 | 227 | 23:00 | 217 | 00:00 | Keranigonj | 223 | 03:00 | 211 | 11:00
Baghabari | 232 | 08:00 | 215 | 22:00 | Khulna(S) | 224 | 02:00 | 209 | 22:00
Barapukuria | 225 | 10:00 | 211 | 23:00 | Korerhat | 224 | 04:00 | 218 | 15:00
Barapukuria-230 | 225 | 10:00 | 211 | 23:00 | Madunaghat | 236 | 00:00 | 232 | 11:00
Barishal | 224 | 00:00 | 216 | 22:00 | Madunaghat-400 | 238 | 02:00 | 235 | 10:00
Bheramara | 234 | 10:00 | 206 | 22:00 | Maniknagar | 227 | 03:00 | 209 | 11:00
Bhulta | 224 | 06:00 | 212 | 11:00 | Meghnaghat | 230 | 05:00 | 218 | 10:00
Bibiana | 220 | 02:00 | 212 | 17:00 | Meghnaghat-400 | 225 | 02:00 | 212 | 12:00
BIPTC | 236 | 10:00 | 207 | 22:00 | Mirsorai | 230 | 19:30 | 224 | 10:00
Bogura | 238 | 09:00 | 225 | 23:00 | Naogaon | 226 | 09:00 | 201 | 22:00
Bogura-400 | 239 | 10:00 | 225 | 22:00 | Purbasadipur | 222 | 19:30 | 207 | 23:00
Borhanuddin | 228 | 01:00 | 223 | 22:00 | Rajshahi | 234 | 10:00 | 204 | 22:00
BSRM | 225 | 01:00 | 221 | 11:00 | Rampal | 223 | 01:00 | 211 | 22:00
Charfasson | 230 | 09:00 | 224 | 21:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 226 | 02:00 | 219 | 15:00 | Rampura | 224 | 05:00 | 210 | 11:00
Cumilla(N) | 222 | 02:00 | 214 | 16:00 | Shikalbaha | 236 | 01:00 | 231 | 13:00
Faridpur | 219 | 01:00 | 210 | 22:00 | Shyampur | 223 | 03:00 | 211 | 11:00
Fenchuganj | 223 | 02:00 | 211 | 18:00 | Siddhirganj | 223 | 01:00 | 213 | 12:00
Feni | 224 | 03:00 | 217 | 12:00 | Sirajgonj | 236 | 10:00 | 228 | 18:30
Ghorashal | 225 | 01:00 | 218 | 11:00 | Sreepur | 222 | 02:00 | 213 | 18:30
Ghorashal-230 | 218 | 06:00 | 198 | 18:30 | Tongi | 217 | 04:00 | 198 | 11:00
Gopalganj | 220 | 01:00 | 213 | 22:00
GPH | 231 | 05:00 | 227 | 12:00
Haripur | 223 | 05:00 | 212 | 11:00
Hasnabad | 222 | 02:00 | 212 | 11:00
Hathazari | 233 | 04:00 | 229 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 01:00 | 129 | 11:00 | Madartek | 138 | 22:00 | 128 | 12:00
Agargaon | 136 | 03:00 | 127 | 11:00 | Madunaghat | 137 | 00:00 | 134 | 11:00
Agrabad | 134 | 00:00 | 131 | 11:00 | Magura | 135 | 10:00 | 110 | 22:00
AKS | 133 | 00:00 | 130 | 10:00 | Mahasthangarh | 135 | 09:00 | 120 | 22:00
Aminbazar | 129 | 22:00 | 120 | 11:00 | Maijdee | 127 | 02:00 | 123 | 15:00
Amnura | 137 | 00:00 | 121 | 12:00 | Manikganj | 125 | 19:00 | 120 | 08:00
Ashuganj | 132 | 23:00 | 26 | 15:00 | Maniknagar | 138 | 05:00 | 128 | 11:00
Ashuganj-230 | 134 | 23:00 | 128 | 18:00 | Matarbari | 133 | 04:00 | 119 | 23:00
Bagerhat | 127 | 00:00 | 114 | 23:00 | Matuail | 133 | 05:00 | 126 | 11:00
Bajitpur | 130 | 23:00 | 119 | 18:00 | Metrorail_Motijheel | 138 | 05:00 | 128 | 11:00
Bakerganj | 130 | 08:00 | 124 | 22:00 | Metrorail_Uttara | 133 | 05:00 | 114 | 14:00
Bakulia | 137 | 06:00 | 132 | 18:30 | Millgate | 133 | 03:00 | 115 | 12:00
Banani | 139 | 22:00 | 128 | 11:00 | Mirpur | 128 | 22:00 | 119 | 11:00
Bangabhaban | 138 | 03:00 | 128 | 11:00 | Mirzapur | 127 | 06:00 | 122 | 09:00
Barapukuria | 137 | 09:00 | 122 | 23:00 | Mithapukur | 132 | 00:00 | 118 | 22:00
Barguna | 131 | 17:00 | 124 | 22:00 | MI_Cement | 131.7 | 06:00 | 121 | 11:00
Barishal | 129 | 00:00 | 124 | 22:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal-230 | 130 | 00:00 | 124 | 22:00 | Mogbazar | 139 | 22:00 | 130 | 13:00
Baroaulia | 135 | 02:00 | 132 | 13:00 | Mongla | 127 | 08:00 | 113 | 22:00
Baroirhat | 131 | 01:00 | 126 | 12:00 | Motijheel | 138 | 03:00 | 128 | 11:00
Bashundhara | 138 | 02:00 | 116 | 14:00 | Muktagacha | 128 | 18:00 | 112 | 00:00
BashundharaCement | 133 | 07:00 | 127 | 11:00 | Munshiganj | 131 | 05:00 | 124 | 10:00
Beanibazar | 123 | 01:00 | 112 | 18:00 | Muradnagar | 128 | 02:00 | 121 | 11:00
Benapole | 131 | 07:00 | 105 | 22:00 | Mymensingh | 127 | 19:30 | 112 | 01:00
Bhaluka | 132 | 02:00 | 121 | 18:30 | Nabinagar | 126 | 06:00 | 119 | 14:00
Bhandaria | 128 | 19:30 | 117 | 22:00 | Naogaon | 136 | 09:00 | 121 | 23:00
Bhangura | 133 | 10:00 | 122 | 22:00 | Narail | 135 | 10:00 | 111 | 22:00
Bheramara | 137 | 10:00 | 120 | 22:00 | Narinda | 138 | 05:00 | 128 | 11:00
Bheramara(GK) | 138 | 10:00 | 120 | 22:00 | Narshingdi | 127 | 22:00 | 116 | 14:00
Bhulta | 128 | 22:00 | 122 | 11:00 | Natore | 136 | 10:00 | 117 | 22:00
Bhulta-400 | 130 | 06:00 | 122 | 11:00 | Nawabganj | 135 | 06:00 | 126 | 11:00
Bog-Sherpur | 134 | 05:00 | 121 | 22:00 | Netrakona | 124 | 22:00 | 110 | 18:30
Bogura | 137 | 09:00 | 126 | 22:00 | New | 132 | 04:00 | 118 | 14:00
Bogura-230 | 137 | 09:00 | 126 | 22:00 | Niamatpur | 138 | 11:00 | 128 | 22:00
Brahmanbaria | 129 | 23:00 | 121 | 00:00 | Noapara | 132 | 03:00 | 119 | 23:00
Cantonment | 136 | 05:00 | 126 | 11:00 | Pabna | 135 | 10:00 | 120 | 22:00
Chandina | 129 | 02:00 | 123 | 12:00 | Palashbari | 130 | 09:00 | 114 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandpur | 133 | 00:00 | 130 | 15:00 | Panchagarh | 135 | 10:00 | 123 | 23:00
Chandraghona | 137 | 06:00 | 134 | 18:30 | Patiya | 136 | 01:00 | 131 | 19:30
Chapai | 135 | 03:00 | 129 | 23:00 | Patnitala | 130 | 19:30 | 115 | 23:00
Charsaidpur | 133 | 22:00 | 127 | 10:00 | Patuakhali | 130 | 04:00 | 124 | 23:00
Chauddagram | 129 | 02:00 | 124 | 12:00 | Payra | 134 | 07:00 | 131 | 22:00
Chhatak | 125 | 02:00 | 107 | 18:30 | PHP | 131 | 03:00 | 127 | 10:00
Chowmuhani | 127 | 01:00 | 124 | 22:00 | Postogola | 133 | 03:00 | 124 | 11:00
Chuadanga | 133 | 10:00 | 111 | 22:00 | Pubail | 127 | 06:00 | 117 | 18:00
Coxsbazar | 132 | 10:00 | 119 | 20:00 | Purbachal | 138 | 01:00 | 128 | 13:00
Cumilla(N) | 129 | 01:00 | 124 | 11:00 | Purbasadipur | 134 | 07:00 | 123 | 23:00
Cumilla(S) | 130 | 00:00 | 122 | 11:00 | Rahanpur | 137 | 09:00 | 130 | 21:00
Daganbhuiyan | 130 | 03:00 | 125 | 12:00 | Rahanpur-400 | 137 | 04:00 | 131 | 22:00
Daudkandi | 127 | 02:00 | 120 | 11:00 | Rahim | 133 | 05:00 | 126 | 11:00
DhakaUniversity | 138 | 01:00 | 129 | 11:00 | Rajbari | 125 | 00:00 | 118 | 22:00
Dhamrai | 127 | 05:00 | 119 | 14:00 | Rajendrapur | 132 | 02:00 | 123 | 18:30
Dhanmondi | 140 | 22:00 | 129 | 11:00 | Rajshahi | 133 | 09:00 | 113 | 22:00
Dohazari | 134 | 00:00 | 128 | 20:00 | Rajshahi-230 | 135 | 10:00 | 116 | 22:00
Faridpur | 127 | 00:00 | 121 | 22:00 | Ramganj | 129 | 01:00 | 123 | 23:00
Fatullah | 133 | 06:00 | 122 | 11:00 | Rampur | 135 | 05:00 | 130 | 18:30
Fenchuganj | 132 | 03:00 | 123 | 16:00 | Rampura | 138 | 02:00 | 129 | 11:00
Feni | 130 | 06:00 | 125 | 15:00 | Rangamati | 136 | 00:00 | 133 | 18:30
Feni-230 | 131 | 03:00 | 126 | 11:00 | Rangpur | 132 | 18:30 | 117 | 23:00
Ghatail | 124 | 20:00 | 116 | 00:00 | Ruppur | 138 | 10:00 | 119 | 22:00
Ghorashal | 129 | 01:00 | 120 | 14:00 | Saidpur | 134 | 09:00 | 123 | 22:00
Goalpara | 134 | 01:00 | 122 | 22:00 | Santhia | 135 | 09:00 | 122 | 22:00
Gollamari | 134 | 01:00 | 124 | 22:00 | Satkhira | 130 | 05:00 | 116 | 23:00
Gopalganj | 131 | 01:00 | 122 | 23:00 | Satmasjid | 136 | 06:00 | 126 | 11:00
Gopalganj-400 | 158 | 15:00 | 125 | 21:00 | Savar | 128 | 22:00 | 118 | 11:00
Gulshan | 136 | 03:00 | 128 | 12:00 | SevenRings | 130 | 03:00 | 119 | 18:30
Halishahar | 136 | 01:00 | 131 | 18:30 | ShahCement | 133 | 22:00 | 127 | 10:00
Haripur | 133 | 02:00 | 127 | 11:00 | Shahjadpur | 136 | 10:00 | 126 | 22:00
HaripurSBU | 133 | 02:00 | 127 | 11:00 | Shahjibazar | 130 | 02:00 | 118 | 16:00
Hasnabad | 133 | 06:00 | 124 | 10:00 | Shahmirpur | 137 | 04:00 | 133 | 15:00
Hathazari | 136 | 01:00 | 134 | 09:00 | Shariatpur | 129 | 06:00 | 121 | 22:00
Hatirjheel | 140 | 22:00 | 129 | 11:00 | Sherpur | 128 | 18:30 | 108 | 05:00
Ishurdi | 139 | 10:00 | 123 | 22:00 | Shikalbaha | 126 | 01:00 | 122 | 13:00
Jaldhaka | 131 | 10:00 | 119 | 23:00 | Shikalbaha-230 | 137 | 01:00 | 134 | 13:00
Jamalpur | 132 | 22:00 | 112 | 03:00 | Shitalakhya | 131.7 | 06:00 | 121 | 11:00
Jashore | 130 | 07:00 | 115 | 23:00 | Sholosohor | 136 | 00:00 | 133 | 18:30
Jhenaidah | 137 | 10:00 | 111 | 22:00 | Shomvuganj | 124 | 23:00 | 115 | 12:00
Jhenaidah-230 | 136 | 02:00 | 115 | 22:00 | Shyampur | 133 | 05:00 | 124 | 12:00
Joydebpur | 125 | 05:00 | 117 | 15:00 | Shyampur-230 | 134 | 22:00 | 125 | 11:00
Joypurhat | 132 | 04:00 | 116 | 22:00 | Siddhirganj | 133 | 02:00 | 127 | 10:00
Juldah | 136 | 00:00 | 133 | 10:00 | Sirajganj | 131 | 10:00 | 118 | 22:00
Kabirpur | 129 | 06:00 | 112 | 11:00 | Sitakunda | 136 | 03:00 | 133 | 11:00
Kachua | 130 | 01:00 | 126 | 15:00 | Sonargaon | 129 | 19:00 | 125 | 11:00
Kaliakoir | 131 | 06:00 | 124 | 17:00 | Sreemongol | 129 | 02:00 | 117 | 16:00
Kaliganj | 135 | 10:00 | 113 | 22:00 | Sreepur | 135 | 02:00 | 128 | 12:00
Kallyanpur | 129 | 22:00 | 120 | 10:00 | Srinagar | 135 | 06:00 | 125 | 11:00
Kalurghat | 136 | 00:00 | 134 | 15:00 | SSM | 140 | 01:00 | 139 | 00:00
Kamrangirchar | 135 | 06:00 | 117 | 11:00 | Sunamganj | 123 | 03:00 | 103 | 18:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 126 | 03:00 | 110 | 18:00
Kasba | 127 | 02:00 | 120 | 22:00 | Sylhet_(South) | 128 | 03:00 | 111 | 18:00
Kazla | 137 | 04:00 | 127 | 13:00 | Tangail | 126 | 06:00 | 117 | 13:00
Keranigonj | 135 | 05:00 | 127 | 11:00 | Taraganj | 132 | 10:00 | 119 | 23:00
Khagrachori | 135 | 00:00 | 132 | 18:30 | Tasnim | 131 | 05:00 | 125 | 11:00
Khulna | 134 | 02:00 | 120 | 22:00 | Thakurgaon | 136 | 09:00 | 124 | 23:00
Khulna(S) | 134 | 00:00 | 124 | 23:00 | TK | 136 | 01:00 | 134 | 11:00
Khulshi | 134 | 05:00 | 130 | 15:00 | Tongi | 135 | 04:00 | 120 | 13:00
Kishoreganj | 130 | 23:00 | 116 | 18:30 | Ullahpara | 133 | 09:00 | 121 | 22:00
Kodda | 130 | 06:00 | 116 | 13:00 | Ullon | 137 | 01:00 | 128 | 11:00
Korerhat | 131 | 00:00 | 129 | 12:00 | Uttara | 131 | 06:00 | 114 | 13:00
KSRM | 135 | 02:00 | 132 | 15:00 | UttaraNew | 133 | 05:00 | 114 | 14:00
Kulaura | 130 | 03:00 | 121 | 18:30 | Zigatola | 135 | 06:00 | 126 | 11:00
Kurigram | 134 | 05:00 | 112 | 22:00
Kushtia | 133 | 10:00 | 109 | 22:00
Laksam | 129 | 00:00 | 125 | 22:00
Lakshmipur | 126 | 01:00 | 122 | 22:00
Lalbag | 135 | 05:00 | 126 | 13:00
Lalmonirhat | 130 | 09:00 | 112 | 22:00
Madanganj | 133 | 07:00 | 127 | 11:00
Madaripur | 130 | 00:00 | 125 | 21:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 12-08-2026 | [28 empty] | Date: | 12-08-2026 | [28 empty] | Date: | 12-08-2026 | [28 empty] | Date: | 12-08-2026 | [28 empty] | Date: | 12-08-2026 | [18 empty] | Date: | 12-08-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [18 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 224 | 17 | 35 | 17 | 141 | 32 | 0 | 35 | 156 | 0 | 0 | 303 | 0 | 0 | 17 | 295 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 0 | 95 | 16 | 46 | 0 | 13 | 50 | 22 | 17 | 12 | 12 | 0 | 222 | 100 | 4 | 1125 | 16 | 0 | 50 | 17 | 89 | 154 | 0 | 0 | 0 | 1224 | 0 | 13 | 8 | 0 | 320 | 120 | 51 | 5 | 172 | 30 | 51 | 85 | 182 | 0 | 19 | 106 | 112 | 52.2 | 0 | 30 | 310 | 0 | 348 | 40 | 39 | 143 | 0 | 8 | 0 | 81 | 28 | 96 | 0 | 122 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 24 | 7850.62 | 874 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 925 | 0 | 0 | 0 | 1275.54 | 0 | 39 | 0 | 57 | 70 | 0 | 100 | 28 | 8 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 158 | 45 | 95 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 180 | 0 | 1050 | 865 | 17 | 6803.54 | 14654.16 | 104.01
01:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 310 | 17 | 17 | 17 | 141 | 32 | 0 | 35 | 72 | 0 | 0 | 307 | 0 | 0 | 17 | 298 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 0 | 90 | 16 | 26 | 0 | 39 | 50 | 22 | 0 | 12 | 12 | 0 | 219 | 101 | 3 | 1125 | 16 | 0 | 50 | 0 | 92 | 180 | 0 | 0 | 0 | 1165 | 0 | 13 | 8 | 0 | 354 | 154 | 51 | 0 | 190 | 30 | 51 | 85 | 180 | 0 | 19 | 105 | 150 | 52.2 | 0 | 30 | 305 | 0 | 348 | 40 | 39 | 138 | 0 | 8 | 0 | 32 | 30 | 20 | 0 | 122 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7715.62 | 874 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 925 | 0 | 0 | 0 | 999.47 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 27 | 8 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 159 | 45 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1050 | 858 | 17 | 6280.47 | 13996.09 | 104.02
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 325 | 0 | 17 | 17 | 141 | 32 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 0 | 97 | 16 | 19 | 0 | 47 | 50 | 22 | 0 | 12 | 12 | 0 | 218 | 98 | 4 | 1125 | 16 | 0 | 50 | 0 | 94 | 180 | 0 | 0 | 0 | 1182 | 0 | 11 | 8 | 0 | 355 | 154 | 51 | 0 | 181 | 30 | 51 | 85 | 186 | 0 | 19 | 105 | 140 | 52.2 | 0 | 30 | 310 | 0 | 347 | 40 | 39 | 147 | 0 | 8 | 0 | 78 | 30 | 0 | 0 | 122 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7662.62 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 925 | 0 | 0 | 0 | 832.58 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 27 | 8 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 159 | 44 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 100 | 220 | 0 | 1050 | 865 | 17 | 6082.58 | 13745.2 | 104.03
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 299 | 0 | 17 | 17 | 141 | 32 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 10 | 21 | 0 | 0 | 96 | 16 | 18 | 0 | 40 | 0 | 22 | 0 | 12 | 12 | 0 | 218 | 100 | 5 | 1125 | 16 | 0 | 50 | 0 | 90 | 180 | 0 | 0 | 0 | 1160 | 0 | 13 | 8 | 0 | 354 | 154 | 51 | 0 | 171 | 30 | 0 | 85 | 176 | 0 | 19 | 106 | 146 | 52.2 | 0 | 31 | 315 | 0 | 347 | 40 | 39 | 139 | 0 | 0 | 0 | 78 | 30 | 0 | 0 | 121 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7331.2 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 925 | 0 | 0 | 0 | 829.11 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 239 | 0 | 0 | 160 | 44 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 100 | 220 | 0 | 1050 | 865 | 17 | 6078.11 | 13409.31 | 104.04
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 339 | 0 | 17 | 17 | 141 | 32 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 123 | 10 | 21 | 0 | 0 | 100 | 16 | 18 | 0 | 20 | 0 | 22 | 0 | 12 | 12 | 0 | 219 | 99 | 4 | 1125 | 16 | 0 | 50 | 0 | 93 | 180 | 0 | 0 | 0 | 1175 | 0 | 13 | 8 | 0 | 355 | 154 | 51 | 0 | 174 | 30 | 0 | 85 | 185 | 0 | 19 | 100 | 136 | 52.2 | 0 | 31 | 310 | 0 | 360 | 40 | 39 | 141 | 0 | 0 | 0 | 79 | 25 | 5 | 0 | 121 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7510.2 | 873 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 925 | 0 | 0 | 0 | 836.02 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 160 | 44 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 100 | 220 | 0 | 1050 | 865 | 17 | 6088.02 | 13598.22 | 104.05
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 330 | 0 | 17 | 17 | 141 | 32 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 0 | 101 | 16 | 19 | 0 | 54 | 0 | 22 | 0 | 12 | 12 | 0 | 220 | 100 | 6 | 1125 | 16 | 0 | 50 | 0 | 89 | 180 | 0 | 0 | 0 | 1163 | 0 | 13 | 8 | 0 | 354 | 77 | 51 | 0 | 196 | 30 | 0 | 85 | 186 | 0 | 19 | 104 | 132 | 8 | 0 | 31 | 305 | 0 | 373 | 40 | 39 | 144 | 0 | 8 | 0 | 79 | 25 | 5 | 0 | 121 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7438.42 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 925 | 0 | 0 | 0 | 846.83 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 157 | 44 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 100 | 220 | 0 | 1000 | 865 | 17 | 6065.83 | 13504.25 | 104.06
06:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 337 | 0 | 0 | 17 | 141 | 32 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 0 | 100 | 16 | 20 | 0 | 50 | 0 | 22 | 0 | 12 | 12 | 0.24 | 222 | 100 | 5 | 1125 | 16 | 0 | 50 | 0 | 94 | 180 | 0 | 0 | 0 | 1166 | 0 | 13 | 8 | 0 | 355 | 10 | 51 | 0 | 205 | 30 | 0 | 85 | 184 | 0 | 19 | 106 | 124 | 8 | 5 | 31 | 300 | 0 | 367 | 40 | 39 | 143 | 0 | 8 | 0 | 79 | 25 | 7 | 0 | 121 | 17 | 49 | 0.22 | 48 | 0 | 0 | 0.83 | 11 | 7347.71 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 2.68 | 925 | 0 | 0 | 0 | 849.99 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 0.37 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 158 | 44 | 95 | 1 | 0 | 0 | 0 | 0 | 0.2 | 4 | 0.02 | 0 | 307 | 100 | 220 | 0 | 1000 | 865 | 17 | 6060.26 | 13407.97 | 104.07
07:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 313 | 0 | 0 | 17 | 111 | 32 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 298 | 0 | 0 | 3 | 143.42 | 9 | 21 | 0 | 0 | 92 | 16 | 19 | 0 | 53 | 0 | 22 | 0 | 12 | 12 | 0.41 | 220 | 99 | 2 | 1125 | 16 | 0 | 50 | 0 | 91 | 180 | 0 | 0 | 0 | 1167 | 0 | 13 | 26 | 0 | 355 | 7 | 51 | 0 | 193 | 30 | 0 | 85 | 178 | 0 | 19 | 106 | 116 | 8 | 25 | 31 | 300 | 0 | 367 | 40 | 39 | 132 | 2 | 8 | 0 | 79 | 25 | 7 | 0 | 121 | 0 | 49 | 3.25 | 48 | 0 | 0.1 | 6.63 | 8 | 7263.81 | 873 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 8.59 | 925 | 0 | 0 | 0 | 880.14 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 6.03 | 3 | 0 | 0 | 1.4 | 150 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 0.38 | 157 | 44 | 95 | 2 | 0 | 0 | 0 | 0 | 0.8 | 20 | 0.05 | 0 | 307 | 100 | 220 | 0 | 1000 | 847 | 17 | 6107.39 | 13371.2 | 104.08
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 321 | 0 | 0 | 11 | 112 | 32 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 313 | 0 | 0 | 4 | 143.42 | 9 | 21 | 0 | 0 | 90 | 16 | 19 | 0 | 48 | 0 | 22 | 0 | 12 | 12 | 2.25 | 222 | 91 | 0 | 1125 | 16 | 0 | 50 | 0 | 90 | 180 | 0 | 0 | 0 | 1169 | 3 | 12 | 26 | 0 | 355 | 7 | 51 | 0 | 207 | 30 | 0 | 85 | 180 | 0 | 19 | 106 | 132 | 8 | 48 | 31 | 300 | 0 | 367 | 40 | 38 | 130 | 5 | 8 | 0 | 79 | 25 | 56 | 0 | 0 | 0 | 49 | 8.55 | 48 | 0 | 0.2 | 35.19 | 12 | 7296.61 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 39 | 925 | 0 | 0 | 0 | 838.02 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 39.26 | 6 | 0 | 0 | 35.67 | 150 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 3.91 | 156 | 45 | 95 | 10 | 0 | 0 | 0 | 0 | 3.3 | 20 | 0.15 | 0 | 307 | 100 | 180 | 0 | 1000 | 848 | 17 | 6144.31 | 13440.92 | 104.09
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 318 | 0 | 0 | 0 | 112 | 32 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 300 | 0 | 0 | 21 | 143.42 | 9 | 21 | 0 | 0 | 97 | 16 | 18 | 0 | 59 | 0 | 20 | 0 | 12 | 12 | 3.3 | 222 | 91 | 0 | 1125 | 16 | 0 | 50 | 0 | 93 | 187 | 0 | 0 | 0 | 1160 | 1 | 13 | 61 | 0 | 354 | 36 | 51 | 0 | 196 | 35 | 0 | 72 | 184 | 0 | 19 | 34 | 146 | 8 | 20 | 30 | 305 | 0 | 368 | 40 | 38 | 146 | 8 | 8 | 0 | 78 | 25 | 139 | 0 | 0 | 10 | 49 | 18.11 | 48 | 0 | 1 | 35.32 | 12 | 7404.15 | 873 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 25 | 925 | 0 | 0 | 0 | 835.74 | 0 | 39 | 0 | 0 | 7 | 0 | 0 | 14 | 34 | 23.11 | 24 | 0 | 0 | 19.43 | 150 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 1.74 | 157 | 45 | 95 | 24 | 0 | 0 | 0 | 0 | 2.9 | 70 | 0.36 | 0 | 307 | 100 | 220 | 0 | 1000 | 860 | 17 | 6228.28 | 13632.43 | 104.11
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 187 | 0 | 10 | 0 | 111 | 32 | 0 | 17 | 0 | 0 | 0 | 274 | 0 | 0 | 0 | 288 | 0 | 0 | 9 | 143.42 | 9 | 21 | 0 | 0 | 89 | 16 | 19 | 0 | 51 | 0 | 21 | 0 | 12 | 12 | 4.22 | 222 | 93 | 0 | 1125 | 16 | 0 | 50 | 0 | 92 | 188 | 0 | 0 | 0 | 1100 | 3 | 13 | 63 | 0 | 340 | 147 | 43 | 0 | 181 | 39 | 6 | 58 | 174 | 0 | 17 | 26 | 182 | 8 | 51 | 30 | 305 | 0 | 368 | 40 | 38 | 127 | 11 | 8 | 0 | 78 | 25 | 139 | 0 | 0 | 17 | 59 | 20.15 | 113 | 0 | 0.7 | 26.79 | 12 | 7380.28 | 845 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 83 | 925 | 0 | 0 | 0 | 894.64 | 0 | 39 | 0 | 0 | 35 | 0 | 0 | 15 | 43 | 41.22 | 80 | 0 | 0 | 23.84 | 150 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 2.48 | 159 | 45 | 95 | 28 | 0 | 0 | 0 | 0 | 6.5 | 138 | 0.27 | 0 | 307 | 100 | 180 | 0 | 1000 | 850 | 17 | 6427.95 | 13808.23 | 104.13
11:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 312 | 0 | 35 | 17 | 125 | 32 | 0 | 35 | 0 | 0 | 0 | 283 | 0 | 0 | 0 | 316 | 0 | 0 | 21 | 143.42 | 9 | 21 | 0 | 0 | 89 | 16 | 20 | 0 | 45 | 0 | 21 | 0 | 12 | 25 | 4.98 | 222 | 91 | 0 | 1125 | 52 | 0 | 49 | 1 | 87 | 199 | 0 | 0 | 0 | 1165 | 0 | 23 | 178 | 0 | 355 | 73 | 43 | 14 | 173 | 36 | 34 | 57 | 177 | 6 | 5 | 17 | 166 | 8 | 55 | 30 | 300 | 0 | 351 | 40 | 38 | 132 | 11 | 8 | 0 | 83 | 25 | 140 | 0 | 0 | 17 | 59 | 20.75 | 116 | 0 | 2.3 | 22.38 | 12 | 7827.83 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 47 | 925 | 0 | 0 | 0 | 920.51 | 0 | 39 | 0 | 0 | 35 | 0 | 0 | 15 | 43 | 26.48 | 100 | 0 | 0 | 38.72 | 150 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 4.21 | 158 | 45 | 95 | 32 | 0 | 0 | 0 | 0 | 7.9 | 124 | 0.39 | 0 | 274 | 100 | 220 | 0 | 1000 | 850 | 17 | 6451.21 | 14279.04 | 104.15
12:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 262 | 35 | 0 | 17 | 137 | 32 | 0 | 35 | 138 | 0 | 0 | 283 | 0 | 0 | 55 | 315 | 0 | 0 | 0 | 143.42 | 9 | 0 | 0 | 0 | 91 | 16 | 36 | 0 | 51 | 0 | 20 | 17 | 24 | 25 | 4.67 | 220 | 93 | 0 | 1125 | 88 | 0 | 0 | 8 | 88 | 203 | 0 | 0 | 0 | 1168 | 0 | 26 | 182 | 0 | 351 | 110 | 43 | 43 | 178 | 35 | 35 | 0 | 180 | 26 | 5 | 17 | 116 | 8 | 78 | 30 | 300 | 0 | 356 | 40 | 38 | 143 | 11 | 0 | 0 | 82 | 25 | 140 | 0 | 0 | 17 | 59 | 18.5 | 116 | 0 | 2.2 | 53.92 | 12 | 8014.71 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 66 | 925 | 0 | 0 | 0 | 931.46 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 15 | 43 | 28.3 | 113 | 0 | 0 | 64.4 | 150 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 5.87 | 158 | 45 | 95 | 29 | 0 | 0 | 0 | 0 | 7.9 | 183 | 0.19 | 0 | 276 | 100 | 220 | 0 | 1000 | 860 | 17 | 6621.12 | 14635.83 | 104.17
13:00 | 0 | 70 | 33 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 223 | 54 | 22 | 19 | 136 | 32 | 0 | 35 | 162 | 0 | 0 | 265 | 0 | 0 | 55 | 317 | 0 | 0 | 12 | 143.42 | 9 | 13 | 0 | 0 | 92 | 16 | 42 | 0 | 46 | 0 | 20 | 17 | 12 | 12 | 5.27 | 218 | 91 | 0 | 1125 | 86 | 0 | 1 | 8 | 89 | 200 | 0 | 0 | 0 | 1101 | 1 | 26 | 187 | 0 | 345 | 220 | 43 | 43 | 159 | 38 | 68 | 0 | 179 | 26 | 5 | 17 | 114 | 16 | 77 | 33 | 300 | 0 | 362 | 40 | 38 | 136 | 12 | 8 | 0 | 81 | 25 | 141 | 0 | 0 | 17 | 58 | 15.5 | 116 | 0 | 2 | 49.38 | 12 | 8078.57 | 875 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 37 | 56 | 925 | 0 | 0 | 0 | 924.97 | 0 | 40 | 0 | 35 | 35 | 0 | 0 | 15 | 43 | 47.81 | 118 | 0 | 0 | 59.48 | 144 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 5.54 | 156 | 45 | 94 | 34 | 0 | 0 | 0 | 0 | 6.8 | 153 | 0.11 | 0 | 258 | 100 | 180 | 0 | 1000 | 865 | 17 | 6531.71 | 14610.28 | 104.21
14:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 253 | 54 | 35 | 17 | 135 | 32 | 0 | 35 | 156 | 0 | 0 | 297 | 0 | 0 | 55 | 315 | 0 | 0 | 6 | 140 | 9 | 20 | 0 | 0 | 89 | 16 | 45 | 0 | 28 | 0 | 20 | 17 | 12 | 12 | 3.55 | 218 | 92 | 0 | 1125 | 88 | 0 | 21 | 8 | 87 | 198 | 0 | 0 | 0 | 1108 | 2 | 26 | 192 | 0 | 340 | 210 | 43 | 42 | 154 | 37 | 69 | 0 | 181 | 26 | 3 | 17 | 134 | 16 | 65 | 30 | 300 | 0 | 362 | 40 | 28 | 136 | 10 | 8 | 0 | 81 | 25 | 141 | 0 | 0 | 17 | 59 | 20 | 116 | 0 | 1.7 | 47.19 | 12 | 8098.44 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 69 | 925 | 0 | 0 | 0 | 934 | 0 | 40 | 0 | 37 | 35 | 0 | 17 | 15 | 52.2 | 9.3 | 63 | 0 | 0 | 30.01 | 143 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 4.37 | 156 | 45 | 95 | 25 | 0 | 0 | 0 | 0 | 4.8 | 133 | 0.23 | 0 | 247 | 100 | 220 | 0 | 1000 | 860 | 17 | 6445.91 | 14544.35 | 104.23
15:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 267 | 54 | 35 | 17 | 135 | 32 | 0 | 35 | 154 | 0 | 0 | 297 | 0 | 0 | 55 | 313 | 0 | 0 | 3 | 142 | 10 | 20 | 0 | 0 | 96 | 16 | 53 | 0 | 52 | 0 | 20 | 17 | 12 | 12 | 0 | 219 | 104 | 0 | 1125 | 88 | 0 | 31 | 8 | 86 | 199 | 0 | 0 | 0 | 1163 | 2 | 26 | 195 | 0 | 340 | 210 | 51 | 39 | 154 | 38 | 56 | 0 | 185 | 27 | 0 | 17 | 124 | 16 | 40 | 28 | 310 | 0 | 362 | 38 | 30 | 145 | 9 | 8 | 0 | 81 | 25 | 139 | 0 | 0 | 17 | 59 | 16.48 | 116 | 0 | 1.6 | 37.01 | 12 | 8190.09 | 874 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 32 | 925 | 0 | 0 | 0 | 936.98 | 0 | 40 | 0 | 37 | 35 | 0 | 17 | 15 | 52.2 | 23.02 | 58 | 0 | 0 | 44.93 | 143 | 0 | 0 | 0 | 0 | 0 | 212 | 0 | 4.52 | 158 | 44 | 95 | 12 | 0 | 0 | 0 | 0 | 0.2 | 75 | 0.25 | 0 | 280 | 100 | 220 | 0 | 1000 | 865 | 35 | 6404.1 | 14594.19 | 104.23
16:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 277 | 54 | 21 | 17 | 133 | 32 | 0 | 35 | 153 | 0 | 0 | 292 | 0 | 0 | 55 | 315 | 0 | 0 | 0 | 143 | 10 | 20 | 0 | 0 | 96 | 16 | 45 | 0 | 60 | 0 | 20 | 17 | 12 | 12 | 0.68 | 222 | 93 | 0 | 1125 | 88 | 0 | 36 | 8 | 88 | 199 | 0 | 0 | 0 | 1162 | 1 | 26 | 93 | 0 | 340 | 215 | 51 | 36 | 190 | 38 | 51 | 21 | 183 | 26 | 0 | 34 | 124 | 16 | 36 | 28 | 305 | 15 | 356 | 38 | 28 | 144 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 59 | 7.2 | 116 | 0 | 1.2 | 20.06 | 12 | 7872.14 | 873 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 24 | 925 | 0 | 0 | 0 | 929.45 | 0 | 40 | 0 | 37 | 35 | 0 | 17 | 15 | 52.2 | 10.74 | 11 | 0 | 0 | 31.24 | 140 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 2.96 | 158 | 44 | 95 | 7 | 12 | 0 | 0 | 0 | 1.4 | 69 | 0.13 | 0 | 282 | 100 | 220 | 0 | 1000 | 860 | 35 | 6302.12 | 14174.26 | 104.25
17:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 244 | 54 | 17 | 17 | 133 | 32 | 0 | 35 | 148 | 0 | 0 | 293 | 0 | 0 | 55 | 318 | 0 | 0 | 8 | 143.42 | 10 | 21 | 0 | 0 | 91 | 16 | 43 | 0 | 45 | 7 | 20 | 17 | 12 | 12 | 0.93 | 222 | 96 | 0 | 1125 | 88 | 0 | 44 | 8 | 86 | 211 | 0 | 0 | 0 | 1140 | 1 | 26 | 86 | 0 | 340 | 225 | 51 | 20 | 190 | 37 | 62 | 31 | 181 | 27 | 0 | 106 | 120 | 34 | 13 | 33 | 310 | 130 | 356 | 39 | 28 | 133 | 2 | 8 | 0 | 30 | 0 | 0 | 15 | 0 | 17 | 59 | 5 | 115 | 0 | 0.4 | 8.49 | 21 | 8046.24 | 873 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 7 | 925 | 0 | 0 | 0 | 926.88 | 0 | 40 | 0 | 35 | 35 | 0 | 17 | 21 | 8 | 7.02 | 23 | 0 | 0 | 10.21 | 138 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0.99 | 158 | 44 | 95 | 4 | 75 | 0 | 0 | 0 | 0.6 | 36 | 0.07 | 0 | 270 | 100 | 220 | 0 | 1000 | 852 | 35 | 6277.77 | 14324.01 | 104.26
18:00 | 0 | 88 | 49 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 292 | 54 | 27 | 17 | 135 | 32 | 0 | 35 | 141 | 0 | 0 | 299 | 0 | 0 | 17 | 322 | 0 | 0 | 1 | 143.42 | 9 | 21 | 0 | 0 | 82 | 16 | 40 | 0 | 45 | 50 | 20 | 17 | 12 | 12 | 0 | 222 | 103 | 0 | 1125 | 86 | 0 | 44 | 8 | 87 | 210 | 0 | 0 | 0 | 1065 | 0 | 36 | 86 | 0 | 340 | 230 | 51 | 20 | 194 | 35 | 68 | 36 | 174 | 27 | 0 | 105 | 114 | 34 | 1 | 38 | 280 | 254 | 382 | 39 | 30 | 121 | 0 | 8 | 0 | 85 | 0 | 93 | 15 | 0 | 17 | 59 | 1.1 | 115 | 0 | 0.1 | 2.32 | 24 | 8336.94 | 873 | 0 | 0 | 16 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 1 | 908 | 0 | 0 | 0 | 1033.7 | 0 | 38 | 0 | 35 | 40 | 0 | 17 | 22 | 8 | 1.71 | 3 | 0 | 0 | 2.32 | 138 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0.19 | 156 | 45 | 75 | 1 | 84 | 0 | 0 | 0 | 0.4 | 4 | 0.03 | 16 | 216 | 100 | 220 | 0 | 1000 | 844 | 17 | 6240.35 | 14577.29 | 103.27
19:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 286 | 54 | 35 | 30 | 136 | 64 | 0 | 14 | 154 | 0 | 0 | 285 | 0 | 0 | 35 | 322 | 0 | 0 | 0 | 143.42 | 10 | 21 | 0 | 0 | 99 | 16 | 44 | 0 | 46 | 50 | 20 | 17 | 12 | 12 | 0 | 222 | 93 | 0 | 1125 | 125 | 0 | 45 | 25.5 | 85 | 210 | 0 | 0 | 0 | 1140 | 0 | 125 | 86 | 0 | 340 | 230 | 51 | 20 | 192 | 39 | 69 | 50 | 186 | 27 | 0 | 105 | 120 | 43 | 0 | 38 | 265 | 80 | 382 | 39 | 30 | 146 | 0 | 8 | 0 | 86 | 0 | 95 | 15 | 0 | 17 | 68 | 0 | 152 | 0 | 0 | 0 | 24 | 8540.92 | 847 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 151 | 0 | 67 | 0 | 920 | 0 | 0 | 0 | 1225.65 | 0 | 37 | 0 | 90 | 50 | 0 | 100 | 28 | 8 | 0 | 0 | 20 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 157 | 45 | 75 | 0 | 86 | 0 | 100 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1000 | 860 | 17 | 6946.65 | 15487.57 | 103.27
19:30 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 238 | 54 | 35 | 52 | 127 | 64 | 0 | 35 | 147 | 0 | 0 | 283 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 143.42 | 9 | 13 | 0 | 0 | 85 | 16 | 42 | 0 | 62 | 50 | 20 | 54 | 12 | 12 | 0 | 222 | 99 | 0 | 1125 | 160 | 0 | 45 | 25.5 | 88 | 210 | 0 | 0 | 0 | 1082 | 0 | 150 | 86 | 0 | 340 | 230 | 51 | 20 | 188 | 39 | 69 | 70 | 178 | 27 | 0 | 105 | 110 | 43 | 0 | 38 | 295 | 0 | 387 | 40 | 30 | 122 | 0 | 8 | 0 | 86 | 0 | 96 | 15 | 0 | 17 | 68 | 0 | 153 | 0 | 0 | 0 | 24 | 8398.92 | 873 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 101 | 0 | 67 | 0 | 910 | 0 | 0 | 0 | 1205.67 | 0 | 34 | 0 | 90 | 110 | 0 | 100 | 29 | 8 | 0 | 0 | 20 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 154 | 45 | 88 | 0 | 106 | 0 | 100 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 180 | 0 | 1000 | 850 | 17 | 6933.67 | 15332.59 | 103.28
20:00 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 308 | 54 | 35 | 52 | 139 | 64 | 0 | 55 | 141 | 0 | 0 | 304 | 0 | 0 | 35 | 320 | 0 | 0 | 0 | 143.42 | 9 | 20 | 0 | 0 | 82 | 16 | 40 | 0 | 55 | 50 | 20 | 41 | 12 | 12 | 0 | 222 | 95 | 0 | 1125 | 160 | 0 | 40 | 25.5 | 86 | 210 | 0 | 0 | 0 | 1172 | 0 | 150 | 86 | 0 | 340 | 230 | 51 | 20 | 210 | 36 | 69 | 40 | 177 | 26 | 0 | 105 | 116 | 43 | 0 | 38 | 290 | 0 | 387 | 40 | 30 | 124 | 0 | 8 | 0 | 86 | 0 | 96 | 15 | 0 | 17 | 68 | 0 | 155 | 0 | 0 | 0 | 24 | 8621.92 | 873 | 0 | 0 | 27 | 0 | 38 | 0 | 0 | 101 | 0 | 67 | 0 | 910 | 0 | 0 | 0 | 1195.77 | 0 | 40 | 0 | 95 | 112 | 0 | 100 | 31 | 8 | 0 | 0 | 20 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 156 | 45 | 94 | 0 | 107 | 0 | 100 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1050 | 845 | 17 | 7035.77 | 15657.69 | 103.29
21:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 308 | 54 | 35 | 56 | 141 | 64 | 0 | 55 | 151 | 0 | 0 | 281 | 0 | 0 | 35 | 325 | 0 | 0 | 0 | 143.42 | 9 | 21 | 0 | 0 | 97 | 16 | 44 | 0 | 58 | 50 | 20 | 54.36 | 12 | 12 | 0 | 222 | 107 | 0 | 1125 | 160 | 0 | 45 | 25.5 | 87 | 212 | 0 | 0 | 0 | 1121 | 0 | 150 | 143 | 0 | 355 | 230 | 51 | 24 | 190 | 39 | 69 | 50 | 183 | 27 | 0 | 105 | 104 | 43 | 0 | 38 | 305 | 0 | 387 | 40 | 30 | 147 | 0 | 8 | 0 | 86 | 0 | 94 | 15 | 102 | 17 | 68 | 0 | 155 | 0 | 0 | 0 | 24 | 8879.28 | 873 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 150 | 0 | 67 | 0 | 925 | 0 | 0 | 0 | 1229.71 | 0 | 40 | 0 | 95 | 113 | 0 | 100 | 22 | 8 | 0 | 0 | 20 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 241 | 0 | 0 | 154 | 45 | 95 | 0 | 105 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1050 | 855 | 17 | 7213.71 | 16092.99 | 103.3
22:00 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 313 | 54 | 35 | 52 | 140 | 64 | 0 | 55 | 145 | 0 | 0 | 309 | 0 | 0 | 35 | 325 | 0 | 0 | 0 | 143.42 | 8.5 | 21 | 0 | 0 | 85 | 16 | 50 | 0 | 62 | 50 | 20 | 54.36 | 12 | 12 | 0 | 222 | 104 | 2 | 1125 | 160 | 0 | 45 | 25.5 | 91 | 212 | 0 | 0 | 0 | 1224 | 0 | 150 | 189 | 0 | 354 | 230 | 51 | 38 | 217 | 33 | 69 | 70 | 175 | 28 | 0 | 105 | 108 | 43 | 0 | 38 | 305 | 0 | 387 | 40 | 30 | 131 | 0 | 8 | 0 | 86 | 0 | 95 | 15 | 102 | 17 | 106 | 0 | 164 | 0 | 0 | 0 | 24 | 9085.78 | 852 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 50 | 0 | 67 | 0 | 918 | 0 | 0 | 0 | 1254.99 | 0 | 40 | 0 | 95 | 113 | 0 | 100 | 22 | 8 | 0 | 0 | 14 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 154 | 45 | 110 | 0 | 106 | 0 | 80 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1050 | 855 | 17 | 7085.99 | 16171.77 | 103.33
23:00 | 0 | 10 | 50 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 346 | 54 | 17 | 21 | 139 | 32 | 0 | 55 | 153 | 0 | 0 | 295 | 0 | 0 | 35 | 325 | 0 | 0 | 0 | 143.42 | 8.5 | 21 | 0 | 0 | 92 | 16 | 47 | 0 | 29 | 50 | 20 | 54.36 | 12 | 12 | 0 | 222 | 98 | 2 | 1125 | 160 | 0 | 49 | 25.5 | 94 | 213 | 0 | 0 | 0 | 1224 | 0 | 127 | 194 | 0 | 356 | 230 | 51 | 41 | 214 | 36 | 68 | 72 | 182 | 27 | 0 | 106 | 112 | 43 | 0 | 30 | 305 | 0 | 387 | 40 | 30 | 144 | 0 | 8 | 0 | 86 | 0 | 95 | 15 | 100 | 17 | 107 | 0 | 164 | 0 | 0 | 0 | 24 | 9037.78 | 874 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 925 | 0 | 0 | 0 | 1258.61 | 0 | 39 | 0 | 95 | 113 | 0 | 100 | 22 | 8 | 0 | 0 | 14 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 154 | 44 | 115 | 0 | 106 | 0 | 50 | 0 | 0 | 0 | 0 | 16 | 307 | 100 | 220 | 0 | 1050 | 856 | 17 | 7061.61 | 16099.39 | 104.3
Total KWH | 0 | 1374720 | 603360 | 0 | 0 | 0 | 0 | 0 | 7671600 | 0 | 7291960 | 685080 | 511560 | 505584 | 3186240 | 893989 | 0 | 564169 | 1990080 | 0 | 0 | 7222167 | 0 | 0 | 573468 | 7587912 | 0 | 0 | 106007 | 3289200 | 208200 | 458640 | 0 | 0 | 2235600 | 386400 | 794880 | 0 | 1117440 | 468589 | 501984 | 400877 | 302400 | 318720 | 22402 | 5351758 | 2351018 | 38400 | 27069090.91 | 1754691 | 0 | 1038720 | 189995.4 | 2209672 | 4516469 | 0 | 0 | 0 | 27965452 | 17820 | 1078909 | 2274909 | 0 | 8713400 | 3748000 | 1233000 | 447360 | 4654000 | 816624 | 1002240 | 1313624 | 4344480 | 341880 | 215710 | 1837680 | 3043200 | 653501 | 484255 | 764976 | 7284000 | 0 | 8958000 | 971000 | 824640 | 3321409.09 | 84648 | 165024 | 0 | 1732800 | 415392 | 1489000 | 116000 | 1880310 | 403920 | 1462800 | 143434 | 2373600 | 0 | 13750 | 356310 | 385200 | 193125299.4 | 21032000 | 0 | 0 | 161280 | 0 | 912000 | 0 | 0 | 417095 | 0 | 1459152 | 474480 | 22203640 | 0 | 0 | 0 | 23415636 | 0 | 914127 | 0 | 762528 | 1011264 | 0 | 680160 | 438590 | 564538 | 271056 | 657420 | 81467 | 0 | 388496 | 3548273 | 0 | 0 | 0 | 0 | 0 | 5725745 | 0 | 35880 | 3909000 | 1043781 | 2270857 | 200723 | 929846 | 0 | 521797.5 | 0 | 41604.84 | 1179360 | 2460 | 132576 | 7069000 | 2403000 | 5335690 | 0 | 24560000 | 21297454.55 | 482400 | 156534376.89 | 349659676.29