## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-08-2026 | during | 15-08-2026 | during | 15-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 265 | 218 | 412 | 412 | 380 | 380 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 225 | 225 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 288 | 203 | 335 | 335 | 120 | 120 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 0 | 0 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 240 | 335 | 335 | 300 | 300 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 0 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 123 | 121 | 149.36 | 149.36 | 142 | 142 | Engine Problem
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 0 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 9 | 11.5 | 33 | 33 | 10 | 10 | Gas shortage
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 22 | 22 | 21 | 21 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 50 | 52.19 | 52.19 | 33 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 18 | 245 | 300 | 300 | 32 | 64 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 32 | 82 | 149 | 149 | 17 | 17 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 88 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 162 | 162 | 17 | 108 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 54 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 280 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 273 | 204 | 718 | 718 | 250 | 250 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1913.42 | 2296.92 | 5220.16 | 5195.16 | 1648.42 | 1888.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 25 | 25 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 4 | 0 | 4 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 23 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 0 | 182 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 184 | 121 | 140 | 140 | 140 | 140 | Gas shortage
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 92 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 15 | 24 | 24 | 14 | 40 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 0 | 3 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 14 | 43 | 95.1 | 95.1 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.31 | 0 | 1.93 | 0 | 1.93 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 1 | 54.36 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 67 | 105 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 23 | 85 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 60 | 152 | 163 | 163 | 88 | 160 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1177 | 1224 | 1224 | 1224 | 1224 | 1224 | FGMO
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 11 | 23 | 40 | 44 | 40 | 44 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 770 | 770 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2467.31 | 3032.86 | 4024.89 | 4076.96 | 3378.93 | 3578
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 212 | 185 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 345 | 355 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 320 | 280 | 342.01 | 342.01 | 270 | 270 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 300 | 306 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 31 | 35 | 41.65 | 41.65 | 36 | 36
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 44 | 45 | 52.82 | 52.82 | 45 | 45
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 92 | 195 | 195 | 45 | 45 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 18 | 135 | 150 | 150 | 50 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 3 | 23 | 40 | 40 | 40 | 40 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 40 | 163 | 163 | 51 | 51 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 103 | 170 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 154 | 106 | 84 | 78 | 120 | 120 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 25 | 52.2 | 52.2 | 8 | 52 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 0 | 24.5 | 24.5 | 0 | 0 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 27 | 80 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 26 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 69 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1741 | 2023 | 2772.44 | 2696.44 | 2061.26 | 2201.26
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-08-2026 | during | 15-08-2026 | during | 15-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 20.36 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 115 | 155 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 33.48 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 24 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 5 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 244.94 | 264 | 537.6 | 516.5 | 280.1 | 259
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | machine problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 39 | 0 | 0 | 30 | 30 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 127 | 163 | 163 | 147 | 147 | FGMO+ AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 140 | 139 | 140 | 140 | 95 | 95 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 102 | 102 | machine problem
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 15 | 15 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 369 | 392 | 390 | 390 | 360 | 360
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 270 | 0 | 0 | 240 | 240 | ST Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1232 | 1495 | 1298 | 1298 | 1430 | 1430
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 876 | 898 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 24 | 36 | 36 | 28 | 28 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 20 | 105 | 105 | 105 | 67 | 67 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 63 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 916 | 925 | 925 | 925 | 925 | 925
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1913 | 1990 | 3253 | 3181 | 2130 | 2058
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 600 | 1000 | 600 | 1000 | 600 | 1000 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 48 | 110 | 110 | 0 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 50 | 50 | 60 | 60 | 100 | 100 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 825 | 820 | 605 | 840 | 605 | 840 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 277 | 280 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.36 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2023.36 | 2435 | 2053 | 2687 | 1850 | 2500
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 50.18 | 0 | 48.25 | 0 | 48.25 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 40 | 38 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 204 | 208 | 214 | 214 | 190 | 190 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 20 | 20 | 20 | 20 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 100 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 75 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 1.59 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1265.46 | 1474.25 | 1469.13 | 1469.13 | 1469.13 | 1469.13 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 16.17 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 2144.4 | 2435.25 | 3253.87 | 3039.12 | 2416.29 | 2351.54
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 156 | 165 | 165 | 165 | 165 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.9 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 75 | 95 | 115 | 115 | 95 | 95 | Liquid fuel shortage
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 41 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 211 | 0 | 177.29 | 0 | 177.29 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 494.9 | 321 | 626.29 | 413 | 543.29 | 365
System Total |  |  |  |  | 28843.2 | 29158.791 | 14174.33 | 16293.03 | 23039.25 | 23103.18 | 15738.29 | 16631.22
Forecast Scenario (15-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15710 |  | 1317.9 |  | 17090
|  |  |  | 1:00 | 14590 |  | 1804.95 |  | 16480
|  |  |  | 2:00 | 14220 |  | 1804.95 |  | 16110
|  |  |  | 3:00 | 14210 |  | 1451.6 |  | 15730
|  |  |  | 4:00 | 14120 |  | 1298.8 |  | 15480
|  |  |  | 5:00 | 14250 |  | 1050.5 |  | 15350
|  |  |  | 6:00 | 14080 |  | 830.85 |  | 14950
|  |  |  | 7:00 | 14120 |  | 706.7 |  | 14860
|  |  |  | 8:00 | 14180 |  | 744.9 |  | 14960
|  |  |  | 9:00 | 14090 |  | 1193.75 |  | 15340
|  |  |  | 10:00 | 14460 |  | 1012.3 |  | 15520
|  |  |  | 11:00 | 14620 |  | 993.2 |  | 15660
|  |  |  | 12:00 | 15060 |  | 1270.15 |  | 16390
|  |  |  | 13:00 | 15230 |  | 1231.95 |  | 16520
|  |  |  | 14:00 | 15060 |  | 1480.25 |  | 16610
|  |  |  | 15:00 | 15140 |  | 1518.45 |  | 16730
|  |  |  | 16:00 | 15050 |  | 1528 |  | 16650
|  |  |  | 17:00 | 14850 |  | 1222.4 |  | 16130
|  |  |  | 18:00 | 14480 |  | 1317.9 |  | 15860
|  |  |  | 18:30 | 15000 |  | 1494.575 |  | 16565
|  |  |  | 19:00 | 15720 |  | 1480.25 |  | 17270
|  |  |  | 19:30 | 16290 |  | 1680.8 |  | 18050
|  |  |  | 20:00 | 16250 |  | 1766.75 |  | 18100
|  |  |  | 21:00 | 16190 |  | 1986.4 |  | 18270
|  |  |  | 22:00 | 16120 |  | 1766.75 |  | 17970
|  |  |  | 23:00 | 16070 |  | 1881.35 |  | 18040
Probable Maximum Temperature:
Probable Maximum Demand at Day Peak: |  |  | 16390.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 18270.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16290.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 357.87 MKWHr. |  | 290 | 200 | 240 | 350 | 130 | 336 | 90 | 190 | 160 | 1986
*** This report is generated digitally from Operation Information System (OIS) at 10:07 hrs on 15-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-08-2026 | [28 empty] | Date: | 14-08-2026 | [28 empty] | Date: | 14-08-2026 | [28 empty] | Date: | 14-08-2026 | [28 empty] | Date: | 14-08-2026 | [18 empty] | Date: | 14-08-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 587 | 54 | 34 | 35 | 139 | 32 | 0 | 55 | 151 | 0 | 0 | 300 | 0 | 0 | 55 | 303 | 0 | 0 | 0 | 143.42 | 9 | 22 | 0 | 0 | 94 | 16 | 31 | 0 | 13 | 50 | 32 | 17 | 12 | 12 | 0 | 222 | 107 | 2 | 920 | 145 | 0 | 50 | 25.5 | 98 | 186 | 0 | 0 | 0 | 1160 | 0 | 18 | 78 | 372 | 354 | 47 | 51 | 46 | 212 | 35 | 69 | 80 | 179 | 9 | 0 | 106 | 112 | 43 | 0 | 39 | 285 | 15 | 381 | 42 | 39 | 146 | 0 | 8 | 0 | 86 | 0 | 94 | 0 | 100 | 17 | 69 | 0 | 156 | 0 | 0 | 0 | 24 | 8989.92 | 876 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 925 | 0 | 0 | 0 | 1236.18 | 0 | 40 | 0 | 95 | 113 | 0 | 100 | 30 | 52.2 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 46 | 95 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 100 | 220 | 0 | 600 | 865 | 17 | 6742.38 | 15732.3 | 104.43
01:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 576 | 54 | 35 | 17 | 139 | 32 | 0 | 55 | 155 | 0 | 0 | 307 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 143.42 | 9 | 22 | 0 | 70 | 96 | 16 | 37 | 0 | 14 | 50 | 23 | 0 | 12 | 12 | 0 | 220 | 107 | 2 | 825 | 143 | 0 | 50 | 25.5 | 102 | 186 | 0 | 0 | 0 | 1190 | 0 | 18 | 78 | 372 | 354 | 88 | 51 | 46 | 205 | 35 | 68 | 80 | 184 | 0 | 0 | 105 | 104 | 43 | 0 | 39 | 305 | 0 | 381 | 40 | 39 | 149 | 0 | 8 | 0 | 86 | 0 | 96 | 0 | 100 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 8746.92 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 925 | 0 | 0 | 0 | 1116.87 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 30 | 52.2 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 46 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 50 | 220 | 0 | 600 | 860 | 17 | 6221.07 | 14967.99 | 104.43
02:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 569 | 0 | 35 | 17 | 140 | 32 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 143.42 | 9 | 22 | 0 | 70 | 104 | 16 | 37 | 0 | 11 | 50 | 16 | 0 | 12 | 12 | 0 | 220 | 97 | 2 | 770 | 34 | 0 | 50 | 25.5 | 105 | 186 | 0 | 0 | 0 | 1190 | 0 | 18 | 78 | 393 | 354 | 100 | 51 | 46 | 209 | 35 | 69 | 70 | 189 | 0 | 0 | 105 | 96 | 43 | 0 | 39 | 310 | 0 | 381 | 40 | 39 | 152 | 0 | 8 | 0 | 86 | 0 | 96 | 0 | 100 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 8267.92 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 925 | 0 | 0 | 0 | 1127.68 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 30 | 52.2 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 40 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 50 | 220 | 0 | 600 | 860 | 17 | 6210.88 | 14478.8 | 104.43
03:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 566 | 0 | 35 | 17 | 140 | 32 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 143.42 | 9 | 22 | 0 | 64 | 102 | 16 | 27 | 0 | 14 | 0 | 16 | 0 | 12 | 12 | 0 | 219 | 94 | 2 | 770 | 17 | 0 | 50 | 25.5 | 105 | 186 | 0 | 0 | 0 | 1175 | 0 | 18 | 78 | 393 | 355 | 114 | 51 | 46 | 206 | 35 | 0 | 70 | 190 | 0 | 0 | 105 | 94 | 52.2 | 0 | 39 | 310 | 0 | 381 | 40 | 39 | 152 | 0 | 8 | 0 | 86 | 0 | 95 | 0 | 100 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 8095.12 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 925 | 0 | 0 | 0 | 1121.47 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 28 | 52.2 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 40 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 50 | 220 | 0 | 600 | 865 | 17 | 6207.67 | 14302.79 | 104.43
04:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 526 | 0 | 35 | 17 | 140 | 32 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 143.42 | 9 | 22 | 0 | 80 | 100 | 16 | 24 | 0 | 24 | 0 | 16 | 0 | 12 | 12 | 0 | 218 | 92 | 2 | 770 | 15 | 0 | 50 | 25.5 | 104 | 187 | 0 | 0 | 0 | 1160 | 0 | 18 | 8 | 393 | 356 | 136 | 51 | 46 | 216 | 35 | 0 | 70 | 185 | 0 | 0 | 104 | 92 | 52.2 | 0 | 39 | 315 | 0 | 381 | 40 | 39 | 153 | 0 | 8 | 0 | 86 | 0 | 95 | 0 | 100 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7961.12 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 925 | 0 | 0 | 0 | 1117.61 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 28 | 52.2 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 158 | 40 | 95 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 50 | 220 | 0 | 600 | 860 | 17 | 6200.81 | 14161.93 | 104.43
05:00 | 0 | 72 | 34 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 524 | 0 | 21 | 17 | 141 | 32 | 0 | 0 | 0 | 0 | 0 | 279 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 143.42 | 9 | 22 | 0 | 115 | 97 | 16 | 24 | 0 | 5 | 0 | 16 | 0 | 12 | 12 | 0 | 219 | 94 | 3 | 770 | 16 | 0 | 50 | 25.5 | 101 | 187 | 0 | 0 | 0 | 1160 | 0 | 18 | 8 | 393 | 354 | 147 | 51 | 46 | 217 | 35 | 0 | 70 | 182 | 0 | 0 | 104 | 96 | 52.2 | 0 | 39 | 310 | 0 | 374 | 40 | 39 | 153 | 0 | 8 | 0 | 86 | 0 | 0 | 0 | 100 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 7804.12 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 925 | 0 | 0 | 0 | 1120.47 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 28 | 52.2 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 45 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 50 | 220 | 0 | 600 | 860 | 17 | 6171.67 | 13975.79 | 104.43
06:00 | 0 | 72 | 34 | 0 | 0 | 0 | 0 | 0 | 261 | 0 | 411 | 0 | 24 | 17 | 141 | 32 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 0 | 0 | 278 | 0 | 0 | 1 | 143.42 | 0 | 22 | 0 | 120 | 90 | 16 | 24 | 0 | 15 | 0 | 16 | 0 | 12 | 12 | 0.09 | 219 | 92 | 3 | 770 | 16 | 0 | 48 | 8 | 95 | 187 | 0 | 0 | 0 | 1150 | 1 | 18 | 8 | 393 | 354 | 170 | 51 | 47 | 217 | 35 | 0 | 50 | 173 | 0 | 0 | 105 | 86 | 8 | 3 | 39 | 310 | 0 | 374 | 40 | 39 | 135 | 0 | 8 | 0 | 86 | 0 | 0 | 0 | 100 | 0 | 49 | 0.33 | 48 | 0 | 0.1 | 1.56 | 12 | 7579.5 | 875 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 2 | 925 | 0 | 0 | 0 | 1118.36 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 28 | 25 | 1.23 | 1 | 0 | 0 | 1.5 | 208 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.17 | 156 | 47 | 95 | 1 | 0 | 0 | 0 | 0 | 0.2 | 5 | 0.01 | 16 | 307 | 50 | 220 | 0 | 600 | 850 | 17 | 6082.47 | 13661.97 | 104.43
07:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 339 | 0 | 17 | 17 | 128 | 32 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 0 | 296 | 0 | 0 | 2 | 143.42 | 0 | 22 | 0 | 150 | 45 | 16 | 24 | 0 | 9 | 0 | 16 | 0 | 12 | 12 | 0.54 | 220 | 91 | 3 | 770 | 16 | 0 | 37 | 8 | 51 | 187 | 0 | 0 | 0 | 1190 | 3 | 18 | 8 | 393 | 354 | 280 | 51 | 46 | 217 | 35 | 0 | 50 | 136 | 0 | 0 | 52 | 86 | 0 | 20 | 0 | 305 | 0 | 375 | 40 | 39 | 140 | 2 | 8 | 0 | 86 | 0 | 0 | 0 | 100 | 0 | 49 | 4.18 | 48 | 0 | 0.5 | 12.26 | 8 | 7466.9 | 875 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 22 | 925 | 0 | 0 | 0 | 1123.04 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 5.42 | 7 | 0 | 0 | 5.5 | 209 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.94 | 160 | 48 | 95 | 6 | 0 | 0 | 0 | 0 | 0.6 | 43 | 0.15 | 16 | 307 | 50 | 220 | 0 | 600 | 835 | 17 | 6084.65 | 13551.55 | 104.43
08:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 261 | 0 | 266 | 0 | 17 | 17 | 128 | 32 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 266 | 0 | 0 | 13 | 143.42 | 0 | 22 | 0 | 150 | 47 | 16 | 24 | 0 | 13 | 0 | 16 | 0 | 12 | 12 | 1.05 | 0 | 93 | 2 | 770 | 17 | 0 | 25 | 8 | 48 | 187 | 0 | 0 | 0 | 1105 | 4 | 18 | 8 | 393 | 355 | 320 | 51 | 46 | 209 | 35 | 0 | 51 | 130 | 0 | 0 | 17 | 88 | 0 | 36 | 0 | 310 | 0 | 367 | 40 | 39 | 141 | 6 | 8 | 0 | 86 | 0 | 6 | 0 | 100 | 0 | 49 | 7.11 | 48 | 0 | 0 | 9.54 | 12 | 7095.12 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 30 | 925 | 0 | 0 | 0 | 1236.36 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 18.84 | 43 | 0 | 0 | 18.5 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.16 | 156 | 46 | 95 | 15 | 0 | 0 | 0 | 0 | 2 | 94 | 0.32 | 16 | 307 | 50 | 220 | 0 | 600 | 825 | 17 | 6341.18 | 13436.3 | 104.48
09:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 264 | 0 | 278 | 0 | 17 | 17 | 127 | 32 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 280 | 0 | 0 | 17 | 143.42 | 9 | 22 | 0 | 160 | 15 | 16 | 24 | 0 | 15 | 0 | 0 | 0 | 12 | 12 | 3.34 | 0 | 91 | 0 | 770 | 16 | 0 | 6 | 8 | 43 | 188 | 0 | 0 | 0 | 1025 | 14 | 18 | 8 | 320 | 300 | 342 | 51 | 45 | 216 | 35 | 0 | 51 | 122 | 0 | 0 | 17 | 90 | 0 | 59 | 0 | 300 | 0 | 369 | 40 | 39 | 124 | 9 | 8 | 0 | 83 | 0 | 8 | 0 | 101 | 0 | 49 | 17.76 | 48 | 0 | 0 | 22.73 | 12 | 6919.25 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 65 | 923 | 0 | 0 | 0 | 1268.54 | 0 | 40 | 0 | 0 | 7 | 0 | 0 | 15 | 8 | 20.75 | 22 | 0 | 0 | 26.5 | 205 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 2.56 | 157 | 46 | 95 | 11 | 0 | 0 | 0 | 0 | 1.6 | 108 | 0.32 | 16 | 274 | 50 | 180 | 0 | 600 | 825 | 17 | 6263.27 | 13182.52 | 104.5
10:00 | 0 | 52 | 50 | 0 | 0 | 0 | 0 | 0 | 264 | 0 | 304 | 0 | 17 | 17 | 127 | 15 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 283 | 0 | 0 | 14 | 143.42 | 9 | 22 | 0 | 300 | 15 | 16 | 12 | 0 | 27 | 0 | 0 | 0 | 12 | 12 | 3.54 | 0 | 32 | 0 | 770 | 16 | 0 | 6 | 8 | 17 | 186 | 0 | 0 | 0 | 1050 | 2 | 18 | 8 | 300 | 300 | 345 | 51 | 45 | 215 | 35 | 0 | 52 | 51 | 0 | 0 | 17 | 94 | 0 | 75 | 0 | 305 | 0 | 369 | 40 | 39 | 124 | 4 | 8 | 0 | 82 | 0 | 51 | 0 | 101 | 0 | 58 | 14.39 | 113 | 0 | 0 | 38.73 | 12 | 7058.08 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 26 | 886 | 0 | 0 | 0 | 1260.71 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 20.56 | 62 | 0 | 0 | 31.5 | 205 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 5.05 | 158 | 40 | 32 | 29 | 0 | 0 | 0 | 0 | 7.4 | 160 | 0.76 | 16 | 276 | 50 | 180 | 0 | 600 | 825 | 17 | 6249.98 | 13308.06 | 104.52
11:00 | 0 | 52 | 50 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 274 | 0 | 0 | 17 | 124 | 15 | 0 | 0 | 17 | 0 | 0 | 281 | 0 | 0 | 0 | 290 | 0 | 0 | 23 | 143.42 | 9 | 14 | 0 | 300 | 16 | 16 | 12 | 0 | 8 | 0 | 0 | 0 | 12 | 12 | 4.56 | 0 | 35 | 0 | 770 | 16 | 0 | 6 | 8 | 20 | 184 | 0 | 0 | 0 | 1102 | 20 | 18 | 8 | 300 | 352 | 342 | 51 | 45 | 215 | 31 | 0 | 51 | 51 | 0 | 0 | 17 | 82 | 0 | 74 | 0 | 320 | 0 | 369 | 40 | 38 | 145 | 5 | 8 | 0 | 85 | 0 | 139 | 0 | 100 | 0 | 58 | 22.1 | 115 | 0 | 2.5 | 44.87 | 12 | 7261.45 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 18 | 859 | 0 | 0 | 0 | 1258.66 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 58.38 | 26 | 0 | 0 | 58.5 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.55 | 158 | 40 | 55 | 22 | 0 | 0 | 0 | 0 | 6.3 | 124 | 0.73 | 16 | 276 | 50 | 220 | 0 | 600 | 825 | 17 | 6325.12 | 13586.57 | 104.54
12:00 | 0 | 52 | 50 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 273 | 0 | 0 | 32 | 123 | 18 | 0 | 0 | 17 | 0 | 0 | 288 | 0 | 0 | 0 | 300 | 0 | 0 | 29 | 143.42 | 9 | 14 | 0 | 300 | 23 | 16 | 14 | 0 | 11 | 0 | 0 | 1 | 12 | 12 | 4.31 | 0 | 67 | 0 | 770 | 60 | 0 | 23 | 8 | 68 | 184 | 0 | 0 | 0 | 1177 | 17 | 18 | 8 | 300 | 345 | 320 | 51 | 44 | 212 | 31 | 0 | 51 | 103 | 0 | 0 | 27 | 154 | 8 | 66 | 3 | 305 | 0 | 369 | 40 | 39 | 140 | 6 | 8 | 0 | 85 | 0 | 140 | 0 | 100 | 5 | 58 | 20.36 | 115 | 0 | 1.1 | 33.48 | 12 | 7598.67 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 20 | 63 | 916 | 0 | 0 | 0 | 1265.46 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 50.18 | 110 | 0 | 0 | 16.17 | 204 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.59 | 160 | 0 | 75 | 41 | 0 | 0 | 0 | 0 | 7.9 | 211 | 0.36 | 16 | 277 | 50 | 220 | 0 | 600 | 825 | 35 | 6575.66 | 14174.33 | 104.56
13:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 272 | 17 | 3 | 34 | 117 | 32 | 0 | 7 | 17 | 0 | 0 | 280 | 0 | 0 | 17 | 278 | 0 | 0 | 29 | 143.42 | 9 | 14 | 0 | 300 | 76 | 16 | 30 | 0 | 22 | 0 | 14 | 17 | 12 | 12 | 4.37 | 0 | 84 | 0 | 770 | 113 | 0 | 43 | 17 | 84 | 184 | 0 | 0 | 0 | 1224 | 8 | 20 | 8 | 391 | 352 | 300 | 51 | 43 | 212 | 34 | 24 | 50 | 169 | 0 | 0 | 107 | 160 | 52.2 | 62 | 13 | 315 | 0 | 369 | 40 | 39 | 149 | 12 | 8 | 0 | 84 | 0 | 140 | 0 | 100 | 17 | 58 | 22.19 | 115 | 0 | 2.3 | 45.2 | 12 | 8295.68 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 96 | 93 | 925 | 0 | 0 | 0 | 1233.17 | 0 | 38 | 0 | 0 | 35 | 0 | 0 | 5 | 8 | 60.82 | 46 | 0 | 0 | 55.94 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 6.04 | 159 | 0 | 93 | 11 | 0 | 0 | 0 | 0 | 7.9 | 205 | 0.5 | 16 | 280 | 50 | 220 | 0 | 600 | 825 | 35 | 6637.37 | 14933.05 | 104.58
14:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 250 | 17 | 35 | 34 | 118 | 32 | 0 | 17 | 17 | 0 | 0 | 294 | 0 | 0 | 17 | 305 | 0 | 0 | 24 | 143.42 | 11 | 14 | 0 | 300 | 84 | 16 | 31 | 0 | 41 | 0 | 15 | 17 | 12 | 12 | 3.89 | 0 | 107 | 0 | 680 | 139 | 0 | 44 | 25.5 | 96 | 184 | 0 | 0 | 0 | 1070 | 0 | 30 | 8 | 350 | 300 | 290 | 51 | 42 | 209 | 31 | 42 | 51 | 172 | 0 | 0 | 105 | 160 | 52.2 | 65 | 23 | 300 | 0 | 342 | 40 | 39 | 128 | 11 | 8 | 0 | 84 | 0 | 140 | 0 | 100 | 17 | 58 | 20.12 | 116 | 0 | 0.8 | 48.29 | 12 | 8071.22 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 20 | 876 | 0 | 0 | 0 | 1244.76 | 0 | 36 | 0 | 0 | 35 | 0 | 0 | 14 | 8 | 44.79 | 104 | 0 | 0 | 54.94 | 150 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 5.04 | 159 | 0 | 93 | 32 | 0 | 0 | 0 | 0 | 8 | 169 | 0.7 | 16 | 203 | 50 | 180 | 0 | 600 | 800 | 17 | 6209.23 | 14280.45 | 104.59
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 286 | 0 | 35 | 34 | 118 | 32 | 0 | 17 | 17 | 0 | 0 | 285 | 0 | 0 | 17 | 280 | 0 | 0 | 21 | 139 | 11.5 | 14 | 0 | 300 | 100 | 16 | 26 | 0 | 23 | 0 | 15 | 17 | 12 | 12 | 3.07 | 0 | 108 | 0 | 740 | 54 | 0 | 44 | 25.5 | 87 | 183 | 0 | 0 | 0 | 1160 | 0 | 30 | 8 | 392 | 350 | 290 | 51 | 43 | 212 | 31 | 51 | 50 | 172 | 0 | 0 | 99 | 150 | 52.2 | 53 | 23 | 320 | 0 | 375 | 40 | 39 | 148 | 8 | 8 | 0 | 84 | 0 | 140 | 0 | 100 | 17 | 59 | 16.91 | 116 | 0 | 0.8 | 24.25 | 12 | 8117.23 | 876 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 40 | 820 | 0 | 0 | 0 | 1260 | 0 | 36 | 0 | 0 | 35 | 0 | 16 | 14 | 8 | 21.47 | 73 | 0 | 0 | 43 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.76 | 160 | 0 | 90 | 26 | 0 | 0 | 0 | 0 | 5.8 | 154 | 0.55 | 16 | 229 | 50 | 220 | 0 | 600 | 811 | 17 | 6360.58 | 14477.81 | 104.6
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 268 | 0 | 258 | 0 | 17 | 34 | 117 | 32 | 0 | 35 | 17 | 0 | 0 | 302 | 0 | 0 | 35 | 287 | 0 | 0 | 15 | 142 | 10 | 14 | 0 | 315 | 15 | 16 | 24 | 0 | 32 | 0 | 15 | 17 | 12 | 12 | 2.15 | 0 | 107 | 2 | 770 | 17 | 0 | 46 | 8 | 51 | 184 | 0 | 0 | 0 | 1194 | 0 | 30 | 8 | 333 | 350 | 300 | 51 | 43 | 197 | 34 | 52 | 72 | 120 | 0 | 0 | 17 | 150 | 8 | 36 | 23 | 310 | 0 | 376 | 40 | 38 | 129 | 6 | 8 | 0 | 84 | 0 | 140 | 0 | 100 | 17 | 59 | 9.4 | 116 | 0 | 1.1 | 28.32 | 12 | 7769.97 | 875 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 9 | 908 | 0 | 0 | 0 | 1249.63 | 0 | 36 | 0 | 0 | 35 | 0 | 17 | 14 | 8 | 32.8 | 60 | 0 | 0 | 2.84 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.35 | 160 | 0 | 91 | 18 | 0 | 0 | 0 | 0 | 4.8 | 100 | 0.11 | 32 | 276 | 50 | 220 | 0 | 600 | 820 | 17 | 6308.53 | 14078.5 | 104.61
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 200 | 0 | 17 | 60 | 117 | 32 | 0 | 35 | 17 | 0 | 0 | 250 | 0 | 0 | 35 | 240 | 0 | 0 | 7 | 143 | 10 | 22 | 0 | 280 | 15 | 16 | 18 | 0 | 50 | 0 | 15 | 17 | 12 | 12 | 0.21 | 86 | 104 | 2 | 750 | 16 | 0 | 46 | 8 | 34 | 183 | 0 | 0 | 0 | 1224 | 0 | 12 | 8 | 315 | 351 | 280 | 51 | 43 | 190 | 33 | 50 | 50 | 80 | 0 | 0 | 17 | 150 | 8 | 15 | 23 | 310 | 0 | 375 | 40 | 38 | 134 | 2 | 8 | 0 | 83 | 0 | 140 | 0 | 100 | 17 | 59 | 5.5 | 116 | 0 | 0.3 | 13.07 | 23 | 7518.08 | 875 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 23.85 | 925 | 0 | 0 | 0 | 1255.35 | 0 | 36 | 0 | 0 | 35 | 0 | 17 | 14 | 8 | 12.66 | 3 | 0 | 0 | 10.15 | 206 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.12 | 160 | 0 | 93 | 9 | 0 | 0 | 0 | 0 | 1.2 | 55 | 0.18 | 16 | 280 | 50 | 220 | 0 | 600 | 815 | 17 | 6205.51 | 13723.59 | 104.61
18:00 | 0 | 34 | 40 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 200 | 17 | 17 | 92 | 119 | 32 | 0 | 35 | 17 | 0 | 0 | 250 | 0 | 0 | 35 | 240 | 0 | 0 | 1 | 143.42 | 10 | 22 | 0 | 280 | 13 | 16 | 23 | 0 | 35 | 0 | 15 | 17 | 12 | 12 | 0.06 | 181 | 66 | 0 | 720 | 15 | 0 | 38 | 8 | 30 | 183 | 0 | 0 | 0 | 1183 | 0 | 12 | 8 | 320 | 300 | 260 | 51 | 43 | 193 | 34 | 51 | 51 | 48 | 0 | 0 | 17 | 130 | 8 | 1 | 23 | 300 | 20 | 320 | 40 | 38 | 121 | 0 | 8 | 0 | 83 | 0 | 140 | 0 | 100 | 17 | 59 | 0.9 | 115 | 0 | 0.1 | 2.58 | 24 | 7340.06 | 873 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 3 | 925 | 0 | 0 | 0 | 1265.26 | 0 | 36 | 0 | 0 | 35 | 0 | 17 | 14 | 8 | 1.8 | 3 | 0 | 0 | 1.99 | 150 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.22 | 157 | 0 | 93 | 1 | 0 | 0 | 0 | 0 | 0.4 | 9 | 0.04 | 16 | 280 | 50 | 180 | 0 | 600 | 815 | 17 | 5904.71 | 13244.77 | 104.61
19:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 254 | 17 | 24 | 108 | 119 | 143 | 0 | 35 | 108 | 0 | 0 | 250 | 0 | 0 | 35 | 270 | 0 | 0 | 0 | 143.42 | 10 | 22 | 0 | 308 | 28 | 16 | 27 | 0 | 30 | 51 | 15 | 17 | 12 | 12 | 0 | 182 | 85 | 0 | 720 | 40 | 0 | 38 | 11 | 46 | 183 | 0 | 0 | 0 | 1224 | 0 | 18 | 60 | 365 | 342 | 335 | 51 | 43 | 212 | 34 | 61 | 51 | 84 | 10 | 0 | 70 | 138 | 9 | 0 | 23 | 310 | 15 | 382 | 40 | 39 | 134 | 0 | 8 | 0 | 85 | 0 | 139 | 0 | 100 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 24 | 8392.42 | 876 | 0 | 0 | 21 | 0 | 38 | 0 | 0 | 0 | 0 | 78 | 0 | 925 | 0 | 0 | 0 | 1459.63 | 0 | 38 | 0 | 50 | 60 | 0 | 100 | 28 | 8 | 0 | 0 | 20 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 0 | 93 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 280 | 50 | 220 | 0 | 800 | 820 | 17 | 6845.63 | 15238.05 | 104.61
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 201 | 54 | 24 | 149 | 121 | 228 | 0 | 35 | 162 | 0 | 0 | 250 | 0 | 0 | 35 | 240 | 0 | 0 | 0 | 143.42 | 11.8 | 14 | 0 | 280 | 84 | 16 | 38 | 0 | 25 | 51 | 15 | 17 | 12 | 12 | 0 | 182 | 104 | 0 | 720 | 142 | 0 | 50 | 25.5 | 98 | 183 | 0 | 0 | 0 | 1224 | 0 | 100 | 63 | 314 | 355 | 285 | 51 | 44 | 191 | 35 | 69 | 51 | 168 | 27 | 0 | 105 | 100 | 52.2 | 0 | 23 | 300 | 15 | 387 | 40 | 39 | 141 | 0 | 8 | 0 | 85 | 0 | 140 | 0 | 100 | 17 | 68 | 0 | 155 | 0 | 0 | 0 | 24 | 8883.92 | 898 | 0 | 0 | 26 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 925 | 0 | 0 | 0 | 1477.41 | 0 | 38 | 0 | 70 | 70 | 0 | 100 | 28 | 8 | 0 | 0 | 20 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 0 | 93 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 280 | 50 | 220 | 0 | 1000 | 820 | 17 | 7175.41 | 16059.33 | 104.61
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 200 | 54 | 38 | 149 | 121 | 245 | 0 | 55 | 162 | 0 | 0 | 251 | 0 | 0 | 35 | 240 | 0 | 0 | 0 | 143.42 | 12 | 18 | 0 | 280 | 90 | 16 | 40 | 0 | 26 | 51 | 15 | 17 | 12 | 12 | 0 | 182 | 107 | 0 | 770 | 140 | 0 | 50 | 25.5 | 94 | 119 | 0 | 0 | 0 | 1224 | 0 | 83 | 63 | 306 | 355 | 280 | 51 | 42 | 187 | 35 | 69 | 51 | 171 | 26 | 0 | 104 | 100 | 40 | 0 | 23 | 305 | 30 | 387 | 40 | 39 | 132 | 0 | 8 | 0 | 85 | 0 | 140 | 0 | 100 | 17 | 68 | 0 | 155 | 0 | 0 | 0 | 24 | 8897.92 | 898 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 925 | 0 | 0 | 0 | 1475.19 | 0 | 38 | 0 | 70 | 70 | 0 | 100 | 30 | 8 | 0 | 0 | 20 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 0 | 95 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 280 | 50 | 220 | 0 | 1000 | 820 | 17 | 7173.19 | 16071.11 | 104.61
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 204 | 54 | 54 | 82 | 121 | 245 | 0 | 55 | 162 | 0 | 0 | 203 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 143.42 | 11.5 | 14 | 0 | 280 | 85 | 16 | 43 | 0 | 23 | 51 | 15 | 54.36 | 12 | 12 | 0 | 182 | 105 | 0 | 770 | 152 | 0 | 50 | 25.5 | 92 | 121 | 0 | 0 | 0 | 1224 | 0 | 135 | 92 | 306 | 355 | 280 | 51 | 45 | 185 | 35 | 69 | 40 | 170 | 26 | 0 | 80 | 106 | 25 | 0 | 23 | 295 | 270 | 392 | 40 | 39 | 127 | 0 | 8 | 0 | 85 | 0 | 139 | 0 | 100 | 17 | 68 | 0 | 155 | 0 | 0 | 0 | 24 | 9111.78 | 898 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 925 | 0 | 0 | 0 | 1474.25 | 0 | 38 | 0 | 75 | 70 | 0 | 100 | 28 | 8 | 0 | 0 | 20 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 0 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 280 | 50 | 220 | 0 | 1000 | 820 | 17 | 7181.25 | 16293.03
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 207 | 54 | 35 | 52 | 123 | 245 | 0 | 55 | 162 | 0 | 0 | 120 | 0 | 0 | 55 | 230 | 0 | 0 | 0 | 143.42 | 11.5 | 14 | 0 | 0 | 84 | 16 | 37 | 0 | 44 | 51 | 15 | 54.36 | 12 | 12 | 0 | 182 | 105 | 0 | 770 | 148 | 0 | 50 | 25.5 | 94 | 121 | 0 | 0 | 0 | 1224 | 0 | 150 | 108 | 380 | 355 | 320 | 51 | 45 | 213 | 35 | 69 | 40 | 174 | 27 | 0 | 78 | 106 | 25 | 0 | 23 | 270 | 262 | 388 | 40 | 39 | 128 | 0 | 8 | 0 | 86 | 0 | 139 | 0 | 100 | 17 | 68 | 0 | 155 | 0 | 0 | 0 | 24 | 8848.78 | 898 | 0 | 0 | 25 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 925 | 0 | 0 | 0 | 1478.48 | 0 | 39 | 0 | 75 | 70 | 0 | 100 | 28 | 8 | 0 | 0 | 14 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 0 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 277 | 50 | 220 | 0 | 1000 | 820 | 17 | 7178.48 | 16027.26
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 237 | 0 | 207 | 54 | 35 | 35 | 123 | 196 | 0 | 35 | 108 | 0 | 0 | 120 | 0 | 0 | 35 | 230 | 0 | 0 | 0 | 143.42 | 11.5 | 14 | 0 | 0 | 101 | 16 | 25 | 0 | 30 | 51 | 15 | 17 | 12 | 12 | 0 | 182 | 110 | 0 | 770 | 145 | 0 | 50 | 25.5 | 105 | 121 | 0 | 0 | 0 | 1224 | 0 | 150 | 110 | 307 | 355 | 285 | 51 | 46 | 179 | 35 | 68 | 40 | 188 | 27 | 0 | 102 | 104 | 52.2 | 0 | 24 | 275 | 266 | 388 | 40 | 39 | 149 | 0 | 8 | 0 | 86 | 0 | 139 | 0 | 100 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 24 | 8626.62 | 890 | 0 | 0 | 24 | 0 | 38 | 0 | 0 | 0 | 0 | 105 | 0 | 925 | 0 | 0 | 0 | 1470.51 | 0 | 39 | 0 | 75 | 70 | 0 | 100 | 22 | 8 | 0 | 0 | 14 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 0 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 277 | 50 | 220 | 0 | 800 | 820 | 17 | 6956.51 | 15583.13
Total KWH | 0 | 1856640 | 906240 | 0 | 0 | 0 | 0 | 0 | 6440400 | 0 | 7998330 | 395280 | 644040 | 989280 | 3043200 | 1693385 | 0 | 420564 | 1177920 | 0 | 0 | 6318895 | 0 | 0 | 442628 | 6647839 | 0 | 0 | 185479 | 3478800 | 218400 | 441000 | 0 | 4841818.18 | 1617109 | 383891 | 639360 | 0 | 524160 | 415566 | 300667 | 325813 | 295680 | 294720 | 26641 | 2866071 | 2259018 | 20160 | 18487272.73 | 1627564 | 0 | 980640 | 422951.4 | 1852545 | 4309308 | 0 | 0 | 0 | 28107270 | 76410 | 1085600 | 853091 | 8508500 | 8592300 | 6144000 | 1247963 | 1069920 | 5066000 | 829944 | 838080 | 1289659 | 3481920 | 130200 | 0 | 1710000 | 2697600 | 673363 | 559527 | 500432 | 7333000 | 890800 | 9133000 | 954000 | 924360 | 3328936.36 | 73641 | 197424 | 0 | 2011200 | 0 | 2277300 | 0 | 2404010 | 276120 | 1369200 | 128804 | 2388000 | 0 | 10100 | 324060 | 385920 | 193660929.67 | 21266181 | 0 | 0 | 128160 | 0 | 912000 | 0 | 0 | 0 | 0 | 1752624 | 519120 | 21985450 | 0 | 0 | 0 | 30261819 | 0 | 930296 | 0 | 395328 | 816768 | 0 | 674864 | 424062 | 474782 | 370256 | 581780 | 75948 | 0 | 361488 | 4890636 | 0 | 0 | 0 | 0 | 0 | 9307054 | 0 | 33180 | 3907000 | 501818 | 2141314 | 194860 | 529603 | 0 | 0 | 0 | 43557.12 | 1487520 | 4501 | 624384 | 6873000 | 1210000 | 5289550 | 0 | 16269091 | 20381090.91 | 442800 | 156061885.03 | 349722814.7

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-08-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14174.33 | MW | 12:00 Hr. | Energy Generated |  |  | 349.7228 |  | MKWHr.
| Day Peak Demand |  |  | 14174.33 | MW | 12:00 Hr. | Energy Unserverd |  |  | 14.294 |  | MKWHr.
| Evening Peak Generation |  |  | 16293.03 | MW | 21:00 Hr. | Energy Demand |  |  | 364.0168 |  | MKWHr.
| Evening Peak Demand |  |  | 16707.03 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 13182.52 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 865.8 |  | MMCFD
| Maximum Generation of the Day |  |  | 16293.03 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.331 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.9067 | 0 | 15.048 | 0 | 0 | 0.18548 | 0 | 0 | 48.1401 | Gas | 120.9888 | Gas | 430780604.2718
| Chattogram Zone |  |  | 4.3295 | 46.5945 | 11.4155 | 0 | 2.8661 | 0.10305 | 0 | 0.52416 | 65.8328 | Coal | 116.512 | Coal | 786541702.8625
| Cumilla Zone |  |  | 33.6014 | 0 | 8.4196 | 0 | 0 | 0.55953 | 2.6976 | 0 | 45.2781 | HFO | 48.7133 | HFO | 914226695.776
| Mymensingh Zone |  |  | 0 | 0 | 4.4192 | 0 | 0 | 0.46296 | 0 | 0 | 4.8822 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.454 | 0 | 0 | 0 | 0 | 0.073641 | 0 | 0 | 29.5277 | Hydro | 2.8661 | Hydro | 286607.1
| Khulna Zone |  |  | 0 | 21.9855 | 1.8808 | 0 | 0 | 0.51912 | 22.1782 | 0 | 46.5635 | Solar | 4.9809 | Solar | 80173445.5496
| Barishal Zone |  |  | 6.4996 | 43.5232 | 1.0672 | 0 | 0 | 0.004501 | 0 | 0 | 51.0944 | Import | 55.1376 | Import | 344099994.39
| Rajshahi Zone |  |  | 14.1977 | 0 | 3.792 | 0 | 0 | 1.3467 | 30.2618 | 0 | 49.5983 | Wind | 0.52416 | Wind | 7710393.6
| Rangpur Zone |  |  | 0 | 4.4088 | 2.6709 | 0 | 0 | 1.7259 | 0 | 0 | 8.8057
| Total |  |  | 120.9888 | 116.512 | 48.7133 | 0 | 2.8661 | 4.9809 | 55.1376 | 0.52416 | 349.7228
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 430780604.2718 |  | Hydro | 286607.1
|  |  |  | Coal | 786541702.8625 |  | Solar | 80173445.5496
|  |  |  | HFO | 914226695.776 |  | Import | 344099994.39
|  |  |  | HSD | 0 |  | Wind | 7710393.6
[5 empty] | Total: | 256,38,19,443 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.2662 | Peak Hr Flow | 898.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 40807454.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.2618 | Peak Hr Flow | 1474.25 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1788 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 2.6976 | Peak Hr Flow | 106.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2214 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.2256 | Peak Hr Flow | 2478.25 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 69 |  | 5579
|  |  |  | Chattogram |  | 0 |  | 1450
|  |  |  | Cumilla |  | 0 |  | 1540
|  |  |  | Mymensingh |  | 255 |  | 1480
|  |  |  | Sylhet |  | 50 |  | 779
|  |  |  | Khulna |  | 0 |  | 1874
|  |  |  | Barishal |  | 0 |  | 507
|  |  |  | Rajshahi |  | 0 |  | 1611
|  |  |  | Rangpur |  | 22 |  | 1111
|  |  |  | Total |  | 396 |  | 15931
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 89
|  |  |  | Total Unavailable Capacity |  |  |  | 389
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:37 | 10:27 | Nawabganj 132/33kV S/S TR-1 LT Forced S/D Due to Red hot maintenance of incomer -01 Bus | [7 empty] | 27.0MW load
|  |  | DS ( B phase bus site). | [7 empty] | interrup.
| 08:38 | 10:32 | Nawabganj 132/33kV S/S TR-1 HT Forced S/D Due to Red hot maintenance of incomer -01 Bus | [7 empty] | 27.0MW load
|  |  | DS ( B phase bus site). | [7 empty] | interrup.
|  | 09:29 | Bogura 132/33kV S/S Transformer-4 LT is restored.
|  | 09:29 | Bogura 132/33kV S/S Transformer-4 HT is restored.
|  | 10:02 | Jamalpur 132/33kV S/S T-2 LT is restored.
|  | 10:02 | Jamalpur 132/33kV S/S T-2 HT is restored.
|  | 10:02 | Jamalpur 132/33kV S/S T-1 HT is restored.
|  | 10:02 | Jamalpur 132/33kV S/S T-1 LT is restored.
| 11:12 |  | Barapukuria TPP Unit-1 Shutdown
| 11:41 |  | Bibiyana South 400 MW Synchronized with remarks:- GT
|  | 11:50 | Meghnaghat 400/230kV S/S ATR -03 HT is restored.
| 11:58 |  | Bibiyana South 400 MW Tripped with remarks:- GT
| 12:00 |  | Day Peak Generation: 14173 MW.
| 13:06 |  | At Barishal South SS, Without Transformer-3, 132 kv side equipments are charged.
| 13:19 |  | At Barishal South SS, Without Transformer-3, 33 kv side equipments are charged.
| 17:24 |  | Bibiyana South 400 MW Synchronized with remarks:- GT
| 17:39 |  | Bheramara P/S-Kushtia 132 kV Ckt-2 Project Work S/D from Bheramara 230/132kV end Due to
Kushtia Grid Maitenance
|  | 18:52 | Barapukuria-Bogura 230 kV Ckt-1 is restored.
| 19:40 |  | Shikalbaha 225 MW CCPP ST tripped.
|  | 20:43 | Khulshi-Madunaghat 132kV Ckt-2 is restored.
|  | 20:50 | Bogura 230/132kV S/S T-03 HT is restored.
|  | 20:51 | Bogura 230/132kV S/S T-03 LT is restored.
| 20:54 | 22:04 | Chandina 132/33kV S/S TR-2 LT Forced S/D Due to PDB feader red hot problem.
| 21:00 |  | Evening Peak Generation: 16293 MW.
| 21:09 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT2
| 21:09 |  | Meghnaghat CCPP(Summit) GT-2 Shutdown with remarks:- As per NLDC instructions,
| 21:21 |  | Meghnaghat CCPP(Summit) GT-2 Ready with remarks:- None
| 21:40 |  | Meghnaghat CCPP(Summit), FGMO is OFF with remarks:-
| 21:51 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- ST
| 21:54 |  | Unique Meghnaghat Power 584 MW CCPP was shutdown due to low gas pressure.
| 21:54 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- GT
| 21:59 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT-2 (This is False SMS, Actually
GT-2 SD).
| 21:59 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT-2 (This is False SMS, Actually
GT-2 SD).
| 01:09 |  | Haripur 412 MW CCPP Shutdown with remarks:- ST
| 01:11 |  | Haripur 412 MW CCPP Shutdown with remarks:- GT
| 06:25 | 06:48 | Brahmanbaria 132/33kV S/S 403T HT Tripped showing O/C and E/F relays. | [7 empty] | 65.0MW load
interrup.
| 06:25 | 06:48 | Brahmanbaria 132/33kV S/S 403T LT Tripped showing E/F and O/C relays. | [7 empty] | 65.0MW load
interrup.
| 06:54 |  | Natore 132/33kV S/S TR-1 (405 T) LT Scheduled S/D | [7 empty] | 21.0MW load
interrup.
| 06:54 |  | Natore 132/33kV S/S TR-2 (415 T) LT Scheduled S/D | [7 empty] | 21.0MW load
interrup.
| 06:55 |  | Natore 132/33kV S/S TR-1 (405 T) HT Scheduled S/D | [7 empty] | 21.0MW load
interrup.
| 06:55 |  | Natore 132/33kV S/S TR-2 (415 T) HT Scheduled S/D | [7 empty] | 21.0MW load
interrup.
| 07:00 |  | Chandpur 132/33kV S/S 412T (T-2) LT Scheduled S/D Due to Maintenance work
| 07:00 |  | Chandpur 132/33kV S/S 33 kV T-5 section Scheduled S/D Due to Maintenance work | [7 empty] | 24.0MW load
interrup.
| 07:00 |  | Chandpur 132/33kV S/S 33 kV T-2 section Scheduled S/D Due to Maintenance work | [7 empty] | 13.0MW load
interrup.
| 07:00 |  | Chandpur 132/33kV S/S 412T (T-2) HT Scheduled S/D Due to Maintenance work
| 07:00 |  | Chandpur 132/33kV S/S 422T(T-5) HT Scheduled S/D Due to Maintenance work
| 07:47 |  | Barapukuria-Bogura 230 kV Ckt-2 Project Work S/D from Bogura 400/230kV end Due to OPGW
will be shifted from double circuit tower to LILO four circuit tower. and from
Barapukuria 230/132/33kV end Due to Project Work
| 07:56 |  | Hathazari 230/132/33kV S/S MT-03 HT Scheduled S/D Due to MT-03 Shutdown required for
132KV R-Ph & Y-Ph Bushing change.
| 07:56 |  | Hathazari 230/132/33kV S/S MT-03 LT Scheduled S/D Due to MT-03 Shutdown required for
132KV R-Ph & Y-Ph Bushing change.
| 07:56 |  | Haripur 412 MW CCPP Synchronized with remarks:- GT
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-08-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 218 | 6440400 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 203 | 6318895 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 240 | 6647839 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 395280 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 121 | 3043200 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 420564 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 442628 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11.5 | 218400 | Gas shortage
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 441000 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 906240 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 245 | 1693385 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 82 | 989280 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1856640 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1177920 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 185479 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 644040 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 280 | 4841818.18 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 204 | 7998330 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3478800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2296.92 | 48140138.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 422951.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 76410 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 980640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 182 | 2866071 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 121 | 4309308 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 92 | 1852545 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 15 | 300667 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 415566 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 295680 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 20160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 43 | 639360 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 26641 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 383891 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 325813 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 105 | 2259018 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 294720 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 85 | 1617109 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 152 | 1627564 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28107270 | FGMO
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 23 | 524160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 770 | 18487272.73 | -
Chattogram Area Total |  |  |  |  | 4885.967 | 3032.86 | 65832817.13
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 185 | 5066000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 355 | 8592300 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 280 | 6144000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 306 | 8508500 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 829944 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 45 | 1069920 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 92 | 853091 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1247963 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 135 | 1085600 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 500432 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 1289659 | Machine Problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 3481920 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 106 | 2697600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 673363 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 0 | 0 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1710000 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 130200 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 838080 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 559527 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 2023 | 45278099
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 128804 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 155 | 2388000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1369200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 324060 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 385920 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 276120 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 264 | 4882204
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 73641 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 954000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 924360 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 127 | 3328936.36 | FGMO+ AGC
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 139 | 2277300 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2011200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2404010 | plant availability zero
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 197424 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7333000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 392 | 9133000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 270 | 890800 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2325 | 1495 | 29527671.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 898 | 21266181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 24 | 128160 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1752624 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 519120 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 925 | 21985450 | FGMO
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1990 | 46563535
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1000 | 16269091 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 624384 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 50 | 1210000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 820 | 20381090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5289550 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 442800 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 280 | 6873000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4501 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2435 | 51094416.91
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 370256 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 930296 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 424062 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 208 | 4890636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 9307054 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 75948 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 474782 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 674864 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 816768 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 75 | 395328 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 33180 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1474.25 | 30261819 | Problem with coal feeding system
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 361488 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 581780 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2435.25 | 49598261
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 501818 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 156 | 3907000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 529603 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 43557.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 2141314 | Liquid fuel shortage
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 194860 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1487520 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 321 | 8805672.12
Eastern Grid Total |  |  |  |  | 17427.666 | 9111.78 | 193660929.67
Western Grid Total |  |  |  |  | 11731.125 | 7181.25 | 156061885.03
National Grid Total |  |  |  |  | 29158.791 | 16293.03 | 349722814.7
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-08-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10454.31 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5080.7 | MW
i) Dhaka area |  |  | 5509.81 |  | MW | i) Khulna area |  |  |  | 1874 | MW
ii) Chattogram area |  |  | 1450.5 |  | MW | ii) Barishal area |  |  |  | 507.1 | MW
iii) Cumilla area |  |  | 1540 |  | MW | iii) Rajshahi area |  |  |  | 1610.6 | MW
iv) Mymensingh area |  |  | 1225 |  | MW | iv) Rangpur area |  |  |  | 1089 | MW
v) Sylhet area |  |  | 729 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15535.01 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 22 | 18:00 | 67 | HaripurSBU | 140 | 00:00 | 133 | Narshingdi | 200 | 20:00 | 199 | Uttara | 98 | 19:00
2 | AKSML | 14 | 18:30 | 68 | Hasnabad | 95 | 00:00 | 134 | Natore | 166 | 19:30 | 200 | UttaraNew | 57 | 23:00
3 | Aftabnagar | 44 | 00:00 | 69 | Hathazari | 91 | 20:00 | 135 | Nawabganj | 67.7 | 22:00 | 201 | Zigatola | 114 | 13:00
4 | Agargaon | 109 | 13:00 | 70 | Hatirjheel | 67 | 15:00 | 136 | Netrakona | 150 | 18:30
5 | Agrabad | 66 | 23:00 | 71 | Ishurdi | 80 | 20:00 | 137 | New | 72 | 00:00
6 | Amnura | 34 | 23:00 | 72 | Jaldhaka | 90 | 22:00 | 138 | Niamatpur | 91 | 22:00
7 | Ashuganj | 94 | 02:00 | 73 | Jamalpur | 144 | 19:30 | 139 | Noapara | 42 | 19:30
8 | BSRM | 201 | 18:00 | 74 | Jashore | 164 | 23:00 | 140 | PHP | 12 | 13:00
9 | Bagerhat | 90.5 | 21:00 | 75 | Jhenaidah | 102 | 19:30 | 141 | Pabna | 100 | 00:00
10 | Bajitpur | 103 | 22:00 | 76 | Joydebpur | 153 | 23:00 | 142 | Palashbari | 136 | 01:00
11 | Bakerganj | 14.4 | 19:00 | 77 | Joypurhat | 73 | 22:00 | 143 | Panchagarh | 76 | 01:00
12 | Bakulia | 87 | 22:00 | 78 | Juldah | 18 | 00:00 | 144 | Patiya | 11 | 19:00
13 | Banani | 52 | 19:00 | 79 | KSRM | 6 | 00:00 | 145 | Patnitala | 0 | 00:00
14 | Bangabhaban | 4 | 10:00 | 80 | Kabirpur | 258 | 00:00 | 146 | Patuakhali | 72.5 | 22:00
15 | Barapukuria | 70 | 19:30 | 81 | Kachua | 102 | 19:30 | 147 | Payra | 38 | 22:00
16 | Barguna | 22 | 19:00 | 82 | Kaliganj | 44 | 23:00 | 148 | Postogola | 61 | 00:00
17 | Barishal | 100 | 13:00 | 83 | Kallyanpur | 126 | 00:00 | 149 | Pubail | 46 | 22:00
18 | Barishal-230 | 106 | 21:00 | 84 | Kalurghat | 34 | 00:00 | 150 | Purbachal | 36 | 13:00
19 | Baroaulia | 63 | 02:00 | 85 | Kamrangirchar | 77 | 01:00 | 151 | Purbasadipur | 151 | 00:00
20 | Baroirhat | 63 | 00:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 45 | 23:00
21 | Bashundhara | 199 | 13:00 | 87 | Kasba | 40 | 21:00 | 153 | Rahim | 53 | 01:00
22 | BashundharaCement | 1 | 00:00 | 88 | Kazla | 115 | 00:00 | 154 | Rajbari | 89.5 | 19:30
23 | Beanibazar | 90 | 20:00 | 89 | Keranigonj | 81 | 13:00 | 155 | Rajendrapur | 122 | 11:00
24 | Benapole | 57 | 00:00 | 90 | Khagrachori | 38 | 21:00 | 156 | Rajshahi | 120 | 00:00
25 | Bhaluka | 179 | 04:00 | 91 | Khulna | 59 | 13:00 | 157 | Rajshahi-230 | 102 | 13:00
26 | Bhandaria | 60 | 21:00 | 92 | Khulshi | 148 | 01:00 | 158 | Ramganj | 118 | 22:00
27 | Bhangura | 41 | 19:30 | 93 | Kishoreganj | 133 | 23:00 | 159 | Rampur | 42 | 00:00
28 | Bheramara(GK) | 69 | 19:30 | 94 | Kodda | 298 | 19:30 | 160 | Rangamati | 17 | 19:00
29 | Bhulta | 225 | 01:00 | 95 | Kulaura | 63 | 21:00 | 161 | Rangpur | 132 | 19:30
30 | Bog-Sherpur | 74 | 21:00 | 96 | Kurigram | 76 | 19:00 | 162 | Ruppur | 4.6 | 11:00
31 | Bogura | 209 | 23:00 | 97 | Kushtia | 140 | 19:30 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 79 | 22:00 | 98 | Laksam | 39 | 22:00 | 164 | Saidpur | 105 | 21:00
33 | Brahmanbaria | 130 | 22:00 | 99 | Lakshmipur | 56 | 22:00 | 165 | Santhia | 38 | 19:00
34 | Cantonment | 126 | 13:00 | 100 | Lalbag | 72 | 00:00 | 166 | Satkhira | 135 | 19:30
35 | Chandina | 24 | 06:00 | 101 | Lalmonirhat | 74 | 19:00 | 167 | Satmasjid | 106 | 14:00
36 | Chandpur | 90 | 22:00 | 102 | MI_Cement | 16.1 | 02:00 | 168 | Savar | 183 | 00:00
37 | Chandraghona | 34 | 19:00 | 103 | Madanganj | 54 | 13:00 | 169 | SevenRings | 17.84 | 02:00
38 | Chapai | 77 | 22:00 | 104 | Madaripur | 124 | 22:00 | 170 | ShahCement | 21 | 01:00
39 | Charfasson | 31 | 19:00 | 105 | Madartek | 87 | 23:00 | 171 | Shahjadpur | 81 | 20:00
40 | Charsaidpur | 39 | 15:00 | 106 | Madunaghat | 55 | 19:00 | 172 | Shahjibazar | 165 | 19:00
41 | Chauddagram | 81 | 22:00 | 107 | Magura | 72 | 19:30 | 173 | Shahmirpur | 52 | 21:00
42 | Chhatak | 35 | 19:30 | 108 | Mahasthangarh | 76 | 04:00 | 174 | Shariatpur | 90 | 20:00
43 | Chowmuhani | 147 | 00:00 | 109 | Maijdee | 38 | 21:00 | 175 | Sherpur | 156 | 23:00
44 | Chuadanga | 122 | 21:00 | 110 | Manikganj | 140 | 19:30 | 176 | Shikalbaha | 27.5 | 00:00
45 | Coxsbazar | 142 | 00:00 | 111 | Maniknagar | 74 | 13:00 | 177 | Shitalakhya | 67.9 | 13:00
46 | Cumilla(N) | 117 | 23:00 | 112 | Matarbari | 57 | 19:00 | 178 | Sholosohor | 46 | 00:00
47 | Cumilla(S) | 182 | 00:00 | 113 | Matuail | 70 | 00:00 | 179 | Shomvuganj | 50 | 01:00
48 | Daganbhuiyan | 35 | 21:00 | 114 | Metrorail_Motijheel | 17 | 20:00 | 180 | Shyampur | 152 | 03:00
49 | Daudkandi | 156 | 21:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 122 | 23:00
50 | DhakaUniversity | 48 | 12:00 | 116 | Millgate | 83 | 00:00 | 182 | Sirajganj | 116 | 00:00
51 | Dhamrai | 104 | 21:00 | 117 | Mirpur | 151.5 | 19:00 | 183 | Sitakunda | 13 | 23:00
52 | Dhanmondi | 94 | 13:00 | 118 | Mirsorai | 11 | 00:00 | 184 | Sonargaon | 156 | 00:00
53 | Dohazari | 110 | 19:30 | 119 | Mirzapur | 55 | 18:30 | 185 | Sreemongol | 95 | 22:00
54 | Faridpur | 183 | 22:00 | 120 | Mithapukur | 82 | 19:00 | 186 | Sreepur | 121 | 06:00
55 | Fatullah | 104 | 00:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 55.6 | 22:00
56 | Fenchuganj | 50 | 21:00 | 122 | Mogbazar | 20.8 | 19:00 | 188 | Sunamganj | 60 | 19:00
57 | Feni | 112 | 22:00 | 123 | Mongla | 49 | 00:00 | 189 | Sylhet | 141 | 19:00
58 | GPH | 1 | 00:00 | 124 | Motijheel | 39 | 13:00 | 190 | Sylhet_(South) | 75 | 00:00
59 | Ghatail | 93 | 10:00 | 125 | Muktagacha | 42 | 13:00 | 191 | TK | 25 | 00:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 128 | 23:00 | 192 | Tangail | 170 | 18:30
61 | Ghorashal-230 | 107 | 21:00 | 127 | Muradnagar | 53 | 19:30 | 193 | Taraganj | 37 | 23:00
62 | Goalpara | 39 | 13:00 | 128 | Mymensingh | 150 | 19:30 | 194 | Tasnim | 38 | 01:00
63 | Gollamari | 106 | 13:00 | 129 | Nabinagar | 98 | 12:00 | 195 | Thakurgaon | 124 | 23:00
64 | Gopalganj | 118 | 21:00 | 130 | Naogaon | 139 | 21:00 | 196 | Tongi | 152 | 00:00
65 | Gulshan | 92 | 15:00 | 131 | Narail | 62 | 19:30 | 197 | Ullahpara | 41 | 20:00
66 | Halishahar | 93 | 00:00 | 132 | Narinda | 53 | 13:00 | 198 | Ullon | 60 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-08-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15732.3 | 1473 |  | 17271.59
1:00 | 14967.99 | 1644 |  | 16685.97
2:00 | 14478.8 | 1809 |  | 16369.21
3:00 | 14302.79 | 1773 |  | 16155.58
4:00 | 14161.93 | 1728 |  | 15967.69
5:00 | 13975.79 | 1590 |  | 15637.34
6:00 | 13661.97 | 642 |  | 14332.86
7:00 | 13551.55 | 304 |  | 13869.23
8:00 | 13436.3 | 185 |  | 13629.63
9:00 | 13182.52 | 169 |  | 13359.13
10:00 | 13308.06 | 0 |  | 13308.06
11:00 | 13586.57 | 0 |  | 13586.57
12:00 | 14174.33 | 0 |  | 14174.33
13:00 | 14933.05 | 52 |  | 14987.05
14:00 | 14280.45 | 22 |  | 14303.45
15:00 | 14477.81 | 0 |  | 14477.81
16:00 | 14078.5 | 48 |  | 14128.5
17:00 | 13723.59 | 48 |  | 13773.59
18:00 | 13244.77 | 20 |  | 13265.67
19:00 | 15238.05 | 273 |  | 15523.05
19:30 | 16059.33 | 186 |  | 16253.33
20:00 | 16071.11 | 211 |  | 16291.11
21:00 | 16293.03 | 396 |  | 16707.03
22:00 | 16027.26 | 411 |  | 16456.26
23:00 | 15583.13 | 1496 |  | 17146.13
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-08-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8989.92 | 6742.38 | 15732.3 | DAILY GENERATION CURVE
00:30 | 8868.42 | 6481.725 | 15350.145
01:00 | 8746.92 | 6221.07 | 14967.99 | 14-08-2026
01:30 | 8507.42 | 6215.975 | 14723.395
02:00 | 8267.92 | 6210.88 | 14478.8
02:30 | 8181.52 | 6209.275 | 14390.795
03:00 | 8095.12 | 6207.67 | 14302.79
03:30 | 8028.12 | 6204.24 | 14232.36
04:00 | 7961.12 | 6200.81 | 14161.93
04:30 | 7882.62 | 6186.24 | 14068.86
05:00 | 7804.12 | 6171.67 | 13975.79
05:30 | 7691.81 | 6127.07 | 13818.88
06:00 | 7579.5 | 6082.47 | 13661.97
06:30 | 7523.2 | 6083.56 | 13606.76
07:00 | 7466.9 | 6084.65 | 13551.55
07:30 | 7281.01 | 6212.915 | 13493.925
08:00 | 7095.12 | 6341.18 | 13436.3
08:30 | 7007.185 | 6302.225 | 13309.41
09:00 | 6919.25 | 6263.27 | 13182.52
09:30 | 6988.665 | 6256.625 | 13245.29
10:00 | 7058.08 | 6249.98 | 13308.06
10:30 | 7159.765 | 6287.55 | 13447.315
11:00 | 7261.45 | 6325.12 | 13586.57
11:30 | 7430.06 | 6450.39 | 13880.45
12:00 | 7598.67 | 6575.66 | 14174.33
12:30 | 7947.175 | 6606.515 | 14553.69
13:00 | 8295.68 | 6637.37 | 14933.05
13:30 | 8183.45 | 6423.3 | 14606.75
14:00 | 8071.22 | 6209.23 | 14280.45
14:30 | 8094.225 | 6284.905 | 14379.13
15:00 | 8117.23 | 6360.58 | 14477.81
15:30 | 7943.6 | 6334.555 | 14278.155
16:00 | 7769.97 | 6308.53 | 14078.5
16:30 | 7644.025 | 6257.02 | 13901.045
17:00 | 7518.08 | 6205.51 | 13723.59
17:30 | 7429.07 | 6055.11 | 13484.18
18:00 | 7340.06 | 5904.71 | 13244.77
18:30 | 7866.24 | 6375.17 | 14241.41
19:00 | 8392.42 | 6845.63 | 15238.05
19:30 | 8883.92 | 7175.41 | 16059.33
20:00 | 8897.92 | 7173.19 | 16071.11
20:30 | 9004.85 | 7177.22 | 16182.07 |  | Executive Engineer
21:00 | 9111.78 | 7181.25 | 16293.03 |  | Network Operation Division
21:30 | 8980.28 | 7179.865 | 16160.145
22:00 | 8848.78 | 7178.48 | 16027.26
22:30 | 8737.7 | 7067.495 | 15805.195
23:00 | 8626.62 | 6956.51 | 15583.13

## En-Curve
QF-LDC-12
Date | 14-08-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3391 | 1840 | 876 | 38 | 112 | 1236.18 | 222 | 4980 | 0 | 857.42 | 2166.7 | 0 | 0 | 13 | 1473 | DAILY ENERGY CURVE
00:30 | 3360 | 1884.5 | 876 | 38 | 108 | 1176.525 | 221 | 4945 | 0 | 782.92 | 1944.7 | 0 | 0 | 13.5 | 1558.5 | 14-08-2026
01:00 | 3329 | 1929 | 876 | 38 | 104 | 1116.87 | 220 | 4910 | 0 | 708.42 | 1722.7 | 0 | 0 | 14 | 1644
01:30 | 3312.5 | 1925.5 | 876 | 38 | 100 | 1122.275 | 220 | 4879.5 | 0 | 705.42 | 1531.7 | 0 | 0 | 12.5 | 1726.5 | Energy Generated | 349.7228 |  | MKWHr
02:00 | 3296 | 1922 | 876 | 38 | 96 | 1127.68 | 220 | 4849 | 0 | 702.42 | 1340.7 | 0 | 0 | 11 | 1809 | Energy not Served | 14.294 |  | MKWHr
02:30 | 3292 | 1917.5 | 876 | 38 | 95 | 1124.575 | 219.5 | 4844 | 0 | 676.42 | 1295.3 | 0 | 0 | 12.5 | 1791 | Total Energy Requirement | 364.0168 |  | MKWHr
03:00 | 3288 | 1913 | 876 | 38 | 94 | 1121.47 | 219 | 4839 | 0 | 650.42 | 1249.9 | 0 | 0 | 14 | 1773
03:30 | 3291.5 | 1863.5 | 876 | 38 | 93 | 1119.54 | 218.5 | 4829.5 | 0 | 650.42 | 1233.4 | 0 | 0 | 19 | 1750.5
04:00 | 3295 | 1814 | 876 | 38 | 92 | 1117.61 | 218 | 4820 | 0 | 650.42 | 1216.9 | 0 | 0 | 24 | 1728
04:30 | 3239 | 1824 | 876 | 38 | 94 | 1119.04 | 218.5 | 4821.5 | 0 | 634.42 | 1189.9 | 0 | 0 | 14.5 | 1659
05:00 | 3183 | 1834 | 876 | 38 | 96 | 1120.47 | 219 | 4823 | 0 | 618.42 | 1162.9 | 0 | 0 | 5 | 1590
05:30 | 3144.5 | 1772 | 875.5 | 38 | 91 | 1119.415 | 219 | 4814 | 9.595 | 618.42 | 1107.45 | 0 | 0 | 10 | 1116
06:00 | 3106 | 1710 | 875 | 38 | 86 | 1118.36 | 219 | 4805 | 19.19 | 618.42 | 1052 | 0 | 0 | 15 | 642
06:30 | 3170.5 | 1685.5 | 875 | 38 | 86 | 1120.7 | 219.5 | 4820 | 77.14 | 563.92 | 938.5 | 0 | 0 | 12 | 473
07:00 | 3235 | 1661 | 875 | 38 | 86 | 1123.04 | 220 | 4835 | 135.09 | 509.42 | 825 | 0 | 0 | 9 | 304
07:30 | 3266.5 | 1630.5 | 875.5 | 38 | 87 | 1179.7 | 110 | 4784.5 | 217.805 | 491.92 | 801.5 | 0 | 0 | 11 | 244.5
08:00 | 3298 | 1600 | 876 | 38 | 88 | 1236.36 | 0 | 4734 | 300.52 | 474.42 | 778 | 0 | 0 | 13 | 185
08:30 | 3228 | 1577 | 876 | 38 | 89 | 1252.45 | 0 | 4677 | 350.54 | 459.42 | 748 | 0 | 0 | 14 | 177
09:00 | 3158 | 1554 | 876 | 38 | 90 | 1268.54 | 0 | 4620 | 400.56 | 444.42 | 718 | 0 | 0 | 15 | 169
09:30 | 3171.5 | 1641.5 | 876 | 38 | 92 | 1264.625 | 0 | 4612.5 | 447.245 | 435.92 | 645 | 0 | 0 | 21 | 84.5
10:00 | 3185 | 1729 | 876 | 38 | 94 | 1260.71 | 0 | 4605 | 493.93 | 427.42 | 572 | 0 | 0 | 27 | 0
10:30 | 3287.5 | 1744.5 | 876 | 38 | 88 | 1259.685 | 0 | 4617.5 | 504.71 | 425.92 | 588 | 0 | 0 | 17.5 | 0
11:00 | 3390 | 1760 | 876 | 38 | 82 | 1258.66 | 0 | 4630 | 515.49 | 424.42 | 604 | 0 | 0 | 8 | 0
11:30 | 3377 | 1752.5 | 876 | 38 | 118 | 1262.06 | 0 | 4677.5 | 596.97 | 427.92 | 745 | 0 | 0 | 9.5 | 0
12:00 | 3364 | 1745 | 876 | 38 | 154 | 1265.46 | 0 | 4725 | 678.45 | 431.42 | 886 | 0 | 0 | 11 | 0
12:30 | 3393.5 | 1749 | 876 | 38 | 157 | 1249.315 | 0 | 4754 | 674.855 | 506.42 | 1139.1 | 0 | 0 | 16.5 | 26
13:00 | 3423 | 1753 | 876 | 38 | 160 | 1233.17 | 0 | 4783 | 671.26 | 581.42 | 1392.2 | 0 | 0 | 22 | 52
13:30 | 3269.5 | 1711.5 | 876 | 38 | 160 | 1238.965 | 0 | 4585.5 | 641.415 | 595.42 | 1458.95 | 0 | 0 | 31.5 | 37
14:00 | 3116 | 1670 | 876 | 38 | 160 | 1244.76 | 0 | 4388 | 611.57 | 609.42 | 1525.7 | 0 | 0 | 41 | 22
14:30 | 3255 | 1724.25 | 876 | 38 | 155 | 1252.38 | 0 | 4454 | 553.09 | 562.71 | 1476.7 | 0 | 0 | 32 | 11
15:00 | 3394 | 1778.5 | 876 | 38 | 150 | 1260 | 0 | 4520 | 494.61 | 516 | 1427.7 | 0 | 0 | 23 | 0
15:30 | 3391 | 1766.25 | 875.5 | 38 | 150 | 1254.815 | 0 | 4624 | 410.24 | 472.5 | 1268.35 | 0 | 0 | 27.5 | 24
16:00 | 3388 | 1754 | 875 | 38 | 150 | 1249.63 | 0 | 4728 | 325.87 | 429 | 1109 | 0 | 0 | 32 | 48
16:30 | 3324 | 1687.5 | 875 | 38 | 150 | 1252.49 | 43 | 4741 | 242.555 | 429.5 | 1077 | 0 | 0 | 41 | 48
17:00 | 3260 | 1621 | 875 | 38 | 150 | 1255.35 | 86 | 4754 | 159.24 | 430 | 1045 | 0 | 0 | 50 | 48
17:30 | 3124.5 | 1588.5 | 874 | 38 | 140 | 1260.305 | 133.5 | 4717 | 92.665 | 443.21 | 1030 | 0 | 0 | 42.5 | 34
18:00 | 2989 | 1556 | 873 | 38 | 130 | 1265.26 | 181 | 4680 | 26.09 | 456.42 | 1015 | 0 | 0 | 35 | 20
18:30 | 3205 | 1655.5 | 874.5 | 38 | 134 | 1362.445 | 181.5 | 4802.5 | 13.045 | 615.42 | 1327 | 0 | 0 | 32.5 | 146.5
19:00 | 3421 | 1755 | 876 | 38 | 138 | 1459.63 | 182 | 4925 | 0 | 774.42 | 1639 | 0 | 0 | 30 | 273
19:30 | 3275 | 1668.8 | 898 | 38 | 100 | 1477.41 | 182 | 5125 | 0 | 825.42 | 2444.7 | 0 | 0 | 25 | 186
20:00 | 3213 | 1667 | 898 | 38 | 100 | 1475.19 | 182 | 5175 | 0 | 825.42 | 2471.5 | 0 | 0 | 26 | 211
20:30 | 3322.5 | 1651.25 | 898 | 38 | 103 | 1474.72 | 182 | 5175 | 0 | 824.42 | 2488.68 | 0 | 0 | 24.5 | 303.5
21:00 | 3432 | 1635.5 | 898 | 38 | 106 | 1474.25 | 182 | 5175 | 0 | 823.42 | 2505.86 | 0 | 0 | 23 | 396
21:30 | 3492.5 | 1452 | 898 | 38 | 106 | 1476.365 | 182 | 5173.5 | 0 | 822.42 | 2485.86 | 0 | 0 | 33.5 | 403.5
22:00 | 3553 | 1268.5 | 898 | 38 | 106 | 1478.48 | 182 | 5172 | 0 | 821.42 | 2465.86 | 0 | 0 | 44 | 411
22:30 | 3493 | 1283 | 894 | 38 | 105 | 1474.495 | 182 | 5072.5 | 0 | 818.42 | 2407.78 | 0 | 0 | 37 | 953.5
23:00 | 3433 | 1297.5 | 890 | 38 | 104 | 1470.51 | 182 | 4973 | 0 | 815.42 | 2349.7 | 0 | 0 | 30 | 1496
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 14-08-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 128 | 48 | 360 | 166 | 1254 | 654 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 88 | 31 | 280 | 152 | 1090 | 594
2:00 | 102 | 36 | 296 | 142 | 1172 | 624 |  | Import | 0
3:00 | 112 | 41 | 310 | 144 | 1230 | 642
4:00 | 118 | 48 | 324 | 140 | 1250 | 604 | Ishurdi-Ghorashal Ckt-2 | Export | 3069454.54
5:00 | 120 | 46 | 346 | 142 | 1274 | 612
6:00 | 111 | 35 | 318 | 130 | 1262 | 564 |  | Import | 0
7:00 | 105 | 25 | 304 | 152 | 1250 | 578
8:00 | 135 | 28 | 418 | 144 | 1474 | 894 | Sirajganj-Sreepur Ckt-1 | Export | 2293000
9:00 | 153 | 39 | 462 | 144 | 1562 | 616
10:00 | 164 | 46 | 480 | 144 | 1524 | 638 |  | Import | 0
11:00 | 166 | 50 | 510 | 164 | 1538 | 668
12:00 | 173 | 48 | 482 | 160 | 1542 | 696 | Sirajganj-Sreepur Ckt-2 | Export | 2305000
13:00 | 135 | 30 | 428 | 158 | 1398 | 658
14:00 | 144 | 41 | 372 | 144 | 1306 | 644 |  | Import | 0
15:00 | 158 | 53 | 438 | 156 | 1390 | 662
16:00 | 155 | 49 | 460 | 158 | 1516 | 642 | Gopalganj-Aminbazar Ckt-1 | Export | 16550000
17:00 | 156 | 48 | 472 | 160 | 1556 | 650
18:00 | 141 | 38 | 418 | 150 | 1480 | 616 |  | Import | 0
18:30 | 132 | 34 | 392 | 154 | 1450 | 590
19:00 | 103 | 1 | 390 | 132 | 1316 | 496 | Gopalganj-Aminbazar Ckt-2 | Export | 16590000
19:30 | 86 | -9 | 344 | 96 | 1390 | 434
20:00 | 89 | -7 | 358 | 98 | 1396 | 446 |  | Import | 0
21:00 | 88 | -5 | 328 | 92 | 1372 | 456
22:00 | 85 | -10 | 304 | 80 | 1376 | 476 |  | Total Export | 40807454.54
23:00 | 123 | 25 | 380 | 100 | 1522 | 628 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-08-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 377 | 06:00 | 367 | 12:00 | Madunaghat | 401 | 06:00 | 393 | 00:00
Amtali | 413 | 09:00 | 408 | 22:00 | Meghnaghat | 383 | 06:00 | 373 | 00:00
Ashuganj | 410 | 0:00 | 395 | 12:00 | Mirsorai | 401 | 14:00 | 392 | 00:00
Bhulta | 398 | 06:00 | 386 | 12:00 | Payra | 414 | 04:00 | 410 | 00:00
Bibiana | 378 | 06:00 | 372 | 00:00 | Rahanpur | 407 | 18:00 | 390 | 22:00
BIPTC | 402 | 05:00 | 394 | 11:00 | Rampal | 398 | 10:00 | 385 | 00:00
Bogura | 393 | 18:30 | 375 | 22:00
Gopalganj | 392 | 06:00 | 382 | 22:00
Kaliakoir | 363 | 06:00 | 352 | 12:00
Korerhat | 400 | 14:00 | 391 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 06:00 | 222 | 12:00 | Ishurdi | 236 | 16:00 | 219 | 22:00
AKSML | 235 | 08:00 | 230 | 00:00 | Jhenaidah | 228 | 04:00 | 207 | 22:00
Aminbazar | 230 | 06:00 | 222 | 12:00 | Kachua | 229 | 14:00 | 221 | 11:00
Ashuganj | 230 | 23:00 | 222 | 00:00 | Kaliakoir | 266 | 22:00 | 220 | 12:00
Ashuganj-400 | 230 | 23:00 | 222 | 00:00 | Keranigonj | 228 | 06:00 | 220 | 12:00
Baghabari | 233 | 23:00 | 222 | 21:00 | Khulna(S) | 228 | 10:00 | 216 | 22:00
Barapukuria | 221 | 03:00 | 209 | 19:30 | Korerhat | 228 | 04:00 | 222 | 00:00
Barapukuria-230 | 221 | 03:00 | 209 | 19:30 | Madunaghat | 240 | 23:00 | 235 | 00:00
Barishal | 227 | 17:00 | 220 | 22:00 | Madunaghat-400 | 240 | 05:00 | 235 | 00:00
Bheramara | 234 | 05:00 | 216 | 22:00 | Maniknagar | 226 | 06:00 | 219 | 00:00
Bhulta | 228 | 06:00 | 221 | 00:00 | Meghnaghat | 233 | 06:00 | 225 | 00:00
Bibiana | 219 | 02:00 | 215 | 00:00 | Meghnaghat-400 | 230 | 06:00 | 223 | 00:00
BIPTC | 237 | 16:00 | 217 | 22:00 | Mirsorai | 234 | 14:00 | 228 | 00:00
Bogura | 238 | 14:00 | 226 | 19:30 | Naogaon | 224 | 15:00 | 200 | 22:00
Bogura-400 | 238 | 14:00 | 228 | 19:30 | Purbasadipur | 218 | 04:00 | 203 | 19:30
Borhanuddin | 229 | 10:00 | 226 | 21:00 | Rajshahi | 233 | 05:00 | 215 | 22:00
BSRM | 229 | 14:00 | 223 | 00:00 | Rampal | 227 | 17:00 | 215 | 00:00
Charfasson | 230 | 08:00 | 224 | 22:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 14:00 | 222 | 00:00 | Rampura | 227 | 06:00 | 220 | 00:00
Cumilla(N) | 225 | 18:00 | 218 | 00:00 | Shikalbaha | 239 | 06:00 | 234 | 00:00
Faridpur | 223 | 18:00 | 215 | 22:00 | Shyampur | 227 | 06:00 | 220 | 00:00
Fenchuganj | 220 | 23:00 | 217 | 00:00 | Siddhirganj | 227 | 05:00 | 222 | 00:00
Feni | 226 | 06:00 | 220 | 00:00 | Sirajgonj | 237 | 23:00 | 230 | 10:00
Ghorashal | 230 | 05:00 | 220 | 00:00 | Sreepur | 223 | 23:00 | 218 | 00:00
Ghorashal-230 | 217 | 20:00 | 204 | 00:00 | Tongi | 223 | 19:30 | 200 | 00:00
Gopalganj | 223 | 09:00 | 216 | 22:00
GPH | 234 | 04:00 | 230 | 00:00
Haripur | 228 | 06:00 | 220 | 00:00
Hasnabad | 228 | 18:00 | 223 | 11:00
Hathazari | 236 | 05:00 | 229 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 03:00 | 133 | 10:00 | Madartek | 139 | 04:00 | 132 | 12:00
Agargaon | 139 | 06:00 | 132 | 13:00 | Madunaghat | 138 | 04:00 | 135 | 00:00
Agrabad | 137 | 23:00 | 133 | 00:00 | Magura | 138 | 17:00 | 122 | 22:00
AKS | 134 | 13:00 | 130 | 00:00 | Mahasthangarh | 132 | 15:00 | 124 | 19:30
Aminbazar | 132 | 18:00 | 124 | 12:00 | Maijdee | 128 | 14:00 | 124 | 00:00
Amnura | 135 | 04:00 | 126 | 13:00 | Manikganj | 129 | 18:00 | 124 | 15:00
Ashuganj | 132 | 23:00 | 126 | 00:00 | Maniknagar | 141 | 06:00 | 135 | 00:00
Ashuganj-230 | 134 | 23:00 | 130 | 00:00 | Matarbari | 129 | 15:00 | 117 | 00:00
Bagerhat | 130 | 09:00 | 121 | 22:00 | Matuail | 136 | 06:00 | 124 | 18:30
Bajitpur | 126 | 05:00 | 120 | 00:00 | Metrorail_Motijheel | 141 | 06:00 | 135 | 00:00
Bakerganj | 132 | 03:00 | 127 | 22:00 | Metrorail_Uttara | 133 | 20:00 | 123 | 00:00
Bakulia | 138 | 04:00 | 132 | 10:00 | Millgate | 134 | 20:00 | 124 | 00:00
Banani | 139 | 04:00 | 132 | 12:00 | Mirpur | 131 | 18:30 | 124 | 12:00
Bangabhaban | 140 | 05:00 | 135 | 00:00 | Mirzapur | 128 | 00:00 | 121 | 12:00
Barapukuria | 134 | 03:00 | 122 | 19:30 | Mithapukur | 129 | 05:00 | 119 | 19:30
Barguna | 132 | 18:00 | 126 | 22:00 | MI_Cement | 134.3 | 06:00 | 128 | 12:00
Barishal | 133 | 17:00 | 128 | 01:00 | Modern | N/A | N/A | N/A | N/A
Barishal-230 | 132 | 17:00 | 127 | 22:00 | Mogbazar | 140 | 04:00 | 135 | 11:00
Baroaulia | 137 | 05:00 | 133 | 00:00 | Mongla | 129 | 05:00 | 121 | 22:00
Baroirhat | 132 | 02:00 | 129 | 00:00 | Motijheel | 140 | 05:00 | 135 | 00:00
Bashundhara | 139 | 03:00 | 123 | 00:00 | Muktagacha | 124 | 10:00 | 113 | 02:00
BashundharaCement | 134 | 08:00 | 130 | 00:00 | Munshiganj | 133 | 05:00 | 129 | 00:00
Beanibazar | 122 | 23:00 | 115 | 19:30 | Muradnagar | 127 | 06:00 | 122 | 00:00
Benapole | 137 | 17:00 | 118 | 19:00 | Mymensingh | 127 | 00:00 | 113 | 13:00
Bhaluka | 129 | 06:00 | 125 | 00:00 | Nabinagar | 127 | 18:30 | 119 | 12:00
Bhandaria | 130 | 18:00 | 120 | 21:00 | Naogaon | 134 | 17:00 | 120 | 22:00
Bhangura | 137 | 17:00 | 127 | 19:30 | Narail | 138 | 17:00 | 121 | 22:00
Bheramara | 137 | 04:00 | 127 | 22:00 | Narinda | 141 | 06:00 | 135 | 00:00
Bheramara(GK) | 137 | 04:00 | 126 | 22:00 | Narshingdi | 129 | 10:00 | 117 | 00:00
Bhulta | 129 | 09:00 | 123 | 00:00 | Natore | 134 | 04:00 | 124 | 22:00
Bhulta-400 | 132 | 06:00 | 127 | 00:00 | Nawabganj | 137 | 06:00 | 131 | 12:00
Bog-Sherpur | 134 | 14:00 | 127 | 19:30 | Netrakona | 120 | 03:00 | 108 | 18:30
Bogura | 135 | 09:00 | 129 | 21:00 | New | 134 | 08:00 | 126 | 00:00
Bogura-230 | 136 | 17:00 | 130 | 19:30 | Niamatpur | 133 | 16:00 | 124 | 22:00
Brahmanbaria | 127 | 23:00 | 123 | 00:00 | Noapara | 134 | 17:00 | 125 | 22:00
Cantonment | 138 | 06:00 | 132 | 12:00 | Pabna | 135 | 16:00 | 125 | 22:00
Chandina | 130 | 15:00 | 126 | 00:00 | Palashbari | 127 | 03:00 | 117 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandpur | 134 | 23:00 | 127 | 10:00 | Panchagarh | 134 | 06:00 | 121 | 19:30
Chandraghona | 138 | 03:00 | 135 | 10:00 | Patiya | 137 | 15:00 | 132 | 00:00
Chapai | 133 | 18:30 | 127 | 22:00 | Patnitala | 131 | 09:00 | 123 | 00:00
Charsaidpur | 134 | 05:00 | 130 | 12:00 | Patuakhali | 132 | 18:00 | 127 | 22:00
Chauddagram | 130 | 05:00 | 126 | 00:00 | Payra | 136 | 18:30 | 132 | 19:30
Chhatak | 120 | 23:00 | 112 | 19:30 | PHP | 132 | 06:00 | 129 | 00:00
Chowmuhani | 128 | 14:00 | 124 | 00:00 | Postogola | 136 | 06:00 | 131 | 00:00
Chuadanga | 136 | 03:00 | 120 | 22:00 | Pubail | 130 | 19:30 | 121 | 00:00
Coxsbazar | 130 | 17:00 | 119 | 00:00 | Purbachal | 139 | 03:00 | 132 | 12:00
Cumilla(N) | 130 | 18:00 | 126 | 00:00 | Purbasadipur | 132 | 02:00 | 122 | 19:30
Cumilla(S) | 132 | 06:00 | 123 | 12:00 | Rahanpur | 136 | 18:30 | 129 | 22:00
Daganbhuiyan | 130 | 06:00 | 126 | 00:00 | Rahanpur-400 | 136 | 14:00 | 129 | 22:00
Daudkandi | 127 | 06:00 | 119 | 22:00 | Rahim | 135 | 05:00 | 130 | 00:00
DhakaUniversity | 139 | 04:00 | 126 | 12:00 | Rajbari | 127 | 18:00 | 121 | 22:00
Dhamrai | 128 | 08:00 | 123 | 12:00 | Rajendrapur | 132 | 06:00 | 126 | 12:00
Dhanmondi | 139.5 | 04:00 | 133 | 12:00 | Rajshahi | 132 | 05:00 | 122 | 22:00
Dohazari | 133 | 02:00 | 128 | 00:00 | Rajshahi-230 | 133 | 05:00 | 124 | 22:00
Faridpur | 129 | 18:00 | 125 | 19:30 | Ramganj | 129 | 23:00 | 123 | 11:00
Fatullah | 137 | 20:00 | 129 | 12:00 | Rampur | 137 | 23:00 | 133 | 10:00
Fenchuganj | 128 | 01:00 | 126 | 21:00 | Rampura | 139 | 06:00 | 132 | 12:00
Feni | 131 | 05:00 | 127 | 00:00 | Rangamati | 137 | 23:00 | 133 | 10:00
Feni-230 | 131 | 06:00 | 128 | 00:00 | Rangpur | 128 | 10:00 | 119 | 21:00
Ghatail | 123 | 00:00 | 113 | 15:00 | Ruppur | 138 | 16:00 | 127 | 18:30
Ghorashal | 130 | 19:30 | 120 | 01:00 | Saidpur | 132 | 02:00 | 124 | 19:30
Goalpara | 137 | 18:00 | 128 | 22:00 | Santhia | 136 | 15:00 | 126 | 19:30
Gollamari | 137 | 18:00 | 128 | 22:00 | Satkhira | 133 | 18:00 | 121 | 22:00
Gopalganj | 133 | 05:00 | 127 | 22:00 | Satmasjid | 138 | 06:00 | 130 | 01:00
Gopalganj-400 | 132 | 04:00 | 128 | 22:00 | Savar | 132 | 19:30 | 122 | 12:00
Gulshan | 138 | 05:00 | 132 | 12:00 | SevenRings | 130 | 20:00 | 121 | 00:00
Halishahar | 137 | 02:00 | 133 | 00:00 | ShahCement | 134 | 05:00 | 130 | 12:00
Haripur | 135 | 04:00 | 131 | 00:00 | Shahjadpur | 136 | 15:00 | 130 | 00:00
HaripurSBU | 135 | 04:00 | 131 | 00:00 | Shahjibazar | 125 | 07:00 | 121 | 13:00
Hasnabad | 135 | 05:00 | 129 | 12:00 | Shahmirpur | 137 | 02:00 | 134 | 00:00
Hathazari | 138 | 05:00 | 135 | 00:00 | Shariatpur | 131 | 18:00 | 125 | 22:00
Hatirjheel | 139 | 04:00 | 132 | 12:00 | Sherpur | 133 | 00:00 | 111 | 07:00
Ishurdi | 138 | 04:00 | 128 | 22:00 | Shikalbaha | 128 | 14:00 | 123 | 00:00
Jaldhaka | 129 | 02:00 | 118 | 19:30 | Shikalbaha-230 | 138 | 05:00 | 135 | 00:00
Jamalpur | 135 | 00:00 | 113 | 02:00 | Shitalakhya | 134.3 | 06:00 | 128 | 12:00
Jashore | 138 | 17:00 | 119 | 19:00 | Sholosohor | 137 | 02:00 | 134 | 16:00
Jhenaidah | 140 | 17:00 | 118 | 22:00 | Shomvuganj | 121 | 07:00 | 111 | 00:00
Jhenaidah-230 | 140 | 17:00 | 125 | 22:00 | Shyampur | 136 | 18:30 | 128 | 00:00
Joydebpur | 129 | 23:00 | 120 | 00:00 | Shyampur-230 | 137 | 18:30 | 131 | 00:00
Joypurhat | 132 | 18:30 | 123 | 19:30 | Siddhirganj | 136 | 06:00 | 131 | 00:00
Juldah | 137 | 14:00 | 133 | 00:00 | Sirajganj | 132 | 18:00 | 123 | 19:30
Kabirpur | 132 | 18:00 | 120 | 00:00 | Sitakunda | 137 | 03:00 | 133 | 00:00
Kachua | 131 | 14:00 | 126 | 10:00 | Sonargaon | 131 | 03:00 | 128 | 00:00
Kaliakoir | 132 | 18:00 | 127 | 12:00 | Sreemongol | 125 | 02:00 | 120 | 13:00
Kaliganj | 139 | 05:00 | 124 | 19:00 | Sreepur | 135 | 04:00 | 131 | 00:00
Kallyanpur | 131 | 19:30 | 124 | 12:00 | Srinagar | 138 | 05:00 | 131 | 00:00
Kalurghat | 138 | 02:00 | 135 | 11:00 | SSM | 140 | 05:00 | 136 | 00:00
Kamrangirchar | 138 | 06:00 | 122 | 12:00 | Sunamganj | 116 | 02:00 | 110 | 19:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 123 | 23:00 | 119 | 19:00
Kasba | 126 | 06:00 | 121 | 00:00 | Sylhet_(South) | 123 | 23:00 | 118 | 20:00
Kazla | 140 | 06:00 | 132 | 00:00 | Tangail | 127 | 09:00 | 117 | 12:00
Keranigonj | 138 | 06:00 | 132 | 13:00 | Taraganj | 129 | 04:00 | 119 | 19:30
Khagrachori | 136 | 02:00 | 132 | 11:00 | Tasnim | 133 | 05:00 | 128 | 00:00
Khulna | 136 | 18:00 | 127 | 22:00 | Thakurgaon | 134 | 04:00 | 122 | 19:30
Khulna(S) | 137 | 18:00 | 128 | 22:00 | TK | 138 | 05:00 | 135 | 00:00
Khulshi | 136 | 03:00 | 132 | 00:00 | Tongi | 135 | 19:30 | 123 | 00:00
Kishoreganj | 124 | 05:00 | 119 | 07:00 | Ullahpara | 133 | 05:00 | 126 | 19:30
Kodda | 131 | 19:00 | 120 | 12:00 | Ullon | 138 | 03:00 | 131 | 12:00
Korerhat | 134 | 14:00 | 131 | 00:00 | Uttara | 134 | 20:00 | 123 | 12:00
KSRM | 137 | 15:00 | 133 | 00:00 | UttaraNew | 133 | 20:00 | 123 | 00:00
Kulaura | 127 | 02:00 | 124 | 13:00 | Zigatola | 138 | 18:30 | 132 | 13:00
Kurigram | 125 | 02:00 | 110 | 19:00
Kushtia | 133 | 05:00 | 120 | 22:00
Laksam | 130 | 14:00 | 126 | 00:00
Lakshmipur | 127 | 14:00 | 123 | 00:00
Lalbag | 137 | 05:00 | 131 | 13:00
Lalmonirhat | 125 | 15:00 | 114 | 19:30
Madanganj | 134 | 08:00 | 130 | 00:00
Madaripur | 131 | 05:00 | 127 | 22:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division