## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-08-2026 | during | 18-08-2026 | during | 18-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 252 | 338 | 412 | 412 | 412 | 412 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 322 | 327 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 35 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 124 | 126 | 149.36 | 149.36 | 142 | 142 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 8.5 | 7.5 | 33 | 33 | 10 | 10 | Gas shortage
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 50 | 52.19 | 52.19 | 33 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 146 | 210 | 300 | 300 | 175 | 145 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 51 | 149 | 149 | 149 | 52 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 105 | 105 | 105 | 88 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 82 | 162 | 162 | 72 | 72 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 24 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 545 | 400 | 584 | 584 | 555 | 555 | AGC+Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 570 | 538 | 718 | 718 | 571 | 571 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 123 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 2519.92 | 2731.5 | 5395.16 | 5370.16 | 2790.42 | 2924.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 17 | 17 | 25.5 | 25.5 | 25 | 25 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 2 | 0 | 4 | 0 | 4 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 219 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 35 | 211 | 210 | 210 | 210 | 210 | Gas shortage
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 83 | 17 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 14 | 40 | 14 | 40 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 25 | 32 | 25 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 45 | 60 | 95.1 | 95.1 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.1 | 0 | 1.66 | 0 | 1.66 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 0 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 1 | 17 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 105 | 67 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 11 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 89 | 15 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 33 | 2 | 163 | 163 | 88 | 160 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 610 | 770 | 1224 | 1224 | 1160 | 1160 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 38 | 25 | 45 | 40 | 45 | 40 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 1125 | 1150 | 1150 | 1125 | 1125 | -
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2445.1 | 2621 | 4114.62 | 4187.96 | 3347.66 | 3545
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 171 | 216 | 221.25 | 221.25 | 205.25 | 205.25 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 300 | 300 | 350.01 | 350.01 | 350.01 | 350.01 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 265 | 265 | 342.01 | 342.01 | 306 | 306 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 240 | 230 | 393 | 393 | 260 | 260 | Line Overload
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 15 | 41.65 | 41.65 | 39 | 39 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 44 | 10 | 52.82 | 52.82 | 47 | 47 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 0 | 195 | 195 | 8 | 8 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 22 | 150 | 150 | 13 | 70 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 2 | 38 | 32 | 32 | 32 | 32 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 141 | 132 | 163 | 163 | 144 | 144 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 187 | 120 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 162 | 176 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 25 | 52.2 | 52.2 | 8 | 52 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 0 | 24.5 | 24.5 | 0 | 0 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 105 | 34 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 45 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 69 | 89 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 25 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1839 | 1768 | 2754.44 | 2688.44 | 2010.26 | 2117.26
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-08-2026 | during | 18-08-2026 | during | 18-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 19.99 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.6 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 111 | 155 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 47 | 68 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 24.11 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 24 | 22 | 22 | 12 | 22 | 00:00-16:00 hrs 12MW&16:00-24:00 hrs 24MW dis.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 216.7 | 282 | 536.6 | 516.5 | 262.1 | 269
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 42 | 0 | 0 | 40 | 40 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 30 | 40 | 40 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 151 | 151 | 163 | 163 | 147 | 147 | AGC
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 142 | 140 | 140 | 140 | 140 | 140 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 25 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 124 | 124 | 120 | 120 | 120 | 120 | plant availability zero
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 290 | 341 | 341 | 307 | 307 | Gas shortage
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 377 | 396 | 390 | 390 | 390 | 390 | Cooling System Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 35.5 | 265 | 15 | 15 | 240 | 240 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1279.5 | 1555 | 1331 | 1331 | 1506 | 1506
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 900 | 900 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 50 | 15 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 8.73 | 0 | 55 | 0 | 55 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 985 | 1100 | 1100 | 1100 | 1100 | 1100 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1981.73 | 2053 | 3457 | 3402 | 2290 | 2235
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 600 | 1000 | 700 | 1000 | 700 | 1000 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 32 | 32 | 110 | 110 | 32 | 32 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 118 | 118 | 120 | 120 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 820 | 815 | 835 | 835 | 835 | 835 | machine problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 250 | 307 | 307 | 250 | 250 | Bad quality coal
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.21 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2057.21 | 2452 | 2443 | 2742 | 2173 | 2509
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 11.42 | 0 | 48.25 | 0 | 48.25 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 20 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 188 | 156 | 214 | 214 | 200 | 200 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 383 | 413.79 | 413.79 | 372 | 372 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 20 | 20 | 20 | 20 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 25 | 8 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 100 | 100 | 0 | 100 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 35 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 1.78 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 824.42 | 1458.97 | 1469.13 | 1469.13 | 820 | 1469 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 7.19 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1606.81 | 2060.97 | 3213.87 | 2999.12 | 1736.75 | 2321
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 50 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 158 | 165 | 165 | 165 | 165 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.8 | 0 | 7 | 0 | 7 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 94 | 90 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 84 | 0 | 97.27 | 0 | 97.27 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 410.8 | 368 | 591.27 | 457 | 478.27 | 379
System Total |  |  |  |  | 28843.2 | 29158.791 | 14356.77 | 15891.47 | 23836.96 | 23694.18 | 16594.46 | 17805.68
Forecast Scenario (18-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15640 |  | 66.85 |  | 15710
|  |  |  | 1:00 | 15150 |  | 133.7 |  | 15290
|  |  |  | 2:00 | 14900 |  | 0 |  | 14810
|  |  |  | 3:00 | 14500 |  | 0 |  | 14370
|  |  |  | 4:00 | 14200 |  | 0 |  | 14100
|  |  |  | 5:00 | 14100 |  | 0 |  | 13830
|  |  |  | 6:00 | 13700 |  | 0 |  | 13470
|  |  |  | 7:00 | 13600 |  | 0 |  | 13510
|  |  |  | 8:00 | 13500 |  | 38.2 |  | 13540
|  |  |  | 9:00 | 13570 |  | 85.95 |  | 13660
|  |  |  | 10:00 | 13890 |  | 85.95 |  | 13980
|  |  |  | 11:00 | 14200 |  | 28.65 |  | 14230
|  |  |  | 12:00 | 14360 |  | 496.6 |  | 14880
|  |  |  | 13:00 | 14370 |  | 639.85 |  | 15040
|  |  |  | 14:00 | 14470 |  | 563.45 |  | 15060
|  |  |  | 15:00 | 14420 |  | 735.35 |  | 15190
|  |  |  | 16:00 | 14080 |  | 754.45 |  | 14870
|  |  |  | 17:00 | 13900 |  | 620.75 |  | 14550
|  |  |  | 18:00 | 14200 |  | 0 |  | 14140
|  |  |  | 18:30 | 14880 |  | 0 |  | 14820
|  |  |  | 19:00 | 15600 |  | 0 |  | 15500
|  |  |  | 19:30 | 15850 |  | 563.45 |  | 16490
|  |  |  | 20:00 | 15720 |  | 678.05 |  | 16430
|  |  |  | 21:00 | 15900 |  | 744.9 |  | 16530
|  |  |  | 22:00 | 15660 |  | 544.35 |  | 16230
|  |  |  | 23:00 | 15400 |  | 869.05 |  | 16310
Probable Maximum Temperature: |  |  | 31.80°C
Probable Maximum Demand at Day Peak: |  |  | 14880.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 744.9
Probable Maximum Demand at Evening Peak: |  |  | 16530.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15900.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 348.88 MKWHr. |  | 150 | 0 | 65 | 200 | 50 | 150 | 0 | 70 | 60 | 745
*** This report is generated digitally from Operation Information System (OIS) at 10:06 hrs on 18-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-08-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14356.77 | MW | 12:00 Hr. | Energy Generated |  |  | 351.292 |  | MKWHr.
| Day Peak Demand |  |  | 15289.77 | MW | 12:00 Hr. | Energy Unserverd |  |  | 7.839 |  | MKWHr.
| Evening Peak Generation |  |  | 15891.47 | MW | 19:30 Hr. | Energy Demand |  |  | 359.131 |  | MKWHr.
| Evening Peak Demand |  |  | 16207.47 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.5 |  | °C
| Minimum Generation of the Day |  |  | 13567.55 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 931.87 |  | MMCFD
| Maximum Generation of the Day |  |  | 15891.47 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 7.3174 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 39.6277 | 0 | 18.0825 | 0 | 0 | 0.094678 | 0 | 0 | 57.8049 | Gas | 128.4963 | Gas | 449207093.9718
| Chattogram Zone |  |  | 2.7499 | 47.3582 | 8.4449 | 0 | 5.1983 | 0.017084 | 0 | 0.92112 | 64.6896 | Coal | 118.3596 | Coal | 825786978.2302
| Cumilla Zone |  |  | 31.0775 | 0 | 8.289 | 0 | 0 | 0.14616 | 3.7306 | 0 | 43.2432 | HFO | 45.2965 | HFO | 926452163.206
| Mymensingh Zone |  |  | 0 | 0 | 4.3802 | 0 | 0 | 0.27068 | 0 | 0 | 4.6509 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 33.1696 | 0 | 0 | 0 | 0 | 0.032588 | 0 | 0 | 33.2022 | Hydro | 5.1983 | Hydro | 519832.5
| Khulna Zone |  |  | 0 | 24.1745 | 0.73861 | 0 | 0 | 0.15048 | 22.6742 | 0 | 47.7378 | Solar | 2.4502 | Solar | 40276079.6744
| Barishal Zone |  |  | 8.1573 | 41.9425 | 1.26 | 0 | 0 | 0.001372 | 0 | 0 | 51.3611 | Import | 50.57 | Import | 314737601.77
| Rajshahi Zone |  |  | 13.7143 | 0 | 1.3168 | 0 | 0 | 0.78381 | 24.1652 | 0 | 39.9801 | Wind | 0.92112 | Wind | 13549675.2
| Rangpur Zone |  |  | 0 | 4.8845 | 2.7844 | 0 | 0 | 0.95339 | 0 | 0 | 8.6223
| Total |  |  | 128.4963 | 118.3596 | 45.2965 | 0 | 5.1983 | 2.4502 | 50.57 | 0.92112 | 351.292
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 449207093.9718 |  | Hydro | 519832.5
|  |  |  | Coal | 825786978.2302 |  | Solar | 40276079.6744
|  |  |  | HFO | 926452163.206 |  | Import | 314737601.77
|  |  |  | HSD | 0 |  | Wind | 13549675.2
[5 empty] | Total: | 257,05,29,424 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7622 | Peak Hr Flow | 900.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 36644000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.1652 | Peak Hr Flow | 1458.97 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 2048 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.7306 | Peak Hr Flow | 176.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2173 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.658 | Peak Hr Flow | 2534.97 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 93 |  | 6023
|  |  |  | Chattogram |  | 0 |  | 1500
|  |  |  | Cumilla |  | 0 |  | 1369
|  |  |  | Mymensingh |  | 207 |  | 1385
|  |  |  | Sylhet |  | 0 |  | 678
|  |  |  | Khulna |  | 0 |  | 1708
|  |  |  | Barishal |  | 0 |  | 467
|  |  |  | Rajshahi |  | 2 |  | 1473
|  |  |  | Rangpur |  | 0 |  | 996
|  |  |  | Total |  | 302 |  | 15599
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Fenchugonj CCPP Phase-2 ST |  |  | 35
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 35
|  |  |  | Total Unavailable Capacity |  |  |  | 335
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:01 | Haripur-Siddirganj 132kV Ckt-1 is restored.
| 08:09 | 09:30 | Saidpur 132/33kV S/S TR-2 (404T) LT Scheduled S/D Due to As the instructions of ALDC,
Bogura
| 08:10 | 09:29 | Saidpur 132/33kV S/S TR-2 (404T) HT Scheduled S/D Due to As the instructions of ALDC,
Bogura
|  | 08:16 | Sonargaon 132/33kV S/S Tr-2 HT is restored.
|  | 08:17 | Sonargaon 132/33kV S/S Tr-2 LT is restored.
| 10:07 | 17:22 | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to For T-2 Breaker Commission
| 10:08 | 17:21 | Feni 132/33kV S/S T-2(415T) HT Scheduled S/D Due to For T-2 Breaker Commission
| 10:29 | 11:35 | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 Scheduled S/D Due to Maintenance work
at Hasnabad ed.
| 10:55 | 17:44 | Khulna(S)-Rupsha 230kV Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end.
|  | 10:57 | Haripur-Siddirganj 132kV Ckt-2 is restored.
|  | 10:58 | Haripur-Siddirganj 230kV Ckt-2 is restored.
| 11:17 | 12:34 | Patnitala 132/33kV S/S T2 HT Project Work S/D Due to Transformer LT side clamp and
conductor moving
| 11:17 | 12:34 | Patnitala 132/33kV S/S T2 LT Project Work S/D Due to Transformer LT side clamp and
conductor moving
| 11:18 | 12:35 | Patnitala 132/33kV S/S T3 LT Project Work S/D Due to Transformer LT side clamp and
conductor moving
| 11:18 | 12:35 | Patnitala 132/33kV S/S T3 HT Project Work S/D Due to Transformer LT side clamp and
conductor moving
| 11:35 | 14:11 | Barishal(N)-Patuakhali 132kV Ckt-2 Scheduled S/D from Patuakhali 132/33kV end Due to Red
hot
| 11:35 | 14:10 | Barishal(N)-Patuakhali 132kV Ckt-1 Scheduled S/D from Patuakhali 132/33kV end Due to Red
hot
| 11:36 | 14:07 | Patuakhali-Payra 132kV Ckt-1 Scheduled S/D from Patuakhali 132/33kV end Due to Red hot
and from Payra 400/132/33kV end Due to Patuakhali line-1 230kV Bay T ponit top junction
point redhot maintenance
| 14:49 | 21:06 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Tripped showing Lockout Relay KT86.1
Operated Lockout Relay KT86.2 Operated Distance =M1 76.3 km /M2 70.80 km Current =
(R-Phase =76 A, Y-Phase = 69 A, B-Phase = 3687 A) relays Due to Over Current
| 14:57 | 17:34 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end.
| 14:57 | 17:34 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Forced S/D from Brahmanbaria 132/33kV end.
| 15:19 |  | Bibiyana South 400 MW Tripped with remarks:- GT
| 17:20 |  | Bibiyana South CCPP GT was sync.
| 17:20 |  | Bibiyana South 400 MW Synchronized with remarks:- GT
| 23:01 |  | Barapukuria TPP Unit-1 Shutdown
| 05:43 |  | Ashuganj-Ghorasal 132kV Ckt-1 Scheduled S/D from Ashuganj 230/132/33kV end Due to
Temperature issue at various clamp & conductor
| 07:09 |  | Kaliakoir 400/230/132kV S/S 132kV Bus 2 Scheduled S/D Due to Jumper connection of 132kV
bus-2 and 230/132kV ATr.
| 07:11 |  | Barapukuria TPP Unit-1 Synchronized
| 07:14 |  | Haripur-Siddirganj 132kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Taken from
other end and from Siddhirganj 132/33kV end Due to Maintenance work
| 07:16 |  | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Dhamrai 132/33kV end Due to কালিয়াকৈর | [7 empty] | 55.0MW load
|  |  | গ্রিড এ বাস শিফট জনিত কারনে সাটডাউন নেওয়া হয়। and from Kaliakoir 400/230/132kV end Due to | [7 empty] | interrup. Dhamrai
|  |  | Jumper connection of 132kV bus-2 and 230/132kV ATr. | [7 empty] | 132/33kV end
| 07:22 |  | Mogbazar 132/33kV S/S GT-1 HT Tripped showing Restricted Earth Fault relays Due to None
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-08-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 338 | 7887600 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 521569 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7442803 | Machine Problem
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 418680 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 126 | 3084480 | Engine Problem
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 815187 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 723622 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 7.5 | 187200 | Gas shortage
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 506880 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 769440 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 210 | 2830255 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1470528 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1701120 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 82 | 1524960 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 94678 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 55 | 868680 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 11376818.18 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 538 | 12226350 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 123 | 3354000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2731.5 | 57804850.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 325402.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 4725 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 437280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 219 | 5198325 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 211 | 2724018 | Gas shortage
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 1650145 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 108579 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 303298 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 292800 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 25920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 60 | 742080 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 12359 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 311127 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 17 | 326548 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 67 | 2070836 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 11 | 286080 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 15 | 1048800 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 2 | 541964 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 770 | 20361816 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 25 | 921120 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1125 | 26996363.64 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 2621 | 64689585.84
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 216 | 4958000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 300 | 7564900 | Line Overload
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 265 | 6506000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 230 | 5811000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 15 | 677808 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 10 | 736320 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 250909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1246686 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 22 | 961818 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 510880 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 132 | 3325881 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 3454560 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 176 | 3730560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 435504 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 0 | 0 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 1065900 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 45 | 343560 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 1516800 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 146155 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1768 | 43243241
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 72543 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 155 | 2448000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 68 | 1327200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 190690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 378240 | 00:00-16:00 hrs 12MW&16:00-24:00 hrs 24MW dis.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 226800 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 282 | 4650923
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 32588 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 42 | 962000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 249960 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3328936.36 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 140 | 3162000 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 25 | 643104 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 2003520 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 124 | 2712680 | plant availability zero
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 185568 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6600000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 396 | 9325000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 265 | 3996800 | Preparation for ST startup
Sylhet Area Total |  |  |  |  | 2325 | 1555 | 33202156.36
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 900 | 21762182 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 53760 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 60032 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 624816 | none
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 150480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1100 | 24174550 | Machine Problem
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2053 | 47737820
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1000 | 16734545 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 819552 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 118 | 2823000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 815 | 19186909.09 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5334340 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 440400 | Avail.100%;NEO cut for BPDB late pay.PPASec13.2(j)
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 250 | 6021000 | Bad quality coal
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1372 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2452 | 51361118.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 153776 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 65458 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 178119 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 156 | 4280091 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 383 | 9434181 | AGC
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 306754 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 119504 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 624096 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 0 | 22848 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 20700 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1458.97 | 24165239 | Coal shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 162320 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 447010 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2060.97 | 39980096
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 953454 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 3931000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 835190 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 38504.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 90 | 1949215 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 17768 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 897120 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 368 | 8622251.04
Eastern Grid Total |  |  |  |  | 17427.666 | 8957.5 | 203590756.38
Western Grid Total |  |  |  |  | 11731.125 | 6933.97 | 147701285.13
National Grid Total |  |  |  |  | 29158.791 | 15891.47 | 351292041.51
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-08-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10655.94 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4642.6 | MW
i) Dhaka area |  |  | 5930.44 |  | MW | i) Khulna area |  |  |  | 1708 | MW
ii) Chattogram area |  |  | 1500.5 |  | MW | ii) Barishal area |  |  |  | 467.2 | MW
iii) Cumilla area |  |  | 1369 |  | MW | iii) Rajshahi area |  |  |  | 1471.4 | MW
iv) Mymensingh area |  |  | 1178 |  | MW | iv) Rangpur area |  |  |  | 996 | MW
v) Sylhet area |  |  | 678 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15298.54 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 15 | 10:00 | 67 | HaripurSBU | 147 | 08:00 | 133 | Narshingdi | 200 | 21:00 | 199 | Uttara | 96 | 12:00
2 | AKSML | 27 | 11:00 | 68 | Hasnabad | 96 | 11:00 | 134 | Natore | 160 | 00:00 | 200 | UttaraNew | 54 | 13:00
3 | Aftabnagar | 46 | 13:00 | 69 | Hathazari | 88 | 19:00 | 135 | Nawabganj | 60.3 | 00:00 | 201 | Zigatola | 99 | 13:00
4 | Agargaon | 126 | 13:00 | 70 | Hatirjheel | 92 | 12:00 | 136 | Netrakona | 131 | 08:00
5 | Agrabad | 68 | 15:00 | 71 | Ishurdi | 80 | 00:00 | 137 | New | 86 | 10:00
6 | Amnura | 35 | 00:00 | 72 | Jaldhaka | 108 | 00:00 | 138 | Niamatpur | 84 | 00:00
7 | Ashuganj | 85 | 01:00 | 73 | Jamalpur | 128 | 21:00 | 139 | Noapara | 47 | 19:00
8 | BSRM | 197 | 17:00 | 74 | Jashore | 148 | 00:00 | 140 | PHP | 10 | 13:00
9 | Bagerhat | 91 | 19:30 | 75 | Jhenaidah | 90 | 01:00 | 141 | Pabna | 99 | 00:00
10 | Bajitpur | 95 | 19:30 | 76 | Joydebpur | 173 | 11:00 | 142 | Palashbari | 132 | 00:00
11 | Bakerganj | 13.6 | 20:00 | 77 | Joypurhat | 67 | 00:00 | 143 | Panchagarh | 74 | 19:30
12 | Bakulia | 89 | 14:00 | 78 | Juldah | 15 | 15:00 | 144 | Patiya | 10.5 | 19:30
13 | Banani | 76 | 13:00 | 79 | KSRM | 30 | 19:00 | 145 | Patnitala | 26 | 00:00
14 | Bangabhaban | 18 | 11:00 | 80 | Kabirpur | 281 | 15:00 | 146 | Patuakhali | 69 | 01:00
15 | Barapukuria | 75 | 00:00 | 81 | Kachua | 96 | 00:00 | 147 | Payra | 36 | 00:00
16 | Barguna | 22 | 01:00 | 82 | Kaliganj | 37 | 00:00 | 148 | Postogola | 62 | 13:00
17 | Barishal | 101 | 19:00 | 83 | Kallyanpur | 126 | 12:00 | 149 | Pubail | 46 | 23:00
18 | Barishal-230 | 102 | 22:00 | 84 | Kalurghat | 42 | 11:00 | 150 | Purbachal | 36 | 13:00
19 | Baroaulia | 54 | 11:00 | 85 | Kamrangirchar | 83 | 12:00 | 151 | Purbasadipur | 147 | 00:00
20 | Baroirhat | 57 | 00:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 45 | 00:00
21 | Bashundhara | 216 | 13:00 | 87 | Kasba | 37 | 00:00 | 153 | Rahim | 57 | 15:00
22 | BashundharaCement | 1 | 00:00 | 88 | Kazla | 126 | 16:00 | 154 | Rajbari | 87.5 | 00:00
23 | Beanibazar | 88 | 00:00 | 89 | Keranigonj | 88 | 19:00 | 155 | Rajendrapur | 119 | 08:00
24 | Benapole | 55 | 00:00 | 90 | Khagrachori | 32 | 19:30 | 156 | Rajshahi | 119 | 00:00
25 | Bhaluka | 191 | 08:00 | 91 | Khulna | 59 | 13:00 | 157 | Rajshahi-230 | 104 | 14:00
26 | Bhandaria | 57 | 23:00 | 92 | Khulshi | 143 | 14:00 | 158 | Ramganj | 112 | 00:00
27 | Bhangura | 36 | 00:00 | 93 | Kishoreganj | 132 | 01:00 | 159 | Rampur | 40 | 19:00
28 | Bheramara(GK) | 68 | 19:30 | 94 | Kodda | 315 | 18:30 | 160 | Rangamati | 15 | 19:30
29 | Bhulta | 235 | 09:00 | 95 | Kulaura | 57 | 00:00 | 161 | Rangpur | 140 | 19:30
30 | Bog-Sherpur | 84 | 00:00 | 96 | Kurigram | 76 | 19:00 | 162 | Ruppur | 4.2 | 09:00
31 | Bogura | 194 | 22:00 | 97 | Kushtia | 150 | 12:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 76 | 00:00 | 98 | Laksam | 35 | 00:00 | 164 | Saidpur | 105 | 19:00
33 | Brahmanbaria | 132 | 20:00 | 99 | Lakshmipur | 53 | 00:00 | 165 | Santhia | 38 | 00:00
34 | Cantonment | 138 | 12:00 | 100 | Lalbag | 79 | 18:30 | 166 | Satkhira | 124 | 00:00
35 | Chandina | 24 | 03:00 | 101 | Lalmonirhat | 73 | 00:00 | 167 | Satmasjid | 109 | 13:00
36 | Chandpur | 86 | 00:00 | 102 | MI_Cement | 17.6 | 12:00 | 168 | Savar | 228 | 16:00
37 | Chandraghona | 32 | 19:00 | 103 | Madanganj | 49 | 21:00 | 169 | SevenRings | 12.91 | 20:00
38 | Chapai | 77 | 02:00 | 104 | Madaripur | 115 | 00:00 | 170 | ShahCement | 23 | 01:00
39 | Charfasson | 34 | 00:00 | 105 | Madartek | 84 | 00:00 | 171 | Shahjadpur | 78 | 21:00
40 | Charsaidpur | 31 | 16:00 | 106 | Madunaghat | 52 | 18:30 | 172 | Shahjibazar | 143 | 21:00
41 | Chauddagram | 72 | 00:00 | 107 | Magura | 61 | 19:00 | 173 | Shahmirpur | 48 | 21:00
42 | Chhatak | 42 | 02:00 | 108 | Mahasthangarh | 77 | 00:00 | 174 | Shariatpur | 95 | 23:00
43 | Chowmuhani | 145 | 06:00 | 109 | Maijdee | 40 | 00:00 | 175 | Sherpur | 146 | 19:00
44 | Chuadanga | 111 | 01:00 | 110 | Manikganj | 132 | 21:00 | 176 | Shikalbaha | 22 | 12:00
45 | Coxsbazar | 133 | 00:00 | 111 | Maniknagar | 80 | 13:00 | 177 | Shitalakhya | 81.5 | 13:00
46 | Cumilla(N) | 107 | 21:00 | 112 | Matarbari | 51 | 00:00 | 178 | Sholosohor | 51 | 14:00
47 | Cumilla(S) | 175 | 19:30 | 113 | Matuail | 78 | 12:00 | 179 | Shomvuganj | 54 | 13:00
48 | Daganbhuiyan | 32 | 00:00 | 114 | Metrorail_Motijheel | 29 | 18:30 | 180 | Shyampur | 138 | 00:00
49 | Daudkandi | 143 | 20:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 138 | 12:00
50 | DhakaUniversity | 98 | 13:00 | 116 | Millgate | 110 | 15:00 | 182 | Sirajganj | 118 | 20:00
51 | Dhamrai | 106 | 20:00 | 117 | Mirpur | 156 | 12:00 | 183 | Sitakunda | 13 | 11:00
52 | Dhanmondi | 123 | 13:00 | 118 | Mirsorai | 49 | 09:00 | 184 | Sonargaon | 165 | 15:00
53 | Dohazari | 100 | 01:00 | 119 | Mirzapur | 47 | 18:30 | 185 | Sreemongol | 87 | 22:00
54 | Faridpur | 170 | 23:00 | 120 | Mithapukur | 82 | 00:00 | 186 | Sreepur | 135 | 08:00
55 | Fatullah | 117 | 12:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 48.3 | 22:00
56 | Fenchuganj | 47 | 00:00 | 122 | Mogbazar | 46.6 | 12:00 | 188 | Sunamganj | 63 | 22:00
57 | Feni | 107 | 19:00 | 123 | Mongla | 40 | 19:00 | 189 | Sylhet | 122 | 19:00
58 | GPH | 68 | 16:00 | 124 | Motijheel | 52 | 12:00 | 190 | Sylhet_(South) | 71 | 00:00
59 | Ghatail | 93 | 19:30 | 125 | Muktagacha | 41 | 19:30 | 191 | TK | 23 | 00:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 110 | 00:00 | 192 | Tangail | 172 | 18:00
61 | Ghorashal-230 | 116 | 09:00 | 127 | Muradnagar | 50 | 22:00 | 193 | Taraganj | 36 | 19:30
62 | Goalpara | 36 | 00:00 | 128 | Mymensingh | 144 | 13:00 | 194 | Tasnim | 42 | 21:00
63 | Gollamari | 106 | 00:00 | 129 | Nabinagar | 126 | 18:30 | 195 | Thakurgaon | 123 | 00:00
64 | Gopalganj | 108 | 21:00 | 130 | Naogaon | 126 | 00:00 | 196 | Tongi | 150 | 11:00
65 | Gulshan | 126 | 12:00 | 131 | Narail | 56 | 06:00 | 197 | Ullahpara | 39 | 00:00
66 | Halishahar | 138 | 14:00 | 132 | Narinda | 76 | 13:00 | 198 | Ullon | 57 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-08-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15631 | 635 |  | 16295
1:00 | 15141.64 | 802 |  | 15979.64
2:00 | 14952.6 | 602 |  | 15581.6
3:00 | 14581.91 | 349 |  | 14946.91
4:00 | 14265.14 | 322 |  | 14601.14
5:00 | 14132.55 | 302 |  | 14448.55
6:00 | 13727.32 | 291 |  | 14031.32
7:00 | 13622.55 | 303 |  | 13939.55
8:00 | 13575.12 | 258 |  | 13845.12
9:00 | 13567.55 | 499 |  | 14088.55
10:00 | 13880.32 | 526 |  | 14430.32
11:00 | 14283.79 | 98 |  | 14385.79
12:00 | 14356.77 | 893 |  | 15289.77
13:00 | 14366.35 | 547 |  | 14938.35
14:00 | 14466.45 | 90 |  | 14560.45
15:00 | 14410.76 | 119 |  | 14534.76
16:00 | 14073.73 | 58 |  | 14134.73
17:00 | 13894.61 | 73 |  | 13970.61
18:00 | 14232.44 | 28 |  | 14261.7
19:00 | 15682.11 | 182 |  | 15872.11
19:30 | 15891.47 | 302 |  | 16207.47
20:00 | 15717.31 | 169 |  | 15894.31
21:00 | 15748.97 | 202 |  | 15959.97
22:00 | 15654.33 | 223 |  | 15887.37
23:00 | 15519.32 | 268 |  | 15799.38
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 17-08-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 68 | 10 | 170 | 140 | 706 | 550 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 63 | 20 | 128 | 148 | 554 | 602
2:00 | 68 | 23 | 160 | 140 | 686 | 594 |  | Import | 0
3:00 | 63 | 24 | 128 | 128 | 726 | 594
4:00 | 69 | 27 | 174 | 144 | 838 | 578 | Ishurdi-Ghorashal Ckt-2 | Export | 2760000
5:00 | 65 | 32 | 142 | 144 | 808 | 594
6:00 | 77 | 38 | 182 | 146 | 900 | 612 |  | Import | 0
7:00 | 74 | 36 | 156 | 136 | 886 | 600
8:00 | 110 | 48 | 272 | 166 | 1150 | 678 | Sirajganj-Sreepur Ckt-1 | Export | 1844000
9:00 | 153 | 61 | 410 | 170 | 1466 | 700
10:00 | 149 | 56 | 374 | 160 | 1472 | 712 |  | Import | 0
11:00 | 155 | 65 | 400 | 180 | 1512 | 776
12:00 | 159 | 63 | 390 | 182 | 1500 | 742 | Sirajganj-Sreepur Ckt-2 | Export | 1850000
13:00 | 158 | 64 | 380 | 166 | 1500 | 710
14:00 | 132 | 41 | 360 | 174 | 1474 | 698 |  | Import | 0
15:00 | 148 | 59 | 390 | 184 | 1540 | 754
16:00 | 158 | 60 | 410 | 190 | 1600 | 754 | Gopalganj-Aminbazar Ckt-1 | Export | 15080000
17:00 | 152 | 62 | 370 | 190 | 1478 | 744
18:00 | 134 | 49 | 390 | 190 | 1426 | 704 |  | Import | 0
18:30 | 141 | 46 | 430 | 184 | 1602 | 620
19:00 | 117 | 27 | 400 | 170 | 1570 | 572 | Gopalganj-Aminbazar Ckt-2 | Export | 15110000
19:30 | 116 | 21 | 390 | 146 | 1542 | 550
20:00 | 116 | 15 | 400 | 150 | 1540 | 548 |  | Import | 0
21:00 | 117 | 19 | 380 | 154 | 1478 | 534
22:00 | 112 | 14 | 360 | 150 | 1508 | 528 |  | Total Export | 36644000
23:00 | 116 | 15 | 350 | 134 | 1498 | 526 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-08-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9333.42 | 6297.58 | 15631 | DAILY GENERATION CURVE
00:30 | 9341.77 | 6044.55 | 15386.32
01:00 | 9350.12 | 5791.52 | 15141.64 | 17-08-2026
01:30 | 9233.37 | 5813.75 | 15047.12
02:00 | 9116.62 | 5835.98 | 14952.6
02:30 | 8966.77 | 5800.485 | 14767.255
03:00 | 8816.92 | 5764.99 | 14581.91
03:30 | 8652.92 | 5770.605 | 14423.525
04:00 | 8488.92 | 5776.22 | 14265.14
04:30 | 8466.92 | 5731.925 | 14198.845
05:00 | 8444.92 | 5687.63 | 14132.55
05:30 | 8259.975 | 5669.96 | 13929.935
06:00 | 8075.03 | 5652.29 | 13727.32
06:30 | 8012.59 | 5662.345 | 13674.935
07:00 | 7950.15 | 5672.4 | 13622.55
07:30 | 7856.475 | 5742.36 | 13598.835
08:00 | 7762.8 | 5812.32 | 13575.12
08:30 | 7691.74 | 5879.595 | 13571.335
09:00 | 7620.68 | 5946.87 | 13567.55
09:30 | 7821.56 | 5902.375 | 13723.935
10:00 | 8022.44 | 5857.88 | 13880.32
10:30 | 8159.175 | 5922.88 | 14082.055
11:00 | 8295.91 | 5987.88 | 14283.79
11:30 | 8298.065 | 6022.215 | 14320.28
12:00 | 8300.22 | 6056.55 | 14356.77
12:30 | 8268.45 | 6093.11 | 14361.56
13:00 | 8236.68 | 6129.67 | 14366.35
13:30 | 8263.025 | 6153.375 | 14416.4
14:00 | 8289.37 | 6177.08 | 14466.45
14:30 | 8322.005 | 6116.6 | 14438.605
15:00 | 8354.64 | 6056.12 | 14410.76
15:30 | 8211.26 | 6030.985 | 14242.245
16:00 | 8067.88 | 6005.85 | 14073.73
16:30 | 8102.445 | 5881.725 | 13984.17
17:00 | 8137.01 | 5757.6 | 13894.61
17:30 | 8188.875 | 5874.65 | 14063.525
18:00 | 8240.74 | 5991.7 | 14232.44
18:30 | 8526.12 | 6431.155 | 14957.275
19:00 | 8811.5 | 6870.61 | 15682.11
19:30 | 8957.5 | 6933.97 | 15891.47
20:00 | 8830.5 | 6886.81 | 15717.31
20:30 | 8833.46 | 6899.68 | 15733.14 |  | Executive Engineer
21:00 | 8836.42 | 6912.55 | 15748.97 |  | Network Operation Division
21:30 | 8791.92 | 6909.73 | 15701.65
22:00 | 8747.42 | 6906.91 | 15654.33
22:30 | 8677.92 | 6908.905 | 15586.825
23:00 | 8608.42 | 6910.9 | 15519.32

## En-Curve
QF-LDC-12
Date | 17-08-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3639 | 1906 | 902 | 38 | 170 | 1268.58 | 222 | 4980 | 0 | 690.42 | 1765 | 0 | 0 | 50 | 635 | DAILY ENERGY CURVE
00:30 | 3641.5 | 1925 | 901 | 38 | 165 | 1138.55 | 222 | 4929.5 | 0 | 675.42 | 1707.35 | 0 | 0 | 43 | 718.5 | 17-08-2026
01:00 | 3644 | 1944 | 900 | 38 | 160 | 1008.52 | 222 | 4879 | 0 | 660.42 | 1649.7 | 0 | 0 | 36 | 802
01:30 | 3593.5 | 1865.25 | 900.5 | 38 | 158 | 1005.25 | 221.5 | 4899.5 | 0 | 665.42 | 1658.2 | 0 | 0 | 42 | 702 | Energy Generated | 351.292 |  | MKWHr
02:00 | 3543 | 1786.5 | 901 | 38 | 156 | 1001.98 | 221 | 4920 | 0 | 670.42 | 1666.7 | 0 | 0 | 48 | 602 | Energy not Served | 7.839 |  | MKWHr
02:30 | 3561.5 | 1797 | 900.5 | 38 | 155 | 1001.985 | 221 | 4958 | 0 | 561.92 | 1523.35 | 0 | 0 | 49 | 475.5 | Total Energy Requirement | 359.131 |  | MKWHr
03:00 | 3580 | 1807.5 | 900 | 38 | 154 | 1001.99 | 221 | 4996 | 0 | 453.42 | 1380 | 0 | 0 | 50 | 349
03:30 | 3573 | 1797.5 | 900 | 38 | 150 | 983.605 | 220.5 | 5042 | 0 | 429.42 | 1244.5 | 0 | 0 | 45 | 335.5
04:00 | 3566 | 1787.5 | 900 | 38 | 146 | 965.22 | 220 | 5088 | 0 | 405.42 | 1109 | 0 | 0 | 40 | 322
04:30 | 3579.5 | 1818 | 900 | 38 | 146 | 892.425 | 219.5 | 5120 | 0 | 386.42 | 1057.5 | 0 | 0 | 41.5 | 312
05:00 | 3593 | 1848.5 | 900 | 38 | 146 | 819.63 | 219 | 5152 | 0 | 367.42 | 1006 | 0 | 0 | 43 | 302
05:30 | 3541 | 1846 | 900 | 38 | 142 | 818.545 | 198.5 | 5151 | 1.68 | 349.21 | 894.5 | 0 | 0 | 49.5 | 296.5
06:00 | 3489 | 1843.5 | 900 | 38 | 138 | 817.46 | 178 | 5150 | 3.36 | 331 | 783 | 0 | 0 | 56 | 291
06:30 | 3515 | 1890.5 | 900.5 | 38 | 138 | 818.965 | 178.5 | 5028.5 | 32.47 | 331 | 746.5 | 0 | 0 | 57 | 297
07:00 | 3541 | 1937.5 | 901 | 38 | 138 | 820.47 | 179 | 4907 | 61.58 | 331 | 710 | 0 | 0 | 58 | 303
07:30 | 3498.5 | 1934 | 900.5 | 38 | 141 | 824.185 | 179 | 4815 | 118.94 | 333.21 | 756 | 0 | 0 | 60.5 | 280.5
08:00 | 3456 | 1930.5 | 900 | 38 | 144 | 827.9 | 179 | 4723 | 176.3 | 335.42 | 802 | 0 | 0 | 63 | 258
08:30 | 3331 | 1850 | 900 | 38 | 144 | 824.81 | 199.5 | 4642.5 | 234.605 | 350.92 | 994 | 0 | 0 | 62 | 378.5
09:00 | 3206 | 1769.5 | 900 | 38 | 144 | 821.72 | 220 | 4562 | 292.91 | 366.42 | 1186 | 0 | 0 | 61 | 499
09:30 | 3229.8 | 1829.5 | 900 | 38 | 148 | 823.03 | 220 | 4551 | 245.185 | 388.92 | 1304.5 | 0 | 0 | 46 | 512.5
10:00 | 3253.6 | 1889.5 | 900 | 38 | 152 | 824.34 | 220 | 4540 | 197.46 | 411.42 | 1423 | 0 | 0 | 31 | 526
10:30 | 3283.4 | 1953.5 | 900 | 38 | 157 | 822.705 | 220 | 4539 | 266.03 | 415.42 | 1457.5 | 0 | 0 | 29.5 | 312
11:00 | 3313.2 | 2017.5 | 900 | 38 | 162 | 821.07 | 220 | 4538 | 334.6 | 419.42 | 1492 | 0 | 0 | 28 | 98
11:30 | 3270.35 | 2007 | 900 | 38 | 162 | 822.745 | 220.5 | 4568 | 337.265 | 429.42 | 1532 | 0 | 0 | 33 | 495.5
12:00 | 3227.5 | 1996.5 | 900 | 38 | 162 | 824.42 | 221 | 4598 | 339.93 | 439.42 | 1572 | 0 | 0 | 38 | 893
12:30 | 3276.95 | 1911 | 900 | 38 | 164 | 824.565 | 221 | 4623 | 340.125 | 433.42 | 1588 | 0 | 0 | 41.5 | 720
13:00 | 3326.4 | 1825.5 | 900 | 38 | 166 | 824.71 | 221 | 4648 | 340.32 | 427.42 | 1604 | 0 | 0 | 45 | 547
13:30 | 3371.2 | 1813 | 900.5 | 38 | 161 | 823.59 | 221 | 4681 | 349.69 | 426.92 | 1591 | 0 | 0 | 39.5 | 318.5
14:00 | 3416 | 1800.5 | 901 | 38 | 156 | 822.47 | 221 | 4714 | 359.06 | 426.42 | 1578 | 0 | 0 | 34 | 90
14:30 | 3427.5 | 1803.75 | 900 | 38 | 159 | 826.72 | 220.5 | 4714 | 312.215 | 440.92 | 1563 | 0 | 0 | 33 | 104.5
15:00 | 3439 | 1807 | 899 | 38 | 162 | 830.97 | 220 | 4714 | 265.37 | 455.42 | 1548 | 0 | 0 | 32 | 119
15:30 | 3448.5 | 1726.5 | 899.5 | 38 | 164 | 831.035 | 219.5 | 4711 | 227 | 401.71 | 1545 | 0 | 0 | 30.5 | 88.5
16:00 | 3458 | 1646 | 900 | 38 | 166 | 831.1 | 219 | 4708 | 188.63 | 348 | 1542 | 0 | 0 | 29 | 58
16:30 | 3450.5 | 1777 | 900.5 | 38 | 158 | 826.705 | 218.5 | 4692.5 | 133.965 | 352 | 1412.5 | 0 | 0 | 24 | 65.5
17:00 | 3443 | 1908 | 901 | 38 | 150 | 822.31 | 218 | 4677 | 79.3 | 356 | 1283 | 0 | 0 | 19 | 73
17:30 | 3531.5 | 1885.25 | 900.5 | 38 | 157 | 924.27 | 218 | 4657 | 46.505 | 387.5 | 1294 | 0 | 0 | 24 | 50.5
18:00 | 3620 | 1862.5 | 900 | 38 | 164 | 1026.23 | 218 | 4637 | 13.71 | 419 | 1305 | 0 | 0 | 29 | 28
18:30 | 3660.5 | 1828.5 | 900 | 38 | 168 | 1193.42 | 218.5 | 4879.5 | 6.855 | 472.5 | 1561.5 | 0 | 0 | 30 | 105
19:00 | 3701 | 1794.5 | 900 | 38 | 172 | 1360.61 | 219 | 5122 | 0 | 526 | 1818 | 0 | 0 | 31 | 182
19:30 | 3713 | 1781.5 | 900 | 38 | 176 | 1458.97 | 219 | 5268 | 0 | 511 | 1801 | 0 | 0 | 25 | 302
20:00 | 3655 | 1660.5 | 900 | 38 | 166 | 1467.81 | 220 | 5349 | 0 | 512 | 1723 | 0 | 0 | 26 | 169
20:30 | 3668.5 | 1679.75 | 901 | 38 | 163 | 1467.68 | 220.5 | 5374 | 0 | 517.21 | 1673.5 | 0 | 0 | 30 | 185.5
21:00 | 3682 | 1699 | 902 | 38 | 160 | 1467.55 | 221 | 5399 | 0 | 522.42 | 1624 | 0 | 0 | 34 | 202
21:30 | 3642.5 | 1724.5 | 902 | 38 | 161 | 1470.73 | 221.5 | 5398.5 | 0 | 531.92 | 1580.5 | 0 | 0 | 30.5 | 212.5
22:00 | 3603 | 1750 | 902 | 38 | 162 | 1473.91 | 222 | 5398 | 0 | 541.42 | 1537 | 0 | 0 | 27 | 223
22:30 | 3632 | 1723.5 | 902 | 38 | 163 | 1475.905 | 222 | 5350 | 0 | 541.92 | 1513.5 | 0 | 0 | 25 | 245.5
23:00 | 3661 | 1697 | 902 | 38 | 164 | 1477.9 | 222 | 5302 | 0 | 542.42 | 1490 | 0 | 0 | 23 | 268
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-08-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 371 | 02:00 | 337 | 00:00 | Madunaghat | 400 | 10:00 | 392 | 21:00
Amtali | 412 | 02:00 | 406 | 22:00 | Meghnaghat | 377 | 06:00 | 370 | 07:00
Ashuganj | 390 | 09:00 | 379 | 23:00 | Mirsorai | 397 | 09:00 | 388 | 21:00
Bhulta | 390 | 06:00 | 379 | 11:00 | Payra | 414 | 06:00 | 409 | 20:00
Bibiana | 378 | 04:00 | 373 | 23:00 | Rahanpur | 408 | 09:00 | 389 | 21:00
BIPTC | 402 | 06:00 | 395 | 00:00 | Rampal | 396 | 16:00 | 383 | 22:00
Bogura | 394 | 09:00 | 372 | 21:00
Gopalganj | 390 | 09:00 | 379 | 23:00
Kaliakoir | 360 | 09:00 | 351 | 12:00
Korerhat | 397 | 09:00 | 387 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 06:00 | 219 | 13:00 | Hathazari | 237 | 08:00 | 231 | 23:00
AKSML | 236 | 00:00 | 230 | 21:00 | Ishurdi | 234 | 09:00 | 217 | 22:00
Aminbazar | 227 | 04:00 | 221 | 11:00 | Jhenaidah | 227 | 09:00 | 207 | 22:00
Ashuganj | 224 | 06:00 | 218 | 22:00 | Kachua | 228 | 09:00 | 222 | 22:00
Ashuganj-400 | 224 | 06:00 | 218 | 22:00 | Kaliakoir | 224 | 02:00 | 219 | 12:00
Baghabari | 231 | 08:00 | 220 | 20:00 | Keranigonj | 224 | 06:00 | 217 | 13:00
Barapukuria | 226 | 10:00 | 213 | 00:00 | Khulna(S) | 227 | 09:00 | 214 | 21:00
Barapukuria-230 | 226 | 10:00 | 213 | 00:00 | Korerhat | 227 | 09:00 | 221 | 22:00
Barishal | 227 | 09:00 | 219 | 21:00 | Madunaghat | 239 | 09:00 | 232 | 20:00
Bheramara | 233 | 09:00 | 216 | 00:00 | Madunaghat-400 | 241 | 10:00 | 234 | 21:00
Bhulta | 222 | 02:00 | 214 | 11:00 | Maniknagar | 220 | 03:00 | 213 | 11:00
Bibiana | 219 | 07:00 | 215 | 03:00 | Meghnaghat | 229 | 02:00 | 223 | 21:00
BIPTC | 236 | 09:00 | 217 | 00:00 | Meghnaghat-400 | 225 | 06:00 | 219 | 11:00
Birulia | 223 | 18:00 | 220 | 15:00 | Mirsorai | 230 | 09:00 | 225 | 20:00
Bogura | 237 | 09:00 | 225 | 00:00 | Naogaon | 224 | 09:00 | 204 | 00:00
Bogura-400 | 237 | 09:00 | 224 | 21:00 | Purbasadipur | 225 | 13:00 | 209 | 00:00
Borhanuddin | 231 | 11:00 | 223 | 21:00 | Rajshahi | 231 | 09:00 | 213 | 22:00
BSRM | 227 | 09:00 | 222 | 20:00 | Rampal | 226 | 15:00 | 214 | 23:00
Charfasson | 231 | 09:00 | 224 | 22:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 225 | 11:00 | 222 | 00:00 | Rampura | 221 | 02:00 | 212 | 12:00
Cumilla(N) | 221 | 09:00 | 217 | 00:00 | Shikalbaha | 239 | 09:00 | 231 | 20:00
Faridpur | 222 | 09:00 | 213 | 22:00 | Shyampur | 223 | 06:00 | 217 | 11:00
Fenchuganj | 220 | 09:00 | 216 | 00:00 | Siddhirganj | 223 | 05:00 | 218 | 19:00
Feni | 224 | 09:00 | 219 | 21:00 | Sirajgonj | 235 | 11:00 | 227 | 00:00
Ghorashal | 230 | 04:00 | 220 | 11:00 | Sreepur | 221 | 10:00 | 211 | 21:00
Ghorashal-230 | 210 | 14:00 | 203 | 13:00 | Tongi | 215 | 04:00 | 204 | 11:00
Gopalganj | 222 | 09:00 | 214 | 23:00
GPH | 235 | 09:00 | 229 | 20:00
Haripur | 222 | 06:00 | 215 | 11:00
Hasnabad | 223 | 02:00 | 217 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 05:00 | 126 | 11:00 | Madaripur | 131 | 16:00 | 126 | 00:00
Agargaon | 137 | 06:00 | 130 | 13:00 | Madartek | 137 | 04:00 | 126 | 11:00
Agrabad | 137 | 00:00 | 33 | 21:00 | Madunaghat | 139 | 09:00 | 133 | 20:00
AKS | 134 | 01:00 | 130 | 21:00 | Magura | 137 | 16:00 | 122 | 21:00
Aminbazar | 130 | 04:00 | 125 | 12:00 | Mahasthangarh | 134 | 10:00 | 122 | 00:00
Amnura | 134 | 09:00 | 124 | 20:00 | Maijdee | 127 | 09:00 | 124 | 00:00
Ashuganj | 129 | 06:00 | 125 | 20:00 | Manikganj | 129 | 13:00 | 120 | 03:00
Ashuganj-230 | 132 | 10:00 | 130 | 00:00 | Maniknagar | 137 | 06:00 | 130 | 12:00
Bagerhat | 131 | 15:00 | 118 | 22:00 | Matarbari | 130 | 10:00 | 120 | 18:30
Bajitpur | 125 | 09:00 | 119 | 21:00 | Matuail | 131 | 02:00 | 126.5 | 11:00
Bakerganj | 134 | 12:00 | 126 | 23:00 | Metrorail_Motijheel | 137 | 06:00 | 130 | 12:00
Bakulia | 137 | 00:00 | 133 | 20:00 | Metrorail_Uttara | 129 | 03:00 | 121 | 13:00
Banani | 135 | 03:00 | 125 | 12:00 | Millgate | 131 | 01:00 | 122 | 12:00
Bangabhaban | 137 | 04:00 | 129 | 12:00 | Mirpur | 129 | 06:00 | 125 | 11:00
Barapukuria | 137 | 12:00 | 124 | 00:00 | Mirzapur | 127 | 09:00 | 122 | 08:00
Barguna | 134 | 10:00 | 126 | 21:00 | Mithapukur | 131 | 09:00 | 120 | 00:00
Barishal | 132 | 09:00 | 125 | 22:00 | MI_Cement | 132 | 04:00 | 125 | 12:00
Barishal-230 | 132 | 08:00 | 126 | 21:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroaulia | 136 | 00:00 | 131 | 22:00 | Mogbazar | 138 | 04:00 | 130 | 11:00
Baroirhat | 131 | 09:00 | 128 | 00:00 | Mongla | 130 | 15:00 | 118 | 23:00
Bashundhara | 135 | 02:00 | 122 | 12:00 | Motijheel | 137 | 04:00 | 129 | 12:00
BashundharaCement | 131 | 05:00 | 127 | 12:00 | Muktagacha | 130 | 00:00 | 113 | 08:00
Beanibazar | 123 | 14:00 | 117 | 22:00 | Munshiganj | 130 | 02:00 | 124 | 11:00
Benapole | 138 | 16:00 | 119 | 21:00 | Muradnagar | 126 | 07:00 | 122 | 21:00
Bhaluka | 130 | 10:00 | 123 | 21:00 | Mymensingh | 130 | 00:00 | 113 | 07:00
Bhandaria | 130 | 10:00 | 120 | 23:00 | Nabinagar | 125 | 09:00 | 119 | 15:00
Bhangura | 133 | 09:00 | 125 | 00:00 | Naogaon | 135 | 13:00 | 123 | 00:00
Bheramara | 136 | 09:00 | 126 | 00:00 | Narail | 139 | 08:00 | 120 | 22:00
Bheramara(GK) | 136 | 09:00 | 125 | 00:00 | Narinda | 137 | 06:00 | 130 | 12:00
Bhulta | 126 | 03:00 | 122 | 11:00 | Narshingdi | 126 | 01:00 | 119 | 17:00
Bhulta-400 | 128 | 02:00 | 123 | 11:00 | Natore | 134 | 09:00 | 123 | 00:00
Birulia | 131 | 14:00 | 129 | 16:00 | Nawabganj | 135 | 06:00 | 130 | 13:00
Bog-Sherpur | 135 | 16:00 | 125 | 00:00 | Netrakona | 120 | 09:00 | 112 | 22:00
Bogura | 136 | 09:00 | 126 | 00:00 | New | 130 | 01:00 | 125 | 00:00
Bogura-230 | 137 | 09:00 | 129 | 00:00 | Niamatpur | 135 | 08:00 | 124 | 00:00
Brahmanbaria | 126 | 09:00 | 122 | 19:00 | Noapara | 134 | 09:00 | 124 | 22:00
Cantonment | 136 | 02:00 | 131 | 11:00 | Pabna | 133 | 09:00 | 124 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandina | 128 | 07:00 | 125 | 22:00 | Palashbari | 131 | 09:00 | 119 | 00:00
Chandpur | 134 | 16:00 | 129 | 07:00 | Panchagarh | 138 | 09:00 | 127 | 23:00
Chandraghona | 139 | 09:00 | 134 | 19:30 | Patiya | 137 | 09:00 | 131 | 21:00
Chapai | 134 | 08:00 | 124 | 00:00 | Patnitala | 133 | 16:00 | 123 | 21:00
Charsaidpur | 131 | 03:00 | 18 | 20:00 | Patuakhali | 133 | 12:00 | 126 | 22:00
Chauddagram | 129 | 09:00 | 125 | 22:00 | Payra | 136 | 09:00 | 132 | 19:30
Chhatak | 121 | 15:00 | 114 | 22:00 | PHP | 131 | 13:00 | 128 | 00:00
Chowmuhani | 127 | 11:00 | 124 | 23:00 | Postogola | 133 | 03:00 | 128 | 12:00
Chuadanga | 136 | 10:00 | 119 | 23:00 | Pubail | 124 | 02:00 | 119 | 08:00
Coxsbazar | 132 | 09:00 | 122 | 18:30 | Purbachal | 135 | 02:00 | 126 | 12:00
Cumilla(N) | 128 | 09:00 | 125 | 00:00 | Purbasadipur | 136 | 12:00 | 126 | 00:00
Cumilla(S) | 130 | 05:00 | 123 | 16:00 | Rahanpur | 136 | 09:00 | 129 | 21:00
Daganbhuiyan | 129 | 09:00 | 126 | 04:00 | Rahanpur-400 | 136 | 09:00 | 130 | 00:00
Daudkandi | 124 | 04:00 | 121 | 00:00 | Rahim | 132 | 06:00 | 126 | 11:00
DhakaUniversity | 135 | 03:00 | 127 | 11:00 | Rajbari | 126 | 09:00 | 120 | 21:00
Dhamrai | 127 | 09:00 | 122 | 11:00 | Rajendrapur | 131 | 10:00 | 125 | 20:00
Dhanmondi | 135.8 | 06:00 | 127 | 12:00 | Rajshahi | 131 | 09:00 | 121 | 00:00
Dohazari | 135 | 09:00 | 128 | 18:30 | Rajshahi-230 | 132 | 09:00 | 122 | 23:00
Faridpur | 128 | 06:00 | 123 | 22:00 | Ramganj | 128 | 10:00 | 124 | 00:00
Fatullah | 133 | 04:00 | 126 | 11:00 | Rampur | 136 | 02:00 | 132 | 18:30
Fenchuganj | 129 | 10:00 | 126 | 02:00 | Rampura | 135 | 06:00 | 127 | 11:00
Feni | 131 | 13:00 | 127 | 05:00 | Rangamati | 137 | 09:00 | 133 | 19:30
Feni-230 | 130 | 09:00 | 127 | 05:00 | Rangpur | 131 | 12:00 | 120 | 00:00
Ghatail | 128 | 00:00 | 116 | 03:00 | Ruppur | 136 | 09:00 | 126 | 00:00
Ghorashal | 125 | 09:00 | 120 | 10:00 | Saidpur | 134 | 09:00 | 124 | 00:00
Goalpara | 137 | 16:00 | 127 | 21:00 | Santhia | 134 | 09:00 | 126 | 00:00
Gollamari | 136 | 09:00 | 127 | 21:00 | Satkhira | 134 | 15:00 | 121 | 00:00
Gopalganj | 132 | 15:00 | 123 | 21:00 | Satmasjid | 136 | 02:00 | 130 | 13:00
Gopalganj-400 | 132 | 09:00 | 127 | 21:00 | Savar | 128 | 04:00 | 124 | 15:00
Gulshan | 134 | 05:00 | 126 | 12:00 | SevenRings | 126 | 04:00 | 121 | 17:00
Halishahar | 137 | 00:00 | 132 | 20:00 | ShahCement | 131 | 03:00 | 126 | 11:00
Haripur | 132 | 06:00 | 127 | 11:00 | Shahjadpur | 135 | 09:00 | 129 | 00:00
HaripurSBU | 132 | 00:00 | 127 | 11:00 | Shahjibazar | 126 | 10:00 | 121 | 21:00
Hasnabad | 134 | 03:00 | 128 | 11:00 | Shahmirpur | 138 | 00:00 | 132 | 19:30
Hathazari | 138 | 08:00 | 133 | 19:30 | Shariatpur | 131 | 09:00 | 123 | 21:00
Hatirjheel | 135 | 03:00 | 127 | 11:00 | Sherpur | 125 | 18:30 | 110 | 08:00
Ishurdi | 137 | 09:00 | 127 | 00:00 | Shikalbaha | 126 | 11:00 | 122 | 19:30
Jaldhaka | 132 | 09:00 | 121 | 00:00 | Shikalbaha-230 | 139 | 10:00 | 133 | 20:00
Jamalpur | 134 | 00:00 | 113 | 08:00 | Shitalakhya | 134 | 07:00 | 125 | 12:00
Jashore | 140 | 16:00 | 120 | 22:00 | Sholosohor | 137 | 00:00 | 133 | 19:30
Jhenaidah | 140 | 16:00 | 117 | 00:00 | Shomvuganj | 122 | 10:00 | 114 | 21:00
Jhenaidah-230 | 139 | 09:00 | 1 | 14:00 | Shyampur | 132 | 06:00 | 129 | 00:00
Joydebpur | 124 | 10:00 | 116 | 17:00 | Shyampur-230 | 134 | 06:00 | 130 | 12:00
Joypurhat | 133 | 10:00 | 121 | 00:00 | Siddhirganj | 132 | 02:00 | 127 | 11:00
Juldah | 137 | 00:00 | 132 | 19:30 | Sirajganj | 131 | 15:00 | 122 | 00:00
Kabirpur | 130 | 09:00 | 117 | 13:00 | Sitakunda | 137 | 09:00 | 132 | 20:00
Kachua | 130 | 09:00 | 127 | 00:00 | Sonargaon | 130 | 07:00 | 123 | 15:00
Kaliakoir | 131 | 00:00 | 126 | 08:00 | Sreemongol | 125 | 10:00 | 120 | 22:00
Kaliganj | 140 | 16:00 | 124 | 22:00 | Sreepur | 133 | 10:00 | 128 | 20:00
Kallyanpur | 135 | 04:00 | 125 | 12:00 | Srinagar | 135 | 02:00 | 130 | 13:00
Kalurghat | 138 | 02:00 | 134 | 19:30 | SSM | 140 | 00:00 | 139 | 01:00
Kamrangirchar | 136 | 05:00 | 123 | 12:00 | Sunamganj | 118 | 13:00 | 112 | 03:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 123 | 09:00 | 120 | 16:00
Kasba | 125 | 07:00 | 121 | 21:00 | Sylhet_(South) | 124 | 14:00 | 120 | 23:00
Kazla | 137 | 03:00 | 130 | 11:00 | Tangail | 127 | 00:00 | 118 | 07:00
Keranigonj | 136 | 06:00 | 131 | 12:00 | Taraganj | 132 | 09:00 | 122 | 00:00
Khagrachori | 137 | 09:00 | 132 | 19:30 | Tasnim | 130 | 07:00 | 124 | 11:00
Khulna | 135 | 09:00 | 125 | 21:00 | Thakurgaon | 137 | 09:00 | 127 | 23:00
Khulna(S) | 137 | 16:00 | 127 | 23:00 | TK | 138 | 09:00 | 134 | 19:30
Khulshi | 135 | 00:00 | 131 | 19:00 | Tongi | 133 | 04:00 | 125 | 11:00
Kishoreganj | 124 | 09:00 | 118 | 21:00 | Ullahpara | 132 | 09:00 | 124 | 00:00
Kodda | 130 | 00:00 | 116 | 08:00 | Ullon | 135 | 03:00 | 126 | 12:00
Korerhat | 133 | 09:00 | 130 | 07:00 | Uttara | 131 | 04:00 | 123 | 17:00
KSRM | 138 | 01:00 | 131 | 20:00 | UttaraNew | 129 | 03:00 | 121 | 13:00
Kulaura | 128 | 09:00 | 125 | 00:00 | Zigatola | 136 | 06:00 | 131 | 12:00
Kurigram | 129 | 09:00 | 114 | 00:00
Kushtia | 132 | 09:00 | 118 | 00:00
Laksam | 129 | 09:00 | 124 | 00:00
Lakshmipur | 127 | 16:00 | 123 | 00:00
Lalbag | 135 | 02:00 | 130 | 13:00
Lalmonirhat | 128 | 09:00 | 118 | 23:00
Madanganj | 131 | 05:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-08-2026 | [28 empty] | Date: | 17-08-2026 | [28 empty] | Date: | 17-08-2026 | [28 empty] | Date: | 17-08-2026 | [28 empty] | Date: | 17-08-2026 | [18 empty] | Date: | 17-08-2026
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 549 | 0 | 35 | 73 | 141 | 145 | 15 | 55 | 72 | 0 | 0 | 0 | 0 | 0 | 55 | 301 | 0 | 0 | 0 | 143.42 | 10 | 22 | 0 | 515 | 51 | 16 | 47 | 0 | 50 | 51 | 42 | 17 | 12 | 12 | 0 | 222 | 103 | 2 | 1125 | 23 | 0 | 30 | 8 | 33 | 0 | 0 | 0 | 0 | 1224 | 0 | 16 | 8 | 260 | 354 | 260 | 51 | 47 | 208 | 39 | 71 | 143 | 135 | 0 | 0 | 100 | 170 | 15 | 0 | 31 | 240 | 263 | 380 | 41 | 0 | 150 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 120 | 17 | 69 | 0 | 155 | 0 | 0 | 0 | 5 | 9333.42 | 902 | 0 | 0 | 27 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 925 | 0 | 0 | 0 | 1268.58 | 0 | 24 | 0 | 35 | 70 | 0 | 50 | 28 | 8 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 50 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 250 | 117 | 220 | 0 | 700 | 550 | 54 | 6297.58 | 15631 | 104.52
01:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 564 | 0 | 35 | 71 | 141 | 97 | 15 | 17 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 309 | 0 | 0 | 0 | 143.42 | 10 | 22 | 0 | 540 | 104 | 16 | 21 | 0 | 36 | 51 | 42 | 0 | 12 | 12 | 0 | 222 | 106 | 3 | 1125 | 33 | 0 | 48 | 25.5 | 103 | 53 | 0 | 0 | 0 | 1224 | 0 | 83 | 8 | 250 | 300 | 280 | 51 | 46 | 214 | 39 | 69 | 143 | 189 | 0 | 0 | 105 | 160 | 52.2 | 0 | 31 | 235 | 263 | 373 | 40 | 0 | 153 | 0 | 8 | 0 | 84 | 25 | 145 | 0 | 120 | 17 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 9350.12 | 900 | 0 | 0 | 23 | 0 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 925 | 0 | 0 | 0 | 1008.52 | 0 | 24 | 0 | 0 | 0 | 0 | 50 | 28 | 8 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 49 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 118 | 220 | 0 | 600 | 550 | 17 | 5791.52 | 15141.64 | 104.52
02:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 476 | 20 | 35 | 71 | 141 | 97 | 15 | 17 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 286 | 0 | 0 | 0 | 143.42 | 9.5 | 22 | 0 | 485 | 91 | 16 | 19 | 0 | 48 | 51 | 42 | 0 | 12 | 12 | 0 | 221 | 101 | 3 | 1125 | 31 | 0 | 48 | 25.5 | 96 | 80 | 0 | 0 | 0 | 1224 | 0 | 145 | 8 | 230 | 300 | 245 | 51 | 45 | 218 | 39 | 68 | 142 | 172 | 0 | 0 | 104 | 156 | 52.2 | 0 | 31 | 235 | 263 | 354 | 40 | 0 | 140 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 120 | 0 | 48 | 0 | 48 | 0 | 0 | 0 | 12 | 9116.62 | 901 | 0 | 0 | 22 | 11 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 925 | 0 | 0 | 0 | 1001.98 | 0 | 24 | 0 | 0 | 0 | 0 | 50 | 28 | 8 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 49 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 118 | 220 | 0 | 600 | 590 | 17 | 5835.98 | 14952.6 | 104.51
03:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 492 | 35 | 35 | 71 | 141 | 45 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 292 | 0 | 0 | 0 | 143.42 | 9.5 | 22 | 0 | 500 | 30 | 16 | 19 | 0 | 50 | 0 | 22 | 0 | 12 | 12 | 0 | 221 | 97 | 5 | 1125 | 28 | 0 | 50 | 8 | 90 | 120 | 0 | 0 | 0 | 1224 | 0 | 150 | 8 | 230 | 300 | 250 | 51 | 46 | 218 | 39 | 69 | 142 | 164 | 0 | 0 | 32 | 154 | 8 | 0 | 31 | 240 | 263 | 360 | 40 | 0 | 122 | 0 | 8 | 0 | 84 | 25 | 139 | 0 | 120 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 8816.92 | 900 | 0 | 0 | 0 | 25 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 925 | 0 | 0 | 0 | 1001.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 158 | 49 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 118 | 220 | 0 | 600 | 665 | 17 | 5764.99 | 14581.91 | 104.5
04:00 | 0 | 51 | 25 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 483 | 35 | 35 | 71 | 142 | 30 | 15 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 288 | 0 | 0 | 0 | 143.42 | 9.5 | 22 | 0 | 490 | 15 | 16 | 15 | 0 | 40 | 0 | 6 | 0 | 12 | 12 | 0 | 220 | 98 | 5 | 1125 | 15 | 0 | 41 | 0 | 68 | 120 | 0 | 0 | 0 | 1224 | 0 | 35 | 8 | 230 | 300 | 250 | 51 | 46 | 219 | 36 | 69 | 142 | 155 | 0 | 0 | 17 | 146 | 0 | 0 | 23 | 240 | 263 | 360 | 40 | 0 | 121 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 121 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 8488.92 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 925 | 0 | 0 | 0 | 965.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 157 | 49 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 118 | 220 | 0 | 600 | 758 | 17 | 5776.22 | 14265.14 | 104.5
05:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 490 | 35 | 30 | 53 | 142 | 30 | 15 | 17 | 31 | 0 | 0 | 0 | 0 | 0 | 17 | 295 | 0 | 0 | 0 | 143.42 | 9.5 | 22 | 0 | 510 | 15 | 16 | 12 | 0 | 43 | 0 | 0 | 0 | 12 | 12 | 0 | 219 | 100 | 5 | 1125 | 16 | 0 | 25 | 0 | 63 | 120 | 0 | 0 | 0 | 1224 | 0 | 20 | 35 | 230 | 300 | 260 | 51 | 46 | 219 | 36 | 69 | 142 | 140 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 240 | 263 | 380 | 40 | 0 | 128 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 120 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 8444.92 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 925 | 0 | 0 | 0 | 819.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 158 | 50 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 118 | 220 | 0 | 600 | 820 | 17 | 5687.63 | 14132.55 | 104.5
06:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 272 | 0 | 489 | 35 | 22 | 0 | 142 | 30 | 15 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 17 | 295 | 0 | 0 | 0 | 123 | 9.5 | 22 | 0 | 500 | 13 | 16 | 12 | 0 | 56 | 0 | 0 | 0 | 12 | 12 | 0.11 | 178 | 68 | 5 | 1125 | 16 | 0 | 0 | 0 | 62 | 30 | 0 | 0 | 0 | 1224 | 0 | 20 | 35 | 230 | 300 | 255 | 51 | 47 | 219 | 36 | 44 | 142 | 100 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 240 | 263 | 392 | 40 | 0 | 133 | 0 | 8 | 0 | 84 | 30 | 140 | 0 | 120 | 0 | 49 | 0.1 | 48 | 0 | 0 | 0.32 | 12 | 8075.03 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 1 | 925 | 0 | 0 | 0 | 817.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0 | 0 | 0 | 0.67 | 193 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.12 | 156 | 50 | 50 | 0 | 34 | 0 | 0 | 0 | 0.2 | 0 | 0 | 32 | 250 | 118 | 220 | 0 | 600 | 820 | 17 | 5652.29 | 13727.32 | 104.5
07:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 522 | 0 | 35 | 0 | 142 | 30 | 15 | 17 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 318 | 0 | 0 | 5 | 123 | 9.5 | 22 | 0 | 555 | 16 | 16 | 12 | 0 | 58 | 0 | 0 | 0 | 12 | 12 | 0.66 | 179 | 66 | 0 | 1126 | 15 | 0 | 0 | 0 | 67 | 30 | 0 | 0 | 0 | 975 | 0 | 20 | 35 | 230 | 300 | 285 | 51 | 46 | 219 | 36 | 17 | 142 | 100 | 0 | 0 | 0 | 138 | 0 | 2 | 0 | 240 | 263 | 392 | 40 | 0 | 145 | 2 | 8 | 0 | 84 | 30 | 140 | 0 | 120 | 0 | 49 | 1.1 | 48 | 0 | 0.1 | 3.79 | 12 | 7950.15 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 4 | 925 | 0 | 0 | 0 | 820.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.89 | 21 | 0 | 0 | 6.36 | 194 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.22 | 156 | 50 | 50 | 3 | 0 | 0 | 0 | 0 | 0.4 | 5 | 0.06 | 32 | 250 | 118 | 220 | 0 | 600 | 825 | 17 | 5672.4 | 13622.55 | 104.4
08:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 267 | 0 | 521 | 0 | 35 | 0 | 126 | 30 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 318 | 0 | 0 | 2 | 143.42 | 9.5 | 22 | 0 | 545 | 16 | 16 | 12 | 0 | 63 | 0 | 0 | 0 | 12 | 12 | 1.01 | 179 | 71 | 0 | 1125 | 16 | 0 | 0 | 0 | 74 | 30 | 0 | 0 | 0 | 800 | 0 | 20 | 35 | 230 | 300 | 290 | 51 | 46 | 183 | 37 | 17 | 143 | 116 | 0 | 0 | 4 | 144 | 0 | 16 | 0 | 240 | 200 | 398 | 40 | 0 | 149 | 5 | 8 | 0 | 84 | 30 | 141 | 0 | 120 | 0 | 49 | 4 | 48 | 0 | 0.1 | 2.77 | 12 | 7762.8 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 18 | 925 | 0 | 0 | 0 | 827.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.92 | 37 | 0 | 0 | 21.4 | 197 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.74 | 153 | 50 | 90 | 4 | 0 | 0 | 0 | 0 | 2.3 | 32 | 0.06 | 32 | 250 | 118 | 220 | 0 | 600 | 820 | 17 | 5812.32 | 13575.12 | 104.4
09:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 482 | 0 | 35 | 37 | 140 | 145 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 294 | 0 | 0 | 11 | 143.42 | 8.5 | 22 | 0 | 430 | 41 | 16 | 12 | 0 | 61 | 0 | 0 | 0 | 12 | 12 | 0.19 | 220 | 102 | 0 | 1125 | 23 | 0 | 0 | 1 | 100 | 30 | 0 | 0 | 0 | 630 | 0 | 20 | 8 | 230 | 270 | 255 | 51 | 46 | 193 | 38 | 17 | 144 | 179 | 0 | 0 | 49 | 144 | 0 | 3 | 0 | 270 | 40 | 367 | 40 | 0 | 140 | 4 | 8 | 0 | 84 | 30 | 141 | 0 | 120 | 0 | 58 | 5.3 | 55 | 0 | 0.5 | 8.77 | 12 | 7620.68 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 11.73 | 925 | 0 | 0 | 0 | 821.72 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 8 | 25.93 | 61 | 0 | 0 | 19.98 | 197 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.52 | 162 | 50 | 95 | 14 | 0 | 0 | 0 | 0 | 3.7 | 120 | 0.29 | 32 | 250 | 117 | 220 | 0 | 600 | 820 | 17 | 5946.87 | 13567.55 | 104.39
10:00 | 0 | 70 | 42 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 530 | 0 | 35 | 51 | 141 | 145 | 15 | 17 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 298 | 0 | 0 | 16 | 143.42 | 8.5 | 22 | 0 | 505 | 90 | 16 | 33 | 0 | 31 | 0 | 0 | 0 | 12 | 12 | 1.23 | 220 | 103 | 0 | 1125 | 34 | 0 | 0 | 17 | 97 | 32 | 0 | 0 | 0 | 610 | 0 | 20 | 8 | 250 | 270 | 270 | 43 | 45 | 212 | 35 | 23 | 141 | 175 | 0 | 0 | 49 | 152 | 0 | 16 | 0 | 285 | 15.6 | 380 | 40 | 0 | 131 | 3 | 8 | 0 | 84 | 30 | 139 | 0 | 120 | 0 | 58 | 3.2 | 115 | 0 | 0.3 | 16.19 | 12 | 8022.44 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 10 | 925 | 0 | 0 | 0 | 824.34 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 19.84 | 57 | 0 | 0 | 6.69 | 196 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.56 | 160 | 50 | 95 | 19 | 0 | 0 | 0 | 0 | 2.4 | 25 | 0.05 | 32 | 250 | 117 | 220 | 0 | 600 | 820 | 17 | 5857.88 | 13880.32 | 104.38
11:00 | 0 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 606 | 0 | 35 | 51 | 141 | 145 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 318 | 0 | 0 | 11 | 143.42 | 8.5 | 22 | 0 | 550 | 91 | 16 | 45 | 0 | 28 | 0 | 0 | 0 | 12 | 12 | 1.99 | 220 | 102 | 0 | 1125 | 34 | 0 | 0 | 17 | 93 | 35 | 0 | 0 | 0 | 610 | 1 | 20 | 8 | 250 | 300 | 285 | 43 | 45 | 194 | 31 | 69 | 140 | 177 | 0 | 0 | 51 | 162 | 0 | 8 | 0 | 290 | 34.2 | 389 | 40 | 0 | 133 | 4 | 8 | 0 | 84 | 30 | 139 | 0 | 124 | 0 | 56 | 4.4 | 111 | 0 | 0.4 | 25 | 12 | 8295.91 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 18.31 | 925 | 0 | 0 | 0 | 821.07 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 20.81 | 35 | 0 | 0 | 17.34 | 194 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.1 | 158 | 50 | 94 | 32 | 0 | 0 | 0 | 0 | 3.2 | 150 | 0.05 | 32 | 250 | 118 | 220 | 0 | 600 | 820 | 17 | 5987.88 | 14283.79 | 104.38
12:00 | 0 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 570 | 0 | 35 | 51 | 124 | 146 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 322 | 0 | 0 | 24 | 143.42 | 8.5 | 22 | 0 | 545 | 89 | 16 | 45 | 0 | 38 | 0 | 0 | 1 | 12 | 12 | 1.1 | 221 | 105 | 0 | 1125 | 33 | 0 | 0 | 17 | 83 | 35 | 0 | 0 | 0 | 610 | 2 | 20 | 8 | 240 | 300 | 265 | 51 | 44 | 171 | 33 | 69 | 141 | 187 | 0 | 0 | 105 | 162 | 16 | 25 | 2 | 285 | 35.5 | 377 | 40 | 0 | 151 | 3 | 8 | 0 | 84 | 30 | 142 | 0 | 124 | 0 | 47 | 19.99 | 111 | 0 | 2.6 | 24.11 | 12 | 8300.22 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 8.73 | 985 | 0 | 0 | 0 | 824.42 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 11.42 | 100 | 0 | 0 | 7.19 | 188 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.78 | 158 | 50 | 94 | 19 | 0 | 0 | 0 | 0 | 5.8 | 84 | 0.21 | 32 | 250 | 118 | 220 | 0 | 600 | 820 | 17 | 6056.55 | 14356.77 | 104.37
13:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 491 | 0 | 28 | 52 | 124 | 146 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 327 | 0 | 0 | 5 | 143.42 | 8.5 | 22 | 0 | 450 | 90 | 16 | 44 | 0 | 45 | 0 | 0 | 17 | 12 | 12 | 2.52 | 221 | 91 | 0 | 1125 | 33 | 0 | 0 | 17 | 86 | 76 | 0 | 0 | 0 | 610 | 1 | 18 | 8 | 230 | 300 | 260 | 51 | 45 | 168 | 36 | 69 | 141 | 178 | 10 | 0 | 103 | 166 | 43 | 29 | 16 | 295 | 34.4 | 367 | 40 | 0 | 144 | 2 | 8 | 0 | 83 | 30 | 140 | 0 | 124 | 0 | 47 | 22.05 | 120 | 0 | 1.7 | 8.09 | 12 | 8236.68 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 17.71 | 1035 | 0 | 0 | 0 | 824.71 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 4.42 | 16 | 0 | 0 | 25.58 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 6.37 | 158 | 50 | 94 | 24 | 0 | 0 | 0 | 0 | 4.6 | 170 | 0.28 | 32 | 250 | 118 | 220 | 0 | 600 | 820 | 17 | 6129.67 | 14366.35 | 104.37
14:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 466 | 0 | 35 | 52 | 123 | 146 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 326 | 0 | 0 | 4 | 143.42 | 8.5 | 22 | 0 | 480 | 91 | 16 | 44 | 0 | 34 | 0 | 0 | 17 | 12 | 12 | 3.22 | 221 | 87 | 0 | 1125 | 41 | 0 | 0 | 17 | 87 | 106 | 0 | 0 | 0 | 610 | 0 | 20 | 8 | 230 | 300 | 255 | 51 | 33 | 170 | 33 | 69 | 141 | 171 | 18 | 0 | 85 | 156 | 16 | 25 | 16 | 300 | 35 | 377 | 40 | 0 | 129 | 2 | 0 | 0 | 83 | 30 | 140 | 0 | 124 | 0 | 47 | 10.64 | 123 | 0 | 0.8 | 47.79 | 12 | 8289.37 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 7.19 | 1100 | 0 | 0 | 0 | 822.47 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 7.12 | 55 | 0 | 0 | 48.62 | 180 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 3.51 | 159 | 50 | 94 | 16 | 0 | 0 | 0 | 0 | 4 | 124 | 0.17 | 32 | 250 | 118 | 220 | 0 | 600 | 820 | 17 | 6177.08 | 14466.45 | 104.37
15:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 530 | 0 | 35 | 52 | 137 | 146 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 326 | 0 | 0 | 2 | 143.42 | 8 | 22 | 0 | 470 | 60 | 16 | 45 | 0 | 32 | 0 | 0 | 17 | 12 | 12 | 0.06 | 220 | 96 | 0 | 1125 | 51 | 0 | 15 | 17 | 88 | 141 | 0 | 0 | 0 | 612 | 0 | 20 | 0 | 220 | 300 | 255 | 51 | 16 | 187 | 15 | 69 | 143 | 173 | 18 | 0 | 47 | 162 | 16 | 8 | 31 | 305 | 15 | 392 | 42 | 20 | 136 | 2 | 8 | 0 | 81 | 28 | 140 | 0 | 124 | 0 | 48 | 22.21 | 125 | 0 | 2.3 | 29.65 | 12 | 8354.64 | 899 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 29.26 | 1100 | 0 | 0 | 0 | 830.97 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 3.01 | 12 | 0 | 0 | 4.36 | 176 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0.61 | 161 | 51 | 92 | 12 | 0 | 0 | 0 | 0 | 5.8 | 132 | 0.11 | 32 | 250 | 118 | 180 | 0 | 600 | 815 | 17 | 6056.12 | 14410.76 | 104.46
16:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 450 | 17 | 35 | 52 | 75 | 146 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 326 | 0 | 0 | 6 | 123 | 8 | 0 | 0 | 425 | 30 | 16 | 43 | 0 | 29 | 0 | 0 | 17 | 12 | 11 | 0.49 | 219 | 97 | 0 | 1125 | 48 | 0 | 30 | 17 | 86 | 182 | 0 | 0 | 0 | 606 | 0 | 20 | 0 | 220 | 300 | 250 | 51 | 10 | 193 | 15 | 69 | 143 | 171 | 20 | 0 | 28 | 166 | 16 | 21 | 41 | 300 | 0 | 357 | 41 | 30 | 133 | 1 | 8 | 0 | 81 | 28 | 141 | 0 | 124 | 0 | 58 | 1.7 | 116 | 0 | 0.1 | 9.59 | 12 | 8067.88 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 21.76 | 1100 | 0 | 0 | 0 | 831.1 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 0.9 | 6 | 0 | 0 | 4.12 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.5 | 160 | 52 | 93 | 7 | 0 | 0 | 0 | 0 | 4.4 | 104 | 0.07 | 48 | 250 | 114 | 180 | 0 | 600 | 815 | 17 | 6005.85 | 14073.73 | 104.35
17:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 580 | 17 | 35 | 52 | 106 | 110 | 15 | 55 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 326 | 0 | 0 | 1 | 123 | 8 | 22 | 0 | 520 | 15 | 16 | 46 | 0 | 19 | 0 | 0 | 17 | 12 | 11 | 0.86 | 218 | 75 | 0 | 1125 | 17 | 0 | 22 | 17 | 34 | 212 | 0 | 0 | 0 | 602 | 0 | 20 | 0 | 220 | 300 | 270 | 51 | 10 | 193 | 15 | 69 | 143 | 85 | 27 | 0 | 17 | 150 | 16 | 7 | 38 | 305 | 0 | 392 | 41 | 30 | 140 | 1 | 8 | 0 | 84 | 28 | 141 | 0 | 124 | 24 | 58 | 5.68 | 116 | 0 | 0.2 | 2.27 | 19 | 8137.01 | 901 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 3.47 | 1077 | 0 | 0 | 0 | 822.31 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 4.83 | 3 | 0 | 0 | 4.8 | 163 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.33 | 158 | 50 | 50 | 3 | 0 | 0 | 0 | 0 | 2.8 | 39 | 0.06 | 32 | 250 | 118 | 180 | 0 | 600 | 815 | 17 | 5757.6 | 13894.61 | 104.45
18:00 | 0 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 555 | 17 | 35 | 52 | 123 | 110 | 15 | 55 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 286 | 0 | 0 | 0 | 123 | 7.5 | 22 | 0 | 450 | 16 | 16 | 54 | 0 | 29 | 0 | 0 | 17 | 12 | 11 | 0.03 | 218 | 68 | 0 | 1125 | 16 | 0 | 18 | 17 | 32 | 211 | 0 | 0 | 0 | 602 | 0 | 18 | 0 | 220 | 300 | 260 | 51 | 10 | 206 | 15 | 69 | 143 | 82 | 27 | 0 | 17 | 164 | 16 | 1 | 38 | 305 | 166 | 392 | 41 | 30 | 150 | 0 | 8 | 0 | 84 | 30 | 139 | 0 | 124 | 35 | 59 | 0.85 | 116 | 0 | 0.1 | 1.26 | 21 | 8240.74 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 3.24 | 1034 | 0 | 0 | 0 | 1026.23 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 0.02 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 161 | 50 | 50 | 1 | 35 | 0 | 0 | 0 | 0.2 | 6 | 0.01 | 32 | 250 | 118 | 220 | 0 | 600 | 815 | 17 | 5991.7 | 14232.44 | 104.44
19:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 532 | 54 | 40 | 85 | 124 | 195 | 52 | 55 | 103 | 0 | 0 | 0 | 0 | 0 | 55 | 327 | 0 | 0 | 0 | 123 | 7.5 | 22 | 0 | 415 | 15 | 16 | 54 | 0 | 31 | 34 | 0 | 17 | 12 | 11 | 0 | 219 | 67 | 0 | 1125 | 16 | 0 | 20 | 17 | 34 | 211 | 0 | 0 | 0 | 690 | 0 | 20 | 0 | 220 | 300 | 260 | 51 | 10 | 213 | 15 | 73 | 132 | 132 | 35 | 0 | 34 | 172 | 16 | 0 | 38 | 300 | 265 | 387 | 42 | 30 | 145 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 124 | 35 | 69 | 0 | 155 | 0 | 0 | 0 | 17 | 8811.5 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1032 | 0 | 0 | 0 | 1360.61 | 0 | 0 | 0 | 35 | 47 | 0 | 0 | 19 | 8 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 160 | 50 | 110 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 118 | 220 | 0 | 1000 | 815 | 17 | 6870.61 | 15682.11 | 104.44
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 538 | 54 | 55 | 149 | 126 | 210 | 55 | 55 | 82 | 0 | 0 | 0 | 0 | 0 | 35 | 327 | 0 | 0 | 0 | 123 | 7.5 | 22 | 0 | 400 | 15 | 0 | 60 | 0 | 25 | 34 | 0 | 17 | 12 | 11 | 0 | 219 | 67 | 0 | 1125 | 2 | 0 | 19 | 17 | 17 | 211 | 0 | 0 | 0 | 770 | 0 | 22 | 0 | 230 | 300 | 265 | 51 | 10 | 216 | 15 | 89 | 132 | 120 | 45 | 0 | 34 | 176 | 25 | 0 | 38 | 290 | 265 | 396 | 42 | 30 | 151 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 124 | 35 | 68 | 0 | 155 | 0 | 0 | 0 | 24 | 8957.5 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1100 | 0 | 0 | 0 | 1458.97 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 158 | 50 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 118 | 220 | 0 | 1000 | 815 | 17 | 6933.97 | 15891.47
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 454 | 54 | 55 | 146 | 126 | 195 | 55 | 55 | 82 | 0 | 0 | 0 | 0 | 0 | 35 | 327 | 0 | 0 | 0 | 123 | 7.5 | 22 | 0 | 415 | 0 | 0 | 48 | 0 | 26 | 34 | 0 | 18 | 12 | 11 | 0 | 220 | 68 | 0 | 1125 | 0 | 0 | 21 | 17 | 16 | 213 | 0 | 0 | 0 | 851 | 0 | 25 | 0 | 230 | 300 | 245 | 51 | 10 | 217 | 15 | 88 | 132 | 100 | 45 | 0 | 17 | 166 | 25 | 0 | 38 | 285 | 265 | 375 | 42 | 30 | 144 | 0 | 8 | 0 | 84 | 25 | 139 | 0 | 124 | 35 | 69 | 0 | 155 | 0 | 0 | 0 | 24 | 8830.5 | 900 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1100 | 0 | 0 | 0 | 1467.81 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 158 | 50 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 118 | 180 | 0 | 1000 | 815 | 17 | 6886.81 | 15717.31 | 104.43
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 461 | 54 | 35 | 149 | 109 | 162 | 30 | 55 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 329 | 0 | 0 | 0 | 143.42 | 7 | 22 | 0 | 420 | 0 | 0 | 24 | 0 | 34 | 34 | 0 | 36 | 12 | 11 | 0 | 221 | 51 | 0 | 1125 | 0 | 0 | 19 | 17 | 17 | 213 | 0 | 0 | 0 | 901 | 0 | 50 | 0 | 250 | 300 | 255 | 51 | 10 | 218 | 15 | 89 | 132 | 104 | 45 | 0 | 34 | 160 | 25 | 0 | 38 | 285 | 265 | 384 | 42 | 30 | 131 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 124 | 17 | 69 | 0 | 156 | 0 | 0 | 0 | 24 | 8836.42 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1100 | 0 | 0 | 0 | 1467.55 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 28 | 8 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 158 | 50 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 118 | 220 | 0 | 1000 | 815 | 17 | 6912.55 | 15748.97 | 104.43
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 523 | 54 | 35 | 85 | 126 | 162 | 30 | 55 | 53 | 0 | 0 | 0 | 0 | 0 | 35 | 290 | 0 | 0 | 0 | 143.42 | 7 | 22 | 0 | 400 | 0 | 0 | 24 | 0 | 27 | 34 | 0 | 36 | 12 | 11 | 0 | 222 | 34 | 0 | 1125 | 0 | 0 | 19 | 17 | 15 | 210 | 0 | 0 | 0 | 902 | 0 | 50 | 0 | 250 | 300 | 260 | 51 | 10 | 219 | 15 | 89 | 125 | 113 | 39 | 0 | 29 | 162 | 25 | 0 | 38 | 285 | 265 | 392 | 42 | 30 | 140 | 0 | 8 | 0 | 84 | 20 | 140 | 0 | 124 | 17 | 69 | 0 | 156 | 0 | 0 | 0 | 24 | 8747.42 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1100 | 0 | 0 | 0 | 1473.91 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 30 | 25 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 156 | 50 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 118 | 220 | 0 | 1000 | 815 | 17 | 6906.91 | 15654.33 | 104.43
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 474 | 17 | 35 | 52 | 125 | 162 | 30 | 55 | 51 | 0 | 0 | 0 | 0 | 0 | 55 | 285 | 0 | 0 | 0 | 143.42 | 4 | 22 | 0 | 400 | 0 | 0 | 25 | 0 | 23 | 34 | 0 | 42 | 12 | 11 | 0 | 222 | 48 | 0 | 1125 | 0 | 0 | 19 | 17 | 16 | 213 | 0 | 0 | 0 | 806 | 0 | 50 | 0 | 270 | 300 | 305 | 51 | 10 | 201 | 15 | 88 | 125 | 114 | 22 | 0 | 29 | 164 | 25 | 0 | 38 | 285 | 265 | 392 | 41 | 30 | 139 | 0 | 8 | 0 | 84 | 25 | 146 | 0 | 124 | 17 | 69 | 0 | 156 | 0 | 0 | 0 | 24 | 8608.42 | 902 | 0 | 0 | 0 | 4 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1100 | 0 | 0 | 0 | 1477.9 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 28 | 25 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 156 | 50 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 118 | 220 | 0 | 1000 | 815 | 17 | 6910.9 | 15519.32 | 104.42
Total KWH | 0 | 1701120 | 769440 | 0 | 0 | 0 | 0 | 0 | 7887600 | 0 | 12226350 | 418680 | 868680 | 1470528 | 3084480 | 2830255 | 521569 | 815187 | 1524960 | 0 | 0 | 0 | 0 | 0 | 723622 | 7442803 | 0 | 0 | 94678 | 3354000 | 187200 | 506880 | 0 | 11376818.18 | 1048800 | 311127 | 742080 | 0 | 921120 | 303298 | 108579 | 326548 | 292800 | 286080 | 12359 | 5198325 | 2070836 | 25920 | 26996363.64 | 541964 | 0 | 437280 | 325402.2 | 1650145 | 2724018 | 0 | 0 | 0 | 20361816 | 4725 | 961818 | 250909 | 5811000 | 7564900 | 6506000 | 1246686 | 736320 | 4958000 | 677808 | 1516800 | 3325881 | 3454560 | 343560 | 0 | 1065900 | 3730560 | 435504 | 146155 | 510880 | 6600000 | 3996800 | 9325000 | 962000 | 249960 | 3328936.36 | 32588 | 185568 | 0 | 2003520 | 643104 | 3162000 | 0 | 2712680 | 226800 | 1327200 | 72543 | 2448000 | 0 | 7450 | 190690 | 378240 | 203590756.38 | 21762182 | 0 | 0 | 53760 | 60032 | 912000 | 0 | 0 | 0 | 0 | 624816 | 150480 | 24174550 | 0 | 0 | 0 | 24165239 | 0 | 65458 | 0 | 22848 | 624096 | 0 | 119504 | 178119 | 306754 | 153776 | 447010 | 0 | 0 | 162320 | 4280091 | 0 | 0 | 0 | 0 | 0 | 9434181 | 0 | 20700 | 3931000 | 953454 | 1949215 | 17768 | 835190 | 0 | 0 | 0 | 38504.04 | 897120 | 1372 | 819552 | 6021000 | 2823000 | 5334340 | 0 | 16734545 | 19186909.09 | 440400 | 147701285.13 | 351292041.51