## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-08-2026 | during | 20-08-2026 | during | 20-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 409 | 375 | 412 | 412 | 412 | 412 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 15 | 55 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 302 | 335 | 335 | 310 | 310 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 10 | 54 | 53.97 | 53.97 | 35 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 126 | 143 | 149.36 | 149.36 | 142 | 142 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 5.5 | 5 | 33 | 33 | 5 | 5 | Gas shortage
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 42 | 50 | 52.19 | 52.19 | 33 | 50 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 45 | 300 | 300 | 175 | 145 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 36 | 115 | 149 | 149 | 52 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 105 | 105 | 105 | 88 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 49 | 115 | 162 | 162 | 72 | 72 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 33 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 350 | 370 | 584 | 584 | 584 | 584 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 441 | 496 | 718 | 718 | 498 | 498 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 2178.92 | 2522.42 | 5395.16 | 5370.16 | 2716.42 | 2890.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25 | 25 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 180 | 220 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 0 | 210 | 210 | 0 | 0 | Under Maintenance
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 14 | 15 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 45 | 14 | 40 | 14 | 40 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 25 | 32 | 25 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 12 | 64 | 95.1 | 95.1 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.57 | 0 | 3.22 | 0 | 3.22 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 54.36 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 67 | 93 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 25 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 16 | 83 | 163 | 163 | 88 | 160 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1224 | 1224 | 1224 | 1224 | 1224 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 7 | 0 | 7 | 11 | 7 | 11 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1125 | 730 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2829.57 | 2639.36 | 4080.18 | 4158.96 | 3192.22 | 3395
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 199 | 217 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 280 | 355 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 240 | 300 | 342.01 | 342.01 | 306 | 306 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 230 | 393 | 393 | 250 | 250 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 30 | 20 | 41.65 | 41.65 | 30 | 30 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 10 | 0 | 52.82 | 52.82 | 10 | 10 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 26 | 0 | 195 | 195 | 26 | 26 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 45 | 45 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 26 | 68 | 150 | 150 | 13 | 70 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 31 | 30 | 40 | 40 | 40 | 40 | Engine Problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 138 | 163 | 163 | 140 | 140 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 78 | 169 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 150 | 176 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 8 | 52 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 15 | 24.5 | 24.5 | 0 | 0 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 16 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 5 | 53 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 88 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 62 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1585 | 1919 | 2772.44 | 2696.44 | 1980.26 | 2077.26
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-08-2026 | during | 20-08-2026 | during | 20-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 19.32 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.3 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 154 | 120 | 160 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 78 | 60 | 70 | 60 | 70 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42.91 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 22 | 22 | 12 | 22 | 00:00-16:00 hrs 12MW&16:00-24:00 hrs 24MW dis.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 250.53 | 249 | 536.6 | 516.5 | 262.1 | 269
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | ps availability is less
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 38 | 40 | 40 | 39 | 39 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 137 | 148 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 140 | 139 | 140 | 140 | 140 | 140 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 28 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 86 | 86 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 125 | 126 | 0 | 0 | 120 | 120 | plant availability zero
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 8 | 8 | 8 | 8 | 8 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 302 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 387 | 378 | 390 | 390 | 362 | 362 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 263 | 260 | 265 | 265 | 0 | 50 | STG Under Maintenance
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1557 | 1554 | 1523 | 1523 | 1277 | 1327
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 902 | 881 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 19 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 57 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1050 | 1100 | 1100 | 1100 | 1100 | 1100 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 38 | 38 | 40 | 40 | 38 | 38 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2047 | 2038 | 3487 | 3402 | 2320 | 2235
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 800 | 1000 | 800 | 1000 | 800 | 1000 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 32 | 32 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 117 | 117 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 735 | 657 | 825 | 825 | 825 | 825 | machine problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 35 | 150 | 150 | 17 | 54 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 230 | 200 | 307 | 307 | 307 | 307 | Bad quality coal
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.72 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2079.72 | 2245 | 2543 | 2742 | 2320 | 2556
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 52.56 | 0 | 12.51 | 0 | 12.51 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 40 | 40 | 40 | 40 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 145 | 144 | 214 | 214 | 145 | 145 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 300 | 332 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 6 | 20 | 20 | 20 | 20 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 50 | 50 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 57 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 1.96 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 822.11 | 1472.96 | 1469.13 | 1469.13 | 830 | 1469 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.77 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 27 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1438.4 | 2081.96 | 3168.13 | 2989.12 | 1746.42 | 2256.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 51 | 54 | 54 | 54 | 54 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 160 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 106 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.6 | 0 | 0 | 0 | 0 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 121 | 0 | 174.42 | 0 | 174.42 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 400.6 | 432 | 680.42 | 476 | 567.42 | 398
System Total |  |  |  |  | 28843.2 | 29158.791 | 14366.74 | 15680.74 | 24185.93 | 23874.18 | 16381.84 | 17404.09
Forecast Scenario (20-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15860 |  | 2062.8 |  | 18020
|  |  |  | 1:00 | 15280 |  | 1957.75 |  | 17330
|  |  |  | 2:00 | 14900 |  | 1900.45 |  | 16890
|  |  |  | 3:00 | 14580 |  | 1852.7 |  | 16520
|  |  |  | 4:00 | 14250 |  | 1613.95 |  | 15940
|  |  |  | 5:00 | 14010 |  | 1547.1 |  | 15630
|  |  |  | 6:00 | 13720 |  | 1356.1 |  | 15140
|  |  |  | 7:00 | 13910 |  | 1165.1 |  | 15130
|  |  |  | 8:00 | 13860 |  | 1222.4 |  | 15140
|  |  |  | 9:00 | 13970 |  | 1212.85 |  | 15240
|  |  |  | 10:00 | 14370 |  | 1107.8 |  | 15530
|  |  |  | 11:00 | 14190 |  | 1785.85 |  | 16060
|  |  |  | 12:00 | 14330 |  | 2129.65 |  | 16560
|  |  |  | 13:00 | 14570 |  | 2120.1 |  | 16790
|  |  |  | 14:00 | 14650 |  | 2072.35 |  | 16820
|  |  |  | 15:00 | 14600 |  | 2301.55 |  | 17010
|  |  |  | 16:00 | 14320 |  | 2129.65 |  | 16550
|  |  |  | 17:00 | 14180 |  | 1881.35 |  | 16150
|  |  |  | 18:00 | 14310 |  | 1365.65 |  | 15740
|  |  |  | 18:30 | 14870 |  | 1351.325 |  | 16285
|  |  |  | 19:00 | 15430 |  | 1337 |  | 16830
|  |  |  | 19:30 | 15300 |  | 2244.25 |  | 17650
|  |  |  | 20:00 | 15630 |  | 1852.7 |  | 17570
|  |  |  | 21:00 | 15890 |  | 1871.8 |  | 17850
|  |  |  | 22:00 | 16190 |  | 1470.7 |  | 17730
|  |  |  | 23:00 | 15820 |  | 1757.2 |  | 17660
Probable Maximum Temperature: |  |  | 34.60°C
Probable Maximum Demand at Day Peak: |  |  | 16560.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1871.8
Probable Maximum Demand at Evening Peak: |  |  | 17850.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15890.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 352.82 MKWHr. |  | 640 | 116 | 155 | 260 | 135 | 180 | 85 | 129 | 172 | 1872
*** This report is generated digitally from Operation Information System (OIS) at 09:07 hrs on 20-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-08-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14366.74 | MW | 10:00 Hr. | Energy Generated |  |  | 357.4496 |  | MKWHr.
| Day Peak Demand |  |  | 14910.35 | MW | 12:00 Hr. | Energy Unserverd |  |  | 22.511 |  | MKWHr.
| Evening Peak Generation |  |  | 15680.74 | MW | 21:00 Hr. | Energy Demand |  |  | 379.9606 |  | MKWHr.
| Evening Peak Demand |  |  | 18070.79 | MW | 19:00 Hr. | Maximum Temperature |  |  | 34.6 |  | °C
| Minimum Generation of the Day |  |  | 13711.06 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 892.53 |  | MMCFD
| Maximum Generation of the Day |  |  | 16358.39 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 7.3624 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 36.9438 | 0 | 18.7631 | 0 | 0 | 0.2082 | 0 | 0 | 55.915 | Gas | 128.5463 | Gas | 448574322.4975
| Chattogram Zone |  |  | 3.9433 | 49.26 | 8.8909 | 0 | 5.2396 | 0.097366 | 0 | 0.24528 | 67.6765 | Coal | 122.3365 | Coal | 865860311.905
| Cumilla Zone |  |  | 31.1702 | 0 | 7.8999 | 0 | 0 | 0.45644 | 3.888 | 0 | 43.4145 | HFO | 45.9686 | HFO | 926870227.374
| Mymensingh Zone |  |  | 0 | 0 | 4.2684 | 0 | 0 | 0.42604 | 0 | 0 | 4.6944 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.6331 | 0 | 0 | 0 | 0 | 0.078686 | 0 | 0 | 36.7118 | Hydro | 5.2396 | Hydro | 523961.1
| Khulna Zone |  |  | 0 | 26 | 0.62734 | 0 | 0 | 0.51408 | 22.6105 | 0 | 49.7519 | Solar | 4.3761 | Solar | 69797386.2508
| Barishal Zone |  |  | 8.1338 | 41.897 | 0.71822 | 0 | 0 | 0.003547 | 0 | 0 | 50.7526 | Import | 50.7374 | Import | 316459517.39
| Rajshahi Zone |  |  | 11.7221 | 0 | 1.9634 | 0 | 0 | 1.3749 | 24.2389 | 0 | 39.2993 | Wind | 0.24528 | Wind | 3608068.8
| Rangpur Zone |  |  | 0 | 5.1795 | 2.8373 | 0 | 0 | 1.2168 | 0 | 0 | 9.2336
| Total |  |  | 128.5463 | 122.3365 | 45.9686 | 0 | 5.2396 | 4.3761 | 50.7374 | 0.24528 | 357.4496
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 448574322.4975 |  | Hydro | 523961.1
|  |  |  | Coal | 865860311.905 |  | Solar | 69797386.2508
|  |  |  | HFO | 926870227.374 |  | Import | 316459517.39
|  |  |  | HSD | 0 |  | Wind | 3608068.8
[5 empty] | Total: | 263,16,93,795 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6985 | Peak Hr Flow | 881.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 36073981.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.2389 | Peak Hr Flow | 1472.96 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1759 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.888 | Peak Hr Flow | 176.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2099 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.8254 | Peak Hr Flow | 2529.96 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 643 |  | 6368
|  |  |  | Chattogram |  | 154 |  | 1596
|  |  |  | Cumilla |  | 244 |  | 1682
|  |  |  | Mymensingh |  | 354 |  | 1516
|  |  |  | Sylhet |  | 134 |  | 759
|  |  |  | Khulna |  | 274 |  | 2089
|  |  |  | Barishal |  | 104 |  | 562
|  |  |  | Rajshahi |  | 159 |  | 1669
|  |  |  | Rangpur |  | 200 |  | 1215
|  |  |  | Total |  | 2266 |  | 17456
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:52 | 18:03 | Madunaghat-Meghnaghat 400kV Ckt-2 Project Work S/D from Meghnaghat 400/230kV end Due to
Requested by NLDC
| 08:54 | 17:58 | Korerhat 400/230/132kV S/S Meghnaghat-2 Project Work S/D Due to Shunt Redactor work
|  | 08:57 | Thakurgaon 132/33kV S/S T-2(412T) HT is restored.
|  | 08:58 | Thakurgaon 132/33kV S/S T-2(412T) LT is restored.
| 09:07 | 11:15 | Gopalganj 132/33kV S/S T1 LT Forced S/D Due to 33kv feeder loop change
| 09:08 | 11:14 | Gopalganj 132/33kV S/S T1 HT Forced S/D Due to 33kv feeder loop change
|  | 09:10 | Purbasadipur 230/132/33kV S/S TR-4 LT is restored.
|  | 09:10 | Purbasadipur 230/132/33kV S/S TR-4 HT is restored.
| 09:54 | 18:01 | Aminbazar 400/230/132kV S/S Bus-1 (400kV) Project Work S/D Due to Ds Shaft connection
| 10:00 |  | Day Peak Generation: 14367 MW.
| 10:34 | 13:56 | Patuakhali 132/33kV S/S 405T (T-1) HT Scheduled S/D Due to Breaker gas pressure problem
fixation
| 10:34 | 13:57 | Patuakhali 132/33kV S/S 405T (T-1) LT Scheduled S/D Due to Breaker gas pressure problem
fixation
| 11:22 | 21:32 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Forced S/D Due to Maintenance work of EGCB.
|  | 13:54 | Rajendrapur 132/33kV S/S 132 kV BUS-1 is restored.
| 16:31 |  | Payra 1320 MW Synchronized with remarks:- unit-2
| 16:34 | 17:59 | Khulna (C) S/S TR-1 425T LT Scheduled S/D Due to Red hot maintenance porpoise.
| 16:35 | 17:58 | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to Red hot maintenance porpoise.
| 16:54 | 18:11 | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to Red hot maintenance on pbs | [7 empty] | 30.0MW load
|  |  | side | [7 empty] | interrup.
| 16:54 | 18:11 | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to Red hot maintenance on pbs | [7 empty] | 30.0MW load
|  |  | side | [7 empty] | interrup.
| 17:28 |  | Rajendrapur 132/33kV S/S 132 kV BUS-2 Project Work S/D
| 18:47 | 18:52 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Definite O/C relays Due to 33kV PBS | [7 empty] | 45.0MW load
|  |  | Charbaria feeder fault | [7 empty] | interrup.
| 19:29 |  | Matarbari 2*600 MW (CPGCBL) Synchronized with remarks:- U1
| 21:00 |  | Evening peak generation is 15681 MW.
| 06:02 |  | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to 33 kv incoming breaker DS R phase | [7 empty] | 68.0MW load
|  |  | red hot | [7 empty] | interrup.
| 06:02 |  | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to 33KV incoming breaker DS finger point | [7 empty] | 68.0MW load
|  |  | red hot | [7 empty] | interrup.
| 06:03 |  | Bibiyana South 400 MW Tripped with remarks:- GT
| 06:05 |  | Haripur-Sonargaon 132kV Ckt-1 Forced S/D from Sonargaon 132/33kV end Due to According
to the direction of NLDC and from Haripur 230/132kV end Due to High Temperature Junction
Point Maintenance.
| 06:39 |  | Haripur 230/132kV S/S 132kV Main Bus Sec-1 Scheduled S/D Due to CB 911 B open for 132 KV
Sonargao-1 Jack bus work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-08-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 375 | 9338400 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 530651 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 302 | 7303130 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 655200 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 3256800 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 664060 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 669710 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 5 | 120000 | Gas shortage
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 519120 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 687360 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 3226440 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 1453824 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1855680 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 115 | 1784160 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 208200 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 597600 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 370 | 8707727.27 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 496 | 10955380 | AGC+Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3381600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2522.42 | 55915042.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 95725.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 74925 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 275040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5239611 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 3915008 | Gas shortage
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 15 | 1050472 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 45 | 382608 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 448408 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 201600 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 28320 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 64 | 960000 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22441 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 311127 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 324873 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 93 | 1993053 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 361920 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 520636 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 83 | 1965455 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28619997 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 245280 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 730 | 20640000 | -
Chattogram Area Total |  |  |  |  | 4885.967 | 2639.36 | 67676499.8
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 217 | 5163000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 355 | 8102500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 300 | 6456000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 230 | 5873500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 644832 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 186720 | Machine Problem
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 301091 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1032930 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 68 | 1150836 | Liquid fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 729696 | Engine Problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 138 | 3283571 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 169 | 3271680 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 176 | 3888000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 295958 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 15 | 126020 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 16 | 784320 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 53 | 404040 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 88 | 1263360 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 456445 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1919 | 43414499
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 114508 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 154 | 2376000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1401600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 299130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 267600 | 00:00-16:00 hrs 12MW&16:00-24:00 hrs 24MW dis.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 223200 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 249 | 4694438
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 78686 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 949000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 922200 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 148 | 3345872.73 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 139 | 3174000 | Gas shortage
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 660000 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 2003520 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 126 | 2734520 | plant availability zero
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 134928 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7286000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 378 | 9156000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 260 | 6267100 | -
Sylhet Area Total |  |  |  |  | 2325 | 1554 | 36711826.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 881 | 21698455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 99840 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 124160 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 19 | 403344 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 514080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1100 | 26000000 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 38 | 912000 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2038 | 49751879
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1000 | 20305455 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 277824 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 117 | 2798000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 657 | 16398545.45 | machine problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5335810 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 440400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 200 | 5193000 | Bad quality coal
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3547 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2245 | 50752581.45
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 311872 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 52208 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 93906 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 144 | 3485545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 332 | 8236509 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 6 | 109100 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 245813 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 253648 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 818976 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 57 | 389760 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 35580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1472.96 | 24238909 | Coal shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 389248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 638200 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2081.96 | 39299274
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 51 | 1244509 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3935000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 863952 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 40637.28 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1973350 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 219271 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 956880 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 432 | 9233599.28
Eastern Grid Total |  |  |  |  | 17427.666 | 8883.78 | 208412305.8
Western Grid Total |  |  |  |  | 11731.125 | 6796.96 | 149037333.73
National Grid Total |  |  |  |  | 29158.791 | 15680.74 | 357449639.53
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-08-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10392.22 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4798.2 | MW
i) Dhaka area |  |  | 5725.12 |  | MW | i) Khulna area |  |  |  | 1815 | MW
ii) Chattogram area |  |  | 1442.1 |  | MW | ii) Barishal area |  |  |  | 458.4 | MW
iii) Cumilla area |  |  | 1438 |  | MW | iii) Rajshahi area |  |  |  | 1509.8 | MW
iv) Mymensingh area |  |  | 1162 |  | MW | iv) Rangpur area |  |  |  | 1015 | MW
v) Sylhet area |  |  | 625 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15190.42 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 150 | 20:00 | 133 | Narshingdi | 206 | 20:00 | 199 | Uttara | 99 | 13:00
2 | AKSML | 11.8 | 18:00 | 68 | Hasnabad | 105 | 23:00 | 134 | Natore | 159 | 23:00 | 200 | UttaraNew | 62 | 23:00
3 | Aftabnagar | 46 | 13:00 | 69 | Hathazari | 94 | 22:00 | 135 | Nawabganj | 68.2 | 22:00 | 201 | Zigatola | 94 | 18:00
4 | Agargaon | 124 | 13:00 | 70 | Hatirjheel | 93 | 14:00 | 136 | Netrakona | 146 | 18:30
5 | Agrabad | 76 | 15:00 | 71 | Ishurdi | 82 | 22:00 | 137 | New | 86.4 | 11:00
6 | Amnura | 28 | 00:00 | 72 | Jaldhaka | 87 | 23:00 | 138 | Niamatpur | 68 | 00:00
7 | Ashuganj | 93 | 01:00 | 73 | Jamalpur | 124 | 20:00 | 139 | Noapara | 45 | 23:00
8 | BSRM | 205 | 05:00 | 74 | Jashore | 176 | 19:00 | 140 | PHP | 9 | 13:00
9 | Bagerhat | 98 | 23:00 | 75 | Jhenaidah | 93 | 23:00 | 141 | Pabna | 105 | 19:30
10 | Bajitpur | 94 | 00:00 | 76 | Joydebpur | 178 | 20:00 | 142 | Palashbari | 132 | 21:00
11 | Bakerganj | 14.8 | 22:00 | 77 | Joypurhat | 63 | 22:00 | 143 | Panchagarh | 72 | 19:30
12 | Bakulia | 96 | 15:00 | 78 | Juldah | 18 | 12:00 | 144 | Patiya | 11 | 21:00
13 | Banani | 71 | 13:00 | 79 | KSRM | 41 | 10:00 | 145 | Patnitala | 33 | 22:00
14 | Bangabhaban | 16 | 13:00 | 80 | Kabirpur | 279 | 20:00 | 146 | Patuakhali | 76 | 22:00
15 | Barapukuria | 68 | 00:00 | 81 | Kachua | 92 | 22:00 | 147 | Payra | 38 | 22:00
16 | Barguna | 24 | 22:00 | 82 | Kaliganj | 41 | 21:00 | 148 | Postogola | 61 | 00:00
17 | Barishal | 108 | 12:00 | 83 | Kallyanpur | 129 | 22:00 | 149 | Pubail | 47 | 00:00
18 | Barishal-230 | 110 | 22:00 | 84 | Kalurghat | 42 | 15:00 | 150 | Purbachal | 35 | 19:00
19 | Baroaulia | 69 | 17:00 | 85 | Kamrangirchar | 86 | 13:00 | 151 | Purbasadipur | 137 | 00:00
20 | Baroirhat | 63 | 23:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 41 | 22:00
21 | Bashundhara | 203 | 13:00 | 87 | Kasba | 41 | 22:00 | 153 | Rahim | 53 | 10:00
22 | BashundharaCement | 12 | 00:00 | 88 | Kazla | 120 | 12:00 | 154 | Rajbari | 96 | 22:00
23 | Beanibazar | 92 | 22:00 | 89 | Keranigonj | 92 | 19:30 | 155 | Rajendrapur | 127 | 23:00
24 | Benapole | 62 | 22:00 | 90 | Khagrachori | 34 | 21:00 | 156 | Rajshahi | 112 | 23:00
25 | Bhaluka | 201 | 17:00 | 91 | Khulna | 68 | 23:00 | 157 | Rajshahi-230 | 102 | 12:00
26 | Bhandaria | 59 | 22:00 | 92 | Khulshi | 184 | 18:30 | 158 | Ramganj | 110 | 00:00
27 | Bhangura | 41 | 22:00 | 93 | Kishoreganj | 137 | 18:30 | 159 | Rampur | 44 | 22:00
28 | Bheramara(GK) | 64 | 00:00 | 94 | Kodda | 324 | 21:00 | 160 | Rangamati | 16 | 12:00
29 | Bhulta | 239 | 10:00 | 95 | Kulaura | 63 | 22:00 | 161 | Rangpur | 136 | 22:00
30 | Bog-Sherpur | 70 | 22:00 | 96 | Kurigram | 74 | 00:00 | 162 | Ruppur | 4.8 | 11:00
31 | Bogura | 201 | 23:00 | 97 | Kushtia | 142 | 23:00 | 163 | SSM | 1 | 23:00
32 | Borhanuddin | 81 | 22:00 | 98 | Laksam | 38 | 22:00 | 164 | Saidpur | 116 | 19:00
33 | Brahmanbaria | 131 | 20:00 | 99 | Lakshmipur | 43 | 23:00 | 165 | Santhia | 42 | 19:00
34 | Cantonment | 137 | 13:00 | 100 | Lalbag | 81 | 18:30 | 166 | Satkhira | 139 | 22:00
35 | Chandina | 25 | 02:00 | 101 | Lalmonirhat | 70 | 22:00 | 167 | Satmasjid | 109 | 14:00
36 | Chandpur | 84 | 00:00 | 102 | MI_Cement | 16.2 | 12:00 | 168 | Savar | 222 | 20:00
37 | Chandraghona | 34 | 19:00 | 103 | Madanganj | 52 | 21:00 | 169 | SevenRings | 21.35 | 13:00
38 | Chapai | 71 | 21:00 | 104 | Madaripur | 117 | 23:00 | 170 | ShahCement | 21 | 00:00
39 | Charfasson | 34 | 22:00 | 105 | Madartek | 85 | 20:00 | 171 | Shahjadpur | 85 | 22:00
40 | Charsaidpur | 26 | 00:00 | 106 | Madunaghat | 54 | 22:00 | 172 | Shahjibazar | 141 | 02:00
41 | Chauddagram | 76 | 18:30 | 107 | Magura | 72 | 22:00 | 173 | Shahmirpur | 60 | 14:00
42 | Chhatak | 41 | 00:00 | 108 | Mahasthangarh | 73 | 00:00 | 174 | Shariatpur | 95 | 23:00
43 | Chowmuhani | 151 | 22:00 | 109 | Maijdee | 48 | 00:00 | 175 | Sherpur | 148 | 19:00
44 | Chuadanga | 116 | 01:00 | 110 | Manikganj | 141 | 13:00 | 176 | Shikalbaha | 26 | 21:00
45 | Coxsbazar | 139 | 23:00 | 111 | Maniknagar | 86 | 13:00 | 177 | Shitalakhya | 83 | 11:00
46 | Cumilla(N) | 124 | 18:30 | 112 | Matarbari | 53 | 20:00 | 178 | Sholosohor | 57 | 15:00
47 | Cumilla(S) | 187 | 19:00 | 113 | Matuail | 78 | 11:00 | 179 | Shomvuganj | 50 | 11:00
48 | Daganbhuiyan | 44 | 23:00 | 114 | Metrorail_Motijheel | 33 | 19:30 | 180 | Shyampur | 156 | 11:00
49 | Daudkandi | 147 | 21:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 131 | 09:00
50 | DhakaUniversity | 98 | 13:00 | 116 | Millgate | 102 | 10:00 | 182 | Sirajganj | 128 | 21:00
51 | Dhamrai | 92 | 01:00 | 117 | Mirpur | 159 | 18:30 | 183 | Sitakunda | 14 | 16:00
52 | Dhanmondi | 128 | 14:00 | 118 | Mirsorai | 49 | 09:00 | 184 | Sonargaon | 150 | 14:00
53 | Dohazari | 107 | 22:00 | 119 | Mirzapur | 46 | 19:30 | 185 | Sreemongol | 96 | 22:00
54 | Faridpur | 195 | 22:00 | 120 | Mithapukur | 77 | 23:00 | 186 | Sreepur | 156 | 12:00
55 | Fatullah | 119 | 10:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 54.9 | 22:00
56 | Fenchuganj | 49 | 22:00 | 122 | Mogbazar | 43.9 | 14:00 | 188 | Sunamganj | 64 | 23:00
57 | Feni | 104 | 21:00 | 123 | Mongla | 46 | 21:00 | 189 | Sylhet | 122 | 20:00
58 | GPH | 6 | 13:00 | 124 | Motijheel | 52 | 12:00 | 190 | Sylhet_(South) | 77 | 20:00
59 | Ghatail | 90 | 00:00 | 125 | Muktagacha | 39 | 14:00 | 191 | TK | 25 | 22:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 122 | 23:00 | 192 | Tangail | 180 | 00:00
61 | Ghorashal-230 | 111 | 12:00 | 127 | Muradnagar | 47 | 00:00 | 193 | Taraganj | 33 | 00:00
62 | Goalpara | 42 | 22:00 | 128 | Mymensingh | 148 | 21:00 | 194 | Tasnim | 37 | 03:00
63 | Gollamari | 108 | 23:00 | 129 | Nabinagar | 112 | 06:00 | 195 | Thakurgaon | 125 | 19:30
64 | Gopalganj | 123 | 22:00 | 130 | Naogaon | 120 | 23:00 | 196 | Tongi | 167 | 15:00
65 | Gulshan | 124 | 14:00 | 131 | Narail | 63 | 22:00 | 197 | Ullahpara | 39 | 20:00
66 | Halishahar | 146 | 14:00 | 132 | Narinda | 76 | 13:00 | 198 | Ullon | 57 | 18:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-08-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15857.79 | 325 |  | 16197.42
1:00 | 15275.21 | 428 |  | 15722.47
2:00 | 14899.93 | 426 |  | 15345.1
3:00 | 14576.12 | 406 |  | 15000.39
4:00 | 14242.02 | 343 |  | 14600.02
5:00 | 14000.78 | 333 |  | 14348.78
6:00 | 13711.06 | 298 |  | 14022.06
7:00 | 13902.24 | 261 |  | 14175.24
8:00 | 13854.37 | 357 |  | 14227.44
9:00 | 13967.08 | 329 |  | 14310.89
10:00 | 14366.74 | 117 |  | 14489.01
11:00 | 14183.65 | 123 |  | 14312.19
12:00 | 14322.35 | 563 |  | 14910.35
13:00 | 14567.64 | 1191 |  | 15812.64
14:00 | 14642.87 | 1067 |  | 15757.87
15:00 | 14596.83 | 1834 |  | 16513.83
16:00 | 14314.37 | 1777 |  | 16171.37
17:00 | 14176.5 | 1804 |  | 16061.5
18:00 | 14300.65 | 1434 |  | 15799.65
19:00 | 15426.79 | 2530 |  | 18070.79
19:30 | 15293.87 | 2447 |  | 17850.87
20:00 | 15420.4 | 1883 |  | 17388.4
21:00 | 15680.74 | 2266 |  | 18048.74
22:00 | 16180.35 | 1237 |  | 17473.35
23:00 | 16358.39 | 1179 |  | 17590.39
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 19-08-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 114 | 21 | 330 | 160 | 1180 | 628 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 88 | 20 | 220 | 154 | 1060 | 600
2:00 | 72 | 20 | 0 | 0 | 962 | 584 |  | Import | 0
3:00 | 82 | 28 | 190 | 170 | 984 | 564
4:00 | 76 | 28 | 184 | 166 | 1000 | 550 | Ishurdi-Ghorashal Ckt-2 | Export | 2846981.82
5:00 | 83 | 32 | 204 | 164 | 1060 | 584
6:00 | 100 | 44 | 222 | 170 | 1094 | 610 |  | Import | 0
7:00 | 88 | 36 | 200 | 192 | 1056 | 608
8:00 | 123 | 55 | 260 | 192 | 1288 | 676 | Sirajganj-Sreepur Ckt-1 | Export | 1721000
9:00 | 155 | 75 | 344 | 208 | 1442 | 782
10:00 | 154 | 83 | 322 | 218 | 1414 | 874 |  | Import | 0
11:00 | 179 | 84 | 432 | 216 | 1488 | 874
12:00 | 135 | 63 | 350 | 216 | 1208 | 810 | Sirajganj-Sreepur Ckt-2 | Export | 1726000
13:00 | 152 | 71 | 330 | 236 | 1304 | 856
14:00 | 146 | 70 | 330 | 220 | 1292 | 852 |  | Import | 0
15:00 | 138 | 66 | 290 | 196 | 1194 | 786
16:00 | 130 | 55 | 320 | 176 | 1286 | 772 | Gopalganj-Aminbazar Ckt-1 | Export | 14840000
17:00 | 126 | 59 | 330 | 192 | 1342 | 766
18:00 | 128 | 54 | 310 | 184 | 1392 | 734 |  | Import | 0
18:30 | 136 | 54 | 360 | 202 | 1462 | 696
19:00 | 101 | 29 | 290 | 130 | 1294 | 554 | Gopalganj-Aminbazar Ckt-2 | Export | 14940000
19:30 | 122 | 30 | 350 | 120 | 1458 | 438
20:00 | 130 | 37 | 350 | 140 | 1404 | 568 |  | Import | 0
21:00 | 123 | 30 | 330 | 130 | 1306 | 520
22:00 | 102 | 5 | 280 | 96 | 1212 | 446 |  | Total Export | 36073981.82
23:00 | 113 | 4 | 328 | 112 | 1222 | 460 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-08-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9088.92 | 6768.87 | 15857.79 | DAILY GENERATION CURVE
00:30 | 8996.92 | 6569.58 | 15566.5
01:00 | 8904.92 | 6370.29 | 15275.21 | 19-08-2026
01:30 | 8859.21 | 6228.36 | 15087.57
02:00 | 8813.5 | 6086.43 | 14899.93
02:30 | 8701.5 | 6036.525 | 14738.025
03:00 | 8589.5 | 5986.62 | 14576.12
03:30 | 8524.75 | 5884.32 | 14409.07
04:00 | 8460 | 5782.02 | 14242.02
04:30 | 8351.75 | 5769.65 | 14121.4
05:00 | 8243.5 | 5757.28 | 14000.78
05:30 | 8134.86 | 5721.06 | 13855.92
06:00 | 8026.22 | 5684.84 | 13711.06
06:30 | 8076.45 | 5730.2 | 13806.65
07:00 | 8126.68 | 5775.56 | 13902.24
07:30 | 8106.39 | 5771.915 | 13878.305
08:00 | 8086.1 | 5768.27 | 13854.37
08:30 | 8074.945 | 5835.78 | 13910.725
09:00 | 8063.79 | 5903.29 | 13967.08
09:30 | 8232.405 | 5934.505 | 14166.91
10:00 | 8401.02 | 5965.72 | 14366.74
10:30 | 8290.135 | 5985.06 | 14275.195
11:00 | 8179.25 | 6004.4 | 14183.65
11:30 | 8341.715 | 5911.285 | 14253
12:00 | 8504.18 | 5818.17 | 14322.35
12:30 | 8547.775 | 5897.22 | 14444.995
13:00 | 8591.37 | 5976.27 | 14567.64
13:30 | 8683.4 | 5921.855 | 14605.255
14:00 | 8775.43 | 5867.44 | 14642.87
14:30 | 8766.905 | 5852.945 | 14619.85
15:00 | 8758.38 | 5838.45 | 14596.83
15:30 | 8649.35 | 5806.25 | 14455.6
16:00 | 8540.32 | 5774.05 | 14314.37
16:30 | 8500.715 | 5744.72 | 14245.435
17:00 | 8461.11 | 5715.39 | 14176.5
17:30 | 8455.925 | 5782.65 | 14238.575
18:00 | 8450.74 | 5849.91 | 14300.65
18:30 | 8675.58 | 6188.14 | 14863.72
19:00 | 8900.42 | 6526.37 | 15426.79
19:30 | 8565.42 | 6728.45 | 15293.87
20:00 | 8703.42 | 6716.98 | 15420.4
20:30 | 8793.6 | 6756.97 | 15550.57 |  | Executive Engineer
21:00 | 8883.78 | 6796.96 | 15680.74 |  | Network Operation Division
21:30 | 9073.78 | 6856.765 | 15930.545
22:00 | 9263.78 | 6916.57 | 16180.35
22:30 | 9254.2 | 7015.17 | 16269.37
23:00 | 9244.62 | 7113.77 | 16358.39

## En-Curve
QF-LDC-12
Date | 19-08-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3662 | 1624.5 | 902 | 38 | 164 | 1475.87 | 222 | 5402 | 0 | 657.42 | 1694 | 0 | 0 | 16 | 325 | DAILY ENERGY CURVE
00:30 | 3625 | 1617.5 | 902.5 | 38 | 160 | 1316.08 | 222 | 5384.5 | 0 | 676.42 | 1608.5 | 0 | 0 | 16 | 376.5 | 19-08-2026
01:00 | 3588 | 1610.5 | 903 | 38 | 156 | 1156.29 | 222 | 5367 | 0 | 695.42 | 1523 | 0 | 0 | 16 | 428
01:30 | 3647 | 1607.5 | 902.5 | 38 | 156 | 982.86 | 222 | 5367.5 | 0 | 680.21 | 1469.5 | 0 | 0 | 14.5 | 427 | Energy Generated | 357.4496 |  | MKWHr
02:00 | 3706 | 1604.5 | 902 | 38 | 156 | 809.43 | 222 | 5368 | 0 | 665 | 1416 | 0 | 0 | 13 | 426 | Energy not Served | 22.511 |  | MKWHr
02:30 | 3710.5 | 1615 | 902 | 38 | 155 | 817.025 | 222 | 5379.5 | 0 | 575.5 | 1310 | 0 | 0 | 13.5 | 416 | Total Energy Requirement | 379.9606 |  | MKWHr
03:00 | 3715 | 1625.5 | 902 | 38 | 154 | 824.62 | 222 | 5391 | 0 | 486 | 1204 | 0 | 0 | 14 | 406
03:30 | 3730.75 | 1639.5 | 902 | 38 | 153 | 822.32 | 221.5 | 5400 | 0 | 443.5 | 1043.5 | 0 | 0 | 15 | 374.5
04:00 | 3746.5 | 1653.5 | 902 | 38 | 152 | 820.02 | 221 | 5409 | 0 | 401 | 883 | 0 | 0 | 16 | 343
04:30 | 3733.25 | 1670.5 | 902 | 38 | 148 | 823.15 | 220 | 5410 | 0 | 401.5 | 761 | 0 | 0 | 14 | 338
05:00 | 3720 | 1687.5 | 902 | 38 | 144 | 826.28 | 219 | 5411 | 0 | 402 | 639 | 0 | 0 | 12 | 333
05:30 | 3716 | 1676 | 902 | 38 | 141 | 822.83 | 218.5 | 5368 | 3.88 | 403.21 | 553 | 0 | 0 | 13.5 | 315.5
06:00 | 3712 | 1664.5 | 902 | 38 | 138 | 819.38 | 218 | 5325 | 7.76 | 404.42 | 467 | 0 | 0 | 15 | 298
06:30 | 3733.5 | 1716 | 902 | 38 | 137 | 819.97 | 218 | 5327 | 42.76 | 404.42 | 455.5 | 0 | 0 | 12.5 | 279.5
07:00 | 3755 | 1767.5 | 902 | 38 | 136 | 820.56 | 218 | 5329 | 77.76 | 404.42 | 444 | 0 | 0 | 10 | 261
07:30 | 3686 | 1682.5 | 902.5 | 38 | 140 | 822.96 | 198 | 5342 | 168.425 | 397.42 | 492.5 | 0 | 0 | 8 | 309
08:00 | 3617 | 1597.5 | 903 | 38 | 144 | 825.36 | 178 | 5355 | 259.09 | 390.42 | 541 | 0 | 0 | 6 | 357
08:30 | 3601 | 1575.5 | 902.5 | 38 | 144 | 820.61 | 179 | 5354.5 | 332.695 | 381.92 | 575.5 | 0 | 0 | 5.5 | 343
09:00 | 3585 | 1553.5 | 902 | 38 | 144 | 815.86 | 180 | 5354 | 406.3 | 373.42 | 610 | 0 | 0 | 5 | 329
09:30 | 3605.5 | 1577.5 | 902 | 38 | 147 | 818.985 | 180 | 5334 | 463.505 | 401.92 | 692.5 | 0 | 0 | 6 | 223
10:00 | 3626 | 1601.5 | 902 | 38 | 150 | 822.11 | 180 | 5314 | 520.71 | 430.42 | 775 | 0 | 0 | 7 | 117
10:30 | 3710.5 | 1675 | 902 | 38 | 153 | 821.46 | 200 | 4922.5 | 575.815 | 429.92 | 829 | 0 | 0 | 18 | 120
11:00 | 3795 | 1748.5 | 902 | 38 | 156 | 820.81 | 220 | 4531 | 630.92 | 429.42 | 883 | 0 | 0 | 29 | 123
11:30 | 3737.5 | 1652.5 | 902 | 38 | 164 | 824.465 | 220 | 4559.5 | 583.47 | 428.92 | 1123.5 | 0 | 0 | 19.145 | 343
12:00 | 3680 | 1556.5 | 902 | 38 | 172 | 828.12 | 220 | 4588 | 536.02 | 428.42 | 1364 | 0 | 0 | 9.29 | 563
12:30 | 3701.5 | 1586 | 902 | 38 | 172 | 826.79 | 220.5 | 4590 | 549.64 | 396.92 | 1456 | 0 | 0 | 5.645 | 877
13:00 | 3723 | 1615.5 | 902 | 38 | 172 | 825.46 | 221 | 4592 | 563.26 | 365.42 | 1548 | 0 | 0 | 2 | 1191
13:30 | 3746 | 1651 | 902 | 38 | 167 | 827.16 | 221.5 | 4592 | 497.175 | 364.92 | 1592 | 0 | 0 | 6.5 | 1129
14:00 | 3769 | 1686.5 | 902 | 38 | 162 | 828.86 | 222 | 4592 | 431.09 | 364.42 | 1636 | 0 | 0 | 11 | 1067
14:30 | 3794.5 | 1728.5 | 902 | 38 | 167 | 828.45 | 222 | 4582 | 376.48 | 372.92 | 1591 | 0 | 0 | 17 | 1450.5
15:00 | 3820 | 1770.5 | 902 | 38 | 172 | 828.04 | 222 | 4572 | 321.87 | 381.42 | 1546 | 0 | 0 | 23 | 1834
15:30 | 3770 | 1708.5 | 902 | 38 | 170 | 827.925 | 222 | 4566.5 | 297.255 | 397.92 | 1540 | 0 | 0 | 15.5 | 1805.5
16:00 | 3720 | 1646.5 | 902 | 38 | 168 | 827.81 | 222 | 4561 | 272.64 | 414.42 | 1534 | 0 | 0 | 8 | 1777
16:30 | 3685 | 1655.35 | 891.5 | 38 | 169 | 826.515 | 221 | 4568.5 | 208.15 | 420.42 | 1552 | 0 | 0 | 10 | 1790.5
17:00 | 3650 | 1664.2 | 881 | 38 | 170 | 825.22 | 220 | 4576 | 143.66 | 426.42 | 1570 | 0 | 0 | 12 | 1804
17:30 | 3560.5 | 1639.6 | 881 | 38 | 169 | 847.635 | 219.5 | 4644 | 85.92 | 482.42 | 1664 | 0 | 0 | 7 | 1619
18:00 | 3471 | 1615 | 881 | 38 | 168 | 870.05 | 219 | 4712 | 28.18 | 538.42 | 1758 | 0 | 0 | 2 | 1434
18:30 | 3520.5 | 1698.5 | 881 | 38 | 178 | 1063.21 | 219 | 4814 | 14.09 | 562.42 | 1874 | 0 | 0 | 1 | 1982
19:00 | 3570 | 1782 | 881 | 38 | 188 | 1256.37 | 219 | 4916 | 0 | 586.42 | 1990 | 0 | 0 | 0 | 2530
19:30 | 3460 | 1580 | 880 | 38 | 176 | 1454.45 | 219 | 4897 | 0 | 587.42 | 1998 | 0 | 0 | 4 | 2447
20:00 | 3492 | 1587 | 880 | 38 | 174 | 1461.98 | 219 | 5035 | 0 | 588.42 | 1940 | 0 | 0 | 5 | 1883
20:30 | 3515.5 | 1652 | 880.5 | 38 | 175 | 1467.47 | 219.5 | 5078.5 | 0 | 589.92 | 1931.68 | 0 | 0 | 2.5 | 2074.5
21:00 | 3539 | 1717 | 881 | 38 | 176 | 1472.96 | 220 | 5122 | 0 | 591.42 | 1923.36 | 0 | 0 | 0 | 2266
21:30 | 3518.5 | 1664 | 885 | 38 | 174 | 1476.265 | 220 | 5237.5 | 0 | 620.92 | 2094.86 | 0 | 0 | 1.5 | 1751.5
22:00 | 3498 | 1611 | 889 | 38 | 172 | 1479.57 | 220 | 5353 | 0 | 650.42 | 2266.36 | 0 | 0 | 3 | 1237
22:30 | 3467.5 | 1603 | 892.5 | 38 | 177 | 1477.57 | 220 | 5352.5 | 0 | 730.92 | 2305.88 | 0 | 0 | 4.5 | 1208
23:00 | 3437 | 1595 | 896 | 38 | 182 | 1475.57 | 220 | 5352 | 0 | 811.42 | 2345.4 | 0 | 0 | 6 | 1179
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-08-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 371 | 19:00 | 358 | 11:00 | Madunaghat | 401 | 18:00 | 389 | 00:00
Amtali | 412 | 17:00 | 406 | 00:00 | Meghnaghat | 376 | 19:00 | 361 | 10:00
Ashuganj | 362 | 19:00 | 343 | 10:00 | Mirsorai | 402 | 18:00 | 383 | 00:00
Bhulta | 392 | 19:00 | 369 | 10:00 | Payra | 413 | 18:00 | 409 | 00:00
Bibiana | 376 | 18:30 | 371 | 00:00 | Rahanpur | 411 | 18:00 | 389 | 00:00
BIPTC | 402 | 05:00 | 395 | 19:30 | Rampal | 392 | 06:00 | 382 | 00:00
Bogura | 395 | 18:00 | 372 | 00:00
Gopalganj | 388 | 18:00 | 377 | 00:00
Kaliakoir | 362 | 19:00 | 343 | 10:00
Korerhat | 398 | 19:00 | 382 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 19:00 | 213 | 10:00 | Hathazari | 238 | 19:30 | 228 | 03:00
AKSML | 241 | 18:00 | 226 | 10:00 | Ishurdi | 235 | 18:00 | 214 | 00:00
Aminbazar | 227 | 19:00 | 214 | 11:00 | Jhenaidah | 226 | 17:00 | 202 | 00:00
Ashuganj | 227 | 19:00 | 216 | 13:00 | Kachua | 229 | 18:00 | 217 | 00:00
Ashuganj-400 | 227 | 19:00 | 216 | 13:00 | Kaliakoir | 224 | 19:00 | 209 | 10:00
Baghabari | 231 | 11:00 | 218 | 00:00 | Keranigonj | 224 | 19:30 | 210 | 10:00
Barapukuria | 228 | 12:00 | 216 | 00:00 | Khulna(S) | 225 | 18:00 | 210 | 00:00
Barapukuria-230 | 228 | 12:00 | 216 | 00:00 | Korerhat | 228 | 18:30 | 218 | 00:00
Barishal | 227 | 00:00 | 217 | 22:00 | Madunaghat | 239 | 19:00 | 230 | 09:00
Bheramara | 233 | 18:00 | 211 | 00:00 | Madunaghat-400 | 240 | 18:00 | 231 | 10:00
Bhulta | 223 | 19:00 | 209 | 10:00 | Maniknagar | 220 | 19:00 | 206 | 11:00
Bibiana | 220 | 18:30 | 213 | 00:00 | Meghnaghat | 230 | 23:00 | 215 | 10:00
BIPTC | 236 | 18:00 | 212 | 00:00 | Meghnaghat-400 | 223 | 21:00 | 212 | 10:00
Birulia | 224 | 19:00 | 211 | 10:00 | Mirsorai | 234 | 18:00 | 222 | 10:00
Bogura | 238 | 17:00 | 225 | 00:00 | Naogaon | 225 | 11:00 | 197 | 22:00
Bogura-400 | 238 | 18:00 | 225 | 00:00 | Purbasadipur | 226 | 12:00 | 211 | 00:00
Borhanuddin | 228 | 13:00 | 223 | 00:00 | Rajshahi | 231 | 18:00 | 208 | 22:00
BSRM | 231 | 18:00 | 218 | 10:00 | Rampal | 223 | 13:00 | 211 | 00:00
Charfasson | 229 | 09:00 | 224 | 22:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 227 | 19:30 | 217 | 00:00 | Rampura | 222 | 19:00 | 207 | 10:00
Cumilla(N) | 223 | 19:30 | 213 | 00:00 | Shikalbaha | 238 | 18:00 | 228 | 10:00
Faridpur | 221 | 18:00 | 211 | 00:00 | Shyampur | 223 | 19:00 | 210 | 10:00
Fenchuganj | 220 | 18:00 | 214 | 00:00 | Siddhirganj | 223 | 19:00 | 208 | 13:00
Feni | 227 | 18:00 | 214 | 00:00 | Sirajgonj | 236 | 16:00 | 226 | 00:00
Ghorashal | 220 | 02:00 | 215 | 00:00 | Sreepur | 221 | 19:30 | 214 | 00:00
Ghorashal-230 | 215 | 19:30 | 198 | 10:00 | Tongi | 212 | 19:30 | 200 | 00:00
Gopalganj | 221 | 16:00 | 213 | 00:00
GPH | 233 | 17:00 | 225 | 10:00
Haripur | 222 | 19:00 | 209 | 10:00
Hasnabad | 224 | 19:00 | 211 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 126 | 10:00 | Madaripur | 130 | 16:00 | 126 | 00:00
Agargaon | 136 | 19:00 | 127 | 10:00 | Madartek | 138 | 00:00 | 124 | 13:00
Agrabad | 135 | 19:00 | 129 | 10:00 | Madunaghat | 138 | 18:00 | 132 | 09:00
AKS | 135 | 18:00 | 127 | 10:00 | Magura | 137 | 18:00 | 119 | 00:00
Aminbazar | 131 | 19:00 | 121 | 11:00 | Mahasthangarh | 135 | 18:00 | 125 | 00:00
Amnura | 135 | 11:00 | 122 | 23:00 | Maijdee | 129 | 18:00 | 121 | 00:00
Ashuganj | 131 | 19:30 | 125 | 00:00 | Manikganj | 128 | 18:00 | 122 | 00:00
Ashuganj-230 | 133 | 19:30 | 128 | 00:00 | Maniknagar | 137 | 19:30 | 126 | 11:00
Bagerhat | 128 | 13:00 | 116 | 00:00 | Matarbari | 133 | 12:00 | 117 | 22:00
Bajitpur | 125 | 19:00 | 119 | 00:00 | Matuail | 132 | 19:00 | 121 | 10:00
Bakerganj | 132 | 16:00 | 125 | 00:00 | Metrorail_Motijheel | 137 | 19:30 | 126 | 11:00
Bakulia | 138 | 18:00 | 130 | 10:00 | Metrorail_Uttara | 129 | 19:30 | 115 | 10:00
Banani | 136 | 06:00 | 125 | 10:00 | Millgate | 130 | 19:00 | 116 | 10:00
Bangabhaban | 137 | 19:30 | 126 | 10:00 | Mirpur | 129 | 19:00 | 118 | 13:00
Barapukuria | 138 | 12:00 | 122 | 03:00 | Mirzapur | 128 | 19:00 | 121 | 00:00
Barguna | 132 | 18:00 | 125 | 22:00 | Mithapukur | 133 | 12:00 | 123 | 00:00
Barishal | 131 | 16:00 | 124 | 00:00 | MI_Cement | 130 | 06:00 | 121 | 10:00
Barishal-230 | 131 | 18:00 | 124 | 22:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroaulia | 135 | 21:00 | 130 | 07:00 | Mogbazar | 137 | 06:00 | 127 | 10:00
Baroirhat | 133 | 18:00 | 125 | 00:00 | Mongla | 126 | 16:00 | 115 | 00:00
Bashundhara | 136 | 19:00 | 115 | 10:00 | Motijheel | 137 | 19:30 | 126 | 10:00
BashundharaCement | 133 | 19:00 | 122 | 10:00 | Muktagacha | 126 | 18:30 | 114 | 02:00
Beanibazar | 121 | 06:00 | 116 | 22:00 | Munshiganj | 132 | 19:00 | 120 | 10:00
Benapole | 136 | 18:00 | 114 | 23:00 | Muradnagar | 127 | 18:00 | 118 | 10:00
Bhaluka | 131 | 19:30 | 123 | 00:00 | Mymensingh | 125 | 12:00 | 112 | 06:00
Bhandaria | 128 | 17:00 | 119 | 00:00 | Nabinagar | 126 | 19:00 | 113 | 10:00
Bhangura | 133 | 11:00 | 123 | 00:00 | Naogaon | 135 | 11:00 | 120 | 22:00
Bheramara | 136 | 18:00 | 123 | 00:00 | Narail | 138 | 18:00 | 118 | 22:00
Bheramara(GK) | 136 | 18:00 | 122 | 00:00 | Narinda | 137 | 19:30 | 126 | 11:00
Bhulta | 125 | 19:00 | 116 | 10:00 | Narshingdi | 128 | 19:00 | 111 | 11:00
Bhulta-400 | 128 | 19:00 | 118 | 10:00 | Natore | 134 | 18:00 | 120 | 22:00
Birulia | 132 | 19:00 | 125 | 10:00 | Nawabganj | 135 | 19:30 | 126 | 10:00
Bog-Sherpur | 135 | 18:00 | 126 | 00:00 | Netrakona | 120 | 19:00 | 112 | 07:00
Bogura | 137 | 18:00 | 128 | 00:00 | New | 132 | 19:00 | 118 | 10:00
Bogura-230 | 138 | 18:00 | 129 | 00:00 | Niamatpur | 135 | 11:00 | 121 | 22:00
Brahmanbaria | 126 | 18:00 | 121 | 00:00 | Noapara | 132 | 18:00 | 120 | 22:00
Cantonment | 136 | 19:00 | 126 | 10:00 | Pabna | 133 | 18:00 | 122 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandina | 130 | 18:00 | 122 | 10:00 | Palashbari | 132 | 12:00 | 120 | 00:00
Chandpur | 135 | 19:30 | 124 | 03:00 | Panchagarh | 141 | 12:00 | 127 | 07:00
Chandraghona | 139 | 18:00 | 133 | 08:00 | Patiya | 138 | 18:00 | 129 | 10:00
Chapai | 136 | 11:00 | 122 | 22:00 | Patnitala | 134 | 11:00 | 120 | 22:00
Charsaidpur | 133 | 19:30 | 121 | 11:00 | Patuakhali | 130 | 02:00 | 126 | 00:00
Chauddagram | 130 | 19:30 | 123 | 00:00 | Payra | 135 | 16:00 | 132 | 00:00
Chhatak | 120 | 13:00 | 113 | 22:00 | PHP | 132 | 18:00 | 125 | 00:00
Chowmuhani | 129 | 19:30 | 121 | 00:00 | Postogola | 132 | 04:00 | 123 | 10:00
Chuadanga | 136 | 16:00 | 117 | 23:00 | Pubail | 129 | 19:00 | 119 | 14:00
Coxsbazar | 127 | 11:00 | 122 | 00:00 | Purbachal | 136 | 04:00 | 125 | 10:00
Cumilla(N) | 130 | 19:30 | 122 | 10:00 | Purbasadipur | 137 | 12:00 | 127 | 00:00
Cumilla(S) | 131 | 19:30 | 121 | 12:00 | Rahanpur | 137 | 02:00 | 124 | 22:00
Daganbhuiyan | 131 | 18:00 | 123 | 00:00 | Rahanpur-400 | 137 | 11:00 | 126 | 22:00
Daudkandi | 126 | 19:00 | 115 | 10:00 | Rahim | 132 | 19:30 | 122 | 10:00
DhakaUniversity | 135 | 03:00 | 125 | 11:00 | Rajbari | 125 | 16:00 | 117 | 00:00
Dhamrai | 127 | 19:00 | 116 | 10:00 | Rajendrapur | 133 | 19:00 | 124 | 00:00
Dhanmondi | 136.7 | 19:00 | 125 | 10:00 | Rajshahi | 132 | 18:00 | 120 | 00:00
Dohazari | 133 | 18:00 | 126 | 10:00 | Rajshahi-230 | 132 | 18:00 | 119 | 22:00
Faridpur | 127 | 09:00 | 122 | 00:00 | Ramganj | 130 | 19:30 | 120 | 00:00
Fatullah | 134 | 19:00 | 122 | 10:00 | Rampur | 138 | 18:00 | 129 | 10:00
Fenchuganj | 129 | 16:00 | 126 | 00:00 | Rampura | 136 | 04:00 | 125 | 11:00
Feni | 130 | 18:00 | 123 | 10:00 | Rangamati | 136 | 18:30 | 132 | 00:00
Feni-230 | 132 | 18:00 | 124 | 00:00 | Rangpur | 132 | 18:30 | 122 | 00:00
Ghatail | 124 | 12:00 | 115 | 01:00 | Ruppur | 136 | 12:00 | 124 | 22:00
Ghorashal | 130 | 19:30 | 120 | 18:00 | Saidpur | 135 | 18:00 | 126 | 00:00
Goalpara | 135 | 16:00 | 124 | 22:00 | Santhia | 134 | 11:00 | 122 | 00:00
Gollamari | 135 | 18:00 | 123 | 22:00 | Satkhira | 131 | 18:00 | 115 | 23:00
Gopalganj | 130 | 16:00 | 122 | 00:00 | Satmasjid | 136 | 19:30 | 126 | 10:00
Gopalganj-400 | 131 | 16:00 | 126 | 00:00 | Savar | 130 | 19:00 | 119 | 11:00
Gulshan | 135 | 05:00 | 125 | 10:00 | SevenRings | 130 | 19:00 | 121 | 00:00
Halishahar | 138 | 18:00 | 129 | 10:00 | ShahCement | 133 | 19:30 | 121 | 11:00
Haripur | 132 | 19:00 | 122 | 10:00 | Shahjadpur | 135 | 07:00 | 127 | 22:00
HaripurSBU | 132 | 20:00 | 122 | 10:00 | Shahjibazar | 126 | 19:30 | 120 | 00:00
Hasnabad | 134 | 19:00 | 123 | 09:00 | Shahmirpur | 136 | 18:00 | 130 | 10:00
Hathazari | 139 | 18:00 | 133 | 02:00 | Shariatpur | 129 | 15:00 | 122 | 00:00
Hatirjheel | 136 | 04:00 | 125 | 11:00 | Sherpur | 126 | 18:30 | 110 | 06:00
Ishurdi | 137 | 18:00 | 125 | 00:00 | Shikalbaha | 127 | 18:30 | 119 | 10:00
Jaldhaka | 134 | 12:00 | 121 | 23:00 | Shikalbaha-230 | 138 | 18:00 | 131 | 10:00
Jamalpur | 131 | 18:30 | 114 | 01:00 | Shitalakhya | 130 | 06:00 | 121 | 10:00
Jashore | 137 | 18:00 | 116 | 23:00 | Sholosohor | 139 | 18:00 | 129 | 10:00
Jhenaidah | 139 | 18:00 | 115 | 23:00 | Shomvuganj | 120 | 17:00 | 111 | 00:00
Jhenaidah-230 | 139 | 18:00 | 122 | 00:00 | Shyampur | 134 | 19:00 | 124 | 10:00
Joydebpur | 129 | 19:00 | 118 | 09:00 | Shyampur-230 | 134 | 19:00 | 125 | 10:00
Joypurhat | 133 | 11:00 | 121 | 22:00 | Siddhirganj | 132 | 19:00 | 122 | 10:00
Juldah | 136 | 18:00 | 130 | 08:00 | Sirajganj | 131 | 18:00 | 121 | 22:00
Kabirpur | 133 | 19:00 | 111 | 10:00 | Sitakunda | 136 | 18:30 | 130 | 09:00
Kachua | 131 | 19:30 | 123 | 00:00 | Sonargaon | 129 | 19:00 | 24 | 08:00
Kaliakoir | 133 | 18:30 | 121 | 10:00 | Sreemongol | 126 | 19:00 | 120 | 22:00
Kaliganj | 138 | 16:00 | 121 | 22:00 | Sreepur | 134 | 19:30 | 128 | 00:00
Kallyanpur | 129 | 19:00 | 120 | 10:00 | Srinagar | 135 | 19:30 | 126 | 10:00
Kalurghat | 140 | 18:00 | 132 | 10:00 | SSM | 140 | 00:00 | 136 | 11:00
Kamrangirchar | 135 | 19:30 | 117 | 13:00 | Sunamganj | 119 | 21:00 | 111 | 22:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 123 | 17:00 | 120 | 00:00
Kasba | 126 | 18:00 | 118 | 10:00 | Sylhet_(South) | 123 | 07:00 | 119 | 22:00
Kazla | 137 | 20:00 | 125 | 12:00 | Tangail | 126 | 12:00 | 117 | 21:00
Keranigonj | 135 | 19:00 | 127 | 10:00 | Taraganj | 132 | 13:00 | 123 | 23:00
Khagrachori | 137 | 18:00 | 131 | 00:00 | Tasnim | 129 | 19:00 | 119 | 10:00
Khulna | 133 | 18:00 | 121 | 23:00 | Thakurgaon | 141 | 12:00 | 125 | 07:00
Khulna(S) | 135 | 18:00 | 124 | 00:00 | TK | 140 | 18:00 | 132 | 01:00
Khulshi | 135 | 18:30 | 127 | 10:00 | Tongi | 131 | 04:00 | 122 | 00:00
Kishoreganj | 124 | 19:00 | 117 | 00:00 | Ullahpara | 132 | 11:00 | 122 | 22:00
Kodda | 132 | 19:00 | 120 | 00:00 | Ullon | 136 | 06:00 | 125 | 11:00
Korerhat | 134 | 18:00 | 127 | 10:00 | Uttara | 128 | 19:00 | 116 | 10:00
KSRM | 137 | 18:00 | 129 | 09:00 | UttaraNew | 129 | 19:30 | 115 | 10:00
Kulaura | 128 | 18:00 | 124 | 00:00 | Zigatola | 136 | 19:00 | 126 | 13:00
Kurigram | 130 | 18:30 | 117 | 23:00
Kushtia | 132 | 16:00 | 117 | 00:00
Laksam | 130 | 19:00 | 122 | 00:00
Lakshmipur | 128 | 18:00 | 121 | 00:00
Lalbag | 134 | 19:00 | 126 | 13:00
Lalmonirhat | 130 | 11:00 | 120 | 22:00
Madanganj | 133 | 19:00 | 122 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-08-2026 | [28 empty] | Date: | 19-08-2026 | [28 empty] | Date: | 19-08-2026 | [28 empty] | Date: | 19-08-2026 | [28 empty] | Date: | 19-08-2026 | [18 empty] | Date: | 19-08-2026
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [18 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 447 | 54 | 35 | 53 | 143 | 145 | 15 | 55 | 66 | 0 | 0 | 0 | 0 | 0 | 17 | 310 | 0 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 370 | 15 | 16 | 51 | 0 | 16 | 50 | 6 | 17 | 12 | 12 | 0 | 222 | 92 | 0 | 1125 | 95 | 0 | 19 | 8 | 47 | 214 | 0 | 0 | 0 | 1193 | 0 | 75 | 8 | 230 | 300 | 260 | 44 | 10 | 220 | 30 | 32 | 130 | 96 | 28 | 0 | 29 | 164 | 16 | 0 | 31 | 305 | 260 | 380 | 40 | 39 | 141 | 0 | 8 | 0 | 84 | 20 | 140 | 0 | 125 | 17 | 68 | 0 | 155 | 0 | 0 | 0 | 24 | 9088.92 | 902 | 0 | 0 | 20 | 20 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1063 | 0 | 0 | 0 | 1475.87 | 0 | 0 | 0 | 35 | 70 | 0 | 51 | 20 | 16 | 0 | 0 | 20 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 157 | 54 | 50 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 230 | 117 | 180 | 0 | 800 | 780 | 35 | 6768.87 | 15857.79 | 104.33
01:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 434 | 35 | 35 | 52 | 143 | 145 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 330 | 47 | 16 | 50 | 0 | 16 | 50 | 19 | 0 | 12 | 12 | 0 | 222 | 91 | 2 | 1125 | 96 | 0 | 24 | 13 | 73 | 215 | 0 | 0 | 0 | 1150 | 0 | 90 | 8 | 230 | 300 | 255 | 44 | 10 | 220 | 30 | 44 | 130 | 114 | 0 | 0 | 68 | 156 | 34 | 0 | 31 | 308 | 260 | 372 | 40 | 39 | 135 | 0 | 8 | 0 | 84 | 20 | 140 | 0 | 125 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 13 | 8904.92 | 903 | 0 | 0 | 28 | 51 | 38 | 0 | 0 | 0 | 0 | 50 | 0 | 1060 | 0 | 0 | 0 | 1156.29 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 20 | 34 | 0 | 0 | 14 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 159 | 53 | 87 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 230 | 117 | 220 | 0 | 800 | 790 | 17 | 6370.29 | 15275.21 | 104.32
02:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 435 | 35 | 35 | 52 | 143 | 145 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 123 | 5.5 | 22 | 0 | 330 | 34 | 16 | 50 | 0 | 13 | 50 | 35 | 0 | 0 | 12 | 0 | 222 | 92 | 2 | 1125 | 96 | 0 | 12 | 0 | 50 | 214 | 0 | 0 | 0 | 1142 | 0 | 100 | 8 | 230 | 300 | 250 | 44 | 10 | 221 | 30 | 59 | 130 | 121 | 0 | 0 | 34 | 156 | 8 | 0 | 31 | 307 | 260 | 380 | 40 | 39 | 129 | 0 | 8 | 0 | 84 | 25 | 142 | 0 | 125 | 17 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 8813.5 | 902 | 0 | 0 | 28 | 51 | 38 | 0 | 0 | 0 | 0 | 32 | 0 | 1071 | 0 | 0 | 0 | 809.43 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 20 | 0 | 0 | 0 | 14 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 157 | 53 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 230 | 118 | 220 | 0 | 800 | 790 | 17 | 6086.43 | 14899.93 | 104.32
03:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 438 | 35 | 35 | 52 | 143 | 95 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 123 | 5.5 | 22 | 0 | 340 | 0 | 16 | 50 | 0 | 14 | 17 | 0 | 0 | 0 | 12 | 0 | 222 | 92 | 2 | 1125 | 95 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 1160 | 0 | 100 | 8 | 230 | 300 | 255 | 44 | 10 | 221 | 30 | 62 | 130 | 128 | 0 | 0 | 0 | 154 | 0 | 0 | 31 | 309 | 260 | 364 | 40 | 39 | 135 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 125 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 8589.5 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1076 | 0 | 0 | 0 | 824.62 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 20 | 0 | 0 | 0 | 14 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 158 | 52 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 118 | 220 | 0 | 800 | 790 | 17 | 5986.62 | 14576.12 | 104.31
04:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 433 | 35 | 35 | 52 | 143 | 95 | 15 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 123 | 5.5 | 22 | 0 | 380 | 0 | 0 | 37 | 0 | 16 | 17 | 0 | 0 | 0 | 12 | 0 | 221 | 93 | 2 | 1125 | 35 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 1160 | 0 | 36 | 8 | 230 | 300 | 255 | 44 | 10 | 221 | 30 | 61 | 137 | 127 | 0 | 0 | 0 | 152 | 0 | 0 | 31 | 309 | 260.5 | 374 | 40 | 39 | 128 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 125 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 8460 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 820.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 157 | 52 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 118 | 220 | 0 | 800 | 790 | 0 | 5782.02 | 14242.02 | 104.31
05:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 447 | 35 | 35 | 52 | 144 | 95 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 123 | 5.5 | 22 | 0 | 370 | 0 | 0 | 0 | 0 | 12 | 17 | 0 | 0 | 0 | 12 | 0 | 219 | 51 | 4 | 1125 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1160 | 0 | 26 | 26 | 230 | 280 | 240 | 44 | 10 | 220 | 25 | 64 | 137 | 125 | 0 | 0 | 0 | 144 | 0 | 0 | 31 | 305 | 260 | 379 | 40 | 39 | 142 | 0 | 8 | 0 | 84 | 25 | 139 | 0 | 126 | 0 | 49 | 0 | 48 | 0 | 0 | 0 | 12 | 8243.5 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 826.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 158 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 118 | 220 | 0 | 800 | 790 | 0 | 5757.28 | 14000.78 | 104.3
06:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 448 | 0 | 35 | 34 | 143 | 95 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 1 | 143.42 | 5.5 | 22 | 0 | 390 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 12 | 0.12 | 218 | 34 | 7 | 1125 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1104 | 0 | 26 | 26 | 230 | 280 | 240 | 44 | 10 | 202 | 30 | 54 | 140 | 51 | 0 | 0 | 0 | 138 | 0 | 1 | 31 | 303 | 260 | 380 | 40 | 39 | 137 | 0 | 8 | 0 | 84 | 28 | 139 | 0 | 125 | 0 | 49 | 0.41 | 48 | 0 | 0 | 1.77 | 12 | 8026.22 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 1 | 1065 | 0 | 0 | 0 | 819.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69 | 0 | 0 | 0 | 0.68 | 143 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0.07 | 158 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.02 | 0 | 230 | 117 | 180 | 0 | 800 | 790 | 0 | 5684.84 | 13711.06 | 104.3
07:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 456 | 0 | 35 | 34 | 143 | 95 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 4 | 143.42 | 5.5 | 22 | 0 | 440 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 12 | 0.92 | 218 | 32 | 7 | 1125 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 1120 | 2 | 26 | 26 | 230 | 280 | 240 | 44 | 10 | 210 | 30 | 34 | 140 | 51 | 0 | 0 | 0 | 136 | 0 | 1 | 31 | 300 | 260 | 398 | 40 | 39 | 153 | 1 | 0 | 0 | 84 | 28 | 140 | 0 | 125 | 0 | 49 | 2.02 | 47 | 0 | 0.3 | 3.52 | 12 | 8126.68 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 22.11 | 1050 | 0 | 0 | 0 | 820.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.47 | 7 | 0 | 0 | 9.23 | 144 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0.87 | 160 | 54 | 0 | 2 | 0 | 0 | 0 | 0 | 0.3 | 11 | 0.02 | 0 | 230 | 117 | 220 | 0 | 800 | 790 | 0 | 5775.56 | 13902.24 | 104.29
08:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 438 | 0 | 35 | 34 | 129 | 95 | 2 | 4 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 16 | 143.42 | 5.5 | 22 | 0 | 340 | 0 | 16 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 12 | 2.32 | 178 | 36 | 0 | 1125 | 6 | 0 | 0 | 0 | 1 | 213 | 0 | 0 | 0 | 1150 | 5 | 26 | 26 | 230 | 280 | 240 | 44 | 10 | 196 | 30 | 34 | 140 | 61 | 0 | 0 | 0 | 144 | 0 | 47 | 31 | 303 | 260 | 377 | 40 | 39 | 145 | 8 | 0 | 0 | 84 | 30 | 141 | 0 | 125 | 0 | 49 | 6.01 | 47 | 0 | 0.5 | 12.35 | 12 | 8086.1 | 903 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 45 | 1050 | 0 | 0 | 0 | 825.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.11 | 14 | 0 | 0 | 9.65 | 144 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.53 | 161 | 54 | 17 | 11 | 0 | 0 | 0 | 0 | 1.5 | 55 | 0.12 | 0 | 230 | 117 | 180 | 0 | 800 | 785 | 2 | 5768.27 | 13854.37 | 104.29
09:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 431 | 0 | 21 | 28 | 112 | 45 | 15 | 17 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 23 | 143.42 | 5.5 | 22 | 0 | 320 | 0 | 16 | 12 | 0 | 5 | 0 | 0 | 0 | 0 | 12 | 1.61 | 180 | 56 | 0 | 1125 | 16 | 0 | 0 | 0 | 15 | 214 | 0 | 0 | 0 | 1150 | 13 | 26 | 26 | 230 | 280 | 240 | 44 | 10 | 190 | 30 | 34 | 140 | 77 | 0 | 0 | 0 | 144 | 0 | 60 | 31 | 300 | 260 | 360 | 40 | 39 | 131 | 7 | 0 | 0 | 84 | 30 | 140 | 0 | 125 | 0 | 49 | 8.51 | 53 | 0 | 1.1 | 22.65 | 12 | 8063.79 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 61 | 1050 | 0 | 0 | 0 | 815.86 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 42.83 | 36 | 0 | 0 | 39.82 | 144 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 3.27 | 160 | 54 | 35 | 19 | 0 | 0 | 0 | 0 | 3 | 64 | 0.51 | 0 | 230 | 117 | 180 | 0 | 800 | 785 | 17 | 5903.29 | 13967.08 | 104.28
10:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 441 | 10 | 33 | 36 | 126 | 45 | 15 | 17 | 49 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 30 | 143.42 | 5.5 | 22 | 0 | 350 | 0 | 16 | 12 | 0 | 7 | 0 | 0 | 0 | 0 | 12 | 2.57 | 180 | 67 | 0 | 1125 | 16 | 0 | 0 | 0 | 14 | 212 | 0 | 0 | 0 | 1160 | 6 | 26 | 26 | 230 | 280 | 240 | 44 | 10 | 199 | 30 | 34 | 140 | 78 | 5 | 0 | 0 | 150 | 0 | 62 | 31 | 302 | 263 | 387 | 40 | 39 | 137 | 10 | 0 | 0 | 84 | 30 | 140 | 0 | 125 | 0 | 58 | 19.32 | 116 | 0 | 2.3 | 42.91 | 12 | 8401.02 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 57 | 1050 | 0 | 0 | 0 | 822.11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 52.56 | 27 | 0 | 0 | 54.77 | 145 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 1.96 | 160 | 54 | 35 | 28 | 0 | 0 | 0 | 0 | 2.6 | 121 | 0.72 | 0 | 230 | 117 | 180 | 0 | 800 | 735 | 17 | 5965.72 | 14366.74 | 104.28
11:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 462 | 17 | 17 | 53 | 125 | 95 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 310 | 0 | 0 | 28 | 143.42 | 5.5 | 22 | 0 | 420 | 0 | 16 | 12 | 0 | 29 | 0 | 0 | 0 | 0 | 12 | 5.13 | 220 | 70 | 0 | 555 | 16 | 0 | 0 | 0 | 15 | 210 | 0 | 0 | 0 | 1170 | 4 | 26 | 26 | 250 | 350 | 240 | 44 | 10 | 208 | 30 | 34 | 141 | 80 | 18 | 0 | 0 | 156 | 0 | 41 | 31 | 309 | 260 | 392 | 40 | 39 | 146 | 12 | 0 | 0 | 84 | 28 | 141 | 0 | 125 | 0 | 58 | 18.5 | 116 | 0 | 1.1 | 38.6 | 12 | 8179.25 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 89 | 1062 | 0 | 0 | 0 | 820.81 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 55.73 | 100 | 0 | 0 | 57.19 | 144 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 4.72 | 161 | 53 | 45 | 30 | 0 | 0 | 0 | 0 | 1.7 | 144 | 0.25 | 16 | 230 | 117 | 220 | 0 | 800 | 500 | 17 | 6004.4 | 14183.65 | 104.27
12:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 422 | 17 | 17 | 52 | 125 | 185 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 285 | 0 | 0 | 21 | 143.42 | 5.5 | 22 | 0 | 310 | 37 | 16 | 25 | 0 | 9.29 | 0 | 0 | 17 | 0 | 12 | 4.8 | 220 | 82 | 0 | 555 | 85 | 0 | 0 | 0 | 56 | 212 | 0 | 0 | 0 | 1224 | 13 | 26 | 26 | 250 | 355 | 240 | 44 | 10 | 183 | 30 | 34 | 140 | 158 | 10 | 0 | 48 | 172 | 6 | 77 | 30 | 303 | 256 | 388 | 40 | 39 | 150 | 12 | 0 | 0 | 84 | 30 | 142 | 0 | 125 | 0 | 58 | 22.24 | 116 | 0 | 0.7 | 57.23 | 12 | 8504.18 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 7 | 1100 | 0 | 0 | 0 | 828.12 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 16 | 57.8 | 48 | 0 | 0 | 63.43 | 144 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 6.82 | 161 | 53 | 90 | 25 | 0 | 0 | 0 | 0 | 6.8 | 113 | 0.2 | 16 | 200 | 115 | 180 | 0 | 800 | 495 | 17 | 5818.17 | 14322.35 | 104.27
13:00 | 0 | 51 | 17 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 435 | 17 | 17 | 51 | 124 | 195 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 289 | 0 | 0 | 35 | 143.42 | 5.5 | 22 | 0 | 330 | 48 | 16 | 50 | 0 | 2 | 0 | 0 | 17 | 12 | 12 | 3.73 | 221 | 92 | 0 | 555 | 120 | 0 | 2 | 0 | 91 | 212 | 0 | 0 | 0 | 1224 | 4 | 26 | 8 | 250 | 354 | 240 | 44 | 10 | 190 | 30 | 33 | 139 | 173 | 8 | 5 | 49 | 172 | 21 | 76 | 30 | 306 | 256 | 376 | 40 | 38 | 147 | 12 | 0 | 0 | 83 | 30 | 140 | 0 | 125 | 6 | 58 | 10.12 | 116 | 0 | 1.1 | 53.5 | 12 | 8591.37 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 39 | 1100 | 0 | 0 | 0 | 825.46 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 40.82 | 100 | 0 | 0 | 62.26 | 144 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 5.83 | 160 | 53 | 110 | 26 | 0 | 0 | 0 | 0 | 4.5 | 89 | 0.4 | 16 | 200 | 117 | 220 | 0 | 800 | 500 | 17 | 5976.27 | 14567.64 | 104.26
14:00 | 0 | 51 | 17 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 452 | 17 | 17 | 52 | 123 | 195 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 305 | 0 | 0 | 26 | 143.42 | 5.5 | 22 | 0 | 385 | 45 | 16 | 57 | 0 | 11 | 0 | 0 | 17 | 12 | 12 | 0.43 | 222 | 91 | 0 | 555 | 112 | 0 | 14 | 0 | 95 | 209 | 0 | 0 | 0 | 1224 | 12 | 26 | 8 | 250 | 349 | 260 | 44 | 10 | 202 | 30 | 34 | 139 | 173 | 9 | 5 | 105 | 162 | 25 | 65 | 30 | 305 | 260 | 382 | 40 | 38 | 139 | 11 | 8 | 0 | 83 | 30 | 141 | 0 | 126 | 17 | 59 | 17.22 | 116 | 0 | 0.9 | 39.96 | 12 | 8775.43 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 37 | 1100 | 0 | 0 | 0 | 828.86 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 15.89 | 100 | 0 | 0 | 6.4 | 145 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0.67 | 161 | 53 | 112 | 28 | 0 | 0 | 0 | 0 | 5.2 | 65 | 0.42 | 16 | 200 | 117 | 220 | 0 | 800 | 499 | 17 | 5867.44 | 14642.87 | 104.26
15:00 | 0 | 51 | 17 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 482 | 17 | 17 | 52 | 125 | 195 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 317 | 0 | 0 | 7 | 143.42 | 5.5 | 22 | 0 | 440 | 15 | 16 | 57 | 0 | 23 | 0 | 0 | 17 | 12 | 12 | 1.26 | 222 | 94 | 0 | 555 | 118 | 0 | 25 | 0 | 65 | 211 | 0 | 0 | 0 | 1224 | 10 | 26 | 8 | 250 | 345 | 300 | 44 | 10 | 209 | 30 | 34 | 139 | 173 | 8 | 5 | 55 | 172 | 25 | 16 | 30 | 305 | 260 | 382 | 40 | 39 | 139 | 8 | 8 | 0 | 82 | 30 | 141 | 0 | 125 | 17 | 59 | 8.4 | 116 | 0 | 0.3 | 14.5 | 12 | 8758.38 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 24 | 1100 | 0 | 0 | 0 | 828.04 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 12.14 | 63 | 0 | 0 | 46.27 | 144 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 4.2 | 161 | 52 | 112 | 29 | 0 | 0 | 0 | 0 | 2.5 | 75 | 0.3 | 16 | 200 | 115 | 220 | 0 | 800 | 480 | 17 | 5838.45 | 14596.83 | 104.25
16:00 | 0 | 51 | 17 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 473 | 17 | 17 | 52 | 138 | 195 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 293 | 0 | 0 | 8 | 143.42 | 5.5 | 22 | 0 | 320 | 16 | 16 | 57 | 0 | 8 | 0 | 20 | 17 | 12 | 12 | 1.11 | 222 | 92 | 0 | 555 | 122 | 0 | 25 | 0 | 51 | 212 | 0 | 0 | 0 | 1224 | 4 | 26 | 8 | 250 | 354 | 290 | 44 | 5 | 214 | 20 | 34 | 138 | 173 | 13 | 5 | 47 | 168 | 25 | 26 | 30 | 310 | 260 | 357 | 40 | 38 | 144 | 5 | 8 | 0 | 82 | 30 | 141 | 0 | 126 | 17 | 59 | 7.1 | 116 | 0 | 1.2 | 1.99 | 12 | 8540.32 | 902 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 8 | 1100 | 0 | 0 | 0 | 827.81 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 31.36 | 22 | 0 | 0 | 28.23 | 145 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 2.93 | 160 | 52 | 114 | 19 | 0 | 0 | 0 | 0 | 1.5 | 105 | 0.22 | 16 | 200 | 115 | 220 | 0 | 800 | 470 | 17 | 5774.05 | 14314.37 | 104.25
17:00 | 0 | 51 | 17 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 472 | 17 | 17 | 52 | 139 | 195 | 25 | 35 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 302 | 0 | 0 | 6 | 143.42 | 5.2 | 22 | 0 | 350 | 15 | 16 | 52 | 0 | 12 | 0 | 31 | 17 | 12 | 12 | 1.18 | 220 | 91 | 0 | 555 | 120 | 0 | 25 | 0 | 47 | 171 | 0 | 0 | 0 | 1224 | 1 | 26 | 8 | 250 | 354 | 275 | 44 | 5 | 214 | 20 | 33 | 138 | 173 | 27 | 5 | 17 | 170 | 8 | 14 | 30 | 305 | 260 | 357 | 40 | 38 | 137 | 1 | 8 | 0 | 83 | 30 | 140 | 0 | 126 | 17 | 59 | 2.4 | 116 | 0 | 0.4 | 5.51 | 12 | 8461.11 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 8 | 1100 | 0 | 0 | 0 | 825.22 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 8 | 14.78 | 15 | 0 | 0 | 5.83 | 145 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0.57 | 160 | 52 | 114 | 6 | 20 | 0 | 0 | 0 | 0.9 | 61 | 0.09 | 16 | 200 | 116 | 220 | 0 | 800 | 485 | 17 | 5715.39 | 14176.5 | 104.24
18:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 443 | 35 | 17 | 52 | 140 | 195 | 45 | 55 | 108 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 1 | 143.42 | 5 | 22 | 0 | 330 | 13 | 16 | 57 | 0 | 2 | 10 | 45 | 17 | 24 | 25 | 0.02 | 219 | 93 | 0 | 555 | 120 | 0 | 25 | 0 | 47 | 0 | 0 | 0 | 0 | 1224 | 0 | 26 | 0 | 250 | 354 | 275 | 44 | 5 | 210 | 20 | 33 | 138 | 172 | 32 | 10 | 14 | 168 | 8 | 2 | 30 | 305 | 260 | 360 | 40 | 38 | 139 | 0 | 8 | 0 | 84 | 30 | 140 | 0 | 126 | 17 | 59 | 0.5 | 116 | 0 | 0 | 1.8 | 12 | 8450.74 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 3 | 1100 | 0 | 0 | 0 | 870.05 | 0 | 0 | 0 | 55 | 40 | 0 | 0 | 0 | 8 | 2.35 | 8 | 0 | 0 | 1.73 | 144 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0.14 | 158 | 50 | 115 | 2 | 39 | 0 | 0 | 0 | 0.6 | 5 | 0.04 | 16 | 200 | 116 | 220 | 0 | 800 | 625 | 17 | 5849.91 | 14300.65 | 104.21
19:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 536 | 54 | 17 | 86 | 142 | 145 | 55 | 55 | 108 | 0 | 0 | 0 | 0 | 0 | 55 | 305 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 410 | 15 | 16 | 70 | 0 | 0 | 50 | 45 | 17 | 24 | 25 | 0 | 219 | 92 | 0 | 555 | 124 | 0 | 25 | 7 | 17 | 0 | 0 | 0 | 0 | 1224 | 0 | 26 | 0 | 260 | 355 | 315 | 44 | 5 | 211 | 10 | 57 | 138 | 173 | 53 | 10 | 16 | 188 | 8 | 0 | 30 | 295 | 260 | 380 | 40 | 38 | 143 | 0 | 8 | 0 | 84 | 30 | 141 | 0 | 126 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 12 | 8900.42 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1100 | 0 | 0 | 0 | 1256.37 | 0 | 0 | 0 | 55 | 70 | 0 | 0 | 0 | 8 | 0 | 0 | 6 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 162 | 50 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 116 | 220 | 0 | 1000 | 625 | 35 | 6526.37 | 15426.79 | 104.22
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 429 | 54 | 17 | 114 | 143 | 95 | 55 | 55 | 108 | 0 | 0 | 0 | 0 | 0 | 55 | 284 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 310 | 0 | 16 | 72 | 0 | 4 | 50 | 45 | 17 | 24 | 25 | 0 | 219 | 93 | 0 | 557 | 115 | 0 | 25 | 8 | 14 | 0 | 0 | 0 | 0 | 1224 | 0 | 35 | 0 | 260 | 354 | 280 | 44 | 0 | 218 | 10 | 88 | 138 | 169 | 53 | 14 | 17 | 176 | 8 | 0 | 30 | 300 | 260 | 354 | 40 | 38 | 144 | 0 | 8 | 0 | 84 | 30 | 141 | 0 | 126 | 17 | 68 | 0 | 154 | 0 | 0 | 0 | 12 | 8565.42 | 880 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1080 | 0 | 0 | 0 | 1454.45 | 0 | 0 | 0 | 55 | 70 | 0 | 0 | 0 | 8 | 0 | 0 | 6 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 160 | 51 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 116 | 220 | 0 | 1000 | 625 | 45 | 6728.45 | 15293.87
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 443 | 54 | 17 | 115 | 144 | 95 | 55 | 55 | 108 | 0 | 0 | 0 | 0 | 0 | 55 | 293 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 315 | 0 | 16 | 72 | 0 | 5 | 50 | 45 | 21 | 24 | 25 | 0 | 219 | 92 | 0 | 675 | 88 | 0 | 0 | 8 | 14 | 0 | 0 | 0 | 0 | 1224 | 0 | 38 | 0 | 260 | 354 | 305 | 44 | 0 | 217 | 10 | 89 | 138 | 168 | 53 | 14 | 17 | 174 | 0 | 0 | 30 | 300 | 260 | 376 | 40 | 38 | 132 | 0 | 8 | 0 | 84 | 30 | 142 | 0 | 126 | 17 | 69 | 0 | 154 | 0 | 0 | 0 | 12 | 8703.42 | 880 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 15 | 0 | 1100 | 0 | 0 | 0 | 1461.98 | 0 | 0 | 0 | 57 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 160 | 51 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 117 | 220 | 0 | 1000 | 625 | 45 | 6716.98 | 15420.4 | 104.23
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 496 | 54 | 17 | 115 | 143 | 45 | 55 | 55 | 115 | 0 | 0 | 0 | 0 | 0 | 55 | 302 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 370 | 0 | 16 | 64 | 0 | 0 | 50 | 45 | 54.36 | 12 | 25 | 0 | 220 | 93 | 0 | 730 | 83 | 0 | 0 | 8 | 15 | 0 | 0 | 0 | 0 | 1224 | 0 | 68 | 0 | 230 | 355 | 300 | 44 | 0 | 217 | 20 | 88 | 138 | 169 | 53 | 15 | 16 | 176 | 0 | 0 | 30 | 305 | 260 | 378 | 40 | 38 | 148 | 0 | 8 | 0 | 84 | 28 | 139 | 0 | 126 | 17 | 78 | 0 | 154 | 0 | 0 | 0 | 0 | 8883.78 | 881 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 19 | 0 | 1100 | 0 | 0 | 0 | 1472.96 | 0 | 0 | 0 | 57 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 160 | 51 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 117 | 220 | 0 | 1000 | 657 | 35 | 6796.96 | 15680.74 | 104.22
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 449 | 54 | 17 | 115 | 143 | 110 | 55 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 330 | 27 | 16 | 64 | 0 | 3 | 50 | 45 | 54.36 | 12 | 25 | 0 | 220 | 92 | 0 | 920 | 133 | 0 | 0 | 8 | 74 | 0 | 0 | 0 | 0 | 1224 | 0 | 100 | 0 | 230 | 355 | 280 | 44 | 0 | 219 | 30 | 89 | 138 | 168 | 45 | 16 | 85 | 172 | 3 | 0 | 30 | 300 | 260 | 378 | 40 | 38 | 133 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 126 | 17 | 78 | 0 | 146 | 0 | 0 | 0 | 0 | 9263.78 | 889 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 1100 | 0 | 0 | 0 | 1479.57 | 0 | 0 | 0 | 57 | 70 | 0 | 0 | 0 | 8 | 0 | 0 | 17 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 158 | 51 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 117 | 220 | 0 | 1000 | 700 | 35 | 6916.57 | 16180.35 | 104.21
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 441 | 54 | 17 | 80 | 142 | 190 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 35 | 295 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 315 | 56 | 16 | 51 | 0 | 6 | 50 | 42 | 17 | 12 | 25 | 0 | 220 | 94 | 0 | 920 | 140 | 0 | 19 | 11 | 94 | 0 | 0 | 0 | 0 | 1225 | 0 | 103 | 0 | 230 | 355 | 270 | 51 | 0 | 219 | 30 | 89 | 138 | 169 | 30 | 16 | 102 | 182 | 52.2 | 0 | 30 | 300 | 260 | 336 | 40 | 39 | 133 | 0 | 8 | 0 | 84 | 25 | 140 | 0 | 126 | 0 | 78 | 0 | 146 | 0 | 0 | 0 | 0 | 9244.62 | 896 | 0 | 0 | 30 | 14 | 38 | 0 | 0 | 0 | 0 | 67 | 0 | 1100 | 0 | 0 | 0 | 1475.57 | 0 | 40 | 0 | 57 | 70 | 0 | 51 | 30 | 52.2 | 0 | 0 | 17 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 157 | 50 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 117 | 220 | 0 | 1000 | 700 | 17 | 7113.77 | 16358.39 | 104.21
Total KWH | 0 | 1855680 | 687360 | 0 | 0 | 0 | 0 | 0 | 9338400 | 0 | 10955380 | 655200 | 597600 | 1453824 | 3256800 | 3226440 | 530651 | 664060 | 1784160 | 0 | 0 | 0 | 0 | 0 | 669710 | 7303130 | 0 | 0 | 208200 | 3381600 | 120000 | 519120 | 0 | 8707727.27 | 520636 | 311127 | 960000 | 0 | 245280 | 448408 | 382608 | 324873 | 201600 | 361920 | 22441 | 5239611 | 1993053 | 28320 | 20640000 | 1965455 | 0 | 275040 | 95725.8 | 1050472 | 3915008 | 0 | 0 | 0 | 28619997 | 74925 | 1150836 | 301091 | 5873500 | 8102500 | 6456000 | 1032930 | 186720 | 5163000 | 644832 | 1263360 | 3283571 | 3271680 | 404040 | 126020 | 784320 | 3888000 | 295958 | 456445 | 729696 | 7286000 | 6267100 | 9156000 | 949000 | 922200 | 3345872.73 | 78686 | 134928 | 0 | 2003520 | 660000 | 3174000 | 0 | 2734520 | 223200 | 1401600 | 114508 | 2376000 | 0 | 12400 | 299130 | 267600 | 208412305.8 | 21698455 | 0 | 0 | 99840 | 124160 | 912000 | 0 | 0 | 0 | 0 | 403344 | 514080 | 26000000 | 0 | 0 | 0 | 24238909 | 0 | 52208 | 0 | 389760 | 818976 | 0 | 253648 | 93906 | 245813 | 311872 | 638200 | 109100 | 0 | 389248 | 3485545 | 0 | 0 | 0 | 0 | 0 | 8236509 | 0 | 35580 | 3935000 | 1244509 | 1973350 | 219271 | 863952 | 0 | 0 | 0 | 40637.28 | 956880 | 3547 | 277824 | 5193000 | 2798000 | 5335810 | 0 | 20305455 | 16398545.45 | 440400 | 149037333.73 | 357449639.53