## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 29-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-08-2026 | during | 29-08-2026 | during | 29-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 338 | 372 | 412 | 412 | 300 | 300 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 0 | 0 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 290 | 305 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 35 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 15 | 115 | 149.36 | 149.36 | 45 | 142 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 8 | 9 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 50 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 81 | 293 | 300 | 300 | 175 | 145 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 53 | 132 | 149 | 149 | 52 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 21 | 0 | 35 | 0 | 35 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 325 | 435 | 584 | 584 | 380 | 450 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 267 | 277 | 718 | 718 | 214 | 214 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 68 | 105 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1783 | 2558 | 5405.16 | 5370.16 | 2047.61 | 2430.61
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 221 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 217 | 216 | 216 | 210 | 210 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 91 | 104 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 21 | 14 | 32 | 14 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 36 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 19 | 37 | 42 | 42 | 25 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 45 | 60 | 95.1 | 95.1 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.34 | 0 | 4.43 | 0 | 4.43 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 91 | 92 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 25 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 84 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 16 | 90 | 163 | 163 | 88 | 160 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 8 | 18 | 28 | 18 | 28 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 557 | 565 | 575 | 575 | 575 | 575 | GT-2 U/M
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2664.84 | 2896.86 | 3322.39 | 3386.96 | 2621.93 | 2815.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 192 | 201 | 221.25 | 221.25 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 280 | 280 | 350.01 | 350.01 | 300 | 300 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 250 | 305 | 342.01 | 342.01 | 250 | 250 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 220 | 250 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 73 | 150 | 150 | 150 | 50 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 24 | 38 | 30 | 30 | 35 | 35 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 138 | 163 | 163 | 140 | 140 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 50 | 190 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 148 | 168 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 103 | 102 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 27 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 89 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 76 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1697.2 | 2016 | 2673.44 | 2608.44 | 1729.7 | 1830.7
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-08-2026 | during | 29-08-2026 | during | 29-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 9 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 174 | 120 | 170 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 78 | 70 | 90 | 70 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 18.82 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 227.02 | 293 | 546.6 | 546.5 | 282.1 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 127 | 151 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 142 | 142 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 22 | 84 | 84 | 22 | 22 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 125 | 125 | 120 | 120 | 120 | 120 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 8 | 8 | 8 | 8 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 265 | 258 | 341 | 341 | 260 | 260 | Gas shortage
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 366 | 380 | 380 | 310 | 310 | Gas shortage
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 300 | 397 | 383 | 383 | 383 | 383 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1455 | 1501 | 1719 | 1719 | 1450 | 1450
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 906 | 905 | 0 | 0 | 0 | 0 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 105 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 63 | 0 | 91 | 0 | 91 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1037 | 920 | 920 | 920 | 1100 | 1100 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2006 | 1930 | 1991 | 1900 | 1236 | 1145
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 945 | 1100 | 1000 | 1000 | 1000 | 1100 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 32 | 64 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 116 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 510 | 510 | 500 | 500 | 500 | 500 | machine problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 35 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 200 | 307 | 307 | 200 | 200 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.19 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2039.19 | 2245 | 2408 | 2407 | 2074 | 2173
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 50.26 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 124 | 129 | 220 | 220 | 130 | 130 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 390 | 414 | 413.79 | 413.79 | 372 | 372 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 10 | 22 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 55 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 4.51 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1233.78 | 1210.09 | 1469.13 | 1469.13 | 900 | 900 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 40.74 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 52 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1948.29 | 2038.09 | 3221.04 | 3003.12 | 1798.12 | 1730.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 45 | 50 | 45 | 45 | 48 | 48 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 159 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 92 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.2 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 114 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 39 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 200 | 0 | 182.21 | 0 | 182.21 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 563.2 | 416 | 685.21 | 467 | 575.21 | 392
System Total |  |  |  |  | 28843.2 | 29158.791 | 14383.74 | 15893.95 | 21971.84 | 21408.18 | 13814.67 | 14256.01
Forecast Scenario (29-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15440 |  | 2320.65 |  | 17870
|  |  |  | 1:00 | 14620 |  | 2454.35 |  | 17190
|  |  |  | 2:00 | 14570 |  | 2091.45 |  | 16760
|  |  |  | 3:00 | 14170 |  | 2311.1 |  | 16590
|  |  |  | 4:00 | 14100 |  | 2234.7 |  | 16440
|  |  |  | 5:00 | 13990 |  | 1843.15 |  | 15920
|  |  |  | 6:00 | 13760 |  | 1317.9 |  | 15140
|  |  |  | 7:00 | 13640 |  | 1279.7 |  | 14980
|  |  |  | 8:00 | 13645 |  | 1160.325 |  | 14860
|  |  |  | 9:00 | 13340 |  | 1451.6 |  | 14860
|  |  |  | 10:00 | 13770 |  | 1002.75 |  | 14820
|  |  |  | 11:00 | 13900 |  | 1012.3 |  | 14960
|  |  |  | 12:00 | 14380 |  | 1203.3 |  | 15640
|  |  |  | 13:00 | 14860 |  | 1117.35 |  | 16030
|  |  |  | 14:00 | 14320 |  | 1470.7 |  | 15860
|  |  |  | 15:00 | 14150 |  | 2483 |  | 16750
|  |  |  | 16:00 | 14045 |  | 2592.825 |  | 16760
|  |  |  | 17:00 | 13710 |  | 2893.65 |  | 16740
|  |  |  | 18:00 | 13750 |  | 2215.6 |  | 16070
|  |  |  | 18:30 | 15400 |  | 1528 |  | 17000
|  |  |  | 19:00 | 15110 |  | 2769.5 |  | 18010
|  |  |  | 19:30 | 15310 |  | 2740.85 |  | 18180
|  |  |  | 20:00 | 15830 |  | 2550 |  | 18500
|  |  |  | 21:00 | 15900 |  | 2703 |  | 18730
|  |  |  | 22:00 | 15700 |  | 2167.85 |  | 17970
|  |  |  | 23:00 | 15500 |  | 2225.15 |  | 17830
Probable Maximum Temperature: |  |  | 27.00°C
Probable Maximum Demand at Day Peak: |  |  | 15640.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2703
Probable Maximum Demand at Evening Peak: |  |  | 18730.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15900.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 346.20 MKWHr. |  | 698 | 190 | 315 | 350 | 150 | 350 | 100 | 300 | 250 | 2703
*** This report is generated digitally from Operation Information System (OIS) at 09:13 hrs on 29-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-08-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14383.74 | MW | 12:00 Hr. | Energy Generated |  |  | 349.7995 |  | MKWHr.
| Day Peak Demand |  |  | 15888.74 | MW | 12:00 Hr. | Energy Unserverd |  |  | 43.007 |  | MKWHr.
| Evening Peak Generation |  |  | 15893.95 | MW | 21:00 Hr. | Energy Demand |  |  | 392.8065 |  | MKWHr.
| Evening Peak Demand |  |  | 17378.95 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.4 |  | °C
| Minimum Generation of the Day |  |  | 13338.92 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 855.71 |  | MMCFD
| Maximum Generation of the Day |  |  | 15893.95 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.6968 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.9776 | 0 | 15.6085 | 0 | 0 | 0.12649 | 0 | 0 | 47.7126 | Gas | 123.2146 | Gas | 425033552.7963
| Chattogram Zone |  |  | 5.8615 | 42.1855 | 11.8614 | 0 | 5.3445 | 0.11499 | 0 | 0.33216 | 65.7 | Coal | 113.5258 | Coal | 806426387.4027
| Cumilla Zone |  |  | 29.465 | 0 | 10.0893 | 0 | 0 | 0.45038 | 3.6154 | 0 | 43.62 | HFO | 51.5005 | HFO | 1051677069.654
| Mymensingh Zone |  |  | 0 | 0 | 4.872 | 0 | 0 | 0.31114 | 0 | 0 | 5.1831 | HSD | 0.83296 | HSD | 21831640.8
| Sylhet Zone |  |  | 35.7502 | 0 | 0 | 0 | 0 | 0.044305 | 0 | 0 | 35.7945 | Hydro | 5.3445 | Hydro | 534448.5
| Khulna Zone |  |  | 0 | 24.2036 | 0.98635 | 0.36424 | 0 | 0.49248 | 21.8029 | 0 | 47.8496 | Solar | 3.9191 | Solar | 63066789.4716
| Barishal Zone |  |  | 8.0538 | 42.1668 | 1.4835 | 0 | 0 | 0.00214 | 0 | 0 | 51.7063 | Import | 51.1299 | Import | 318881225.72
| Rajshahi Zone |  |  | 12.1065 | 0 | 2.7879 | 0 | 0 | 0.99021 | 25.7116 | 0 | 41.5962 | Wind | 0.33216 | Wind | 4886073.6
| Rangpur Zone |  |  | 0 | 4.9699 | 3.8115 | 0.46872 | 0 | 1.387 | 0 | 0 | 10.6371
| Total |  |  | 123.2146 | 113.5258 | 51.5005 | 0.83296 | 5.3445 | 3.9191 | 51.1299 | 0.33216 | 349.7995
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 425033552.7963 |  | Hydro | 534448.5
|  |  |  | Coal | 806426387.4027 |  | Solar | 63066789.4716
|  |  |  | HFO | 1051677069.654 |  | Import | 318881225.72
|  |  |  | HSD | 21831640.8 |  | Wind | 4886073.6
[5 empty] | Total: | 269,23,37,187 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8029 | Peak Hr Flow | 905.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35860836.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.7116 | Peak Hr Flow | 1210.09 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1253 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.6154 | Peak Hr Flow | 168.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2100 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.1299 | Peak Hr Flow | 2283.09 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 335 |  | 5726
|  |  |  | Chattogram |  | 29 |  | 1494
|  |  |  | Cumilla |  | 266 |  | 1717
|  |  |  | Mymensingh |  | 326 |  | 1504
|  |  |  | Sylhet |  | 49 |  | 715
|  |  |  | Khulna |  | 70 |  | 2020
|  |  |  | Barishal |  | 0 |  | 533
|  |  |  | Rajshahi |  | 195 |  | 1779
|  |  |  | Rangpur |  | 151 |  | 1188
|  |  |  | Total |  | 1421 |  | 16676
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:56 | 14:53 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Scheduled S/D Due to From other end.
| 09:09 |  | Maniknagar 132/33kV S/S Haripur Ckt-2 Project Work S/D Due to Requirement of DPDC for
their project work at Green Model Town area, Only Earth switch operated ( close). CB and
DS were open always from our end
| 09:14 | 21:29 | Noapara 132/33kV S/S T-2 LT Scheduled S/D Due to Changing Conductor, Clump & Connector of
(33kV REB-1 & T-3) Feeder.
| 09:15 | 21:27 | Noapara 132/33kV S/S T-2 HT Scheduled S/D Due to Changing Conductor, Clump & Connector of
(33kV REB-1 & T-3) Feeder.
| 09:21 | 21:34 | Noapara 132/33kV S/S Bus Section-2 Scheduled S/D Due to Changing Conductor, Clump &
Connector of (33kV REB-1 & T-3) Feeder.
| 09:44 | 21:21 | Halishahar-Julda 132kV Ckt-1 Forced S/D from Juldah 132/33kV end Due to Due to the earth
wire of the river-crossing tower on the 132 kV Julda-Halishahar circuit has snapped and
fallen into the river.
|  | 10:22 | Fenchuganj 230/132/33kV S/S TR-02 LT is restored.
|  | 10:22 | Fenchuganj 230/132/33kV S/S TR-02 HT is restored.
|  | 11:14 | Bheramara HVDC-Baharampur 400kV Ckt-2 is restored.
|  | 14:05 | Cox'sbazar-Dohazari 132 kV Ckt-2 is restored.
|  | 14:51 | Maniknagar-Matuail 132kV Ckt-1 is restored.
|  | 18:09 | Barapukuria-Bogura 230 kV Ckt-2 is restored.
| 19:38 | 19:54 | Cumilla(S) 132/33kV S/S TR-1 LT Tripped showing RET 650 & REF 615 relays Due to 33 KV | [7 empty] | 30.0MW load
|  |  | Laksam PDB feeder fault. | [7 empty] | interrup.
| 21:00 |  | Evening Peak Generation: 15894 MW.
| 00:05 | 01:12 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Forced S/D Due to Red hot maintenance | [7 empty] | 30.0MW load
|  |  | of 33kv Bus | [7 empty] | interrup.
| 00:07 | 01:10 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Forced S/D Due to Red hot maintenance | [7 empty] | 30.0MW load
|  |  | of 33kv Bus | [7 empty] | interrup.
|  | 01:57 | Ashuganj-Kishoreganj 132kV Ckt-1 is restored.
|  | 01:58 | Kishoreganj-Mymensingh 132kV Ckt-1 is restored.
| 02:07 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- ST
| 03:12 |  | Ashuganj North CCPP was shut down due to offline water wash purposes.
| 03:12 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
| 05:20 | 06:27 | Brahmanbaria 132/33kV S/S 403T LT Tripped showing EF & OC relays. | [7 empty] | 60.0MW load
interrup.
| 06:08 |  | Brahmanbaria 132/33kV S/S 401T HT Forced S/D | [7 empty] | 30.0MW load
interrup.
| 07:02 |  | Patiya 132/33kV S/S TRAFO-01 LT Scheduled S/D Due to Corrective red hot maintenance | [7 empty] | 15.0MW load
interrup.
| 07:02 |  | Patiya 132/33kV S/S TRAFO-01 HT Scheduled S/D Due to Corrective red hot maintenance | [7 empty] | 16.0MW load
interrup.
| 07:10 |  | Chandpur 132/33kV S/S 402T (T-01) LT Scheduled S/D Due to Bus section -01 shutdown
| 07:10 |  | Chandpur 132/33kV S/S 402T (T-01) HT Scheduled S/D Due to Bus section-1 shutdown
| 07:10 |  | Chandpur 132/33kV S/S 33 kV T-1 Section Scheduled S/D Due to Maintenance Work for High | [7 empty] | 17.0MW load
|  |  | Temperature | [7 empty] | interrup.
|  | 07:10 | Chandpur 132/33kV S/S 412T (T-2) LT is restored.
| 07:30 |  | Mongla 132/33kV S/S 33 KV Bus Scheduled S/D Due to 33 KV Bus-Bar Shutdown Due to Red Hot | [7 empty] | 27.0MW load
|  |  | Mentanence by WZPDCL | [7 empty] | interrup.
| 07:30 |  | Mongla 132/33kV S/S T-2 LT Scheduled S/D Due to 33 KV Bus-Bar Shutdown Due to Red Hot | [7 empty] | 21.0MW load
|  |  | Mentanence BY WZPDCL. | [7 empty] | interrup.
| 07:30 |  | Mongla 132/33kV S/S T-1 LT Scheduled S/D Due to 33 KV Bus-Bar Shutdown Due to Red Hot | [7 empty] | 21.0MW load
|  |  | Mentanence by WZPDCL. | [7 empty] | interrup.
| 07:31 |  | Mongla 132/33kV S/S T-1 HT Scheduled S/D Due to 33 KV Bus-Bar Shutdown Due to Red Hot | [7 empty] | 6.0MW load
|  |  | Mentanence by WZPDCL. | [7 empty] | interrup.
| 07:31 |  | Mongla 132/33kV S/S T-2 HT Scheduled S/D Due to 33 KV Bus-Bar Shutdown Due to Red Hot | [7 empty] | 21.0MW load
|  |  | Mentanence by WZPDCL. | [7 empty] | interrup.
|  | 07:35 | Bagerhat-Goalpara 132 kV Ckt-1 is restored.
| 07:41 |  | Noapara 132/33kV S/S T-1 LT Scheduled S/D Due to T-1 Transformer 33 kv side (Y-phase)
high tem. point maintenance.
| 07:42 |  | Noapara 132/33kV S/S T-1 HT Scheduled S/D Due to T-1 Transformer 33 kv side (Y-phase)
high tem. point maintenance.
| 07:45 |  | Bagerhat-Labanchura 132 kV Ckt-2 Project Work S/D from Bagerhat 132/33kV end Due to Tower
errection and stringing work on Tower No 69.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-08-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 372 | 8388000 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 96711 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | -
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 305 | 7148194 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 695160 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 115 | 1661280 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 706251 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 656978 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 9 | 208830 | Gas shortage
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 485640 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 816960 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 293 | 2903771 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1569456 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1752960 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2031840 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 126487 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 644760 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 435 | 9564090.91 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 277 | 6182880 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 105 | 2072400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2558 | 47712648.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 402193.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 90990 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1211040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5344485 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 5165487 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 104 | 2461418 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 21 | 287088 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 347865 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 36 | 420480 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 37 | 696000 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 60 | 1043520 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24000 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 381382 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 390331 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 2240618 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 369600 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 1518000 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 90 | 787855 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28614543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 332160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 565 | 13570909.09 | GT-2 U/M
Chattogram Area Total |  |  |  |  | 4885.967 | 2896.86 | 65699964.89
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 201 | 4951000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 280 | 7454000 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 305 | 6772000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 250 | 5596000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 83952 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1246350 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 2213018 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 706656 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 138 | 2917140 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 190 | 2407680 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 168 | 3615360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 767414 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 444550 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 102 | 2470380 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 177240 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 1346880 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 450382 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 2016 | 43620002
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 110656 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10850 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 174 | 2683200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1480800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 189630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 558960 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 149040 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 293 | 5183136
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 44305 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 951000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3449372.73 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 3241700 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 22 | 697920 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 125 | 3723660 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 44400 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 258 | 6063000 | Gas shortage
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 8601000 | Gas shortage
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 397 | 8978100 | -
Sylhet Area Total |  |  |  |  | 2325 | 1501 | 35794457.73
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 905 | 21802909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 183840 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 802512 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 492480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 364236 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 920 | 24203640 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1930 | 47849617
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 24116364 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 64 | 1016736 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 116 | 2762000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 510 | 13185454.55 | machine problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5291820 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 466800 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 200 | 4865000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2140 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2245 | 51706314.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 244648 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 241018 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 129 | 3219282 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 414 | 8887200 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 316516 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 200443 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 808400 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 823872 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 55 | 397632 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 29280 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1210.09 | 25711636 | Coal shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 317632 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 398650 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2038.09 | 41596209
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 468720 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1063854 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 159 | 3906000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 1086326 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 40525.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2725190 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 167126 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1179360 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 416 | 10637101.56
Eastern Grid Total |  |  |  |  | 17427.666 | 9264.86 | 198010209.53
Western Grid Total |  |  |  |  | 11731.125 | 6629.09 | 151789242.11
National Grid Total |  |  |  |  | 29158.791 | 15893.95 | 349799451.64
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-08-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10151.45 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5103.8 | MW
i) Dhaka area |  |  | 5391.05 |  | MW | i) Khulna area |  |  |  | 1950 | MW
ii) Chattogram area |  |  | 1465.4 |  | MW | ii) Barishal area |  |  |  | 533.2 | MW
iii) Cumilla area |  |  | 1451 |  | MW | iii) Rajshahi area |  |  |  | 1583.6 | MW
iv) Mymensingh area |  |  | 1178 |  | MW | iv) Rangpur area |  |  |  | 1037 | MW
v) Sylhet area |  |  | 666 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15255.25 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 140 | 20:00 | 133 | Narshingdi | 198 | 20:00 | 199 | Uttara | 98 | 19:00
2 | AKSML | 151.9 | 10:00 | 68 | Hasnabad | 97 | 21:00 | 134 | Natore | 177 | 20:00 | 200 | UttaraNew | 57 | 00:00
3 | Aftabnagar | 50 | 00:00 | 69 | Hathazari | 109 | 01:00 | 135 | Nawabganj | 54.7 | 20:00 | 201 | Zigatola | 118 | 00:00
4 | Agargaon | 121 | 00:00 | 70 | Hatirjheel | 63 | 15:00 | 136 | Netrakona | 119 | 20:00
5 | Agrabad | 60 | 20:00 | 71 | Ishurdi | 78 | 18:30 | 137 | New | 86.5 | 00:00
6 | Amnura | 34 | 22:00 | 72 | Jaldhaka | 96 | 21:00 | 138 | Niamatpur | 71 | 22:00
7 | Ashuganj | 91 | 01:00 | 73 | Jamalpur | 138 | 22:00 | 139 | Noapara | 42.5 | 23:00
8 | BSRM | 207 | 02:00 | 74 | Jashore | 177 | 00:00 | 140 | PHP | 11 | 02:00
9 | Bagerhat | 94 | 19:30 | 75 | Jhenaidah | 106 | 22:00 | 141 | Pabna | 104 | 19:00
10 | Bajitpur | 92 | 18:30 | 76 | Joydebpur | 138 | 12:00 | 142 | Palashbari | 136 | 21:00
11 | Bakerganj | 15.2 | 21:00 | 77 | Joypurhat | 57 | 20:00 | 143 | Panchagarh | 80 | 00:00
12 | Bakulia | 90 | 19:30 | 78 | Juldah | 15 | 00:00 | 144 | Patiya | 19.6 | 14:00
13 | Banani | 40 | 15:00 | 79 | KSRM | 36 | 22:00 | 145 | Patnitala | 33 | 19:30
14 | Bangabhaban | 4 | 10:00 | 80 | Kabirpur | 240 | 20:00 | 146 | Patuakhali | 75 | 21:00
15 | Barapukuria | 62 | 22:00 | 81 | Kachua | 94 | 22:00 | 147 | Payra | 38 | 18:30
16 | Barguna | 22 | 19:00 | 82 | Kaliganj | 41 | 22:00 | 148 | Postogola | 68 | 00:00
17 | Barishal | 100 | 12:00 | 83 | Kallyanpur | 138 | 00:00 | 149 | Pubail | 46 | 21:00
18 | Barishal-230 | 110 | 19:00 | 84 | Kalurghat | 31 | 00:00 | 150 | Purbachal | 26 | 00:00
19 | Baroaulia | 68 | 07:00 | 85 | Kamrangirchar | 80 | 00:00 | 151 | Purbasadipur | 138 | 13:00
20 | Baroirhat | 69 | 21:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 36 | 18:30
21 | Bashundhara | 225 | 00:00 | 87 | Kasba | 36 | 19:30 | 153 | Rahim | 34 | 11:00
22 | BashundharaCement | 6 | 00:00 | 88 | Kazla | 113 | 01:00 | 154 | Rajbari | 96 | 21:00
23 | Beanibazar | 86 | 20:00 | 89 | Keranigonj | 85 | 13:00 | 155 | Rajendrapur | 115 | 12:00
24 | Benapole | 56 | 13:00 | 90 | Khagrachori | 36 | 18:30 | 156 | Rajshahi | 126 | 12:00
25 | Bhaluka | 159 | 19:00 | 91 | Khulna | 61 | 13:00 | 157 | Rajshahi-230 | 110 | 13:00
26 | Bhandaria | 62 | 21:00 | 92 | Khulshi | 173 | 16:00 | 158 | Ramganj | 108 | 18:30
27 | Bhangura | 40 | 04:00 | 93 | Kishoreganj | 112 | 19:00 | 159 | Rampur | 44 | 18:30
28 | Bheramara(GK) | 69 | 03:00 | 94 | Kodda | 296 | 12:00 | 160 | Rangamati | 21 | 13:00
29 | Bhulta | 233 | 19:30 | 95 | Kulaura | 59 | 20:00 | 161 | Rangpur | 128 | 13:00
30 | Bog-Sherpur | 70 | 04:00 | 96 | Kurigram | 80 | 20:00 | 162 | Ruppur | 4 | 10:00
31 | Bogura | 220 | 00:00 | 97 | Kushtia | 157 | 21:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 82 | 21:00 | 98 | Laksam | 37 | 22:00 | 164 | Saidpur | 93 | 23:00
33 | Brahmanbaria | 129 | 21:00 | 99 | Lakshmipur | 42 | 21:00 | 165 | Santhia | 38 | 23:00
34 | Cantonment | 132 | 13:00 | 100 | Lalbag | 78 | 01:00 | 166 | Satkhira | 139 | 21:00
35 | Chandina | 31 | 02:00 | 101 | Lalmonirhat | 60 | 18:30 | 167 | Satmasjid | 110 | 00:00
36 | Chandpur | 84 | 22:00 | 102 | MI_Cement | 16.5 | 01:00 | 168 | Savar | 180 | 09:00
37 | Chandraghona | 35 | 18:30 | 103 | Madanganj | 45 | 11:00 | 169 | SevenRings | 16.69 | 00:00
38 | Chapai | 74 | 22:00 | 104 | Madaripur | 121 | 21:00 | 170 | ShahCement | 30 | 10:00
39 | Charfasson | 35 | 21:00 | 105 | Madartek | 96 | 23:00 | 171 | Shahjadpur | 80 | 21:00
40 | Charsaidpur | 43 | 15:00 | 106 | Madunaghat | 53 | 11:00 | 172 | Shahjibazar | 134 | 00:00
41 | Chauddagram | 72 | 20:00 | 107 | Magura | 68 | 18:30 | 173 | Shahmirpur | 56 | 00:00
42 | Chhatak | 41 | 21:00 | 108 | Mahasthangarh | 76 | 03:00 | 174 | Shariatpur | 114 | 21:00
43 | Chowmuhani | 149 | 23:00 | 109 | Maijdee | 35 | 19:30 | 175 | Sherpur | 170 | 21:00
44 | Chuadanga | 131 | 20:00 | 110 | Manikganj | 151 | 19:30 | 176 | Shikalbaha | 33 | 22:00
45 | Coxsbazar | 145 | 21:00 | 111 | Maniknagar | 81 | 13:00 | 177 | Shitalakhya | 72.2 | 00:00
46 | Cumilla(N) | 137 | 18:30 | 112 | Matarbari | 56 | 20:00 | 178 | Sholosohor | 44 | 20:00
47 | Cumilla(S) | 176 | 23:00 | 113 | Matuail | 76 | 00:00 | 179 | Shomvuganj | 46 | 19:30
48 | Daganbhuiyan | 40 | 18:30 | 114 | Metrorail_Motijheel | 23 | 17:00 | 180 | Shyampur | 156 | 12:00
49 | Daudkandi | 136 | 20:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 128 | 00:00
50 | DhakaUniversity | 52 | 00:00 | 116 | Millgate | 78 | 00:00 | 182 | Sirajganj | 126 | 00:00
51 | Dhamrai | 110 | 21:00 | 117 | Mirpur | 157 | 00:00 | 183 | Sitakunda | 13 | 18:30
52 | Dhanmondi | 97 | 19:00 | 118 | Mirsorai | 44 | 09:00 | 184 | Sonargaon | 144 | 00:00
53 | Dohazari | 110 | 20:00 | 119 | Mirzapur | 46 | 21:00 | 185 | Sreemongol | 88 | 21:00
54 | Faridpur | 191 | 23:00 | 120 | Mithapukur | 76 | 18:30 | 186 | Sreepur | 120 | 20:00
55 | Fatullah | 104 | 00:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 54.2 | 21:00
56 | Fenchuganj | 47 | 20:00 | 122 | Mogbazar | 29.2 | 23:00 | 188 | Sunamganj | 62 | 20:00
57 | Feni | 105 | 19:00 | 123 | Mongla | 40 | 00:00 | 189 | Sylhet | 117 | 00:00
58 | GPH | 1 | 00:00 | 124 | Motijheel | 44 | 00:00 | 190 | Sylhet_(South) | 69 | 00:00
59 | Ghatail | 98 | 21:00 | 125 | Muktagacha | 43 | 08:00 | 191 | TK | 0 | 00:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 116 | 20:00 | 192 | Tangail | 198 | 20:00
61 | Ghorashal-230 | 106 | 21:00 | 127 | Muradnagar | 48 | 23:00 | 193 | Taraganj | 34 | 18:30
62 | Goalpara | 42 | 00:00 | 128 | Mymensingh | 136 | 22:00 | 194 | Tasnim | 37 | 00:00
63 | Gollamari | 108 | 12:00 | 129 | Nabinagar | 106 | 00:00 | 195 | Thakurgaon | 114 | 23:00
64 | Gopalganj | 127 | 20:00 | 130 | Naogaon | 128 | 21:00 | 196 | Tongi | 144 | 19:30
65 | Gulshan | 94 | 18:30 | 131 | Narail | 59 | 23:00 | 197 | Ullahpara | 40 | 09:00
66 | Halishahar | 80.5 | 10:00 | 132 | Narinda | 53 | 00:00 | 198 | Ullon | 67 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-08-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15439.91 | 3131 |  | 18711.91
1:00 | 14623.84 | 3244 |  | 18013.84
2:00 | 14570.69 | 3066 |  | 17774.69
3:00 | 14171.48 | 3090 |  | 17400.48
4:00 | 14093.4 | 2915 |  | 17139.4
5:00 | 13986.52 | 2840 |  | 16954.52
6:00 | 13758.99 | 2636 |  | 16513.99
7:00 | 13644.94 | 2249 |  | 15994.94
8:00 | 13645.29 | 1996 |  | 15731.29
9:00 | 13338.92 | 1396 |  | 14797.92
10:00 | 13766.3 | 1206 |  | 15026.3
11:00 | 13899.4 | 1343 |  | 15302.4
12:00 | 14383.74 | 1440 |  | 15888.74
13:00 | 14859.67 | 1066 |  | 15973.67
14:00 | 14322.06 | 1062 |  | 15432.06
15:00 | 14147.61 | 1282 |  | 15487.61
16:00 | 14045.05 | 1038 |  | 15130.05
17:00 | 13708.62 | 923 |  | 14673.62
18:00 | 13751.94 | 386 |  | 14154.94
19:00 | 15113.88 | 1286 |  | 16457.75
19:30 | 15314.95 | 1229 |  | 16599.26
20:00 | 15835.21 | 742 |  | 16610.21
21:00 | 15893.95 | 1421 |  | 17378.95
22:00 | 15623.97 | 1495 |  | 17185.97
23:00 | 15553.84 | 1754 |  | 17386.84
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 28-08-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 160 | 47 | 386 | 146 | 1554 | 646 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 129 | 36 | 336 | 116 | 1508 | 590
2:00 | 124 | 35 | 330 | 130 | 1438 | 582 |  | Import | 0
3:00 | 93 | 41 | 204 | 136 | 1228 | 588
4:00 | 86 | 40 | 192 | 142 | 1142 | 578 | Ishurdi-Ghorashal Ckt-2 | Export | 2622836.36
5:00 | 98 | 42 | 234 | 154 | 1162 | 564
6:00 | 104 | 42 | 246 | 140 | 1182 | 560 |  | Import | 0
7:00 | 88 | 34 | 228 | 146 | 1142 | 528
8:00 | 93 | 36 | 244 | 162 | 1144 | 548 | Sirajganj-Sreepur Ckt-1 | Export | 1741000
9:00 | 133 | 46 | 322 | 160 | 1284 | 602
10:00 | 129 | 32 | 320 | 144 | 1356 | 598 |  | Import | 0
11:00 | 132 | 33 | 340 | 140 | 1360 | 600
12:00 | 141 | 25 | 404 | 134 | 1406 | 590 | Sirajganj-Sreepur Ckt-2 | Export | 1747000
13:00 | 139 | 33 | 380 | 164 | 1408 | 652
14:00 | 114 | 39 | 290 | 170 | 1274 | 622 |  | Import | 0
15:00 | 116 | 44 | 306 | 176 | 1292 | 638
16:00 | 119 | 46 | 320 | 180 | 1264 | 662 | Gopalganj-Aminbazar Ckt-1 | Export | 14860000
17:00 | 121 | 48 | 312 | 172 | 1258 | 678
18:00 | 110 | 36 | 268 | 142 | 1196 | 640 |  | Import | 0
18:30 | 111 | 28 | 310 | 170 | 1222 | 596
19:00 | 93 | 32 | 294 | 144 | 1154 | 536 | Gopalganj-Aminbazar Ckt-2 | Export | 14890000
19:30 | 97 | 28 | 292 | 140 | 1126 | 534
20:00 | 79 | 9 | 264 | 144 | 998 | 488 |  | Import | 0
21:00 | 67 | 6 | 222 | 126 | 964 | 470
22:00 | 85 | 17 | 254 | 130 | 1042 | 506 |  | Total Export | 35860836.36
23:00 | 99 | 23 | 310 | 142 | 1142 | 534 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-08-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8423.2 | 7016.71 | 15439.91 | DAILY GENERATION CURVE
00:30 | 8216.7 | 6815.175 | 15031.875
01:00 | 8010.2 | 6613.64 | 14623.84 | 28-08-2026
01:30 | 7989.45 | 6607.815 | 14597.265
02:00 | 7968.7 | 6601.99 | 14570.69
02:30 | 8051.2 | 6319.885 | 14371.085
03:00 | 8133.7 | 6037.78 | 14171.48
03:30 | 8130.45 | 6001.99 | 14132.44
04:00 | 8127.2 | 5966.2 | 14093.4
04:30 | 8069.7 | 5970.26 | 14039.96
05:00 | 8012.2 | 5974.32 | 13986.52
05:30 | 7944.97 | 5927.785 | 13872.755
06:00 | 7877.74 | 5881.25 | 13758.99
06:30 | 7787.655 | 5914.31 | 13701.965
07:00 | 7697.57 | 5947.37 | 13644.94
07:30 | 7647.105 | 5998.01 | 13645.115
08:00 | 7596.64 | 6048.65 | 13645.29
08:30 | 7470.215 | 6021.89 | 13492.105
09:00 | 7343.79 | 5995.13 | 13338.92
09:30 | 7472.815 | 6079.795 | 13552.61
10:00 | 7601.84 | 6164.46 | 13766.3
10:30 | 7657.55 | 6175.3 | 13832.85
11:00 | 7713.26 | 6186.14 | 13899.4
11:30 | 7770.16 | 6371.41 | 14141.57
12:00 | 7827.06 | 6556.68 | 14383.74
12:30 | 8002.165 | 6619.54 | 14621.705
13:00 | 8177.27 | 6682.4 | 14859.67
13:30 | 8178.725 | 6412.14 | 14590.865
14:00 | 8180.18 | 6141.88 | 14322.06
14:30 | 8112.33 | 6122.505 | 14234.835
15:00 | 8044.48 | 6103.13 | 14147.61
15:30 | 8010.33 | 6086 | 14096.33
16:00 | 7976.18 | 6068.87 | 14045.05
16:30 | 7886.11 | 5990.725 | 13876.835
17:00 | 7796.04 | 5912.58 | 13708.62
17:30 | 7857.845 | 5872.435 | 13730.28
18:00 | 7919.65 | 5832.29 | 13751.94
18:30 | 8288.285 | 6144.625 | 14432.91
19:00 | 8656.92 | 6456.96 | 15113.88
19:30 | 8817.92 | 6497.03 | 15314.95
20:00 | 9202.92 | 6632.29 | 15835.21
20:30 | 9233.89 | 6630.69 | 15864.58 |  | Executive Engineer
21:00 | 9264.86 | 6629.09 | 15893.95 |  | Network Operation Division
21:30 | 9140.36 | 6618.6 | 15758.96
22:00 | 9015.86 | 6608.11 | 15623.97
22:30 | 8965.68 | 6623.225 | 15588.905
23:00 | 8915.5 | 6638.34 | 15553.84

## En-Curve
QF-LDC-12
Date | 28-08-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3568 | 1411 | 905 | 0 | 176 | 1393.71 | 222 | 4799 | 0 | 576 | 2068.2 | 315 | 0 | 6 | 3131 | DAILY ENERGY CURVE
00:30 | 3551 | 1388.5 | 904.5 | 0 | 173 | 1352.175 | 221 | 4784.5 | 0 | 506.5 | 1824.2 | 315 | 0 | 11.5 | 3187.5 | 28-08-2026
01:00 | 3534 | 1366 | 904 | 0 | 170 | 1310.64 | 220 | 4770 | 0 | 437 | 1580.2 | 315 | 0 | 17 | 3244
01:30 | 3559 | 1360 | 904.5 | 0 | 166 | 1303.815 | 219.5 | 4771.5 | 0 | 399 | 1588.45 | 315 | 0 | 10.5 | 3155 | Energy Generated | 349.7995 |  | MKWHr
02:00 | 3584 | 1354 | 905 | 0 | 162 | 1296.99 | 219 | 4773 | 0 | 361 | 1596.7 | 315 | 0 | 4 | 3066 | Energy not Served | 43.007 |  | MKWHr
02:30 | 3663 | 1398 | 904.5 | 0 | 157 | 1131.885 | 218 | 4776.5 | 0 | 344 | 1590.2 | 182.5 | 0 | 5.5 | 3078 | Total Energy Requirement | 392.8065 |  | MKWHr
03:00 | 3742 | 1442 | 904 | 0 | 152 | 966.78 | 217 | 4780 | 0 | 327 | 1583.7 | 50 | 0 | 7 | 3090
03:30 | 3749.5 | 1452 | 904 | 0 | 149 | 952.49 | 217 | 4783 | 0 | 327 | 1564.45 | 25 | 0 | 9 | 3002.5
04:00 | 3757 | 1462 | 904 | 0 | 146 | 938.2 | 217 | 4786 | 0 | 327 | 1545.2 | 0 | 0 | 11 | 2915
04:30 | 3749 | 1452 | 904 | 0 | 144 | 939.26 | 218 | 4778.5 | 0 | 326.5 | 1513.7 | 0 | 0 | 15 | 2877.5
05:00 | 3741 | 1442 | 904 | 0 | 142 | 940.32 | 219 | 4771 | 0 | 326 | 1482.2 | 0 | 0 | 19 | 2840
05:30 | 3728.5 | 1414.5 | 904 | 0 | 141 | 929.86 | 219.5 | 4746.5 | 2.695 | 312.5 | 1457.7 | 0 | 0 | 16 | 2738
06:00 | 3716 | 1387 | 904 | 0 | 140 | 919.4 | 220 | 4722 | 5.39 | 299 | 1433.2 | 0 | 0 | 13 | 2636
06:30 | 3689 | 1388.5 | 904.5 | 0 | 139 | 924.225 | 221 | 4725 | 39.54 | 260.5 | 1401.7 | 0 | 0 | 9 | 2442.5
07:00 | 3662 | 1390 | 905 | 0 | 138 | 929.05 | 222 | 4728 | 73.69 | 222 | 1370.2 | 0 | 0 | 5 | 2249
07:30 | 3631 | 1379 | 905 | 0 | 134 | 928.205 | 221.5 | 4743 | 128.21 | 204.5 | 1363.2 | 0 | 0 | 7.5 | 2122.5
08:00 | 3600 | 1368 | 905 | 0 | 130 | 927.36 | 221 | 4758 | 182.73 | 187 | 1356.2 | 0 | 0 | 10 | 1996
08:30 | 3433 | 1313.5 | 901.5 | 0 | 133 | 928.48 | 221.5 | 4720 | 270.425 | 181 | 1378.2 | 0 | 0 | 11.5 | 1696
09:00 | 3266 | 1259 | 898 | 0 | 136 | 929.6 | 222 | 4682 | 358.12 | 175 | 1400.2 | 0 | 0 | 13 | 1396
09:30 | 3321.5 | 1385.5 | 902 | 0 | 140 | 932.79 | 222 | 4672.5 | 375.87 | 175 | 1412.95 | 0 | 0 | 12.5 | 1301
10:00 | 3377 | 1512 | 906 | 0 | 144 | 935.98 | 222 | 4663 | 393.62 | 175 | 1425.7 | 0 | 0 | 12 | 1206
10:30 | 3447 | 1436 | 905.5 | 0 | 141 | 942.08 | 222 | 4639.5 | 437.57 | 228 | 1426.2 | 0 | 0 | 8 | 1274.5
11:00 | 3517 | 1360 | 905 | 0 | 138 | 948.18 | 222 | 4616 | 481.52 | 281 | 1426.7 | 0 | 0 | 4 | 1343
11:30 | 3519.5 | 1378.5 | 905.5 | 0 | 143 | 1090.98 | 222 | 4614 | 544.39 | 280.5 | 1438.2 | 0 | 0 | 5 | 1391.5
12:00 | 3522 | 1397 | 906 | 0 | 148 | 1233.78 | 222 | 4612 | 607.26 | 280 | 1449.7 | 0 | 0 | 6 | 1440
12:30 | 3632 | 1400 | 906 | 0 | 154 | 1290.115 | 221 | 4635.5 | 602.39 | 316.5 | 1451.7 | 0 | 0 | 12.5 | 1253
13:00 | 3742 | 1403 | 906 | 0 | 160 | 1346.45 | 220 | 4659 | 597.52 | 353 | 1453.7 | 0 | 0 | 19 | 1066
13:30 | 3755.5 | 1390 | 905.5 | 0 | 158 | 1176.735 | 219 | 4664.5 | 485.43 | 351 | 1464.2 | 0 | 0 | 21 | 1064
14:00 | 3769 | 1377 | 905 | 0 | 156 | 1007.02 | 218 | 4670 | 373.34 | 349 | 1474.7 | 0 | 0 | 23 | 1062
14:30 | 3735 | 1401.5 | 905 | 0 | 156 | 955 | 218.5 | 4684 | 383.235 | 320 | 1456.1 | 0 | 0 | 20.5 | 1172
15:00 | 3701 | 1426 | 905 | 0 | 156 | 902.98 | 219 | 4698 | 393.13 | 291 | 1437.5 | 0 | 0 | 18 | 1282
15:30 | 3677 | 1407.5 | 905 | 0 | 152 | 901.285 | 219.5 | 4684 | 337.295 | 299.5 | 1486.75 | 0 | 0 | 26.5 | 1160
16:00 | 3653 | 1389 | 905 | 0 | 148 | 899.59 | 220 | 4670 | 281.46 | 308 | 1536 | 0 | 0 | 35 | 1038
16:30 | 3616.5 | 1362.5 | 905 | 0 | 147 | 903.96 | 220 | 4608.5 | 181.875 | 327 | 1568 | 0 | 0 | 36.5 | 980.5
17:00 | 3580 | 1336 | 905 | 0 | 146 | 908.33 | 220 | 4547 | 82.29 | 346 | 1600 | 0 | 0 | 38 | 923
17:30 | 3461 | 1303.5 | 905.5 | 0 | 145 | 936.985 | 221 | 4521 | 49.085 | 453.71 | 1696.5 | 0 | 0 | 37 | 654.5
18:00 | 3342 | 1271 | 906 | 0 | 144 | 965.64 | 222 | 4495 | 15.88 | 561.42 | 1793 | 0 | 0 | 36 | 386
18:30 | 3457 | 1275 | 873.5 | 0 | 156 | 1088.8 | 222 | 4606 | 7.94 | 673.92 | 2042.75 | 0 | 0 | 30 | 836
19:00 | 3572 | 1279 | 841 | 0 | 168 | 1211.96 | 222 | 4717 | 0 | 786.42 | 2292.5 | 0 | 0 | 24 | 1286
19:30 | 3509 | 1249 | 906 | 0 | 166 | 1202.03 | 222 | 4727 | 0 | 788.42 | 2518.5 | 0 | 0 | 27 | 1229
20:00 | 3743 | 1489 | 905 | 0 | 162 | 1216.29 | 222 | 4724 | 0 | 790.42 | 2573.5 | 0 | 0 | 10 | 742
20:30 | 3770 | 1495 | 905 | 0 | 165 | 1213.19 | 221.5 | 4726 | 0 | 766.21 | 2593.68 | 0 | 0 | 9 | 1081.5
21:00 | 3797 | 1501 | 905 | 0 | 168 | 1210.09 | 221 | 4728 | 0 | 742 | 2613.86 | 0 | 0 | 8 | 1421
21:30 | 3772.5 | 1493 | 905 | 0 | 171 | 1210.1 | 221 | 4727 | 0 | 746.5 | 2504.36 | 0 | 0 | 8.5 | 1458
22:00 | 3748 | 1485 | 905 | 0 | 174 | 1210.11 | 221 | 4726 | 0 | 751 | 2394.86 | 0 | 0 | 9 | 1495
22:30 | 3709 | 1508.5 | 905.5 | 0 | 176 | 1210.225 | 221 | 4726.5 | 0 | 767.5 | 2356.68 | 0 | 0 | 8 | 1624.5
23:00 | 3670 | 1532 | 906 | 0 | 178 | 1210.34 | 221 | 4727 | 0 | 784 | 2318.5 | 0 | 0 | 7 | 1754
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 28-08-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 374 | 05:00 | 367 | 00:00 | Madunaghat | 401 | 07:00 | 397 | 13:00
Amtali | 414 | 18:00 | 408 | 13:00 | Meghnaghat | 381 | 18:00 | 369 | 13:00
Ashuganj | 393 | 18:00 | 382 | 13:00 | Mirsorai | 401 | 19:30 | 391 | 13:00
Bhulta | 394 | 06:00 | 378 | 13:00 | Payra | 415 | 17:00 | 410 | 00:00
Bibiana | 380 | 09:00 | 373 | 13:00 | Rahanpur | 410 | 18:00 | 397 | 13:00
BIPTC | 406 | 18:00 | 391 | 00:00 | Rampal | 396 | 03:00 | 388 | 13:00
Bogura | 397 | 18:00 | 380 | 13:00
Gopalganj | 393 | 18:00 | 382 | 13:00
Kaliakoir | 368 | 18:30 | 353 | 13:00
Korerhat | 400 | 19:30 | 390 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 19:00 | 218 | 13:00 | Hasnabad | 226 | 06:00 | 219 | 00:00
AKSML | 239 | 09:00 | 231 | 13:00 | Hathazari | 236 | 08:00 | 233 | 13:00
Aminbazar | 229 | 06:00 | 222 | 13:00 | Ishurdi | 237 | 06:00 | 224 | 13:00
Ashuganj | 228 | 06:00 | 221 | 14:00 | Jhenaidah | 227 | 03:00 | 213 | 13:00
Ashuganj-400 | 228 | 06:00 | 221 | 14:00 | Kachua | 231 | 19:30 | 223 | 13:00
Baghabari | 232 | 06:00 | 225 | 21:00 | Kaliakoir | 228 | 19:00 | 219 | 13:00
Barapukuria | 228 | 17:00 | 218 | 13:00 | Keranigonj | 227 | 19:00 | 216 | 13:00
Barapukuria-230 | 228 | 17:00 | 218 | 13:00 | Khulna(S) | 228 | 18:00 | 217 | 13:00
Barapukuria(N) | N/A | N/A | N/A | N/A | Korerhat | 229 | 19:30 | 222 | 13:00
Barishal | 228 | 18:00 | 221 | 13:00 | Madunaghat | 240 | 23:00 | 230 | 10:00
Bheramara | 235 | 06:00 | 222 | 12:00 | Madunaghat-400 | 241 | 21:00 | 237 | 13:00
Bhulta | 225 | 06:00 | 215 | 13:00 | Maniknagar | 222 | 06:00 | 213 | 13:00
Bibiana | 220 | 10:00 | 217 | 00:00 | Meghnaghat | 231 | 05:00 | 225 | 13:00
BIPTC | 237 | 06:00 | 223 | 12:00 | Meghnaghat-400 | 226 | 05:00 | 218 | 13:00
Birulia | 228 | 06:00 | 219 | 13:00 | Mirsorai | 233 | 19:30 | 227 | 13:00
Bogura | 239 | 17:00 | 230 | 13:00 | Naogaon | 226 | 18:00 | 209 | 13:00
Bogura-400 | 239 | 18:00 | 229 | 13:00 | Purbasadipur | 225 | 06:00 | 215 | 13:00
Borhanuddin | 229 | 11:00 | 226 | 00:00 | Rajshahi | 233 | 06:00 | 220 | 13:00
BSRM | 229 | 09:00 | 223 | 13:00 | Rampal | 226 | 18:00 | 217 | 13:00
Charfasson | 230 | 06:00 | 225 | 17:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 09:00 | 225 | 14:00 | Rampura | 224 | 06:00 | 213 | 13:00
Cumilla(N) | 224 | 05:00 | 218 | 13:00 | Shikalbaha | 239 | 16:00 | 236 | 12:00
Faridpur | 223 | 18:00 | 216 | 13:00 | Shyampur | 225 | 06:00 | 216 | 13:00
Fenchuganj | 221 | 07:00 | 218 | 00:00 | Siddhirganj | 225 | 23:00 | 218 | 00:00
Feni | 227 | 09:00 | 221 | 13:00 | Sirajgonj | 237 | 18:00 | 230 | 13:00
Ghorashal | 230 | 01:00 | 222 | 14:00 | Sreepur | 223 | 06:00 | 216 | 13:00
Ghorashal-230 | 218 | 19:00 | 205 | 13:00 | Tongi | 222 | 18:30 | 210 | 09:00
Gopalganj | 223 | 18:00 | 217 | 13:00
GPH | 235 | 08:00 | 230 | 07:00
Haripur | 224 | 06:00 | 215 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 06:00 | 130 | 00:00 | Madaripur | 132 | 18:00 | 128 | 13:00
Agargaon | 138 | 19:30 | 130 | 13:00 | Madartek | 135 | 05:00 | 129 | 13:00
Agrabad | 137 | 07:00 | 133 | 12:00 | Madunaghat | 139 | 19:30 | 134 | 13:00
AKS | 135 | 00:00 | 132 | 12:00 | Magura | 135 | 06:00 | 126 | 13:00
Aminbazar | 132 | 21:00 | 127 | 12:00 | Mahasthangarh | 135 | 17:00 | 128 | 13:00
Amnura | 135 | 19:30 | 128 | 12:00 | Maijdee | 129 | 19:30 | 125 | 13:00
Ashuganj | 130 | 01:00 | 126 | 18:30 | Manikganj | 128 | 18:30 | 124 | 10:00
Ashuganj-230 | 133 | 06:00 | 130 | 13:00 | Maniknagar | 139 | 06:00 | 131 | 13:00
Bagerhat | 131 | 18:00 | 122 | 13:00 | Matarbari | 126 | 18:30 | 111 | 12:00
Bajitpur | 127 | 00:00 | 121 | 18:30 | Matuail | 133 | 05:00 | 128 | 00:00
Bakerganj | 133 | 18:00 | 129 | 20:00 | Metrorail_Motijheel | 139 | 06:00 | 121 | 13:00
Bakulia | 138 | 09:00 | 135 | 00:00 | Metrorail_Uttara | 132 | 19:00 | 124 | 13:00
Banani | 135 | 06:00 | 128 | 13:00 | Millgate | 133 | 19:00 | 125 | 13:00
Bangabhaban | 139 | 05:00 | 131 | 13:00 | Mirpur | 131 | 07:00 | 123 | 13:00
Barapukuria | 138 | 06:00 | 128 | 13:00 | Mirzapur | 130 | 19:00 | 125 | 07:00
Barguna | 132 | 16:00 | 129 | 13:00 | Mithapukur | 133 | 06:00 | 123 | 13:00
Barishal | 134 | 18:00 | 128 | 13:00 | MI_Cement | 133 | 19:00 | 127 | 00:00
Barishal-230 | 133 | 18:00 | 128 | 13:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroaulia | 137 | 07:00 | 134 | 12:00 | Mogbazar | 138 | 00:00 | 132 | 12:00
Baroirhat | 133 | 09:00 | 129 | 13:00 | Mongla | 129 | 17:00 | 121 | 13:00
Bashundhara | 136 | 06:00 | 125 | 13:00 | Motijheel | 139 | 05:00 | 131 | 13:00
BashundharaCement | 133 | 06:00 | 126 | 13:00 | Muktagacha | 127 | 19:30 | 116 | 08:00
Beanibazar | 123 | 04:00 | 118 | 20:00 | Munshiganj | 131 | 06:00 | 125 | 13:00
Benapole | 136 | 18:00 | 119 | 13:00 | Muradnagar | 128 | 06:00 | 124 | 00:00
Bhaluka | 130 | 01:00 | 124 | 13:00 | Mymensingh | 127 | 19:00 | 115 | 17:00
Bhandaria | 129 | 17:00 | 123 | 21:00 | Nabinagar | 130 | 18:00 | 122 | 13:00
Bhangura | 134 | 18:00 | 129 | 21:00 | Naogaon | 136 | 18:00 | 126 | 13:00
Bheramara | 137 | 03:00 | 130 | 13:00 | Narail | 137 | 03:00 | 125 | 21:00
Bheramara(GK) | 138 | 09:00 | 130 | 13:00 | Narinda | 139 | 06:00 | 131 | 13:00
Bhulta | 128 | 05:00 | 123 | 13:00 | Narshingdi | 132 | 19:00 | 121 | 12:00
Bhulta-400 | 130 | 06:00 | 124 | 13:00 | Natore | 135 | 06:00 | 127 | 13:00
Birulia | 134 | 18:30 | 129 | 13:00 | Nawabganj | 136 | 06:00 | 129 | 13:00
Bog-Sherpur | 136 | 17:00 | 130 | 12:00 | Netrakona | 120 | 01:00 | 114 | 08:00
Bogura | 138 | 18:00 | 131 | 13:00 | New | 134 | 19:00 | 128 | 00:00
Bogura-230 | 139 | 18:00 | 132 | 13:00 | Niamatpur | 134 | 05:00 | 128 | 13:00
Brahmanbaria | 127 | 04:00 | 123 | 13:00 | Noapara | 134 | 18:00 | 125 | 13:00
Cantonment | 137 | 06:00 | 130 | 13:00 | Pabna | 135 | 06:00 | 129 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandina | 131 | 09:00 | 127 | 13:00 | Palashbari | 132 | 18:00 | 124 | 13:00
Chandpur | 136 | 18:00 | 129 | 13:00 | Panchagarh | 140 | 17:00 | 128 | 21:00
Chandraghona | 138 | 05:00 | 136 | 12:00 | Patiya | 137 | 19:30 | 132 | 13:00
Chapai | 132 | 15:00 | 130 | 00:00 | Patnitala | 133 | 18:00 | 127 | 10:00
Charsaidpur | 132 | 07:00 | 125 | 13:00 | Patuakhali | 133 | 18:00 | 130 | 02:00
Chauddagram | 131 | 19:00 | 127 | 13:00 | Payra | 136 | 18:00 | 134 | 00:00
Chhatak | 120 | 01:00 | 114 | 20:00 | PHP | 133 | 19:30 | 129 | 13:00
Chowmuhani | 128 | 09:00 | 126 | 12:00 | Postogola | 135 | 04:00 | 128 | 13:00
Chuadanga | 135 | 19:30 | 123 | 20:00 | Pubail | 132 | 19:00 | 125 | 08:00
Coxsbazar | 126 | 05:00 | 110 | 13:00 | Purbachal | 136 | 05:00 | 128 | 13:00
Cumilla(N) | 131 | 04:00 | 126 | 13:00 | Purbasadipur | 136 | 06:00 | 130 | 13:00
Cumilla(S) | 131 | 04:00 | 121 | 20:00 | Rahanpur | 137 | 17:00 | 132 | 12:00
Daganbhuiyan | 131 | 18:00 | 127 | 13:00 | Rahanpur-400 | 137 | 17:00 | 132 | 13:00
Daudkandi | 126 | 04:00 | 122 | 00:00 | Rahim | 134 | 00:00 | 127 | 13:00
DhakaUniversity | 136 | 06:00 | 129 | 13:00 | Rajbari | 126 | 03:00 | 121 | 13:00
Dhamrai | 131 | 18:00 | 124 | 12:00 | Rajendrapur | 135 | 18:00 | 128 | 13:00
Dhanmondi | 136 | 06:00 | 128.6 | 13:00 | Rajshahi | 133 | 17:00 | 124 | 13:00
Dohazari | 135 | 04:00 | 128 | 12:00 | Rajshahi-230 | 134 | 06:00 | 126 | 13:00
Faridpur | 128 | 03:00 | 124 | 13:00 | Ramganj | 130 | 18:30 | 124 | 13:00
Fatullah | 135 | 18:00 | 127 | 13:00 | Rampur | 138 | 09:00 | 134 | 13:00
Fenchuganj | 130 | 11:00 | 127 | 00:00 | Rampura | 136 | 06:00 | 128 | 13:00
Feni | 132 | 19:30 | 129 | 15:00 | Rangamati | 138 | 09:00 | 134 | 13:00
Feni-230 | 132 | 09:00 | 128 | 13:00 | Rangpur | 132 | 17:00 | 124 | 10:00
Ghatail | 126 | 19:00 | 116 | 08:00 | Ruppur | 137 | 04:00 | 131 | 09:00
Ghorashal | 132 | 21:00 | 127 | 00:00 | Saidpur | 135 | 01:00 | 127 | 13:00
Goalpara | 137 | 18:00 | 128 | 13:00 | Santhia | 135 | 09:00 | 129 | 20:00
Gollamari | 137 | 18:00 | 130 | 12:00 | Satkhira | 132 | 18:00 | 122 | 13:00
Gopalganj | 134 | 18:00 | 125 | 13:00 | Satmasjid | 138 | 19:00 | 129 | 13:00
Gopalganj-400 | 133 | 18:00 | 128 | 13:00 | Savar | 132 | 19:30 | 123 | 13:00
Gulshan | 135 | 06:00 | 128 | 13:00 | SevenRings | 138 | 16:00 | 126 | 13:00
Halishahar | 138 | 08:00 | 134 | 12:00 | ShahCement | 132 | 06:00 | 125 | 13:00
Haripur | 133 | 06:00 | 127 | 13:00 | Shahjadpur | 135 | 00:00 | 131 | 20:00
HaripurSBU | 133 | 08:00 | 129 | 15:00 | Shahjibazar | 127 | 10:00 | 121 | 13:00
Hasnabad | 134 | 05:00 | 129 | 00:00 | Shahmirpur | 140 | 18:30 | 135 | 12:00
Hathazari | 138 | 08:00 | 136 | 13:00 | Shariatpur | 131 | 17:00 | 121 | 21:00
Hatirjheel | 135 | 04:00 | 128 | 13:00 | Sherpur | 127 | 19:00 | 112 | 17:00
Ishurdi | 139 | 06:00 | 131 | 21:00 | Shikalbaha | 128 | 18:30 | 123 | 13:00
Jaldhaka | 133 | 17:00 | 124 | 13:00 | Shikalbaha-230 | 139 | 16:00 | 136 | 12:00
Jamalpur | 131 | 19:00 | 117 | 17:00 | Shitalakhya | 133 | 19:00 | 126 | 13:00
Jashore | 136 | 06:00 | 121 | 13:00 | Sholosohor | 138 | 09:00 | 134 | 13:00
Jhenaidah | 139 | 06:00 | 128 | 13:00 | Shomvuganj | 122 | 00:00 | 117 | 08:00
Jhenaidah-230 | 139 | 03:00 | 128 | 20:00 | Shyampur | 138 | 15:00 | 129 | 13:00
Joydebpur | 130 | 19:00 | 122 | 09:00 | Shyampur-230 | 136 | 19:30 | 35 | 22:00
Joypurhat | 132 | 05:00 | 126 | 13:00 | Siddhirganj | 134 | 06:00 | 129 | 00:00
Juldah | 138 | 17:00 | 135 | 13:00 | Sirajganj | 132 | 17:00 | 126 | 13:00
Kabirpur | 133 | 19:00 | 122 | 13:00 | Sitakunda | 137 | 03:00 | 134 | 13:00
Kachua | 132 | 19:00 | 127 | 13:00 | Sonargaon | 130 | 06:00 | 125 | 13:00
Kaliakoir | 135 | 19:00 | 128 | 13:00 | Sreemongol | 127 | 10:00 | 121 | 13:00
Kaliganj | 138 | 09:00 | 127 | 13:00 | Sreepur | 135 | 01:00 | 129 | 13:00
Kallyanpur | 131 | 19:30 | 122 | 13:00 | Srinagar | 137 | 06:00 | 129 | 13:00
Kalurghat | 139 | 19:30 | 136 | 12:00 | SSM | 140 | 00:00 | 140 | 00:00
Kamrangirchar | 137 | 19:30 | 121 | 13:00 | Sunamganj | 120 | 10:00 | 112 | 20:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 124 | 10:00 | 121 | 00:00
Kasba | 128 | 05:00 | 122 | 13:00 | Sylhet_(South) | 125 | 09:00 | 120 | 20:00
Kazla | 139 | 07:00 | 132 | 13:00 | Tangail | 127 | 19:00 | 119 | 18:30
Keranigonj | 137 | 18:00 | 130 | 13:00 | Taraganj | 133 | 16:00 | 125 | 13:00
Khagrachori | 137 | 23:00 | 133 | 13:00 | Tasnim | 131 | 06:00 | 126 | 00:00
Khulna | 135 | 18:00 | 126 | 13:00 | Thakurgaon | 140 | 17:00 | 130 | 13:00
Khulna(S) | 137 | 18:00 | 128 | 13:00 | TK | 138 | 18:00 | 135 | 07:00
Khulshi | 136 | 08:00 | 132 | 13:00 | Tongi | 136 | 18:30 | 129 | 13:00
Kishoreganj | 125 | 01:00 | 118 | 00:00 | Ullahpara | 134 | 17:00 | 128 | 13:00
Kodda | 138 | 19:30 | 124 | 08:00 | Ullon | 136 | 06:00 | 130 | 00:00
Korerhat | 135 | 09:00 | 131 | 13:00 | Uttara | 131 | 06:00 | 123 | 13:00
KSRM | 138 | 19:30 | 134 | 09:00 | UttaraNew | 132 | 19:00 | 124 | 13:00
Kulaura | 129 | 09:00 | 125 | 20:00 | Zigatola | 137 | 06:00 | 131 | 00:00
Kurigram | 130 | 17:00 | 120 | 10:00
Kushtia | 137 | 03:00 | 127 | 13:00
Laksam | 131 | 19:00 | 126 | 13:00
Lakshmipur | 129 | 19:30 | 124 | 13:00
Lalbag | 137 | 18:00 | 130 | 13:00
Lalmonirhat | 128 | 18:00 | 120 | 11:00
Madanganj | 133 | 06:00 | 126 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-08-2026 | [28 empty] | Date: | 28-08-2026 | [28 empty] | Date: | 28-08-2026 | [28 empty] | Date: | 28-08-2026 | [28 empty] | Date: | 28-08-2026 | [18 empty] | Date: | 28-08-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 233 | 35 | 35 | 53 | 90 | 147 | 0 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 55 | 305 | 0 | 0 | 0 | 68 | 8 | 22 | 0 | 420 | 97 | 16 | 44 | 0 | 6 | 34 | 8 | 17 | 12 | 12 | 0 | 222 | 110 | 8 | 565 | 16 | 0 | 50 | 1 | 105 | 217 | 0 | 0 | 0 | 1207 | 0 | 53 | 0 | 220 | 290 | 270 | 51 | 0 | 194 | 20 | 88 | 70 | 79 | 5 | 19 | 102 | 176 | 52.2 | 0 | 29 | 250 | 396 | 342 | 40 | 0 | 150 | 0 | 8 | 0 | 22 | 0 | 142 | 0 | 127 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 24 | 8423.2 | 905 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 150 | 0 | 15 | 0 | 1050 | 0 | 0 | 0 | 1393.71 | 0 | 0 | 0 | 55 | 70 | 0 | 100 | 21 | 8 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 350 | 0 | 0 | 156 | 41 | 115 | 0 | 63 | 0 | 165 | 0 | 0 | 0 | 0 | 48 | 200 | 115 | 220 | 0 | 1000 | 580 | 17 | 7016.71 | 15439.91 | 104.26
01:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 219 | 35 | 35 | 51 | 90 | 147 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 297 | 0 | 0 | 0 | 68 | 8 | 22 | 0 | 390 | 92 | 16 | 32 | 0 | 17 | 34 | 8 | 0 | 12 | 12 | 0 | 220 | 101 | 13 | 565 | 16 | 0 | 50 | 17 | 105 | 216 | 0 | 0 | 0 | 1190 | 0 | 68 | 0 | 220 | 290 | 255 | 51 | 0 | 207 | 10 | 73 | 70 | 51 | 0 | 19 | 102 | 170 | 52.2 | 0 | 29 | 255 | 397 | 342 | 40 | 0 | 140 | 0 | 7 | 0 | 22 | 0 | 141 | 0 | 126 | 17 | 58 | 0 | 66 | 0 | 0 | 0 | 24 | 8010.2 | 904 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 1310.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 350 | 0 | 0 | 159 | 41 | 115 | 0 | 34 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 565 | 17 | 6613.64 | 14623.84 | 104.29
02:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 212 | 35 | 35 | 51 | 91 | 147 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 290 | 0 | 0 | 0 | 68 | 8 | 22 | 0 | 385 | 86 | 16 | 29 | 0 | 4 | 34 | 8 | 0 | 12 | 12 | 0 | 219 | 93 | 23 | 565 | 16 | 0 | 50 | 25.5 | 105 | 216 | 0 | 0 | 0 | 1192 | 0 | 100 | 0 | 220 | 290 | 250 | 51 | 0 | 219 | 10 | 69 | 111 | 51 | 0 | 19 | 98 | 162 | 52.2 | 0 | 29 | 250 | 400 | 342 | 40 | 0 | 135 | 0 | 7 | 0 | 22 | 0 | 143 | 0 | 127 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 24 | 7968.7 | 905 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 1296.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 350 | 0 | 0 | 161 | 40 | 115 | 0 | 34 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 565 | 17 | 6601.99 | 14570.69 | 104.33
03:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 238 | 35 | 35 | 51 | 91 | 147 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 310 | 0 | 0 | 0 | 68 | 8 | 22 | 0 | 440 | 95 | 16 | 30 | 0 | 7 | 0 | 8 | 0 | 12 | 12 | 0 | 217 | 95 | 25 | 565 | 16 | 0 | 50 | 25.5 | 105 | 216 | 0 | 0 | 0 | 1202 | 0 | 100 | 0 | 240 | 300 | 285 | 51 | 0 | 206 | 10 | 68 | 136 | 50 | 0 | 19 | 92 | 152 | 52.2 | 0 | 29 | 248 | 400 | 342 | 40 | 0 | 149 | 0 | 0 | 0 | 22 | 0 | 142 | 0 | 127 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 24 | 8133.7 | 904 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 966.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 381 | 0 | 0 | 158 | 40 | 115 | 0 | 34 | 0 | 50 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 565 | 17 | 6037.78 | 14171.48 | 104.36
04:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 241 | 35 | 35 | 51 | 91 | 97 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 316 | 0 | 0 | 0 | 68 | 8 | 22 | 0 | 445 | 95 | 16 | 31 | 0 | 11 | 0 | 8 | 0 | 12 | 12 | 0 | 217 | 110 | 31 | 565 | 16 | 0 | 50 | 8 | 105 | 217 | 0 | 0 | 0 | 1207 | 0 | 102 | 0 | 240 | 300 | 285 | 51 | 0 | 190 | 5 | 69 | 139 | 50 | 0 | 19 | 102 | 146 | 52.2 | 0 | 29 | 245 | 400 | 353 | 40 | 0 | 152 | 0 | 6 | 0 | 22 | 0 | 143 | 0 | 127 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 24 | 8127.2 | 904 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 938.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 387 | 0 | 0 | 159 | 40 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 565 | 17 | 5966.2 | 14093.4 | 104.39
05:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 229 | 17 | 35 | 51 | 91 | 97 | 0 | 17 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 307 | 0 | 0 | 0 | 68 | 8 | 22 | 0 | 430 | 101 | 16 | 30 | 0 | 19 | 0 | 8 | 0 | 12 | 12 | 0 | 219 | 98 | 38 | 565 | 16 | 0 | 50 | 8 | 105 | 217 | 0 | 0 | 0 | 1192 | 0 | 100 | 0 | 230 | 300 | 275 | 51 | 0 | 197 | 5 | 69 | 139 | 51 | 0 | 19 | 101 | 142 | 52.2 | 0 | 29 | 245 | 400 | 354 | 40 | 0 | 152 | 0 | 6 | 0 | 22 | 0 | 142 | 0 | 127 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 24 | 8012.2 | 904 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 940.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 394 | 0 | 0 | 158 | 41 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 565 | 17 | 5974.32 | 13986.52 | 104.42
06:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 221 | 17 | 35 | 45 | 91 | 97 | 0 | 17 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 68 | 8 | 22 | 0 | 400 | 91 | 16 | 31 | 0 | 13 | 0 | 8 | 0 | 12 | 12 | 0.02 | 220 | 93 | 30 | 565 | 16 | 0 | 50 | 8 | 105 | 217 | 0 | 0 | 0 | 1195 | 1 | 100 | 0 | 230 | 300 | 265 | 51 | 0 | 210 | 5 | 42 | 139 | 50 | 0 | 19 | 102 | 140 | 52.2 | 1 | 29 | 244 | 400 | 342 | 40 | 0 | 144 | 0 | 6 | 0 | 22 | 0 | 142 | 0 | 127 | 0 | 58 | 0.25 | 67 | 0 | 0 | 0.27 | 22 | 7877.74 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 1050 | 0 | 0 | 0 | 919.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 0.5 | 0 | 11 | 0 | 0.05 | 0 | 0 | 127 | 0 | 0 | 0 | 398 | 0 | 0.03 | 159 | 41 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 2 | 0 | 32 | 200 | 116 | 220 | 0 | 947 | 565 | 17 | 5881.25 | 13758.99 | 104.45
07:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 226 | 17 | 35 | 34 | 46 | 97 | 0 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 296 | 0 | 0 | 2 | 68 | 8 | 22 | 0 | 410 | 90 | 16 | 30 | 0 | 5 | 0 | 8 | 0 | 12 | 12 | 0.47 | 222 | 91 | 33 | 565 | 16 | 0 | 50 | 8 | 105 | 218 | 0 | 0 | 0 | 1192 | 6 | 78 | 0 | 230 | 300 | 270 | 51 | 0 | 200 | 5 | 34 | 139 | 50 | 0 | 8 | 101 | 138 | 52.2 | 10 | 24 | 248 | 400 | 304 | 40 | 0 | 138 | 0 | 4 | 0 | 22 | 0 | 141 | 0 | 126 | 0 | 58 | 3.6 | 67 | 0 | 0.3 | 5 | 23 | 7697.57 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 1050 | 0 | 0 | 0 | 929.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 2.8 | 10 | 11 | 0 | 6.01 | 0 | 0 | 128 | 0 | 0 | 0 | 400 | 0 | 0.58 | 159 | 41 | 115 | 1 | 34 | 0 | 0 | 0 | 0.9 | 13 | 0.03 | 32 | 200 | 116 | 220 | 0 | 956 | 565 | 17 | 5947.37 | 13644.94 | 104.48
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 214 | 17 | 35 | 35 | 15 | 97 | 0 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 291 | 0 | 0 | 3 | 68 | 8 | 22 | 0 | 380 | 89 | 16 | 35 | 0 | 10 | 0 | 8 | 0 | 12 | 12 | 1.2 | 221 | 92 | 35 | 565 | 16 | 0 | 50 | 8 | 105 | 218 | 0 | 0 | 0 | 1192 | 5 | 55 | 0 | 230 | 300 | 250 | 51 | 0 | 206 | 5 | 34 | 139 | 51 | 0 | 19 | 102 | 130 | 52.2 | 19 | 24 | 253 | 400 | 307 | 40 | 0 | 144 | 1 | 0 | 0 | 22 | 0 | 142 | 0 | 125 | 0 | 58 | 12.69 | 67 | 0 | 1.1 | 9.45 | 24 | 7596.64 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1050 | 0 | 0 | 0 | 927.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 6.29 | 22 | 10 | 0 | 17.29 | 0 | 0 | 127 | 0 | 0 | 0 | 394 | 0 | 1.63 | 157 | 41 | 115 | 10 | 34 | 0 | 0 | 0 | 3 | 53 | 0.08 | 32 | 200 | 116 | 220 | 0 | 973 | 580 | 17 | 6048.65 | 13645.29 | 104.5
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 175 | 17 | 35 | 35 | 15 | 97 | 0 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 278 | 0 | 0 | 7 | 68 | 8 | 22 | 0 | 350 | 87 | 16 | 43 | 0 | 13 | 0 | 8 | 17 | 12 | 12 | 3.02 | 222 | 91 | 35 | 565 | 16 | 0 | 48 | 8 | 105 | 217 | 0 | 0 | 0 | 1165 | 16 | 53 | 0 | 220 | 280 | 230 | 51 | 0 | 177 | 0 | 34 | 138 | 51 | 0 | 19 | 102 | 136 | 52.2 | 31 | 24 | 260 | 265 | 324 | 40 | 0 | 137 | 2 | 0 | 0 | 22 | 0 | 143 | 0 | 126 | 0 | 58 | 6.84 | 113 | 0 | 0.9 | 12.83 | 0 | 7343.79 | 898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 1050 | 0 | 0 | 0 | 929.6 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 8 | 12.03 | 25 | 10 | 0 | 37.92 | 0 | 0 | 127 | 0 | 0 | 0 | 295 | 0 | 2.41 | 159 | 41 | 115 | 22 | 34 | 0 | 0 | 0 | 4.9 | 135 | 0.27 | 32 | 200 | 115 | 180 | 0 | 962 | 540 | 17 | 5995.13 | 13338.92 | 104.51
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 260 | 17 | 35 | 36 | 15 | 81 | 0 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 290 | 0 | 0 | 11 | 68 | 8 | 22 | 0 | 410 | 94 | 16 | 44 | 0 | 12 | 0 | 8 | 17 | 12 | 12 | 3.74 | 222 | 92 | 20 | 556 | 16 | 0 | 50 | 25.5 | 105 | 216 | 0 | 0 | 0 | 1160 | 17 | 55 | 0 | 220 | 280 | 265 | 51 | 0 | 191 | 0 | 34 | 139 | 51 | 0 | 19 | 103 | 144 | 52.2 | 36 | 24 | 270 | 200 | 340 | 40 | 0 | 151 | 3 | 0 | 0 | 81 | 0 | 142 | 0 | 125 | 0 | 58 | 4.1 | 115 | 0 | 0.7 | 15.6 | 10 | 7601.84 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 1050 | 0 | 0 | 0 | 935.98 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 16.92 | 42 | 10 | 0 | 47.57 | 0 | 0 | 127 | 0 | 0 | 0 | 394 | 0 | 4.68 | 160 | 40 | 115 | 16 | 0 | 0 | 0 | 0 | 6 | 113 | 0.31 | 32 | 200 | 115 | 220 | 0 | 987 | 510 | 17 | 6164.46 | 13766.3 | 104.51
11:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 215 | 17 | 35 | 53 | 15 | 81 | 0 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 290 | 0 | 0 | 25 | 68 | 8 | 22 | 0 | 320 | 85 | 16 | 44 | 0 | 4 | 0 | 8 | 17 | 12 | 12 | 4.18 | 222 | 83 | 16 | 557 | 16 | 0 | 50 | 25.5 | 97 | 216 | 0 | 0 | 0 | 1160 | 11 | 55 | 0 | 220 | 280 | 285 | 51 | 0 | 191 | 0 | 34 | 136 | 51 | 0 | 19 | 102 | 138 | 52.2 | 57 | 24 | 275 | 275 | 350 | 40 | 0 | 130 | 3 | 0 | 0 | 84 | 0 | 141 | 0 | 125 | 0 | 58 | 5.6 | 115 | 0 | 1.4 | 7.38 | 22 | 7713.26 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 1047 | 0 | 0 | 0 | 948.18 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 16.09 | 50 | 11 | 0 | 32.8 | 0 | 0 | 125 | 0 | 0 | 0 | 390 | 0 | 3.21 | 157 | 40 | 114 | 11 | 0 | 0 | 0 | 0 | 5.5 | 197 | 0.36 | 32 | 200 | 115 | 220 | 0 | 945 | 510 | 17 | 6186.14 | 13899.4 | 104.52
12:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 267 | 17 | 35 | 53 | 15 | 81 | 0 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 290 | 0 | 0 | 21 | 68 | 8 | 22 | 0 | 325 | 84 | 16 | 45 | 0 | 6 | 0 | 8 | 17 | 12 | 12 | 4.34 | 222 | 91 | 19 | 557 | 16 | 0 | 50 | 25.5 | 91 | 213 | 0 | 0 | 0 | 1160 | 16 | 73 | 0 | 220 | 280 | 250 | 51 | 0 | 192 | 0 | 34 | 136 | 50 | 0 | 8 | 103 | 148 | 52.2 | 76 | 24 | 265 | 300 | 367 | 40 | 0 | 127 | 4 | 0 | 0 | 85 | 0 | 142 | 0 | 125 | 0 | 58 | 9 | 116 | 0 | 1.2 | 18.82 | 24 | 7827.06 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 1037 | 0 | 0 | 0 | 1233.78 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 50.26 | 52 | 10 | 0 | 40.74 | 0 | 0 | 124 | 0 | 0 | 0 | 390 | 0 | 4.51 | 158 | 45 | 114 | 39 | 0 | 0 | 0 | 0 | 7.2 | 200 | 0.19 | 32 | 200 | 115 | 220 | 0 | 945 | 510 | 17 | 6556.68 | 14383.74 | 104.52
13:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 221 | 17 | 0 | 53 | 60 | 81 | 0 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 299 | 0 | 0 | 19 | 68 | 8 | 14 | 0 | 425 | 91 | 16 | 45 | 0 | 19 | 0 | 8 | 17 | 12 | 12 | 4.05 | 220 | 77 | 25 | 558 | 16 | 0 | 50 | 25.5 | 96 | 213 | 0 | 0 | 0 | 1160 | 10 | 80 | 0 | 225 | 310 | 275 | 51 | 0 | 214 | 0 | 34 | 136 | 86 | 0 | 19 | 102 | 160 | 52.2 | 76 | 31 | 255 | 394 | 393 | 41 | 0 | 143 | 6 | 0 | 0 | 22 | 0 | 142 | 0 | 125 | 0 | 57 | 20.35 | 116 | 0 | 1.1 | 50.07 | 24 | 8177.27 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 1050 | 0 | 0 | 0 | 1346.45 | 0 | 0 | 0 | 0 | 35 | 0 | 21 | 0 | 8 | 44.23 | 61 | 10 | 0 | 19.08 | 0 | 0 | 123 | 0 | 0 | 0 | 383 | 0 | 1.76 | 160 | 49 | 114 | 13 | 0 | 0 | 0 | 0 | 6.6 | 169 | 0.28 | 32 | 200 | 115 | 220 | 0 | 972 | 510 | 17 | 6682.4 | 14859.67 | 104.53
14:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 234 | 17 | 0 | 53 | 45 | 81 | 0 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 310 | 0 | 0 | 16 | 68 | 10 | 14 | 0 | 400 | 86 | 16 | 40 | 0 | 23 | 0 | 8 | 17 | 12 | 12 | 2.81 | 218 | 92 | 25 | 558 | 16 | 0 | 50 | 25.5 | 96 | 212 | 0 | 0 | 0 | 1185 | 2 | 82 | 0 | 240 | 310 | 325 | 51 | 0 | 211 | 0 | 34 | 136 | 101 | 0 | 17 | 102 | 156 | 52.2 | 44 | 30 | 244 | 394 | 397 | 40 | 0 | 140 | 10 | 0 | 0 | 22 | 0 | 142 | 0 | 125 | 0 | 58 | 14 | 116 | 0 | 1.1 | 21.57 | 24 | 8180.18 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 1050 | 0 | 0 | 0 | 1007.02 | 0 | 0 | 0 | 0 | 35 | 0 | 33 | 0 | 8 | 24.53 | 45 | 10 | 0 | 31.48 | 0 | 0 | 123 | 0 | 0 | 0 | 336 | 0 | 3.78 | 158 | 47 | 112 | 33 | 0 | 0 | 0 | 0 | 3.9 | 47 | 0.17 | 32 | 200 | 115 | 220 | 0 | 962 | 510 | 17 | 6141.88 | 14322.06 | 104.53
15:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 230 | 17 | 0 | 53 | 45 | 81 | 0 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 309 | 0 | 0 | 12 | 68 | 9 | 14 | 0 | 445 | 95 | 16 | 37 | 0 | 18 | 0 | 14 | 17 | 12 | 12 | 2.44 | 219 | 94 | 23 | 558 | 16 | 0 | 50 | 25.5 | 100 | 212 | 0 | 0 | 0 | 1178 | 0 | 80 | 0 | 220 | 310 | 320 | 51 | 0 | 192 | 0 | 34 | 134 | 100 | 0 | 17 | 102 | 156 | 8 | 53 | 29 | 246 | 395 | 367 | 40 | 0 | 149 | 3 | 0 | 0 | 22 | 0 | 140 | 0 | 125 | 0 | 58 | 10.56 | 116 | 0 | 1.4 | 24.58 | 24 | 8044.48 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 69 | 1050 | 0 | 0 | 0 | 902.98 | 0 | 0 | 0 | 0 | 35 | 0 | 33 | 0 | 8 | 21.58 | 24 | 10 | 0 | 35.57 | 0 | 0 | 122 | 0 | 0 | 0 | 330 | 0 | 2.77 | 157 | 49 | 110 | 13 | 0 | 0 | 0 | 0 | 2.2 | 118 | 0.03 | 32 | 200 | 115 | 220 | 0 | 996 | 510 | 17 | 6103.13 | 14147.61 | 104.54
16:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 222 | 17 | 25 | 70 | 45 | 81 | 0 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 304 | 0 | 0 | 7 | 68 | 9 | 14 | 0 | 410 | 94 | 16 | 49 | 0 | 35 | 0 | 14 | 17 | 12 | 12 | 2.47 | 220 | 86 | 24 | 558 | 16 | 0 | 50 | 8 | 98 | 212 | 0 | 0 | 0 | 1190 | 11 | 75 | 0 | 220 | 310 | 290 | 51 | 0 | 178 | 0 | 34 | 134 | 101 | 0 | 19 | 100 | 148 | 8 | 28 | 29 | 250 | 395 | 368 | 40 | 0 | 148 | 6 | 0 | 0 | 22 | 0 | 142 | 0 | 125 | 0 | 58 | 14.9 | 116 | 0 | 1.1 | 12.71 | 24 | 7976.18 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 12 | 1015 | 0 | 0 | 0 | 899.59 | 0 | 0 | 0 | 0 | 35 | 0 | 33 | 0 | 8 | 18.26 | 21 | 10 | 0 | 30.2 | 0 | 0 | 123 | 0 | 0 | 0 | 330 | 0 | 2.8 | 159 | 48 | 115 | 3 | 74 | 0 | 0 | 0 | 1 | 110 | 0.02 | 32 | 200 | 115 | 220 | 0 | 990 | 510 | 17 | 6068.87 | 14045.05 | 104.54
17:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 224 | 17 | 35 | 115 | 45 | 81 | 0 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 275 | 0 | 0 | 3 | 68 | 9 | 14 | 0 | 350 | 0 | 16 | 55 | 0 | 38 | 0 | 14 | 17 | 12 | 12 | 0.49 | 220 | 84 | 30 | 558 | 16 | 0 | 50 | 8 | 95 | 211 | 0 | 0 | 0 | 1190 | 2 | 80 | 0 | 220 | 310 | 260 | 51 | 0 | 198 | 0 | 34 | 134 | 134 | 5 | 19 | 101 | 146 | 8 | 14 | 29 | 256 | 399 | 343 | 40 | 0 | 141 | 3 | 0 | 0 | 22 | 0 | 142 | 0 | 125 | 0 | 48 | 4.43 | 116 | 0 | 0.3 | 6.82 | 24 | 7796.04 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 4 | 920 | 0 | 0 | 0 | 908.33 | 0 | 0 | 0 | 35 | 35 | 0 | 36 | 0 | 8 | 6.23 | 17 | 10 | 0 | 9.93 | 0 | 0 | 125 | 0 | 0 | 0 | 330 | 0 | 1.06 | 159 | 48 | 115 | 2 | 91 | 0 | 0 | 0 | 0 | 8 | 0.03 | 48 | 200 | 115 | 220 | 0 | 962 | 510 | 17 | 5912.58 | 13708.62 | 104.55
18:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 221 | 17 | 35 | 115 | 45 | 95 | 4 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 270 | 0 | 0 | 2 | 143.42 | 9 | 18 | 0 | 330 | 0 | 16 | 56 | 0 | 36 | 0 | 21 | 17 | 24 | 25 | 0.11 | 222 | 93 | 32 | 560 | 16 | 0 | 50 | 8 | 90 | 186 | 0 | 0 | 0 | 1190 | 0 | 80 | 0 | 220 | 280 | 250 | 51 | 0 | 200 | 0 | 44 | 134 | 194 | 26 | 19 | 101 | 144 | 8 | 3 | 29 | 257 | 396 | 330 | 40 | 0 | 132 | 0 | 0 | 0 | 22 | 0 | 142 | 0 | 125 | 2 | 58 | 0.87 | 115 | 0 | 0 | 1.25 | 24 | 7919.65 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 1 | 920 | 0 | 0 | 0 | 965.64 | 0 | 0 | 0 | 55 | 41 | 0 | 41 | 0 | 8 | 1.36 | 0 | 22 | 0 | 1.18 | 0 | 0 | 127 | 0 | 0 | 0 | 240 | 0 | 0.09 | 160 | 50 | 115 | 1 | 92 | 0 | 0 | 0 | 0 | 4 | 0.02 | 64 | 200 | 100 | 180 | 0 | 905 | 510 | 17 | 5832.29 | 13751.94 | 104.55
19:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 213 | 54 | 17 | 115 | 124 | 145 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 35 | 270 | 0 | 0 | 0 | 143.42 | 9 | 22 | 0 | 330 | 0 | 16 | 56 | 0 | 24 | 51 | 21 | 19 | 36 | 25 | 0 | 222 | 93 | 37 | 560 | 46 | 0 | 50 | 25.5 | 99 | 217 | 0 | 0 | 0 | 1224 | 0 | 108 | 0 | 220 | 280 | 245 | 51 | 0 | 215 | 0 | 87 | 136 | 190 | 26 | 19 | 101 | 168 | 8 | 0 | 37 | 255 | 400 | 330 | 40 | 0 | 141 | 0 | 0 | 0 | 22 | 0 | 139 | 0 | 125 | 17 | 77 | 0 | 170 | 0 | 0 | 0 | 24 | 8656.92 | 841 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 920 | 0 | 0 | 0 | 1211.96 | 0 | 0 | 0 | 55 | 70 | 0 | 100 | 28 | 8 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 129 | 0 | 0 | 0 | 370 | 0 | 0 | 154 | 49 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 180 | 0 | 1100 | 510 | 17 | 6456.96 | 15113.88 | 104.56
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 206 | 54 | 17 | 120 | 126 | 245 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 35 | 290 | 0 | 0 | 0 | 143.42 | 9 | 22 | 0 | 320 | 0 | 16 | 56 | 0 | 27 | 51 | 21 | 36 | 36 | 25 | 0 | 222 | 93 | 37 | 565 | 89 | 0 | 50 | 25.5 | 89 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 220 | 280 | 235 | 51 | 0 | 184 | 0 | 90 | 136 | 193 | 26 | 19 | 102 | 166 | 8 | 0 | 37 | 255 | 396 | 330 | 40 | 0 | 128 | 0 | 0 | 0 | 22 | 0 | 142 | 0 | 125 | 17 | 78 | 0 | 173 | 0 | 0 | 0 | 24 | 8817.92 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 920 | 0 | 0 | 0 | 1202.03 | 0 | 0 | 0 | 55 | 70 | 0 | 100 | 28 | 8 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 129 | 0 | 0 | 0 | 332 | 0 | 0 | 159 | 49 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 180 | 0 | 1100 | 510 | 35 | 6497.03 | 15314.95
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 256 | 54 | 17 | 124 | 126 | 293 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 35 | 313 | 0 | 0 | 0 | 143.42 | 9 | 22 | 0 | 460 | 0 | 16 | 54 | 0 | 10 | 51 | 21 | 38 | 36 | 25 | 0 | 222 | 93 | 37 | 565 | 88 | 0 | 50 | 25.5 | 97 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 220 | 280 | 305 | 51 | 0 | 214 | 0 | 89 | 138 | 191 | 26 | 19 | 102 | 162 | 8 | 0 | 37 | 256 | 400 | 342 | 40 | 0 | 137 | 0 | 0 | 0 | 22 | 0 | 141 | 0 | 125 | 17 | 77 | 0 | 173 | 0 | 0 | 0 | 24 | 9202.92 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 920 | 0 | 0 | 0 | 1216.29 | 0 | 0 | 0 | 55 | 70 | 0 | 100 | 30 | 8 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 49 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1100 | 510 | 35 | 6632.29 | 15835.21 | 104.56
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 277 | 54 | 17 | 132 | 115 | 293 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 35 | 305 | 0 | 0 | 0 | 105 | 9 | 22 | 0 | 435 | 0 | 16 | 60 | 0 | 8 | 51 | 21 | 54.36 | 36 | 25 | 0 | 221 | 92 | 37 | 565 | 90 | 0 | 50 | 25.5 | 104 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 250 | 280 | 305 | 51 | 0 | 201 | 0 | 89 | 138 | 190 | 27 | 19 | 102 | 168 | 8 | 0 | 38 | 258 | 397 | 366 | 40 | 0 | 151 | 0 | 0 | 0 | 22 | 0 | 142 | 0 | 125 | 17 | 78 | 0 | 174 | 0 | 0 | 0 | 24 | 9264.86 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 920 | 0 | 0 | 0 | 1210.09 | 0 | 0 | 0 | 55 | 70 | 0 | 100 | 30 | 8 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 129 | 0 | 0 | 0 | 414 | 0 | 0 | 159 | 50 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1100 | 510 | 35 | 6629.09 | 15893.95 | 104.59
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 273 | 54 | 17 | 63 | 124 | 146 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 55 | 302 | 0 | 0 | 0 | 105 | 9 | 22 | 0 | 435 | 0 | 16 | 63 | 0 | 9 | 51 | 21 | 54.36 | 36 | 25 | 0 | 221 | 93 | 33 | 565 | 86 | 0 | 50 | 25.5 | 100 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 250 | 280 | 305 | 51 | 0 | 200 | 0 | 88 | 92 | 191 | 27 | 19 | 102 | 174 | 8 | 0 | 38 | 250 | 397 | 373 | 40 | 0 | 151 | 0 | 0 | 0 | 22 | 0 | 142 | 0 | 125 | 17 | 78 | 0 | 173 | 0 | 0 | 0 | 24 | 9015.86 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 920 | 0 | 0 | 0 | 1210.11 | 0 | 0 | 0 | 55 | 70 | 0 | 100 | 28 | 8 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 414 | 0 | 0 | 158 | 49 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1100 | 510 | 17 | 6608.11 | 15623.97 | 104.62
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 400 | 54 | 17 | 52 | 126 | 146 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 105 | 9 | 22 | 0 | 350 | 0 | 16 | 48 | 0 | 7 | 51 | 23 | 17 | 36 | 25 | 0 | 221 | 93 | 37 | 565 | 88 | 0 | 50 | 25.5 | 103 | 218 | 0 | 0 | 0 | 1224 | 0 | 130 | 0 | 230 | 300 | 280 | 51 | 0 | 214 | 0 | 89 | 92 | 192 | 27 | 19 | 102 | 178 | 8 | 0 | 38 | 250 | 397 | 373 | 40 | 0 | 152 | 0 | 0 | 0 | 22 | 0 | 142 | 0 | 126 | 17 | 78 | 0 | 173 | 0 | 0 | 0 | 24 | 8915.5 | 906 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 920 | 0 | 0 | 0 | 1210.34 | 0 | 0 | 0 | 55 | 70 | 0 | 99 | 28 | 8 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 414 | 0 | 0 | 159 | 49 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1100 | 510 | 17 | 6638.34 | 15553.84 | 104.65
Total KWH | 0 | 1752960 | 816960 | 0 | 0 | 0 | 0 | 0 | 8388000 | 0 | 6182880 | 695160 | 644760 | 1569456 | 1661280 | 2903771 | 96711 | 706251 | 2031840 | 0 | 0 | 0 | 0 | 0 | 656978 | 7148194 | 0 | 0 | 126487 | 2072400 | 208830 | 485640 | 0 | 9564090.91 | 1518000 | 381382 | 1043520 | 0 | 332160 | 347865 | 287088 | 390331 | 420480 | 369600 | 24000 | 5344485 | 2240618 | 696000 | 13570909.09 | 787855 | 0 | 1211040 | 402193.8 | 2461418 | 5165487 | 0 | 0 | 0 | 28614543 | 90990 | 2213018 | 0 | 5596000 | 7454000 | 6772000 | 1246350 | 0 | 4951000 | 83952 | 1346880 | 2917140 | 2407680 | 177240 | 444550 | 2470380 | 3615360 | 767414 | 450382 | 706656 | 6063000 | 8978100 | 8601000 | 951000 | 0 | 3449372.73 | 44305 | 44400 | 0 | 697920 | 0 | 3241700 | 0 | 3723660 | 149040 | 1480800 | 110656 | 2683200 | 0 | 10850 | 189630 | 558960 | 198010209.53 | 21802909 | 0 | 0 | 183840 | 0 | 0 | 0 | 0 | 364236 | 0 | 802512 | 492480 | 24203640 | 0 | 0 | 0 | 25711636 | 0 | 0 | 0 | 397632 | 823872 | 0 | 808400 | 241018 | 200443 | 244648 | 398650 | 316516 | 0 | 317632 | 0 | 0 | 3219282 | 0 | 0 | 0 | 8887200 | 0 | 29280 | 3906000 | 1063854 | 2725190 | 167126 | 1086326 | 0 | 468720 | 0 | 40525.56 | 1179360 | 2140 | 1016736 | 4865000 | 2762000 | 5291820 | 0 | 24116364 | 13185454.55 | 466800 | 151789242.11 | 349799451.64