## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 30-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-08-2026 | during | 30-08-2026 | during | 30-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 348 | 331 | 412 | 412 | 300 | 300 | Gas shortage
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 0 | 0 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 312 | 318 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 35 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 126 | 149.36 | 149.36 | 45 | 142 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 6 | 5 | 33 | 33 | 33 | 33 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 50 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 81 | 278 | 300 | 300 | 175 | 145 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 122 | 149 | 149 | 52 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 88 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 5 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 340 | 340 | 584 | 584 | 380 | 450 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 289 | 248 | 718 | 718 | 214 | 214 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1839.42 | 2397.42 | 5398.16 | 5370.16 | 2040.61 | 2430.61
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 182 | 222 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 216 | 210 | 210 | 210 | 210 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 87 | 88 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 24 | 14 | 32 | 14 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 50 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 2 | 0 | 25 | 32 | 25 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 37 | 58 | 95.1 | 95.1 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.69 | 0 | 4.33 | 0 | 4.33 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 37 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 105 | 104 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 50 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 21 | 71 | 163 | 163 | 88 | 160 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1192 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 46 | 28 | 18 | 8 | 18 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 558 | 558 | 575 | 575 | 575 | 575 | GT-2 U/M
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2579.69 | 2871.5 | 3295.29 | 3350.96 | 2617.83 | 2797.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 211 | 194 | 221.25 | 221.25 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 0 | 24 | 350.01 | 350.01 | 300 | 300 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 320 | 290 | 342.01 | 342.01 | 250 | 250 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 375 | 393 | 393 | 230 | 230 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 53 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 82 | 150 | 150 | 150 | 50 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 37 | 36 | 40 | 40 | 35 | 35 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 20 | 163 | 163 | 140 | 140 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 101 | 190 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 164 | 176 | 0 | 0 | 0 | 0 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 102 | 86 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 34 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 89 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1752 | 1742 | 2683.44 | 2618.44 | 1729.7 | 1830.7
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-08-2026 | during | 30-08-2026 | during | 30-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.7 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 163 | 120 | 170 | 120 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 87 | 70 | 90 | 70 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.53 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 0 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 256.23 | 267 | 547.6 | 546.5 | 283.1 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 143 | 137 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 140 | 142 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 22 | 83 | 84 | 84 | 22 | 22 | Gas shortage
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 126 | 126 | 125 | 125 | 120 | 120 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 16 | 8 | 8 | 8 | 8 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 246 | 293 | 341 | 341 | 260 | 260 | Gas shortage
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 380 | 235 | 380 | 390 | 310 | 310 | Gas shortage
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 393 | 392 | 383 | 383 | 383 | 383 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1501 | 1464 | 1714 | 1724 | 1450 | 1450
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 906 | 920 | 750 | 750 | 750 | 750 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 32 | 32 | 30 | 30 | Engine Problem
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 67 | 85 | 105 | 105 | 15 | 15 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 37 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 220 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 920 | 920 | 920 | 920 | 1100 | 1100 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1930 | 2145 | 2967 | 2882 | 1980 | 1895
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 922 | 1130 | 1000 | 1100 | 1000 | 1100 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 32 | 64 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 116 | 116 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 510 | 510 | 580 | 580 | 500 | 500 | machine problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 200 | 307 | 307 | 200 | 200 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.58 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2017.58 | 2257 | 2488 | 2587 | 2074 | 2173
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 60.27 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 27 | 40 | 40 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 0 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 125 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 350 | 382 | 413.79 | 413.79 | 372 | 372 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 10 | 20 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 55 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 2.89 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 910.4 | 1307.94 | 1469.13 | 1469.13 | 900 | 900 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 50.07 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 54 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1605.63 | 2044.14 | 3261.04 | 3043.12 | 1668.12 | 1600.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 150 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 46 | 48 | 48 | 48 | 48 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 159 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 99 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.9 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 99 | 114 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 158 | 0 | 158.71 | 0 | 158.71 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 497.9 | 568 | 664.71 | 470 | 551.71 | 392
System Total |  |  |  |  | 28843.2 | 29158.791 | 13979.45 | 15756.06 | 23019.24 | 22592.18 | 14395.07 | 14858.01
Forecast Scenario (30-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15390 |  | 2865 |  | 18390
|  |  |  | 1:00 | 14270 |  | 3313.85 |  | 17740
|  |  |  | 2:00 | 14270 |  | 2941.4 |  | 17350
|  |  |  | 3:00 | 14190 |  | 2674 |  | 16990
|  |  |  | 4:00 | 14190 |  | 2368.4 |  | 16670
|  |  |  | 5:00 | 14240 |  | 2072.35 |  | 16410
|  |  |  | 6:00 | 13980 |  | 1852.7 |  | 15920
|  |  |  | 7:00 | 13900 |  | 1833.6 |  | 15820
|  |  |  | 8:00 | 14110 |  | 1594.85 |  | 15780
|  |  |  | 9:00 | 14270 |  | 1489.8 |  | 15830
|  |  |  | 10:00 | 14430 |  | 1346.55 |  | 15840
|  |  |  | 11:00 | 14570 |  | 1461.15 |  | 16100
|  |  |  | 12:00 | 14630 |  | 1967.3 |  | 16690
|  |  |  | 13:00 | 14480 |  | 2148.75 |  | 16730
|  |  |  | 14:00 | 14650 |  | 1948.2 |  | 16690
|  |  |  | 15:00 | 14450 |  | 2416.15 |  | 16980
|  |  |  | 16:00 | 14210 |  | 2320.65 |  | 16640
|  |  |  | 17:00 | 14310 |  | 1871.8 |  | 16270
|  |  |  | 18:00 | 14450 |  | 1394.3 |  | 15910
|  |  |  | 18:30 | 15000 |  | 1637.825 |  | 16715
|  |  |  | 19:00 | 15630 |  | 1804.95 |  | 17520
|  |  |  | 19:30 | 15550 |  | 2320.65 |  | 17980
|  |  |  | 20:00 | 15950 |  | 1900.45 |  | 17940
|  |  |  | 21:00 | 16060 |  | 1938.65 |  | 18090
|  |  |  | 22:00 | 16140 |  | 1652.15 |  | 17870
|  |  |  | 23:00 | 15500 |  | 2301.55 |  | 17910
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 16690.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1938.65
Probable Maximum Demand at Evening Peak: |  |  | 18090.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16060.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 352.27 MKWHr. |  | 569 | 150 | 150 | 250 | 100 | 250 | 70 | 200 | 200 | 1939
*** This report is generated digitally from Operation Information System (OIS) at 08:51 hrs on 30-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 29-08-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13979.45 | MW | 10:00 Hr. | Energy Generated |  |  | 348.5842 |  | MKWHr.
| Day Peak Demand |  |  | 16562.04 | MW | 12:00 Hr. | Energy Unserverd |  |  | 60.796 |  | MKWHr.
| Evening Peak Generation |  |  | 15756.06 | MW | 20:00 Hr. | Energy Demand |  |  | 409.3802 |  | MKWHr.
| Evening Peak Demand |  |  | 18830.06 | MW | 20:00 Hr. | Maximum Temperature |  |  | 32 |  | °C
| Minimum Generation of the Day |  |  | 13417.74 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 836.55 |  | MMCFD
| Maximum Generation of the Day |  |  | 15756.06 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 7.8318 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.6008 | 0 | 16.4055 | 0 | 0 | 0.22814 | 0 | 0 | 54.2345 | Gas | 121.2532 | Gas | 402834197.6776
| Chattogram Zone |  |  | 5.2564 | 42.4309 | 11.3586 | 0 | 4.7678 | 0.11517 | 0 | 0.72624 | 64.6551 | Coal | 111.864 | Coal | 793497549.1478
| Cumilla Zone |  |  | 26.1993 | 0 | 9.9068 | 0 | 0 | 0.41693 | 3.8237 | 0 | 40.3467 | HFO | 52.7273 | HFO | 1072095660.472
| Mymensingh Zone |  |  | 0 | 0 | 4.5817 | 0 | 0 | 0.44556 | 0 | 0 | 5.0273 | HSD | 2.4998 | HSD | 64483475.24
| Sylhet Zone |  |  | 32.9611 | 0 | 0 | 0 | 0 | 0.084771 | 0 | 0 | 33.0459 | Hydro | 4.7678 | Hydro | 476778.9
| Khulna Zone |  |  | 0 | 22.1673 | 2.1866 | 1.1902 | 0 | 0.55728 | 21.9927 | 0 | 48.0941 | Solar | 4.7931 | Solar | 76980390.6808
| Barishal Zone |  |  | 8.0886 | 42.2216 | 1.5208 | 0 | 0 | 0.004153 | 0 | 0 | 51.8351 | Import | 49.9528 | Import | 308980858.12
| Rajshahi Zone |  |  | 11.147 | 0 | 3.0086 | 0 | 0 | 1.4811 | 24.1364 | 0 | 39.773 | Wind | 0.72624 | Wind | 10682990.4
| Rangpur Zone |  |  | 0 | 5.0441 | 3.7587 | 1.3096 | 0 | 1.46 | 0 | 0 | 11.5724
| Total |  |  | 121.2532 | 111.864 | 52.7273 | 2.4998 | 4.7678 | 4.7931 | 49.9528 | 0.72624 | 348.5842
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 402834197.6776 |  | Hydro | 476778.9
|  |  |  | Coal | 793497549.1478 |  | Solar | 76980390.6808
|  |  |  | HFO | 1072095660.472 |  | Import | 308980858.12
|  |  |  | HSD | 64483475.24 |  | Wind | 10682990.4
[5 empty] | Total: | 273,00,31,900 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9927 | Peak Hr Flow | 920.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 40634400 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.1364 | Peak Hr Flow | 1307.94 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1901 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.8237 | Peak Hr Flow | 176.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2342 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.9528 | Peak Hr Flow | 2403.94 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 697 |  | 6378
|  |  |  | Chattogram |  | 196 |  | 1678
|  |  |  | Cumilla |  | 261 |  | 1697
|  |  |  | Mymensingh |  | 463 |  | 1663
|  |  |  | Sylhet |  | 220 |  | 811
|  |  |  | Khulna |  | 427 |  | 2197
|  |  |  | Barishal |  | 86 |  | 586
|  |  |  | Rajshahi |  | 333 |  | 1900
|  |  |  | Rangpur |  | 259 |  | 1257
|  |  |  | Total |  | 2942 |  | 18167
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 0
|  |  |  | Total Unavailable Capacity |  |  |  | 300
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:28 | 16:12 | Kasba 132/33kV S/S TR-2 HT Project Work S/D Due to Replacement of poles for PBS 33kV
double circuit line.
| 08:28 | 16:13 | Kasba 132/33kV S/S TR-2 LT Project Work S/D Due to Replacement of poles for PBS 33kV | [7 empty] | 20.0MW load
|  |  | double circuit line. | [7 empty] | interrup.
| 08:30 | 11:45 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to Insulator change PBS side
| 08:30 | 11:38 | Kodda 132/33kV S/S 33kV BUS-1 of Section-3 Scheduled S/D Due to PBS WORK | [7 empty] | 65.0MW load
interrup.
| 08:30 | 11:38 | Kodda 132/33kV S/S 33kV BUS-2 of Section-3 Scheduled S/D Due to PBS WORK | [7 empty] | 65.0MW load
interrup.
| 08:30 | 11:45 | Kodda 132/33kV S/S Tr-5 (446T) HT Scheduled S/D Due to PBS WORK
| 08:40 |  | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 LT Project Work S/D Due to SAS integration
| 08:41 |  | Kaliakoir 400/230/132kV S/S 400/132kV TR-3 HT Project Work S/D Due to SAS Integration
|  | 08:55 | Chandpur 132/33kV S/S 402T (T-01) HT is restored.
|  | 08:55 | Chandpur 132/33kV S/S 402T (T-01) LT is restored.
|  | 08:55 | Chandpur 132/33kV S/S 33 kV T-1 Section is restored.
| 08:55 |  | Chandpur 132/33kV S/S 412T (T-2) LT Forced S/D Due to N/A
|  | 09:13 | Noapara 132/33kV S/S T-1 HT is restored.
|  | 09:15 | Noapara 132/33kV S/S T-1 LT is restored.
| 09:32 | 13:03 | Kaliakoir 400/230/132kV S/S 230kV Bus 1 Project Work S/D Due to measurement of tube bus
| 10:00 |  | Day Peak Generation: 13979 MW.
|  | 10:02 | Patiya 132/33kV S/S TRAFO-01 HT is restored.
|  | 10:03 | Patiya 132/33kV S/S TRAFO-01 LT is restored.
| 10:13 | 15:16 | Goalpara- Khulna (C) 132kV Ckt-2 Scheduled S/D from Goalpara 132/33kV end Due to KHULNA
POWER STATION WORKS
| 10:13 | 11:23 | Amnura 132/33kV S/S T-1 (406T) HT Scheduled S/D Due to Maintenance work
| 10:13 | 15:14 | Goalpara- Khulna (C) 132kV Ckt-1 Scheduled S/D from Goalpara 132/33kV end Due to KHULNA
POWER STATION WOEKS.
| 10:14 | 11:32 | Amnura 132/33kV S/S T-1 (406T) LT Scheduled S/D Due to Maintenance work
| 10:25 |  | Mirsorai 400/230/33kV S/S ATR-2 LT Project Work S/D Due to Project Work (CAF/DFDR)
| 10:28 |  | Mirsorai 400/230/33kV S/S ATR-2 HT Project Work S/D Due to Project Work (CAF/DFDR)
| 10:34 | 19:28 | Bhulta 400/230/132kV S/S 132kV Araihazar-01 Scheduled S/D Due to Teleprotection Test
| 10:36 | 19:28 | Bhulta 400/230/132kV S/S 132kV Araihazar-02 Scheduled S/D Due to Teleprotection Test
| 10:42 | 11:56 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to T2 33 kv cb SF6 Leak check.
| 10:43 | 11:55 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to T2 33 kv CB SF6 leak check
| 11:11 | 11:26 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) LT Forced S/D | [7 empty] | 5.0MW load
interrup.
| 11:11 | 11:25 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) HT Forced S/D Due to 132 kv Y-phase CT | [7 empty] | 5.0MW load
|  |  | high tempareture. | [7 empty] | interrup.
| 11:35 | 12:54 | Amnura 132/33kV S/S T-2 (416T) HT Scheduled S/D Due to Maintenance work
| 11:36 | 12:57 | Amnura 132/33kV S/S T-2 (416T) LT Scheduled S/D Due to Maintenance work
| 12:25 | 12:38 | Fenchuganj-Sreemangal 132kV Ckt-2 Tripped from Sreemongol 132/33kV end showing Distance
relays Due to Fault Trip-Aided trip
| 12:37 | 16:12 | Kasba 132/33kV S/S TR-1 HT Scheduled S/D Due to PBS work new line construction | [7 empty] | 20.0MW load
interrup.
| 12:40 | 16:15 | Kasba 132/33kV S/S TR-1 LT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
| 12:53 | 18:14 | Ishurdi 230/132kV S/S 230/132 kV T-02 LT Scheduled S/D Due to maintenance
| 12:54 | 18:14 | Ishurdi 230/132kV S/S 230/132 kV T-02 HT Scheduled S/D
|  | 13:17 | Chapai 132/33kV S/S T-4 (435T) HT is restored.
|  | 13:17 | Chapai 132/33kV S/S T-4 (435T) HT is restored.
|  | 13:54 | Mongla 132/33kV S/S T-1 HT is restored.
|  | 13:54 | Mongla 132/33kV S/S T-1 LT is restored.
|  | 13:54 | Mongla 132/33kV S/S 33 KV Bus is restored.
|  | 13:55 | Mongla 132/33kV S/S T-2 LT is restored.
|  | 13:55 | Mongla 132/33kV S/S T-2 HT is restored.
| 15:24 |  | Sirajgonj 225MW CCPP Unit-2 Tripped with remarks:- ST
| 15:31 |  | Sirajgonj 225MW CCPP Unit-2 Tripped with remarks:- GT
| 17:13 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 17:23 |  | Ashuganj 450 MW CCPP(North) Synchronized with remarks:- gt
| 20:00 |  | Evening Peak Generation: 15756 MW.
| 05:59 | 06:08 | Mymensingh 132/33kV S/S Transformer-2 (414T) LT Tripped showing Over current relays. | [7 empty] | 60.0MW load
interrup.
| 05:59 | 06:08 | Mymensingh 132/33kV S/S Transformer-1 (404T) LT Tripped showing Over current relays. | [7 empty] | 60.0MW load
interrup.
| 07:00 |  | SS Power Tripped with remarks:- U-1
| 07:00 |  | Fenchuganj-Sreemangal 132kV Ckt-1 Project Work S/D from Sreemongol 132/33kV end Due to
Power Grid Network Strengthening Project under PGCB
| 07:01 |  | SS Power Synchronized with remarks:- U-2
| 07:01 |  | SS Power Synchronized with remarks:- U-2 False
| 07:01 |  | SS Power Synchronized with remarks:- U-2( False sms)
| 07:20 |  | Fenchuganj-Sreemangal 132kV Ckt-1 Project Work S/D from Fenchuganj 230/132/33kV end Due
to G to G Project Work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 29-08-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 331 | 7344000 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 377950 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 318 | 6754685 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 742320 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 126 | 2028480 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 719525 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 699325 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 5 | 163200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 5230800 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 638880 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 278 | 2919327 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 122 | 1527552 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1276800 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2181600 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 228137 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 5 | 304560 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 340 | 7946363.64 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 248 | 10161790 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 2989200 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2397.42 | 54234494.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 348539.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 89370 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1212480 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 4767789 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 216 | 4927141 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 88 | 2166181 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 275236 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 594916 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 548160 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 329280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 58 | 928320 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 25805 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 373855 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 37 | 382853 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 104 | 2545891 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 552000 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 71 | 1430182 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28947270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 28 | 726240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 558 | 13483636.36 | GT-2 U/M
Chattogram Area Total |  |  |  |  | 4885.967 | 2871.5 | 64655144.76
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 194 | 5041000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 24 | 1121300 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 290 | 7524000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 375 | 8622000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 223704 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 836364 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1221804 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1719563 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 862944 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 20 | 1185428 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 190 | 3096000 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 176 | 3823680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 200011 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 423680 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 86 | 2373480 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 34 | 250320 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 1404480 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 416927 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1742 | 40346685
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 140961 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 2596800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1543200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 292000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 297360 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 144360 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 267 | 5027281
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 84771 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 948000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 137 | 2943163.64 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 3238300 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 788160 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 126 | 2738450 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 152544 | Two Engine's is in under maintenance
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 293 | 5784000 | Gas shortage
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 235 | 6951000 | Gas shortage
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 392 | 9417500 | -
Sylhet Area Total |  |  |  |  | 2325 | 1464 | 33045888.64
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 920 | 21992727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 165600 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 2021040 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 557280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 220 | 1190229 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 920 | 22167270 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2145 | 48094146
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1130 | 24436363 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 64 | 1077984 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 116 | 2777000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 510 | 12919272.73 | machine problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5311560 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 442800 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 200 | 4866000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4153 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2257 | 51835132.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 391408 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 27 | 170697 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 251531 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 2084145 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 382 | 9062836 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 20 | 287930 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 457579 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 583728 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 819840 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 55 | 437280 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 36060 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1307.94 | 24136364 | Coal shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 372848 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 680750 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2044.14 | 39772996
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 150 | 1309613 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1144145 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 159 | 3900000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 1075756 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44651.28 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 114 | 2682897 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 172631 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1242720 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 568 | 11572413.28
Eastern Grid Total |  |  |  |  | 17427.666 | 8741.92 | 197309494.04
Western Grid Total |  |  |  |  | 11731.125 | 7014.14 | 151274688.01
National Grid Total |  |  |  |  | 29158.791 | 15756.06 | 348584182.05
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 29-08-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10389.8 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4834.6 | MW
i) Dhaka area |  |  | 5680.8 |  | MW | i) Khulna area |  |  |  | 1770 | MW
ii) Chattogram area |  |  | 1482 |  | MW | ii) Barishal area |  |  |  | 500 | MW
iii) Cumilla area |  |  | 1436 |  | MW | iii) Rajshahi area |  |  |  | 1566.6 | MW
iv) Mymensingh area |  |  | 1200 |  | MW | iv) Rangpur area |  |  |  | 998 | MW
v) Sylhet area |  |  | 591 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15224.4 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 145 | 21:00 | 133 | Narshingdi | 194 | 20:00 | 199 | Uttara | 108 | 18:30
2 | AKSML | 182 | 14:00 | 68 | Hasnabad | 118 | 21:00 | 134 | Natore | 163 | 20:00 | 200 | UttaraNew | 57 | 00:00
3 | Aftabnagar | 46 | 00:00 | 69 | Hathazari | 89 | 23:00 | 135 | Nawabganj | 59.9 | 20:00 | 201 | Zigatola | 114 | 00:00
4 | Agargaon | 124 | 13:00 | 70 | Hatirjheel | 77 | 14:00 | 136 | Netrakona | 127 | 19:30
5 | Agrabad | 68 | 11:00 | 71 | Ishurdi | 81 | 20:00 | 137 | New | 96.8 | 18:30
6 | Amnura | 36 | 13:00 | 72 | Jaldhaka | 80 | 22:00 | 138 | Niamatpur | 74 | 05:00
7 | Ashuganj | 87 | 20:00 | 73 | Jamalpur | 130 | 00:00 | 139 | Noapara | 41 | 19:30
8 | BSRM | 198 | 04:00 | 74 | Jashore | 186 | 19:00 | 140 | PHP | 9 | 02:00
9 | Bagerhat | 78 | 02:00 | 75 | Jhenaidah | 92 | 21:00 | 141 | Pabna | 103 | 22:00
10 | Bajitpur | 100 | 21:00 | 76 | Joydebpur | 192 | 19:00 | 142 | Palashbari | 122 | 07:00
11 | Bakerganj | 15.4 | 21:00 | 77 | Joypurhat | 63 | 22:00 | 143 | Panchagarh | 75 | 19:00
12 | Bakulia | 94 | 20:00 | 78 | Juldah | 16 | 14:00 | 144 | Patiya | 20 | 14:00
13 | Banani | 48 | 13:00 | 79 | KSRM | 35 | 05:00 | 145 | Patnitala | 38 | 22:00
14 | Bangabhaban | 8 | 12:00 | 80 | Kabirpur | 294 | 19:30 | 146 | Patuakhali | 64 | 20:00
15 | Barapukuria | 60 | 19:30 | 81 | Kachua | 86 | 01:00 | 147 | Payra | 32 | 00:00
16 | Barguna | 22 | 19:30 | 82 | Kaliganj | 39 | 00:00 | 148 | Postogola | 63 | 18:00
17 | Barishal | 102 | 20:00 | 83 | Kallyanpur | 132 | 19:00 | 149 | Pubail | 48 | 21:00
18 | Barishal-230 | 106 | 20:00 | 84 | Kalurghat | 39 | 20:00 | 150 | Purbachal | 22 | 21:00
19 | Baroaulia | 72 | 13:00 | 85 | Kamrangirchar | 77 | 18:00 | 151 | Purbasadipur | 127 | 22:00
20 | Baroirhat | 60 | 05:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 31 | 00:00
21 | Bashundhara | 225 | 18:30 | 87 | Kasba | 52 | 18:30 | 153 | Rahim | 55 | 21:00
22 | BashundharaCement | 5 | 11:00 | 88 | Kazla | 128 | 14:00 | 154 | Rajbari | 78 | 00:00
23 | Beanibazar | 66 | 21:00 | 89 | Keranigonj | 96 | 21:00 | 155 | Rajendrapur | 116 | 20:00
24 | Benapole | 67 | 12:00 | 90 | Khagrachori | 36 | 21:00 | 156 | Rajshahi | 98 | 00:00
25 | Bhaluka | 167 | 19:30 | 91 | Khulna | 61 | 18:30 | 157 | Rajshahi-230 | 110 | 22:00
26 | Bhandaria | 58 | 22:00 | 92 | Khulshi | 193 | 18:30 | 158 | Ramganj | 94 | 11:00
27 | Bhangura | 36 | 07:00 | 93 | Kishoreganj | 134 | 22:00 | 159 | Rampur | 44 | 23:00
28 | Bheramara(GK) | 66 | 00:00 | 94 | Kodda | 297 | 19:30 | 160 | Rangamati | 18 | 18:00
29 | Bhulta | 225 | 21:00 | 95 | Kulaura | 52 | 02:00 | 161 | Rangpur | 129 | 19:30
30 | Bog-Sherpur | 78 | 21:00 | 96 | Kurigram | 62 | 11:00 | 162 | Ruppur | 3 | 10:00
31 | Bogura | 225 | 19:00 | 97 | Kushtia | 143 | 20:00 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 72 | 19:30 | 98 | Laksam | 36 | 00:00 | 164 | Saidpur | 107 | 19:00
33 | Brahmanbaria | 123 | 19:30 | 99 | Lakshmipur | 39 | 20:00 | 165 | Santhia | 36 | 22:00
34 | Cantonment | 142 | 13:00 | 100 | Lalbag | 92 | 13:00 | 166 | Satkhira | 133 | 19:00
35 | Chandina | 32 | 15:00 | 101 | Lalmonirhat | 62 | 22:00 | 167 | Satmasjid | 118 | 14:00
36 | Chandpur | 76 | 22:00 | 102 | MI_Cement | 16.7 | 01:00 | 168 | Savar | 218 | 19:30
37 | Chandraghona | 33 | 22:00 | 103 | Madanganj | 44 | 09:00 | 169 | SevenRings | 19.56 | 12:00
38 | Chapai | 70 | 21:00 | 104 | Madaripur | 97 | 00:00 | 170 | ShahCement | 20 | 00:00
39 | Charfasson | 32 | 20:00 | 105 | Madartek | 97 | 00:00 | 171 | Shahjadpur | 80 | 19:00
40 | Charsaidpur | 35 | 01:00 | 106 | Madunaghat | 56 | 19:30 | 172 | Shahjibazar | 131 | 22:00
41 | Chauddagram | 68 | 18:30 | 107 | Magura | 64 | 00:00 | 173 | Shahmirpur | 53 | 18:00
42 | Chhatak | 34 | 21:00 | 108 | Mahasthangarh | 79 | 22:00 | 174 | Shariatpur | 88 | 20:00
43 | Chowmuhani | 151 | 19:00 | 109 | Maijdee | 28 | 03:00 | 175 | Sherpur | 156 | 00:00
44 | Chuadanga | 113 | 13:00 | 110 | Manikganj | 129 | 20:00 | 176 | Shikalbaha | 41 | 19:30
45 | Coxsbazar | 136 | 18:30 | 111 | Maniknagar | 83 | 14:00 | 177 | Shitalakhya | 85.7 | 14:00
46 | Cumilla(N) | 148 | 19:30 | 112 | Matarbari | 54 | 19:00 | 178 | Sholosohor | 48 | 19:30
47 | Cumilla(S) | 183 | 19:00 | 113 | Matuail | 78.8 | 14:00 | 179 | Shomvuganj | 40 | 19:30
48 | Daganbhuiyan | 39 | 20:00 | 114 | Metrorail_Motijheel | 32 | 11:00 | 180 | Shyampur | 164 | 10:00
49 | Daudkandi | 129 | 20:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 150 | 13:00
50 | DhakaUniversity | 88 | 13:00 | 116 | Millgate | 97 | 18:30 | 182 | Sirajganj | 134 | 19:00
51 | Dhamrai | 100 | 17:00 | 117 | Mirpur | 167 | 18:30 | 183 | Sitakunda | 0 | 00:00
52 | Dhanmondi | 118 | 14:00 | 118 | Mirsorai | 41 | 12:00 | 184 | Sonargaon | 140 | 21:00
53 | Dohazari | 100 | 20:00 | 119 | Mirzapur | 44 | 00:00 | 185 | Sreemongol | 71 | 18:30
54 | Faridpur | 180 | 22:00 | 120 | Mithapukur | 72 | 19:30 | 186 | Sreepur | 120 | 19:30
55 | Fatullah | 116 | 17:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 55.83 | 20:00
56 | Fenchuganj | 40 | 22:00 | 122 | Mogbazar | 55 | 18:30 | 188 | Sunamganj | 50 | 21:00
57 | Feni | 102 | 21:00 | 123 | Mongla | 46 | 19:00 | 189 | Sylhet | 134 | 20:00
58 | GPH | 63 | 12:00 | 124 | Motijheel | 49 | 14:00 | 190 | Sylhet_(South) | 65 | 23:00
59 | Ghatail | 89 | 21:00 | 125 | Muktagacha | 51 | 11:00 | 191 | TK | 0 | 00:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 124 | 20:00 | 192 | Tangail | 178 | 00:00
61 | Ghorashal-230 | 104 | 20:00 | 127 | Muradnagar | 46 | 20:00 | 193 | Taraganj | 29 | 22:00
62 | Goalpara | 39 | 19:00 | 128 | Mymensingh | 150 | 12:00 | 194 | Tasnim | 44 | 21:00
63 | Gollamari | 104 | 00:00 | 129 | Nabinagar | 110 | 21:00 | 195 | Thakurgaon | 115 | 19:00
64 | Gopalganj | 100 | 20:00 | 130 | Naogaon | 124 | 22:00 | 196 | Tongi | 149 | 17:00
65 | Gulshan | 114 | 14:00 | 131 | Narail | 60 | 19:30 | 197 | Ullahpara | 42 | 20:00
66 | Halishahar | 145 | 12:00 | 132 | Narinda | 60 | 18:30 | 198 | Ullon | 62 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 29-08-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14925.14 | 2792 |  | 17842.78
1:00 | 14274.96 | 2576 |  | 16966.88
2:00 | 14116.59 | 2486 |  | 16714.46
3:00 | 14021.37 | 2447 |  | 16578.37
4:00 | 13662.04 | 2451 |  | 16223.04
5:00 | 13620.56 | 2359 |  | 16085.56
6:00 | 13417.74 | 2159 |  | 15673.74
7:00 | 13491.46 | 1909 |  | 15486.46
8:00 | 13592.99 | 1855 |  | 15531.47
9:00 | 13601.96 | 1711 |  | 15389.96
10:00 | 13979.45 | 1378 |  | 15419.46
11:00 | 13924.53 | 1764 |  | 15767.91
12:00 | 13945.04 | 2504 |  | 16562.04
13:00 | 14172.64 | 2263 |  | 16537.64
14:00 | 14283.84 | 2247 |  | 16631.84
15:00 | 13580.22 | 3612 |  | 17355.22
16:00 | 13592.18 | 3407 |  | 17152.18
17:00 | 13511.02 | 3517 |  | 17186.02
18:00 | 13817.41 | 3027 |  | 16980.41
19:00 | 14874.32 | 3010 |  | 18019.32
19:30 | 15590.05 | 2532 |  | 18236.05
20:00 | 15756.06 | 2942 |  | 18830.06
21:00 | 15722.64 | 2572 |  | 18410.64
22:00 | 15539.53 | 2862 |  | 18530.53
23:00 | 15384.98 | 2946 |  | 18463.98
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 29-08-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 117 | 32 | 330 | 140 | 1216 | 538 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 115 | 29 | 310 | 134 | 1246 | 510
2:00 | 114 | 26 | 296 | 130 | 1262 | 474 |  | Import | 0
3:00 | 106 | 24 | 228 | 120 | 1238 | 458
4:00 | 80 | 13 | 228 | 108 | 610 | 424 | Ishurdi-Ghorashal Ckt-2 | Export | 3146400
5:00 | 89 | 18 | 228 | 114 | 1118 | 420
6:00 | 81 | 13 | 220 | 112 | 1074 | 400 |  | Import | 0
7:00 | 89 | 13 | 226 | 110 | 1136 | 420
8:00 | 105 | 25 | 254 | 136 | 1222 | 496 | Sirajganj-Sreepur Ckt-1 | Export | 1941000
9:00 | 143 | 44 | 324 | 140 | 1436 | 618
10:00 | 161 | 64 | 338 | 158 | 1474 | 724 |  | Import | 0
11:00 | 149 | 55 | 350 | 160 | 1446 | 688
12:00 | 172 | 58 | 410 | 166 | 1596 | 742 | Sirajganj-Sreepur Ckt-2 | Export | 1947000
13:00 | 157 | 50 | 360 | 170 | 1494 | 720
14:00 | 190 | 75 | 458 | 192 | 1694 | 846 |  | Import | 0
15:00 | 161 | 57 | 350 | 144 | 1552 | 738
16:00 | 151 | 50 | 310 | 144 | 1514 | 694 | Gopalganj-Aminbazar Ckt-1 | Export | 16780000
17:00 | 155 | 51 | 320 | 134 | 1500 | 702
18:00 | 151 | 51 | 320 | 152 | 1500 | 732 |  | Import | 0
18:30 | 136 | 36 | 310 | 136 | 1420 | 652
19:00 | 134 | 30 | 320 | 122 | 1432 | 582 | Gopalganj-Aminbazar Ckt-2 | Export | 16820000
19:30 | 142 | 26 | 400 | 156 | 1496 | 574
20:00 | 131 | 19 | 360 | 142 | 1410 | 550 |  | Import | 0
21:00 | 119 | 14 | 390 | 160 | 1430 | 572
22:00 | 128 | 26 | 370 | 148 | 1396 | 534 |  | Total Export | 40634400
23:00 | 111 | 18 | 350 | 142 | 1388 | 554 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 29-08-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8514.5 | 6410.64 | 14925.14 | DAILY GENERATION CURVE
00:30 | 8290.25 | 6309.8 | 14600.05
01:00 | 8066 | 6208.96 | 14274.96 | 29-08-2026
01:30 | 8009.5 | 6186.275 | 14195.775
02:00 | 7953 | 6163.59 | 14116.59
02:30 | 7904 | 6164.98 | 14068.98
03:00 | 7855 | 6166.37 | 14021.37
03:30 | 7834 | 6007.705 | 13841.705
04:00 | 7813 | 5849.04 | 13662.04
04:30 | 7789 | 5852.3 | 13641.3
05:00 | 7765 | 5855.56 | 13620.56
05:30 | 7682.215 | 5836.935 | 13519.15
06:00 | 7599.43 | 5818.31 | 13417.74
06:30 | 7611.385 | 5843.215 | 13454.6
07:00 | 7623.34 | 5868.12 | 13491.46
07:30 | 7617.75 | 5924.475 | 13542.225
08:00 | 7612.16 | 5980.83 | 13592.99
08:30 | 7597.37 | 6000.105 | 13597.475
09:00 | 7582.58 | 6019.38 | 13601.96
09:30 | 7755.46 | 6035.245 | 13790.705
10:00 | 7928.34 | 6051.11 | 13979.45
10:30 | 7895.33 | 6056.66 | 13951.99
11:00 | 7862.32 | 6062.21 | 13924.53
11:30 | 7772.125 | 6162.66 | 13934.785
12:00 | 7681.93 | 6263.11 | 13945.04
12:30 | 7811.555 | 6247.285 | 14058.84
13:00 | 7941.18 | 6231.46 | 14172.64
13:30 | 7989.645 | 6238.595 | 14228.24
14:00 | 8038.11 | 6245.73 | 14283.84
14:30 | 7797.465 | 6134.565 | 13932.03
15:00 | 7556.82 | 6023.4 | 13580.22
15:30 | 7605.46 | 5980.74 | 13586.2
16:00 | 7654.1 | 5938.08 | 13592.18
16:30 | 7630.14 | 5921.46 | 13551.6
17:00 | 7606.18 | 5904.84 | 13511.02
17:30 | 7745.765 | 5918.45 | 13664.215
18:00 | 7885.35 | 5932.06 | 13817.41
18:30 | 8041.885 | 6303.98 | 14345.865
19:00 | 8198.42 | 6675.9 | 14874.32
19:30 | 8581.92 | 7008.13 | 15590.05
20:00 | 8741.92 | 7014.14 | 15756.06
20:30 | 8734.6 | 7004.75 | 15739.35 |  | Executive Engineer
21:00 | 8727.28 | 6995.36 | 15722.64 |  | Network Operation Division
21:30 | 8623.78 | 7007.305 | 15631.085
22:00 | 8520.28 | 7019.25 | 15539.53
22:30 | 8551.1 | 6911.155 | 15462.255
23:00 | 8581.92 | 6803.06 | 15384.98

## En-Curve
QF-LDC-12
Date | 29-08-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3385 | 1625 | 905 | 0 | 170 | 1207.64 | 221 | 4620 | 0 | 686 | 2098.5 | 0 | 0 | 7 | 2792 | DAILY ENERGY CURVE
00:30 | 3369 | 1640 | 905 | 0 | 171 | 1085.8 | 220 | 4618 | 0 | 591.5 | 1832.75 | 157.5 | 0 | 9.5 | 2684 | 29-08-2026
01:00 | 3353 | 1655 | 905 | 0 | 172 | 963.96 | 219 | 4616 | 0 | 497 | 1567 | 315 | 0 | 12 | 2576
01:30 | 3333 | 1634.5 | 905 | 0 | 170 | 932.775 | 218.5 | 4615.5 | 0 | 489.5 | 1570 | 315 | 0 | 12 | 2531 | Energy Generated | 348.5842 |  | MKWHr
02:00 | 3313 | 1614 | 905 | 0 | 168 | 901.59 | 218 | 4615 | 0 | 482 | 1573 | 315 | 0 | 12 | 2486 | Energy not Served | 60.796 |  | MKWHr
02:30 | 3278.5 | 1623 | 905 | 0 | 166 | 902.98 | 217.5 | 4615 | 0 | 458.5 | 1567 | 315 | 0 | 20.5 | 2466.5 | Total Energy Requirement | 409.3802 |  | MKWHr
03:00 | 3244 | 1632 | 905 | 0 | 164 | 904.37 | 217 | 4615 | 0 | 435 | 1561 | 315 | 0 | 29 | 2447
03:30 | 3241 | 1657.5 | 905.5 | 0 | 159 | 905.205 | 217 | 4615 | 0 | 430 | 1531 | 157.5 | 0 | 23 | 2449
04:00 | 3238 | 1683 | 906 | 0 | 154 | 906.04 | 217 | 4615 | 0 | 425 | 1501 | 0 | 0 | 17 | 2451
04:30 | 3242 | 1700 | 905.5 | 0 | 156 | 907.8 | 217.5 | 4617 | 0 | 411 | 1471.5 | 0 | 0 | 13 | 2405
05:00 | 3246 | 1717 | 905 | 0 | 158 | 909.56 | 218 | 4619 | 0 | 397 | 1442 | 0 | 0 | 9 | 2359
05:30 | 3243 | 1717.5 | 905 | 0 | 152 | 908.96 | 218.5 | 4582.5 | 5.69 | 375.5 | 1400.5 | 0 | 0 | 10 | 2259
06:00 | 3240 | 1718 | 905 | 0 | 146 | 908.36 | 219 | 4546 | 11.38 | 354 | 1359 | 0 | 0 | 11 | 2159
06:30 | 3277.5 | 1714.5 | 905 | 0 | 143 | 907.71 | 198 | 4563.5 | 52.39 | 354.5 | 1330.5 | 0 | 0 | 8 | 2034
07:00 | 3315 | 1711 | 905 | 0 | 140 | 907.06 | 177 | 4581 | 93.4 | 355 | 1302 | 0 | 0 | 5 | 1909
07:30 | 3365.5 | 1641 | 905.5 | 0 | 144 | 906.735 | 179 | 4567 | 188.49 | 354.5 | 1286 | 0 | 0 | 4.5 | 1882
08:00 | 3416 | 1571 | 906 | 0 | 148 | 906.41 | 181 | 4553 | 283.58 | 354 | 1270 | 0 | 0 | 4 | 1855
08:30 | 3412.5 | 1416.75 | 905.5 | 0 | 153 | 907.955 | 181 | 4567.5 | 366.56 | 382.21 | 1288 | 0 | 0 | 16.5 | 1783
09:00 | 3409 | 1262.5 | 905 | 0 | 158 | 909.5 | 181 | 4582 | 449.54 | 410.42 | 1306 | 0 | 0 | 29 | 1711
09:30 | 3494 | 1337.75 | 905.5 | 0 | 161 | 909.95 | 181.5 | 4545.5 | 516.085 | 385.92 | 1316 | 0 | 0 | 37.5 | 1544.5
10:00 | 3579 | 1413 | 906 | 0 | 164 | 910.4 | 182 | 4509 | 582.63 | 361.42 | 1326 | 0 | 0 | 46 | 1378
10:30 | 3579.5 | 1387 | 905.5 | 0 | 160 | 913.86 | 182 | 4532.5 | 543.21 | 370.42 | 1328.5 | 0 | 0 | 49.5 | 1571
11:00 | 3580 | 1361 | 905 | 0 | 156 | 917.32 | 182 | 4556 | 503.79 | 379.42 | 1331 | 0 | 0 | 53 | 1764
11:30 | 3493 | 1338.25 | 905.5 | 0 | 160 | 920.04 | 182 | 4573 | 599.575 | 379.42 | 1337.5 | 0 | 0 | 46.5 | 2134
12:00 | 3406 | 1315.5 | 906 | 0 | 164 | 922.76 | 182 | 4590 | 695.36 | 379.42 | 1344 | 0 | 0 | 40 | 2504
12:30 | 3425.5 | 1325 | 906 | 0 | 163 | 922.88 | 182 | 4578.5 | 657.54 | 388.42 | 1473 | 0 | 0 | 37 | 2383.5
13:00 | 3445 | 1334.5 | 906 | 0 | 162 | 923 | 182 | 4567 | 619.72 | 397.42 | 1602 | 0 | 0 | 34 | 2263
13:30 | 3448.5 | 1371.5 | 905.5 | 0 | 160 | 925.97 | 182 | 4572 | 609.85 | 412.42 | 1615 | 0 | 0 | 25.5 | 2255
14:00 | 3452 | 1408.5 | 905 | 0 | 158 | 928.94 | 182 | 4577 | 599.98 | 427.42 | 1628 | 0 | 0 | 17 | 2247
14:30 | 3350 | 1419 | 905 | 0 | 143 | 927.155 | 180 | 4558.5 | 506.955 | 426.92 | 1492 | 0 | 0 | 23.5 | 2929.5
15:00 | 3248 | 1429.5 | 905 | 0 | 128 | 925.37 | 178 | 4540 | 413.93 | 426.42 | 1356 | 0 | 0 | 30 | 3612
15:30 | 3209.5 | 1445.5 | 905.5 | 0 | 134 | 923.015 | 178 | 4548.5 | 352.765 | 425.92 | 1433 | 0 | 0 | 30.5 | 3509.5
16:00 | 3171 | 1461.5 | 906 | 0 | 140 | 920.66 | 178 | 4557 | 291.6 | 425.42 | 1510 | 0 | 0 | 31 | 3407
16:30 | 3148.5 | 1439 | 910 | 0 | 142 | 922.41 | 178 | 4570.5 | 213.27 | 424.92 | 1568.5 | 0 | 0 | 34.5 | 3462
17:00 | 3126 | 1416.5 | 914 | 0 | 144 | 924.16 | 178 | 4584 | 134.94 | 424.42 | 1627 | 0 | 0 | 38 | 3517
17:30 | 3143 | 1425 | 915.5 | 0 | 149 | 924.605 | 179 | 4600.5 | 74.59 | 488.42 | 1716.1 | 0 | 0 | 48.5 | 3272
18:00 | 3160 | 1433.5 | 917 | 0 | 154 | 925.05 | 180 | 4617 | 14.24 | 552.42 | 1805.2 | 0 | 0 | 59 | 3027
18:30 | 3057.5 | 1387.5 | 917.5 | 0 | 169 | 1067.375 | 180.5 | 4667.5 | 7.12 | 652.92 | 2032.45 | 160 | 0 | 46.5 | 3018.5
19:00 | 2955 | 1341.5 | 918 | 0 | 184 | 1209.7 | 181 | 4718 | 0 | 753.42 | 2259.7 | 320 | 0 | 34 | 3010
19:30 | 3154 | 1378 | 919 | 0 | 180 | 1317.93 | 181 | 4745 | 0 | 736.42 | 2560.7 | 381 | 0 | 37 | 2532
20:00 | 3201 | 1434 | 920 | 0 | 176 | 1307.94 | 222 | 4747 | 0 | 779.42 | 2570.7 | 370 | 0 | 28 | 2942
20:30 | 3212 | 1419.5 | 921.5 | 0 | 173 | 1311.55 | 222 | 4755.5 | 0 | 783.42 | 2567.88 | 335 | 0 | 38 | 2757
21:00 | 3223 | 1405 | 923 | 0 | 170 | 1315.16 | 222 | 4764 | 0 | 787.42 | 2565.06 | 300 | 0 | 48 | 2572
21:30 | 3238.5 | 1408 | 923 | 0 | 171 | 1310.105 | 222 | 4786.5 | 0 | 791.42 | 2437.56 | 300 | 0 | 43 | 2717
22:00 | 3254 | 1411 | 923 | 0 | 172 | 1305.05 | 222 | 4809 | 0 | 795.42 | 2310.06 | 300 | 0 | 38 | 2862
22:30 | 3289 | 1393 | 923 | 0 | 177 | 1312.455 | 222 | 4808 | 0 | 812.92 | 2281.88 | 200 | 0 | 43 | 2904
23:00 | 3324 | 1375 | 923 | 0 | 182 | 1319.86 | 222 | 4807 | 0 | 830.42 | 2253.7 | 100 | 0 | 48 | 2946
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 29-08-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 394 | 14:00 | 364 | 14:00 | Madunaghat | 404 | 05:00 | 391 | 17:00
Amtali | 414 | 03:00 | 410 | 20:00 | Meghnaghat | 394 | 06:00 | 369 | 14:00
Ashuganj | 397 | 03:00 | 386 | 14:00 | Mirsorai | 406 | 04:00 | 393 | 14:00
Bhulta | 399 | 05:00 | 374 | 13:00 | Payra | 418 | 05:00 | 411 | 14:00
Bibiana | 383 | 03:00 | 376 | 12:00 | Rahanpur | 410 | 02:00 | 401 | 20:00
BIPTC | 406 | 06:00 | 398 | 21:00 | Rampal | 401 | 02:00 | 392 | 14:00
Bogura | 395 | 02:00 | 386 | 20:00
Gopalganj | 397 | 03:00 | 386 | 14:00
Kaliakoir | 375 | 04:00 | 352 | 14:00
Korerhat | 402 | 07:00 | 392 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 03:00 | 218 | 14:00 | Hasnabad | 233 | 06:00 | 216 | 14:00
AKSML | 241 | 06:00 | 231 | 12:00 | Hathazari | 238 | 22:00 | 229 | 10:00
Aminbazar | 234 | 03:00 | 220 | 13:00 | Ishurdi | 237 | 02:00 | 226 | 20:00
Ashuganj | 232 | 05:00 | 221 | 14:00 | Jhenaidah | 229 | 03:00 | 218 | 13:00
Ashuganj-400 | 232 | 05:00 | 221 | 14:00 | Kachua | 232 | 06:00 | 225 | 14:00
Baghabari | 233 | 01:00 | 225 | 20:00 | Kaliakoir | 233 | 04:00 | 217 | 14:00
Barapukuria | 228 | 02:00 | 222 | 11:00 | Keranigonj | 233 | 04:00 | 216 | 14:00
Barapukuria-230 | 228 | 02:00 | 222 | 11:00 | Khulna(S) | 230 | 02:00 | 222 | 23:00
Barapukuria(N) | 228 | 02:00 | 222 | 11:00 | Korerhat | 230 | 01:00 | 224 | 14:00
Barishal | 228 | 02:00 | 223 | 14:00 | Madunaghat | 240 | 01:00 | 236 | 10:00
Bheramara | 234 | 00:00 | 224 | 20:00 | Madunaghat-400 | 242 | 06:00 | 237 | 11:00
Bhulta | 230 | 04:00 | 213 | 14:00 | Maniknagar | 229 | 05:00 | 211 | 14:00
Bibiana | 221 | 05:00 | 217 | 12:00 | Meghnaghat | 237 | 04:00 | 223 | 13:00
BIPTC | 236 | 00:00 | 224 | 20:00 | Meghnaghat-400 | 233 | 04:00 | 217 | 14:00
Birulia | 234 | 04:00 | 217 | 14:00 | Mirsorai | 236 | 04:00 | 229 | 11:00
Bogura | 239 | 02:00 | 233 | 20:00 | Naogaon | 229 | 22:00 | 212 | 20:00
Bogura-400 | 238 | 02:00 | 233 | 20:00 | Purbasadipur | 226 | 02:00 | 219 | 11:00
Borhanuddin | 230 | 09:00 | 224 | 02:00 | Rajshahi | 233 | 01:00 | 224 | 13:00
BSRM | 232 | 04:00 | 224 | 14:00 | Rampal | 229 | 02:00 | 221 | 23:00
Charfasson | 235 | 09:00 | 227 | 19:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 230 | 08:00 | 225 | 11:00 | Rampura | 230 | 06:00 | 210 | 14:00
Cumilla(N) | 229 | 04:00 | 218 | 14:00 | Shikalbaha | 239 | 01:00 | 234 | 11:00
Faridpur | 225 | 03:00 | 218 | 20:00 | Shyampur | 232 | 06:00 | 215 | 14:00
Fenchuganj | 222 | 05:00 | 219 | 01:00 | Siddhirganj | 231 | 05:00 | 220 | 19:00
Feni | 230 | 05:00 | 221 | 14:00 | Sirajgonj | 237 | 03:00 | 230 | 20:00
Ghorashal | 230 | 01:00 | 220 | 10:00 | Sreepur | 225 | 02:00 | 216 | 21:00
Ghorashal-230 | 223 | 04:00 | 202 | 14:00 | Tongi | 220 | 04:00 | 202 | 13:00
Gopalganj | 225 | 03:00 | 220 | 14:00
GPH | 239 | 14:00 | 230 | 14:00
Haripur | 230 | 04:00 | 213 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 140 | 06:00 | 126 | 14:00 | Madaripur | 133 | 03:00 | 130 | 00:00
Agargaon | 139 | 01:00 | 126 | 14:00 | Madartek | 139 | 04:00 | 127 | 14:00
Agrabad | 138 | 05:00 | 134 | 10:00 | Madunaghat | 139 | 02:00 | 137 | 10:00
AKS | 135 | 00:00 | 131 | 05:00 | Magura | 136 | 09:00 | 130 | 13:00
Aminbazar | 136 | 06:00 | 125 | 13:00 | Mahasthangarh | 135 | 17:00 | 130 | 20:00
Amnura | 135 | 00:00 | 130 | 07:00 | Maijdee | 130 | 04:00 | 125 | 14:00
Ashuganj | 132 | 04:00 | 126 | 13:00 | Manikganj | 131 | 03:00 | 125 | 10:00
Ashuganj-230 | 135 | 05:00 | 130 | 13:00 | Maniknagar | 142 | 04:00 | 129 | 14:00
Bagerhat | 132 | 09:00 | 123 | 20:00 | Matarbari | 127 | 11:00 | 119 | 04:00
Bajitpur | 127 | 04:00 | 119 | 13:00 | Matuail | 137.5 | 06:00 | 126 | 14:00
Bakerganj | 133 | 06:00 | 130 | 19:30 | Metrorail_Motijheel | 142 | 04:00 | 129 | 14:00
Bakulia | 139 | 00:00 | 133 | 12:00 | Metrorail_Uttara | 135 | 06:00 | 119 | 14:00
Banani | 139 | 04:00 | 125 | 14:00 | Millgate | 137 | 03:00 | 120 | 14:00
Bangabhaban | 142 | 04:00 | 129 | 14:00 | Mirpur | 134 | 05:00 | 123 | 13:00
Barapukuria | 139 | 02:00 | 131 | 11:00 | Mirzapur | 132 | 03:00 | 122 | 14:00
Barguna | 133 | 09:00 | 129 | 19:30 | Mithapukur | 134 | 02:00 | 127 | 11:00
Barishal | 134 | 15:00 | 130 | 19:30 | MI_Cement | 136 | 03:00 | 124 | 14:00
Barishal-230 | 133 | 01:00 | 130 | 19:30 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 137 | 02:00 | 134 | 10:00 | Mogbazar | 140 | 03:00 | 14 | 05:00
Baroirhat | 134 | 07:00 | 130 | 14:00 | Mongla | 131 | 10:00 | 123 | 00:00
Bashundhara | 140 | 06:00 | 120 | 14:00 | Motijheel | 142 | 04:00 | 129 | 14:00
BashundharaCement | 136 | 06:00 | 127 | 14:00 | Muktagacha | 130 | 18:30 | 118 | 07:00
Beanibazar | 124 | 16:00 | 121 | 01:00 | Munshiganj | 136 | 03:00 | 125 | 14:00
Benapole | 136 | 09:00 | 125 | 11:00 | Muradnagar | 132 | 05:00 | 125 | 14:00
Bhaluka | 131 | 05:00 | 122 | 21:00 | Mymensingh | 130 | 19:00 | 112 | 21:00
Bhandaria | 130 | 08:00 | 125 | 19:30 | Nabinagar | 133 | 03:00 | 120 | 12:00
Bhangura | 134 | 03:00 | 130 | 15:00 | Naogaon | 136 | 18:00 | 127 | 20:00
Bheramara | 137 | 01:00 | 131 | 20:00 | Narail | 137 | 09:00 | 129 | 19:30
Bheramara(GK) | 137 | 01:00 | 130 | 13:00 | Narinda | 142 | 04:00 | 129 | 14:00
Bhulta | 130 | 05:00 | 120 | 13:00 | Narshingdi | 130 | 00:00 | 118 | 14:00
Bhulta-400 | 133 | 04:00 | 122 | 14:00 | Natore | 135 | 17:00 | 128 | 13:00
Birulia | 137 | 03:00 | 128 | 14:00 | Nawabganj | 140 | 03:00 | 129 | 14:00
Bog-Sherpur | 135 | 02:00 | 131 | 11:00 | Netrakona | 120 | 00:00 | 110 | 19:30
Bogura | 138 | 18:00 | 134 | 07:00 | New | 136 | 01:00 | 122 | 14:00
Bogura-230 | 138 | 00:00 | 134 | 11:00 | Niamatpur | 134 | 15:00 | 120 | 22:00
Brahmanbaria | 130 | 06:00 | 125 | 10:00 | Noapara | 135 | 03:00 | 129 | 20:00
Cantonment | 139 | 01:00 | 125 | 13:00 | Pabna | 134 | 00:00 | 129 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandina | 134 | 06:00 | 127 | 14:00 | Palashbari | 133 | 02:00 | 125 | 11:00
Chandpur | 135 | 19:00 | 130 | 11:00 | Panchagarh | 137 | 14:00 | 131 | 11:00
Chandraghona | 139 | 00:00 | 136 | 12:00 | Patiya | 137 | 17:00 | 132 | 14:00
Chapai | 134 | 00:00 | 130 | 16:00 | Patnitala | 133 | 18:00 | 128 | 22:00
Charsaidpur | 137 | 05:00 | 126 | 14:00 | Patuakhali | 133 | 15:00 | 130 | 00:00
Chauddagram | 133 | 05:00 | 127 | 13:00 | Payra | 136 | 01:00 | 134 | 20:00
Chhatak | 121 | 05:00 | 118 | 00:00 | PHP | 134 | 02:00 | 130 | 11:00
Chowmuhani | 129 | 08:00 | 126 | 00:00 | Postogola | 139 | 06:00 | 127 | 13:00
Chuadanga | 135 | 01:00 | 126 | 13:00 | Pubail | 131 | 03:00 | 120 | 11:00
Coxsbazar | 132 | 15:00 | 119 | 19:30 | Purbachal | 140 | 05:00 | 125 | 14:00
Cumilla(N) | 133 | 04:00 | 127 | 21:00 | Purbasadipur | 137 | 02:00 | -36 | 18:30
Cumilla(S) | 133 | 03:00 | 119 | 14:00 | Rahanpur | 137 | 18:00 | 131 | 21:00
Daganbhuiyan | 133 | 06:00 | 128 | 14:00 | Rahanpur-400 | 137 | 02:00 | 134 | 08:00
Daudkandi | 131 | 06:00 | 124 | 11:00 | Rahim | 138 | 06:00 | 126 | 14:00
DhakaUniversity | 138 | 02:00 | 126 | 14:00 | Rajbari | 128 | 03:00 | 123 | 19:30
Dhamrai | 136 | 04:00 | 121 | 13:00 | Rajendrapur | 134 | 04:00 | 128 | 20:00
Dhanmondi | 140 | 06:00 | 126 | 14:00 | Rajshahi | 133 | 01:00 | 128 | 13:00
Dohazari | 137 | 14:00 | 131 | 03:00 | Rajshahi-230 | 134 | 01:00 | 128 | 20:00
Faridpur | 130 | 04:00 | 126 | 19:30 | Ramganj | 130 | 06:00 | 125 | 14:00
Fatullah | 139 | 05:00 | 126 | 14:00 | Rampur | 138 | 00:00 | 133 | 12:00
Fenchuganj | 131 | 09:00 | 128 | 14:00 | Rampura | 140 | 06:00 | 125 | 14:00
Feni | 134 | 05:00 | 128 | 14:00 | Rangamati | 138 | 00:00 | 135 | 10:00
Feni-230 | 134 | 04:00 | 129 | 14:00 | Rangpur | 134 | 02:00 | 127 | 11:00
Ghatail | 126 | 00:00 | 118 | 12:00 | Ruppur | 137 | 01:00 | 131 | 19:30
Ghorashal | 132 | 05:00 | 122 | 14:00 | Saidpur | 136 | 02:00 | 130 | 11:00
Goalpara | 138 | 04:00 | 132 | 20:00 | Santhia | 135 | 02:00 | 130 | 19:30
Gollamari | 137 | 01:00 | 132 | 20:00 | Satkhira | 134 | 15:00 | 126 | 19:00
Gopalganj | 134 | 03:00 | 130 | 20:00 | Satmasjid | 139 | 01:00 | 126 | 14:00
Gopalganj-400 | 134 | 03:00 | 131 | 09:00 | Savar | 134 | 02:00 | 124 | 14:00
Gulshan | 139 | 06:00 | 125 | 14:00 | SevenRings | 134 | 04:00 | 122 | 13:00
Halishahar | 138 | 01:00 | 133 | 14:00 | ShahCement | 137 | 05:00 | 126 | 14:00
Haripur | 138 | 06:00 | 126 | 14:00 | Shahjadpur | 135 | 00:00 | 131 | 20:00
HaripurSBU | 137 | 04:00 | 126 | 14:00 | Shahjibazar | 128 | 16:00 | 122 | 12:00
Hasnabad | 136 | 03:00 | 127 | 14:00 | Shahmirpur | 138 | 00:00 | 134 | 13:00
Hathazari | 139 | 00:00 | 136 | 10:00 | Shariatpur | 132 | 04:00 | 128 | 19:30
Hatirjheel | 140 | 06:00 | 125 | 14:00 | Sherpur | 132 | 19:00 | 114 | 07:00
Ishurdi | 139 | 02:00 | 133 | 13:00 | Shikalbaha | 128 | 00:00 | 124 | 10:00
Jaldhaka | 133 | 01:00 | 127 | 11:00 | Shikalbaha-230 | 139 | 02:00 | 136 | 10:00
Jamalpur | 133 | 18:30 | 117 | 08:00 | Shitalakhya | 136 | 03:00 | 124 | 14:00
Jashore | 137 | 09:00 | 126 | 19:30 | Sholosohor | 138 | 00:00 | 135 | 14:00
Jhenaidah | 139 | 01:00 | 130 | 20:00 | Shomvuganj | 122 | 04:00 | 115 | 14:00
Jhenaidah-230 | 139 | 01:00 | 131 | 13:00 | Shyampur | 137 | 05:00 | 127 | 13:00
Joydebpur | 130 | 00:00 | 117 | 14:00 | Shyampur-230 | 139 | 06:00 | 28 | 14:00
Joypurhat | 134 | 18:00 | 128 | 20:00 | Siddhirganj | 138 | 04:00 | 127 | 14:00
Juldah | 137 | 01:00 | 135 | 10:00 | Sirajganj | 131 | 02:00 | 126 | 20:00
Kabirpur | 135 | 21:00 | 116 | 13:00 | Sitakunda | 137 | 07:00 | 135 | 03:00
Kachua | 132 | 03:00 | 128 | 12:00 | Sonargaon | 135 | 04:00 | 125 | 14:00
Kaliakoir | 138 | 02:00 | 126 | 14:00 | Sreemongol | 127 | 06:00 | 122 | 13:00
Kaliganj | 137 | 17:00 | 131 | 13:00 | Sreepur | 136 | 02:00 | 130 | 13:00
Kallyanpur | 134 | 05:00 | 126 | 09:00 | Srinagar | 141 | 06:00 | 129 | 14:00
Kalurghat | 139 | 00:00 | 136 | 10:00 | SSM | 141 | 07:00 | 136 | 14:00
Kamrangirchar | 140 | 06:00 | 121 | 14:00 | Sunamganj | 120 | 18:00 | 116 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 124 | 18:30 | 122 | 00:00
Kasba | 131 | 04:00 | 123 | 18:30 | Sylhet_(South) | 125 | 06:00 | 122 | 13:00
Kazla | 142 | 06:00 | 129 | 14:00 | Tangail | 127 | 05:00 | 118 | 14:00
Keranigonj | 141 | 04:00 | 130 | 14:00 | Taraganj | 134 | 12:00 | 129 | 11:00
Khagrachori | 137 | 00:00 | 134 | 10:00 | Tasnim | 135 | 05:00 | 11 | 00:00
Khulna | 136 | 02:00 | 130 | 20:00 | Thakurgaon | 139 | 14:00 | 132 | 11:00
Khulna(S) | 138 | 03:00 | 133 | 19:30 | TK | 139 | 05:00 | 136 | 10:00
Khulshi | 136 | 00:00 | 130 | 15:00 | Tongi | 136 | 04:00 | 123 | 13:00
Kishoreganj | 127 | 17:00 | 118 | 13:00 | Ullahpara | 133 | 03:00 | 127 | 20:00
Kodda | 135 | 03:00 | 117 | 10:00 | Ullon | 139 | 05:00 | 125 | 14:00
Korerhat | 136 | 01:00 | 132 | 10:00 | Uttara | 137 | 06:00 | 119 | 13:00
KSRM | 138 | 07:00 | 134 | 10:00 | UttaraNew | 135 | 06:00 | 119 | 14:00
Kulaura | 130 | 18:30 | 127 | 01:00 | Zigatola | 141 | 06:00 | 129 | 14:00
Kurigram | 133 | 02:00 | 124 | 13:00
Kushtia | 136 | 02:00 | 130 | 19:30
Laksam | 132 | 04:00 | 127 | 11:00
Lakshmipur | 129 | 03:00 | 125 | 14:00
Lalbag | 141 | 04:00 | 128 | 13:00
Lalmonirhat | 129 | 14:00 | 121 | 13:00
Madanganj | 136 | 06:00 | 127 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 29-08-2026 | [28 empty] | Date: | 29-08-2026 | [28 empty] | Date: | 29-08-2026 | [28 empty] | Date: | 29-08-2026 | [28 empty] | Date: | 29-08-2026 | [18 empty] | Date: | 29-08-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [18 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 610 | 54 | 17 | 53 | 94 | 146 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 86 | 9 | 22 | 0 | 280 | 0 | 16 | 45 | 0 | 7 | 51 | 23 | 17 | 12 | 12 | 0 | 221 | 93 | 38 | 565 | 85 | 0 | 50 | 25.5 | 102 | 218 | 0 | 0 | 0 | 1224 | 0 | 100 | 0 | 230 | 300 | 245 | 51 | 0 | 217 | 0 | 88 | 20 | 118 | 0 | 19 | 102 | 170 | 8 | 0 | 38 | 225 | 400 | 300 | 40 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 127 | 17 | 78 | 0 | 173 | 0 | 0 | 0 | 24 | 8514.5 | 905 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 920 | 0 | 0 | 0 | 1207.64 | 0 | 0 | 0 | 55 | 70 | 0 | 90 | 27 | 8 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 390 | 0 | 0 | 152 | 49 | 115 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 200 | 116 | 220 | 0 | 1000 | 510 | 17 | 6410.64 | 14925.14 | 104.68
01:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 728 | 35 | 17 | 52 | 95 | 146 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 240 | 0 | 0 | 0 | 86 | 9 | 22 | 0 | 280 | 0 | 16 | 35 | 0 | 12 | 51 | 15 | 0 | 12 | 12 | 0 | 219 | 95 | 38 | 558 | 86 | 0 | 50 | 8 | 103 | 218 | 0 | 0 | 0 | 1224 | 0 | 102 | 0 | 220 | 300 | 265 | 51 | 0 | 215 | 0 | 73 | 20 | 104 | 0 | 19 | 102 | 172 | 8 | 0 | 38 | 175 | 400 | 283 | 40 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 127 | 0 | 58 | 0 | 66 | 0 | 0 | 0 | 24 | 8066 | 905 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 150 | 0 | 67 | 0 | 920 | 0 | 0 | 0 | 963.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 8 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 388 | 0 | 0 | 155 | 49 | 115 | 0 | 34 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 510 | 17 | 6208.96 | 14274.96 | 104.76
02:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 724 | 35 | 17 | 52 | 95 | 146 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 240 | 0 | 0 | 0 | 86 | 9 | 22 | 0 | 280 | 0 | 16 | 31 | 0 | 12 | 51 | 8 | 0 | 12 | 12 | 0 | 218 | 110 | 38 | 558 | 86 | 0 | 50 | 8 | 104 | 218 | 0 | 0 | 0 | 1224 | 0 | 102 | 0 | 260 | 167 | 310 | 51 | 0 | 220 | 0 | 69 | 20 | 103 | 0 | 19 | 101 | 168 | 8 | 0 | 38 | 175 | 400 | 282 | 40 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 127 | 0 | 58 | 0 | 66 | 0 | 0 | 0 | 24 | 7953 | 905 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 150 | 0 | 67 | 0 | 920 | 0 | 0 | 0 | 901.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 8 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 414 | 0 | 0 | 154 | 49 | 115 | 0 | 34 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 510 | 17 | 6163.59 | 14116.59 | 104.84
03:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 727 | 35 | 17 | 52 | 95 | 146 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 240 | 0 | 0 | 0 | 86 | 9 | 22 | 0 | 280 | 0 | 16 | 31 | 0 | 29 | 4 | 8 | 0 | 12 | 12 | 0 | 217 | 110 | 38 | 558 | 88 | 0 | 50 | 8 | 94 | 218 | 0 | 0 | 0 | 1224 | 0 | 102 | 16 | 370 | 48 | 310 | 51 | 0 | 202 | 0 | 69 | 20 | 104 | 0 | 19 | 96 | 164 | 8 | 0 | 38 | 175 | 400 | 242 | 40 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 127 | 0 | 58 | 0 | 66 | 0 | 0 | 0 | 24 | 7855 | 905 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 150 | 0 | 67 | 0 | 920 | 0 | 0 | 0 | 904.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 8 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 414 | 0 | 0 | 154 | 49 | 115 | 0 | 34 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 510 | 17 | 6166.37 | 14021.37 | 104.92
04:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 729 | 35 | 17 | 52 | 95 | 97 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 240 | 0 | 0 | 0 | 86 | 9 | 22 | 0 | 280 | 0 | 16 | 31 | 0 | 17 | 0 | 8 | 0 | 12 | 12 | 0 | 217 | 104 | 25 | 558 | 88 | 0 | 50 | 8 | 87 | 218 | 0 | 0 | 0 | 1224 | 0 | 100 | 75 | 393 | 0 | 325 | 51 | 0 | 203 | 0 | 69 | 20 | 105 | 0 | 19 | 98 | 154 | 8 | 0 | 38 | 175 | 400 | 242 | 40 | 0 | 74 | 0 | 4 | 0 | 0 | 0 | 142 | 0 | 127 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 24 | 7813 | 906 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 920 | 0 | 0 | 0 | 906.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 414 | 0 | 0 | 153 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 510 | 17 | 5849.04 | 13662.04 | 105
05:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 732 | 17 | 17 | 52 | 94 | 97 | 15 | 17 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 0 | 86 | 9 | 22 | 0 | 280 | 0 | 16 | 29 | 0 | 9 | 0 | 8 | 0 | 12 | 12 | 0 | 218 | 106 | 35 | 558 | 86 | 0 | 50 | 8 | 85 | 218 | 0 | 0 | 0 | 1224 | 0 | 97 | 100 | 393 | 0 | 330 | 51 | 0 | 215 | 0 | 69 | 20 | 103 | 0 | 19 | 102 | 158 | 8 | 0 | 38 | 170 | 400 | 232 | 40 | 0 | 75 | 0 | 4 | 0 | 0 | 0 | 142 | 0 | 127 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 24 | 7765 | 905 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 920 | 0 | 0 | 0 | 909.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 51 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 510 | 17 | 5855.56 | 13620.56 | 105.08
06:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 735 | 17 | 17 | 40 | 94 | 97 | 15 | 17 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 1 | 86 | 3 | 22 | 0 | 280 | 0 | 16 | 31 | 0 | 11 | 0 | 8 | 0 | 12 | 12 | 0.08 | 219 | 108 | 40 | 558 | 34 | 0 | 50 | 8 | 88 | 219 | 0 | 0 | 0 | 1150 | 1 | 100 | 100 | 393 | 0 | 305 | 51 | 0 | 196 | 20 | 41 | 20 | 104 | 0 | 19 | 102 | 146 | 8 | 3 | 38 | 170 | 400 | 252 | 40 | 0 | 74 | 0 | 4 | 0 | 0 | 0 | 140 | 0 | 126 | 0 | 58 | 0.2 | 67 | 0 | 0 | 0.15 | 22 | 7599.43 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 1 | 920 | 0 | 0 | 0 | 908.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0.89 | 0 | 10 | 0 | 0.04 | 0 | 0 | 128 | 0 | 0 | 0 | 414 | 0 | 0 | 158 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 4 | 0.02 | 32 | 200 | 116 | 220 | 0 | 1000 | 510 | 17 | 5818.31 | 13417.74 | 105.16
07:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 738 | 17 | 17 | 34 | 95 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 5 | 86 | 9 | 22 | 0 | 280 | 0 | 16 | 31 | 0 | 5 | 0 | 8 | 0 | 12 | 12 | 0.88 | 177 | 108 | 27 | 558 | 16 | 0 | 50 | 8 | 89 | 218 | 0 | 0 | 0 | 1185 | 3 | 93 | 100 | 393 | 0 | 325 | 51 | 0 | 214 | 20 | 34 | 30 | 103 | 0 | 19 | 101 | 140 | 8 | 20 | 38 | 170 | 400 | 280 | 40 | 0 | 75 | 2 | 0 | 0 | 0 | 0 | 140 | 0 | 126 | 0 | 58 | 1.3 | 67 | 0 | 0.4 | 2.76 | 22 | 7623.34 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 8 | 920 | 0 | 0 | 0 | 907.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 3.23 | 11 | 10 | 0 | 7.86 | 0 | 0 | 127 | 0 | 0 | 0 | 414 | 0 | 0.69 | 159 | 49 | 115 | 3 | 34 | 0 | 0 | 0 | 1.2 | 23 | 0.08 | 32 | 200 | 116 | 220 | 0 | 1000 | 510 | 17 | 5868.12 | 13491.46 | 105.24
08:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 595 | 17 | 17 | 35 | 94 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 240 | 0 | 0 | 16 | 86 | 8 | 22 | 0 | 280 | 0 | 16 | 31 | 0 | 4 | 0 | 8 | 0 | 12 | 12 | 2 | 181 | 107 | 18 | 558 | 16 | 0 | 50 | 8 | 87 | 216 | 0 | 0 | 0 | 1160 | 11 | 82 | 100 | 393 | 0 | 340 | 51 | 0 | 210 | 20 | 34 | 93 | 99 | 0 | 11 | 102 | 148 | 8 | 39 | 38 | 177 | 395 | 315 | 40 | 0 | 79 | 4 | 0 | 0 | 10 | 0 | 140 | 0 | 126 | 0 | 58 | 11.96 | 67 | 0 | 0.1 | 25.1 | 6 | 7612.16 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 22 | 920 | 0 | 0 | 0 | 906.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 9.99 | 25 | 10 | 0 | 16.41 | 0 | 0 | 126 | 0 | 0 | 0 | 414 | 0 | 1.23 | 156 | 49 | 115 | 11 | 34 | 0 | 0 | 0 | 3.7 | 85 | 0.09 | 32 | 200 | 116 | 220 | 0 | 1000 | 510 | 17 | 5980.83 | 13592.99 | 105.3
09:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 224 | 17 | 17 | 35 | 94 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 283 | 0 | 0 | 16 | 143.42 | 7.5 | 22 | 0 | 320 | 0 | 16 | 37 | 0 | 29 | 0 | 8 | 17 | 12 | 12 | 2.9 | 181 | 106 | 2 | 558 | 16 | 0 | 50 | 8 | 87 | 215 | 0 | 0 | 0 | 1192 | 13 | 82 | 53 | 393 | 0 | 280 | 51 | 0 | 196 | 20 | 34 | 92 | 100 | 0 | 11 | 101 | 158 | 8 | 55 | 37 | 252 | 400 | 380 | 40 | 0 | 118 | 8 | 0 | 0 | 22 | 0 | 140 | 0 | 126 | 0 | 58 | 12.13 | 70 | 0 | 0.5 | 22.13 | 18 | 7582.58 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 68 | 920 | 0 | 0 | 0 | 909.5 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 8 | 20.19 | 28 | 10 | 0 | 39.73 | 0 | 0 | 126 | 0 | 0 | 0 | 350 | 0 | 3.83 | 159 | 48 | 110 | 20 | 34 | 0 | 0 | 0 | 4.9 | 135 | 0.23 | 32 | 200 | 115 | 180 | 0 | 995 | 510 | 17 | 6019.38 | 13601.96 | 105.36
10:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 289 | 17 | 17 | 35 | 45 | 81 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 312 | 0 | 0 | 30 | 143.42 | 6 | 22 | 0 | 340 | 0 | 16 | 37 | 0 | 46 | 0 | 8 | 17 | 12 | 12 | 3.69 | 182 | 105 | 2 | 558 | 21 | 0 | 50 | 8 | 87 | 214 | 0 | 0 | 0 | 1192 | 9 | 82 | 53 | 393 | 0 | 320 | 51 | 0 | 211 | 20 | 34 | 91 | 101 | 0 | 19 | 102 | 164 | 8 | 66 | 37 | 246 | 393 | 380 | 40 | 0 | 143 | 11 | 0 | 0 | 22 | 0 | 140 | 0 | 126 | 0 | 58 | 20 | 114 | 0 | 0.7 | 45.53 | 18 | 7928.34 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 37 | 920 | 0 | 0 | 0 | 910.4 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 60.27 | 54 | 10 | 0 | 50.07 | 0 | 0 | 125 | 0 | 0 | 0 | 350 | 0 | 2.89 | 158 | 49 | 99 | 28 | 0 | 0 | 0 | 0 | 5.9 | 158 | 0.58 | 32 | 200 | 116 | 220 | 0 | 922 | 510 | 17 | 6051.11 | 13979.45 | 105.42
11:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 258 | 17 | 17 | 43 | 45 | 81 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 315 | 0 | 0 | 32 | 143.42 | 6 | 22 | 0 | 340 | 0 | 16 | 36 | 0 | 53 | 0 | 8 | 17 | 12 | 12 | 3.9 | 182 | 92 | 0 | 558 | 34 | 0 | 50 | 10 | 88 | 211 | 0 | 0 | 0 | 1192 | 6 | 82 | 53 | 385 | 0 | 335 | 43 | 0 | 213 | 20 | 34 | 90 | 101 | 0 | 19 | 101 | 156 | 8 | 62 | 37 | 245 | 388 | 368 | 40 | 0 | 150 | 6 | 0 | 0 | 5 | 0 | 140 | 0 | 126 | 0 | 58 | 21.75 | 115 | 0 | 2.4 | 57.85 | 18 | 7862.32 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 43 | 920 | 0 | 0 | 0 | 917.32 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 45.31 | 57 | 10 | 0 | 55.68 | 0 | 0 | 123 | 0 | 0 | 0 | 384 | 0 | 6.05 | 158 | 47 | 94 | 18 | 0 | 0 | 0 | 0 | 4.4 | 82 | 0.45 | 32 | 200 | 114 | 220 | 0 | 971 | 510 | 17 | 6062.21 | 13924.53 | 105.48
12:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 226 | 17 | 0 | 52 | 45 | 81 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 285 | 0 | 0 | 35 | 143.42 | 7.5 | 22 | 0 | 310 | 0 | 16 | 38 | 0 | 40 | 0 | 8 | 17 | 12 | 12 | 4.35 | 182 | 91 | 0 | 558 | 33 | 0 | 50 | 17 | 89 | 210 | 0 | 0 | 0 | 1192 | 11 | 80 | 53 | 385 | 0 | 270 | 43 | 0 | 186 | 20 | 34 | 90 | 101 | 0 | 19 | 102 | 164 | 8 | 73 | 37 | 253 | 391 | 352 | 40 | 0 | 149 | 5 | 8 | 0 | 5 | 0 | 140 | 0 | 126 | 0 | 58 | 22.26 | 115 | 0 | 2 | 56.4 | 12 | 7681.93 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 45 | 920 | 0 | 0 | 0 | 922.76 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 54.16 | 115 | 10 | 0 | 63.83 | 0 | 0 | 123 | 0 | 0 | 0 | 350 | 0 | 6.1 | 158 | 47 | 104 | 37 | 0 | 0 | 0 | 0 | 4.5 | 160 | 0.76 | 32 | 200 | 114 | 220 | 0 | 1000 | 515 | 35 | 6263.11 | 13945.04 | 105.54
13:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 242 | 54 | 0 | 56 | 44 | 90 | 15 | 35 | 162 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 32 | 143.42 | 7.5 | 22 | 0 | 300 | 0 | 16 | 37 | 0 | 34 | 16 | 8 | 17 | 12 | 12 | 2 | 182 | 108 | 0 | 558 | 36 | 0 | 50 | 17 | 87 | 218 | 0 | 0 | 0 | 1192 | 14 | 80 | 53 | 385 | 0 | 305 | 51 | 0 | 199 | 20 | 60 | 80 | 101 | 6 | 19 | 101 | 162 | 8 | 47 | 37 | 260 | 385 | 332 | 40 | 0 | 147 | 12 | 8 | 0 | 5 | 0 | 142 | 0 | 126 | 0 | 58 | 22 | 115 | 0 | 2.4 | 37.86 | 6 | 7941.18 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 42 | 920 | 0 | 0 | 0 | 923 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 3 | 0 | 63.24 | 85 | 10 | 0 | 38 | 0 | 0 | 126 | 0 | 0 | 0 | 350 | 0 | 4.59 | 157 | 47 | 110 | 19 | 0 | 0 | 0 | 0 | 5.3 | 193 | 0.33 | 48 | 200 | 113 | 220 | 0 | 978 | 515 | 35 | 6231.46 | 14172.64 | 105.59
14:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 266 | 17 | 0 | 78 | 60 | 97 | 15 | 35 | 162 | 0 | 0 | 0 | 0 | 0 | 35 | 309 | 0 | 0 | 30 | 143.42 | 7.5 | 22 | 0 | 345 | 0 | 16 | 37 | 0 | 17 | 33 | 8 | 17 | 12 | 12 | 4.01 | 182 | 104 | 0 | 558 | 72 | 0 | 50 | 17 | 87 | 215 | 0 | 0 | 0 | 1202 | 12 | 78 | 53 | 370 | 0 | 330 | 51 | 0 | 207 | 20 | 84 | 80 | 100 | 9 | 19 | 99 | 158 | 8 | 12 | 37 | 267 | 380 | 316 | 40 | 0 | 145 | 11 | 8 | 0 | 5 | 0 | 142 | 0 | 126 | 0 | 58 | 21.51 | 115 | 0 | 2 | 28.67 | 6 | 8038.11 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 90 | 920 | 0 | 0 | 0 | 928.94 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 47.6 | 104 | 10 | 0 | 26.02 | 0 | 0 | 129 | 0 | 0 | 0 | 350 | 0 | 5.13 | 159 | 46 | 108 | 17 | 0 | 0 | 0 | 0 | 6.3 | 182 | 0.74 | 48 | 200 | 114 | 220 | 0 | 982 | 510 | 17 | 6245.73 | 14283.84 | 105.64
15:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 245 | 17 | 0 | 78 | 59 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 24 | 143.42 | 7.5 | 22 | 0 | 365 | 0 | 16 | 38 | 0 | 30 | 33 | 8 | 17 | 12 | 12 | 3.34 | 178 | 93 | 0 | 558 | 70 | 0 | 50 | 17 | 88 | 215 | 0 | 0 | 0 | 1192 | 16 | 28 | 16 | 360 | 0 | 290 | 51 | 0 | 195 | 20 | 34 | 70 | 101 | 7 | 19 | 94 | 128 | 8 | 4 | 37 | 272 | 380 | 214 | 40 | 0 | 144 | 9 | 8 | 0 | 60 | 0 | 142 | 0 | 126 | 0 | 58 | 13.57 | 105 | 0 | 0.5 | 23.49 | 6 | 7556.82 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 83 | 920 | 0 | 0 | 0 | 925.37 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 43.01 | 40 | 10 | 0 | 38.02 | 0 | 0 | 126 | 0 | 0 | 0 | 320 | 0 | 4.32 | 161 | 45 | 107 | 14 | 0 | 0 | 0 | 0 | 4.1 | 93 | 0.58 | 48 | 200 | 115 | 220 | 0 | 954 | 510 | 17 | 6023.4 | 13580.22 | 105.69
16:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 266 | 17 | 0 | 78 | 59 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 305 | 0 | 0 | 15 | 143.42 | 7.5 | 22 | 0 | 365 | 0 | 16 | 37 | 0 | 31 | 33 | 8 | 17 | 24 | 25 | 1.61 | 178 | 104 | 0 | 558 | 71 | 0 | 50 | 17 | 88 | 217 | 0 | 0 | 0 | 1192 | 2 | 26 | 8 | 360 | 0 | 305 | 51 | 0 | 202 | 10 | 34 | 70 | 101 | 8 | 19 | 104 | 140 | 8 | 11 | 36 | 290 | 380 | 235 | 40 | 0 | 145 | 5 | 8 | 0 | 60 | 0 | 142 | 0 | 126 | 0 | 58 | 7.74 | 114 | 0 | 0.6 | 12.23 | 6 | 7654.1 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 46 | 920 | 0 | 0 | 0 | 920.66 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 9 | 29.54 | 59 | 10 | 0 | 9.07 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 1.71 | 158 | 45 | 110 | 13 | 53 | 0 | 0 | 0 | 0.6 | 77 | 0.5 | 48 | 200 | 115 | 220 | 0 | 974 | 510 | 17 | 5938.08 | 13592.18 | 105.74
17:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 246 | 17 | 4 | 72 | 59 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 298 | 0 | 0 | 6 | 143.42 | 6.5 | 22 | 0 | 325 | 0 | 16 | 37 | 0 | 38 | 33 | 8 | 17 | 50 | 38 | 0.42 | 178 | 107 | 0 | 558 | 70 | 0 | 50 | 17 | 88 | 216 | 0 | 0 | 0 | 1197 | 1 | 26 | 0 | 350 | 0 | 295 | 51 | 0 | 197 | 0 | 34 | 20 | 123 | 13 | 19 | 94 | 144 | 8 | 10 | 35 | 292 | 383 | 248 | 40 | 0 | 145 | 2 | 8 | 0 | 82 | 0 | 143 | 0 | 126 | 15 | 58 | 4.49 | 114 | 0 | 0.4 | 11.95 | 6 | 7606.18 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 29 | 920 | 0 | 0 | 0 | 924.16 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 0 | 16 | 12.15 | 26 | 10 | 0 | 9.93 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 1.05 | 159 | 45 | 112 | 3 | 90 | 0 | 0 | 0 | 0.5 | 17 | 0.05 | 48 | 200 | 116 | 220 | 0 | 995 | 510 | 17 | 5904.84 | 13511.02 | 105.8
18:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 249 | 17 | 17 | 71 | 59 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 1 | 143.42 | 6.5 | 22 | 0 | 340 | 0 | 16 | 35 | 0 | 59 | 33 | 24 | 17 | 50 | 50 | 0 | 180 | 108 | 0 | 558 | 68 | 0 | 50 | 17 | 88 | 216 | 0 | 0 | 0 | 1224 | 0 | 26 | 0 | 330 | 20 | 295 | 51 | 0 | 196 | 0 | 38 | 20 | 189 | 26 | 19 | 86 | 154 | 8 | 1 | 36 | 292 | 384 | 242 | 40 | 0 | 145 | 0 | 8 | 0 | 81 | 0 | 142 | 0 | 126 | 17 | 58 | 0.57 | 112 | 0 | 0 | 0.86 | 6 | 7885.35 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 2 | 920 | 0 | 0 | 0 | 925.05 | 0 | 7 | 0 | 55 | 42 | 0 | 0 | 0 | 52.2 | 1.36 | 3 | 10 | 0 | 1.18 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0.05 | 160 | 45 | 113 | 0 | 92 | 0 | 0 | 0 | 0.2 | 3 | 0.02 | 64 | 200 | 116 | 220 | 0 | 1000 | 510 | 17 | 5932.06 | 13817.41 | 105.86
19:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 217 | 54 | 0 | 72 | 120 | 160 | 15 | 17 | 162 | 0 | 0 | 0 | 0 | 0 | 35 | 287 | 0 | 0 | 0 | 143.42 | 6.5 | 22 | 0 | 310 | 0 | 16 | 36 | 0 | 34 | 50 | 24 | 20 | 50 | 50 | 0 | 181 | 107 | 0 | 558 | 70 | 0 | 50 | 25.5 | 88 | 216 | 0 | 0 | 0 | 1224 | 0 | 92 | 0 | 290 | 18 | 250 | 51 | 0 | 160 | 0 | 86 | 20 | 192 | 26 | 19 | 86 | 184 | 8 | 0 | 36 | 295 | 393 | 242 | 40 | 0 | 143 | 0 | 16 | 0 | 82 | 0 | 142 | 0 | 126 | 17 | 86 | 0 | 162 | 0 | 0 | 0 | 6 | 8198.42 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 85 | 0 | 920 | 0 | 0 | 0 | 1209.7 | 0 | 19 | 0 | 55 | 70 | 0 | 91 | 20 | 52.2 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 160 | 46 | 114 | 0 | 99 | 0 | 150 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 180 | 0 | 1100 | 510 | 17 | 6675.9 | 14874.32 | 105.92
19:30 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 233 | 54 | 2 | 120 | 107 | 260 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 310 | 0 | 16 | 60 | 0 | 37 | 50 | 24 | 36 | 50 | 50 | 0 | 181 | 107 | 0 | 558 | 70 | 0 | 50 | 25.5 | 88 | 216 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 345 | 19 | 305 | 51 | 0 | 198 | 0 | 90 | 20 | 192 | 36 | 19 | 86 | 180 | 8 | 0 | 36 | 288 | 394 | 230 | 40 | 0 | 132 | 0 | 16 | 0 | 82 | 0 | 142 | 0 | 126 | 17 | 86 | 0 | 163 | 0 | 0 | 0 | 6 | 8581.92 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 85 | 0 | 920 | 0 | 0 | 0 | 1317.93 | 0 | 19 | 0 | 55 | 70 | 0 | 100 | 24 | 52.2 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 157 | 46 | 114 | 0 | 99 | 0 | 150 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1130 | 510 | 17 | 7008.13 | 15590.05
20:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 248 | 54 | 5 | 122 | 126 | 278 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 35 | 318 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 340 | 0 | 16 | 58 | 0 | 28 | 50 | 24 | 37 | 50 | 50 | 0 | 222 | 104 | 0 | 558 | 71 | 0 | 50 | 25.5 | 88 | 216 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 375 | 24 | 290 | 51 | 0 | 194 | 0 | 89 | 20 | 190 | 34 | 19 | 86 | 176 | 8 | 0 | 36 | 293 | 392 | 235 | 40 | 0 | 137 | 0 | 16 | 0 | 83 | 0 | 142 | 0 | 126 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 0 | 8741.92 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 85 | 0 | 920 | 0 | 0 | 0 | 1307.94 | 0 | 27 | 0 | 55 | 70 | 0 | 100 | 30 | 52.2 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 159 | 46 | 114 | 0 | 99 | 0 | 150 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1130 | 510 | 17 | 7014.14 | 15756.06 | 105.98
21:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 219 | 54 | 17 | 149 | 126 | 278 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 55 | 302 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 330 | 0 | 16 | 61 | 0 | 48 | 50 | 24 | 54.36 | 50 | 50 | 0 | 222 | 106 | 0 | 558 | 70 | 0 | 50 | 25.5 | 88 | 216 | 0 | 0 | 0 | 1224 | 0 | 61 | 0 | 375 | 33 | 285 | 51 | 0 | 193 | 0 | 88 | 20 | 191 | 37 | 19 | 86 | 170 | 8 | 0 | 29 | 298 | 396 | 241 | 40 | 0 | 142 | 0 | 16 | 0 | 83 | 0 | 142 | 0 | 126 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 0 | 8727.28 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 95 | 0 | 920 | 0 | 0 | 0 | 1315.16 | 0 | 32 | 0 | 55 | 70 | 0 | 100 | 28 | 52.2 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 161 | 46 | 114 | 0 | 99 | 0 | 150 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1130 | 525 | 17 | 6995.36 | 15722.64 | 105.99
22:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 235 | 54 | 17 | 72 | 124 | 147 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 55 | 275 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 325 | 0 | 16 | 57 | 0 | 38 | 50 | 24 | 54.36 | 50 | 50 | 0 | 222 | 106 | 2 | 558 | 70 | 0 | 50 | 25.5 | 88 | 216 | 0 | 0 | 0 | 1224 | 0 | 13 | 0 | 350 | 105 | 280 | 51 | 0 | 184 | 0 | 88 | 20 | 190 | 36 | 19 | 93 | 172 | 8 | 0 | 29 | 294 | 400 | 284 | 40 | 0 | 146 | 0 | 8 | 0 | 84 | 0 | 143 | 0 | 126 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 0 | 8520.28 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 105 | 0 | 920 | 0 | 0 | 0 | 1305.05 | 0 | 32 | 0 | 55 | 70 | 0 | 100 | 28 | 52.2 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 161 | 46 | 114 | 0 | 99 | 0 | 150 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1130 | 570 | 17 | 7019.25 | 15539.53 | 105.99
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 223 | 54 | 17 | 51 | 124 | 147 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 55 | 288 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 310 | 0 | 16 | 47 | 0 | 48 | 50 | 22 | 17 | 50 | 50 | 0 | 222 | 104 | 2 | 558 | 70 | 0 | 50 | 25.5 | 88 | 216 | 0 | 0 | 0 | 1224 | 0 | 12 | 0 | 320 | 127 | 270 | 51 | 0 | 200 | 0 | 86 | 84 | 191 | 38 | 19 | 106 | 182 | 8 | 0 | 29 | 280 | 396 | 340 | 40 | 0 | 143 | 0 | 16 | 0 | 84 | 0 | 141 | 0 | 126 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 0 | 8581.92 | 923 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 920 | 0 | 0 | 0 | 1319.86 | 0 | 32 | 0 | 55 | 70 | 0 | 100 | 28 | 52.2 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 159 | 46 | 115 | 0 | 99 | 0 | 100 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1130 | 570 | 17 | 6803.06 | 15384.98 | 105.99
Total KWH | 0 | 1276800 | 638880 | 0 | 0 | 0 | 0 | 0 | 7344000 | 0 | 10161790 | 742320 | 304560 | 1527552 | 2028480 | 2919327 | 377950 | 719525 | 2181600 | 0 | 0 | 0 | 0 | 0 | 699325 | 6754685 | 0 | 0 | 228137 | 2989200 | 163200 | 5230800 | 0 | 7946363.64 | 0 | 373855 | 928320 | 0 | 726240 | 594916 | 275236 | 382853 | 548160 | 552000 | 25805 | 4767789 | 2545891 | 329280 | 13483636.36 | 1430182 | 0 | 1212480 | 348539.4 | 2166181 | 4927141 | 0 | 0 | 0 | 28947270 | 89370 | 1719563 | 836364 | 8622000 | 1121300 | 7524000 | 1221804 | 0 | 5041000 | 223704 | 1404480 | 1185428 | 3096000 | 250320 | 423680 | 2373480 | 3823680 | 200011 | 416927 | 862944 | 5784000 | 9417500 | 6951000 | 948000 | 0 | 2943163.64 | 84771 | 152544 | 0 | 788160 | 0 | 3238300 | 0 | 2738450 | 144360 | 1543200 | 140961 | 2596800 | 0 | 12600 | 292000 | 297360 | 197309494.04 | 21992727 | 0 | 0 | 165600 | 0 | 0 | 0 | 0 | 1190229 | 0 | 2021040 | 557280 | 22167270 | 0 | 0 | 0 | 24136364 | 0 | 170697 | 0 | 437280 | 819840 | 0 | 583728 | 251531 | 457579 | 391408 | 680750 | 287930 | 0 | 372848 | 0 | 0 | 2084145 | 0 | 0 | 0 | 9062836 | 0 | 36060 | 3900000 | 1144145 | 2682897 | 172631 | 1075756 | 0 | 1309613 | 0 | 44651.28 | 1242720 | 4153 | 1077984 | 4866000 | 2777000 | 5311560 | 0 | 24436363 | 12919272.73 | 442800 | 151274688.01 | 348584182.05