## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 31-08-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-08-2026 | during | 31-08-2026 | during | 31-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 365 | 353 | 412 | 412 | 380 | 380 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 285 | 281 | 335 | 335 | 301.5 | 301.5 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 35 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 45 | 139 | 149.36 | 149.36 | 45 | 142 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 5 | 5.5 | 33 | 33 | 5 | 5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 50 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 97 | 294 | 300 | 300 | 175 | 145 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 116 | 149 | 149 | 52 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 34 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 152 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 35 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 5 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 360 | 330 | 584 | 584 | 526 | 526 | AGC+FGMO
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 232 | 248 | 718 | 718 | 646.2 | 646.2 | AGC+FGMO
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 51 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1682 | 2325.5 | 5396.16 | 5370.16 | 2563.12 | 2992.12
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 5 | 0 | 5 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 44 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 221 | 222 | 222 | 222 | 222 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 219 | 210 | 210 | 210 | 210 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 97 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 15 | 15 | 14 | 32 | 14 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 20 | 50 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 2 | 25 | 30 | 25 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 18 | 43 | 95.1 | 95.1 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.68 | 0 | 4.34 | 0 | 4.34 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 54.36 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 104 | 106 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 50 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 35 | 55 | 163 | 163 | 88 | 160 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 580 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 13 | 41 | 30 | 15 | 30 | 15 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 558 | 555 | 1150 | 1150 | 575 | 575 | GT-2 U/M
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 1998.68 | 2867.86 | 4103.3 | 4152.96 | 2850.84 | 3024.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 206 | 217 | 221.25 | 221.25 | 220 | 220 | Gas shortage
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 300 | 300 | 350.01 | 350.01 | 300 | 300 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 290 | 260 | 342.01 | 342.01 | 306.01 | 306.01 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 360 | 230 | 393 | 393 | 270 | 270 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 53 | 150 | 150 | 150 | 50 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 15 | 32 | 32 | 32 | 32 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 132 | 96 | 163 | 163 | 134 | 134 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 179 | 177 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 148 | 168 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 0 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 100 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 28 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 44 | 89 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 39 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1868 | 1900 | 2764.44 | 2690.44 | 1947.01 | 2043.01
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-08-2026 | during | 31-08-2026 | during | 31-08-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 20.53 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.8 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 163 | 120 | 170 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 87 | 70 | 90 | 70 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.55 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 06 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 234.88 | 273 | 548.6 | 546.5 | 284.1 | 299
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 147 | 163 | 163 | 147 | 147 | AGC+FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 142 | 142 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 83 | 84 | 84 | 84 | 84 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 126 | 126 | 125 | 125 | 120 | 120 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 15 | 16 | 16 | 8 | 8 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 259 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 249 | 394 | 380 | 380 | 380 | 380 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 386 | 400 | 383 | 383 | 383 | 383 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1485 | 1606 | 1702 | 1702 | 1643 | 1643
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 933 | 933 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 32 | 32 | 32 | 32 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 1 | 33 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 50 | 85 | 105 | 105 | 67 | 67 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 6.02 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1115 | 1070 | 1070 | 1070 | 1100 | 1100 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2105.02 | 2121 | 3412 | 3322 | 2289 | 2199
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 982 | 1100 | 1000 | 1100 | 1000 | 1100 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 32 | 64 | 110 | 110 | 16 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 117 | 120 | 120 | 117 | 117 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 580 | 565 | 580 | 580 | 500 | 500 | machine problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 200 | 307 | 307 | 200 | 200 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.1 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2146.1 | 2283 | 2488 | 2587 | 2071 | 2170
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 64.84 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 31 | 32 | 47 | 47 | 32 | 32 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 12 | 135 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 414 | 348 | 413.79 | 413.79 | 413.79 | 413.79 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 0 | 0 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 100 | 100 | 0 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 55 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.34 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 914.03 | 1111.26 | 1469.13 | 1469.13 | 900 | 900 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63.72 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1702.13 | 1904.46 | 3244.04 | 3026.12 | 1741.91 | 1673.99
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 45 | 46 | 46 | 46 | 48 | 48 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 165 | 158 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.1 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 109 | 109 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 38 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 156 | 0 | 154.56 | 0 | 154.56 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 514.1 | 548 | 658.56 | 468 | 547.56 | 392
System Total |  |  |  |  | 28843.2 | 29158.791 | 13735.91 | 15828.82 | 24317.1 | 23865.18 | 15937.54 | 16436.62
Forecast Scenario (31-08-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15210 |  | 2397.05 |  | 17720
|  |  |  | 1:00 | 14330 |  | 2798.15 |  | 17260
|  |  |  | 2:00 | 14150 |  | 2645.35 |  | 16920
|  |  |  | 3:00 | 14200 |  | 2129.65 |  | 16430
|  |  |  | 4:00 | 14200 |  | 1709.45 |  | 15990
|  |  |  | 5:00 | 14080 |  | 1508.9 |  | 15660
|  |  |  | 6:00 | 14030 |  | 1088.7 |  | 15170
|  |  |  | 7:00 | 14070 |  | 964.55 |  | 15080
|  |  |  | 8:00 | 13480 |  | 1365.65 |  | 14910
|  |  |  | 9:00 | 13530 |  | 1489.8 |  | 15090
|  |  |  | 10:00 | 13480 |  | 1690.35 |  | 15250
|  |  |  | 11:00 | 13650 |  | 1719 |  | 15450
|  |  |  | 12:00 | 13740 |  | 2215.6 |  | 16060
|  |  |  | 13:00 | 13700 |  | 2311.1 |  | 16120
|  |  |  | 14:00 | 13840 |  | 1871.8 |  | 15800
|  |  |  | 15:00 | 13510 |  | 2454.35 |  | 16080
|  |  |  | 16:00 | 13640 |  | 1967.3 |  | 15700
|  |  |  | 17:00 | 13720 |  | 1661.7 |  | 15460
|  |  |  | 18:00 | 14220 |  | 1050.5 |  | 15320
|  |  |  | 18:30 | 14860 |  | 1093.475 |  | 16005
|  |  |  | 19:00 | 15510 |  | 1126.9 |  | 16690
|  |  |  | 19:30 | 15590 |  | 1633 |  | 17300
|  |  |  | 20:00 | 15700 |  | 1623 |  | 17400
|  |  |  | 21:00 | 15720 |  | 1652 |  | 17450
|  |  |  | 22:00 | 15540 |  | 1680.8 |  | 17300
|  |  |  | 23:00 | 15380 |  | 1862.25 |  | 17330
Probable Maximum Temperature: |  |  | 35.40°C
Probable Maximum Demand at Day Peak: |  |  | 16060.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1652
Probable Maximum Demand at Evening Peak: |  |  | 17450.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15720.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 342.63 MKWHr. |  | 450 | 100 | 150 | 300 | 100 | 200 | 40 | 170 | 142 | 1652
*** This report is generated digitally from Operation Information System (OIS) at 09:18 hrs on 31-08-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 30-08-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13735.91 | MW | 12:00 Hr. | Energy Generated |  |  | 344.533 |  | MKWHr.
| Day Peak Demand |  |  | 17487.91 | MW | 12:00 Hr. | Energy Unserverd |  |  | 71.476 |  | MKWHr.
| Evening Peak Generation |  |  | 15828.82 | MW | 21:00 Hr. | Energy Demand |  |  | 416.009 |  | MKWHr.
| Evening Peak Demand |  |  | 18329.82 | MW | 21:00 Hr. | Maximum Temperature |  |  | 31 |  | °C
| Minimum Generation of the Day |  |  | 13478.48 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 867.04 |  | MMCFD
| Maximum Generation of the Day |  |  | 15828.82 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.7392 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.8576 | 0 | 15.0685 | 0 | 0 | 0.18806 | 0 | 0 | 47.1142 | Gas | 122.4055 | Gas | 421640404.8312
| Chattogram Zone |  |  | 5.1936 | 36.1855 | 10.6639 | 0 | 5.2648 | 0.026711 | 0 | 0.76704 | 58.1016 | Coal | 109.2499 | Coal | 771967205.09
| Cumilla Zone |  |  | 29.8957 | 0 | 9.9876 | 0 | 0 | 0.23586 | 3.8525 | 0 | 43.9716 | HFO | 51.4586 | HFO | 1042549896.932
| Mymensingh Zone |  |  | 0 | 0 | 4.3846 | 0 | 0 | 0.45552 | 0 | 0 | 4.8401 | HSD | 1.361 | HSD | 42026383.04
| Sylhet Zone |  |  | 36.8085 | 0 | 0 | 0 | 0 | 0.074418 | 0 | 0 | 36.8829 | Hydro | 5.2648 | Hydro | 526482.2
| Khulna Zone |  |  | 0 | 24.7927 | 2.3207 | 0 | 0 | 0.44784 | 22.528 | 0 | 50.0893 | Solar | 4.4476 | Solar | 72547846.5132
| Barishal Zone |  |  | 8.0279 | 43.1607 | 1.4128 | 0 | 0 | 0.00318 | 0 | 0 | 52.6046 | Import | 49.5787 | Import | 303868438.82
| Rajshahi Zone |  |  | 10.6222 | 0 | 4.0909 | 0 | 0 | 1.5131 | 23.1982 | 0 | 39.4244 | Wind | 0.76704 | Wind | 11283158.4
| Rangpur Zone |  |  | 0 | 5.111 | 3.5295 | 1.361 | 0 | 1.5029 | 0 | 0 | 11.5044
| Total |  |  | 122.4055 | 109.2499 | 51.4586 | 1.361 | 5.2648 | 4.4476 | 49.5787 | 0.76704 | 344.533
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 421640404.8312 |  | Hydro | 526482.2
|  |  |  | Coal | 771967205.09 |  | Solar | 72547846.5132
|  |  |  | HFO | 1042549896.932 |  | Import | 303868438.82
|  |  |  | HSD | 42026383.04 |  | Wind | 11283158.4
[5 empty] | Total: | 266,64,09,815 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.528 | Peak Hr Flow | 933.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43522545.45 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.1982 | Peak Hr Flow | 1111.26 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1676 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.8525 | Peak Hr Flow | 168.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2681 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.5787 | Peak Hr Flow | 2212.26 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 573 |  | 6231
|  |  |  | Chattogram |  | 13 |  | 1543
|  |  |  | Cumilla |  | 282 |  | 1641
|  |  |  | Mymensingh |  | 530 |  | 1617
|  |  |  | Sylhet |  | 172 |  | 800
|  |  |  | Khulna |  | 311 |  | 2135
|  |  |  | Barishal |  | 12 |  | 502
|  |  |  | Rajshahi |  | 262 |  | 1821
|  |  |  | Rangpur |  | 238 |  | 1270
|  |  |  | Total |  | 2393 |  | 17560
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Karnaphuli Hydro PP Unit-1 |  |  | 40
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Karnaphuli Hydro PP Unit-2 |  |  | 40
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 80
|  |  |  | Total Unavailable Capacity |  |  |  | 380
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:39 |  | Aminbazar-Kaliakoir 400kV Ckt-1 was shutdown due to SAS integration work at Kaliakoir S/S
end.
| 10:20 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
| 10:45 |  | Birulia 230/132kV S/S ATR-2 LT Project Work S/D Due to NLDC SCADA integration work
| 10:45 |  | Birulia 230/132kV S/S ATR-2 HT Project Work S/D Due to NLDC SCADA integration work
| 11:11 | 20:33 | Bhulta 400/230/132kV S/S 132kV Araihazar-01 Scheduled S/D
| 11:13 | 20:35 | Bhulta 400/230/132kV S/S 132kV Araihazar-02 Scheduled S/D
| 11:21 | 14:35 | Ghatail 132/33kV S/S T-1 LT Tripped showing REC 650 relays Due to The bus D/S insulator | [7 empty] | 35.0MW load
|  |  | of a 33kV spare feeder of 33kV switching station has been broken due to heavy flashing. | [7 empty] | interrup.
The reason of flashing discovered as a reason of bird landing.
| 13:20 | 15:32 | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to 33 kv Feeder maintenance | [7 empty] | 50.0MW load
interrup.
| 13:22 | 15:32 | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to 33 kv Feeder Maintenance | [7 empty] | 50.0MW load
interrup.
| 13:29 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 13:34 | 14:34 | Ghatail 132/33kV S/S T-1 HT Forced S/D Due to Maintenance work on 33 kV spare feeder of | [7 empty] | 35.0MW load
|  |  | Bus D/S insulator and conductor of bus section-1. | [7 empty] | interrup.
|  | 17:13 | Fenchuganj-Sreemangal 132kV Ckt-1 is restored.
| 23:04 | 00:19 | Nabinagar 132/33kV S/S T-1 HT Scheduled S/D Due to 33 kv bus section red hot maintenance | [7 empty] | 75.0MW load
|  |  | by Dhaka PBS-1 | [7 empty] | interrup.
| 23:04 | 00:20 | Nabinagar 132/33kV S/S T-1 LT Scheduled S/D Due to 33 kv bus section red hot maintenance | [7 empty] | 75.0MW load
|  |  | by Dhaka PBS-1 | [7 empty] | interrup.
| 05:51 |  | Khulna (C) S/S Tr-2 415 T HT Tripped showing No operate any relay. relays Due to Unknown
| 06:34 |  | Bhulta 132/33kV S/S GT1 HT Scheduled S/D Due to Red Hot Maintenance | [7 empty] | 60.0MW load
interrup.
| 07:07 |  | Bhulta 400/230/132kV S/S 132kV Araihazar-01 Scheduled S/D
| 07:09 |  | Bhulta 400/230/132kV S/S 132kV Araihazar-02 Scheduled S/D
| 07:38 |  | Naogaon 132/33kV S/S T-4 LT Scheduled S/D Due to 33KV Aux. Tr. Bus Ds | [7 empty] | 45.0MW load
|  |  | Maintenance. Shutdown taken by AE. Nazmul Haque, - NESCO Division-1. | [7 empty] | interrup.
| 07:38 |  | Naogaon 132/33kV S/S T-4 HT Scheduled S/D Due to 33KV Aux. Tr. Bus Ds | [7 empty] | 45.0MW load
|  |  | Maintenance. Shutdown taken by AE. Nazmul Haque, - NESCO Division-1. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 30-08-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 353 | 8668800 | Gas shortage
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 378660 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 281 | 6962521 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 694080 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 139 | 1721760 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 705341 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 710330 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 5.5 | 120000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 522720 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 671040 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | -
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 2995353 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 116 | 1465056 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1376640 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 152 | 1972800 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 188058 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 55440 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 330 | 8893636.36 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 248 | 6689950 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 51 | 2322000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2325.5 | 47114185.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 305582.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 2430 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 1142400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5264822 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5006414 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 97 | 2396181 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 15 | 363984 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 353552 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 567360 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 187200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 43 | 598080 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 24281 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 371345 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 54.36 | 388052 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 106 | 2532509 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 582720 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 55 | 1062182 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 22745452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 41 | 767040 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 555 | 13440000 | GT-2 U/M
Chattogram Area Total |  |  |  |  | 4885.967 | 2867.86 | 58101586.4
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 217 | 5072000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 300 | 7299000 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 260 | 6818000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 230 | 6321000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1236628 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1649309 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 15 | 480336 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2694594 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 177 | 4386720 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 168 | 3852480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 151589 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 454430 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1816020 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 179760 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 1323840 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 235855 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1900 | 43971561
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 116665 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 2577600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1549200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 327250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 134640 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 123120 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 273 | 4840075
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 74418 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 947000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine Problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3498300 | AGC+FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 3383600 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1841280 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 126 | 2731400 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 15 | 276096 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 259 | 6490000 | Gas shortage
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 394 | 8312000 | Gas shortage
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9328800 | -
Sylhet Area Total |  |  |  |  | 2325 | 1606 | 36882894
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 933 | 22528000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 168480 | Engine Problem
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 33 | 283580 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 1868688 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 447840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1070 | 24792730 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2121 | 50089318
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1100 | 24392727 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 64 | 971232 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 117 | 2790000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 565 | 13968000 | machine problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5237870 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 441600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 200 | 4800000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3180 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2283 | 52604609
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 358368 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 740074 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 280732 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 135 | 1382091 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 348 | 9240145 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 295019 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1201368 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 347200 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 820032 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 55 | 406464 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 34860 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1111.26 | 23198182 | Coal shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 377088 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 742750 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1904.46 | 39424373
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 1360958 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 46 | 1093964 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 4017000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 825321 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 35778.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 109 | 2704224 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 156048 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1311120 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 548 | 11504413.12
Eastern Grid Total |  |  |  |  | 17427.666 | 8972.36 | 190910301.76
Western Grid Total |  |  |  |  | 11731.125 | 6856.46 | 153622713.12
National Grid Total |  |  |  |  | 29158.791 | 15828.82 | 344533014.88
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 30-08-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10261.99 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4903.6 | MW
i) Dhaka area |  |  | 5657.99 |  | MW | i) Khulna area |  |  |  | 1824 | MW
ii) Chattogram area |  |  | 1530 |  | MW | ii) Barishal area |  |  |  | 489.5 | MW
iii) Cumilla area |  |  | 1359 |  | MW | iii) Rajshahi area |  |  |  | 1558.6 | MW
iv) Mymensingh area |  |  | 1087 |  | MW | iv) Rangpur area |  |  |  | 1031.5 | MW
v) Sylhet area |  |  | 628 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15165.59 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 140 | 19:30 | 133 | Narshingdi | 203 | 21:00 | 199 | Uttara | 112 | 14:00
2 | AKSML | 162 | 07:00 | 68 | Hasnabad | 107 | 20:00 | 134 | Natore | 163 | 20:00 | 200 | UttaraNew | 62 | 00:00
3 | Aftabnagar | 48 | 00:00 | 69 | Hathazari | 98 | 21:00 | 135 | Nawabganj | 55.6 | 21:00 | 201 | Zigatola | 102 | 14:00
4 | Agargaon | 131 | 12:00 | 70 | Hatirjheel | 92 | 14:00 | 136 | Netrakona | 107 | 15:00
5 | Agrabad | 70 | 20:00 | 71 | Ishurdi | 81 | 20:00 | 137 | New | 94 | 09:00
6 | Amnura | 35 | 20:00 | 72 | Jaldhaka | 80 | 19:30 | 138 | Niamatpur | 70 | 06:00
7 | Ashuganj | 93 | 00:00 | 73 | Jamalpur | 122 | 23:00 | 139 | Noapara | 41 | 19:30
8 | BSRM | 207 | 04:00 | 74 | Jashore | 182 | 00:00 | 140 | PHP | 13 | 18:30
9 | Bagerhat | 87 | 22:00 | 75 | Jhenaidah | 98 | 22:00 | 141 | Pabna | 107 | 23:00
10 | Bajitpur | 102 | 22:00 | 76 | Joydebpur | 187 | 19:30 | 142 | Palashbari | 138 | 21:00
11 | Bakerganj | 15 | 00:00 | 77 | Joypurhat | 64 | 22:00 | 143 | Panchagarh | 75 | 00:00
12 | Bakulia | 95 | 19:30 | 78 | Juldah | 15 | 00:00 | 144 | Patiya | 23 | 04:00
13 | Banani | 64 | 13:00 | 79 | KSRM | 35 | 08:00 | 145 | Patnitala | 37 | 18:30
14 | Bangabhaban | 18 | 13:00 | 80 | Kabirpur | 281 | 19:00 | 146 | Patuakhali | 71.5 | 20:00
15 | Barapukuria | 63 | 22:00 | 81 | Kachua | 90 | 20:00 | 147 | Payra | 40 | 20:00
16 | Barguna | 24 | 22:00 | 82 | Kaliganj | 42 | 07:00 | 148 | Postogola | 66 | 01:00
17 | Barishal | 105 | 20:00 | 83 | Kallyanpur | 132 | 13:00 | 149 | Pubail | 49 | 18:30
18 | Barishal-230 | 112 | 20:00 | 84 | Kalurghat | 40 | 18:30 | 150 | Purbachal | 22 | 21:00
19 | Baroaulia | 65 | 01:00 | 85 | Kamrangirchar | 78 | 18:30 | 151 | Purbasadipur | 131 | 20:00
20 | Baroirhat | 60 | 21:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 33 | 06:00
21 | Bashundhara | 256 | 14:00 | 87 | Kasba | 37 | 20:00 | 153 | Rahim | 55 | 17:00
22 | BashundharaCement | 1 | 16:00 | 88 | Kazla | 112 | 18:30 | 154 | Rajbari | 82 | 22:00
23 | Beanibazar | 64 | 19:00 | 89 | Keranigonj | 108 | 19:30 | 155 | Rajendrapur | 117 | 21:00
24 | Benapole | 58 | 21:00 | 90 | Khagrachori | 36 | 20:00 | 156 | Rajshahi | 121 | 23:00
25 | Bhaluka | 162 | 00:00 | 91 | Khulna | 58 | 20:00 | 157 | Rajshahi-230 | 114 | 19:30
26 | Bhandaria | 62 | 21:00 | 92 | Khulshi | 174 | 21:00 | 158 | Ramganj | 104 | 22:00
27 | Bhangura | 32 | 22:00 | 93 | Kishoreganj | 122 | 15:00 | 159 | Rampur | 45 | 20:00
28 | Bheramara(GK) | 72 | 07:00 | 94 | Kodda | 321 | 21:00 | 160 | Rangamati | 15 | 07:00
29 | Bhulta | 227 | 13:00 | 95 | Kulaura | 51 | 21:00 | 161 | Rangpur | 139 | 20:00
30 | Bog-Sherpur | 68 | 22:00 | 96 | Kurigram | 70 | 19:30 | 162 | Ruppur | 4.8 | 10:00
31 | Bogura | 213 | 19:00 | 97 | Kushtia | 146 | 21:00 | 163 | SSM | 8 | 04:00
32 | Borhanuddin | 79 | 20:00 | 98 | Laksam | 34 | 03:00 | 164 | Saidpur | 106 | 22:00
33 | Brahmanbaria | 134 | 21:00 | 99 | Lakshmipur | 52 | 23:00 | 165 | Santhia | 34 | 22:00
34 | Cantonment | 154 | 13:00 | 100 | Lalbag | 95 | 14:00 | 166 | Satkhira | 132 | 22:00
35 | Chandina | 21 | 00:00 | 101 | Lalmonirhat | 60 | 20:00 | 167 | Satmasjid | 114 | 19:00
36 | Chandpur | 78 | 20:00 | 102 | MI_Cement | 13.2 | 22:00 | 168 | Savar | 225 | 19:00
37 | Chandraghona | 34 | 20:00 | 103 | Madanganj | 47 | 20:00 | 169 | SevenRings | 16.58 | 16:00
38 | Chapai | 69 | 19:30 | 104 | Madaripur | 99 | 22:00 | 170 | ShahCement | 21 | 08:00
39 | Charfasson | 34 | 22:00 | 105 | Madartek | 102 | 00:00 | 171 | Shahjadpur | 85 | 21:00
40 | Charsaidpur | 48 | 16:00 | 106 | Madunaghat | 53 | 21:00 | 172 | Shahjibazar | 129 | 21:00
41 | Chauddagram | 68 | 22:00 | 107 | Magura | 63 | 22:00 | 173 | Shahmirpur | 60 | 22:00
42 | Chhatak | 35 | 20:00 | 108 | Mahasthangarh | 71 | 05:00 | 174 | Shariatpur | 87 | 20:00
43 | Chowmuhani | 138 | 05:00 | 109 | Maijdee | 28 | 00:00 | 175 | Sherpur | 158 | 23:00
44 | Chuadanga | 109 | 22:00 | 110 | Manikganj | 158 | 21:00 | 176 | Shikalbaha | 35.5 | 00:00
45 | Coxsbazar | 136 | 20:00 | 111 | Maniknagar | 83 | 14:00 | 177 | Shitalakhya | 86.4 | 13:00
46 | Cumilla(N) | 130 | 09:00 | 112 | Matarbari | 54 | 22:00 | 178 | Sholosohor | 50 | 20:00
47 | Cumilla(S) | 184 | 18:30 | 113 | Matuail | 81 | 00:00 | 179 | Shomvuganj | 35 | 00:00
48 | Daganbhuiyan | 37 | 01:00 | 114 | Metrorail_Motijheel | 30 | 18:30 | 180 | Shyampur | 172 | 17:00
49 | Daudkandi | 136 | 19:30 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 139 | 11:00
50 | DhakaUniversity | 104 | 13:00 | 116 | Millgate | 96 | 09:00 | 182 | Sirajganj | 134 | 20:00
51 | Dhamrai | 100 | 05:00 | 117 | Mirpur | 163 | 18:30 | 183 | Sitakunda | 14 | 18:30
52 | Dhanmondi | 139.6 | 13:00 | 118 | Mirsorai | 48 | 10:00 | 184 | Sonargaon | 146 | 19:00
53 | Dohazari | 124 | 20:00 | 119 | Mirzapur | 43 | 20:00 | 185 | Sreemongol | 74 | 18:30
54 | Faridpur | 185 | 21:00 | 120 | Mithapukur | 68 | 20:00 | 186 | Sreepur | 122 | 22:00
55 | Fatullah | 114 | 09:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 52.37 | 19:30
56 | Fenchuganj | 40 | 22:00 | 122 | Mogbazar | 53.6 | 18:30 | 188 | Sunamganj | 50 | 00:00
57 | Feni | 102 | 22:00 | 123 | Mongla | 51 | 19:00 | 189 | Sylhet | 132 | 21:00
58 | GPH | 74 | 01:00 | 124 | Motijheel | 57 | 13:00 | 190 | Sylhet_(South) | 73 | 18:30
59 | Ghatail | 87 | 22:00 | 125 | Muktagacha | 46 | 13:00 | 191 | TK | 0 | 00:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 112 | 20:00 | 192 | Tangail | 188 | 20:00
61 | Ghorashal-230 | 108 | 22:00 | 127 | Muradnagar | 46 | 22:00 | 193 | Taraganj | 32 | 20:00
62 | Goalpara | 36 | 00:00 | 128 | Mymensingh | 132 | 18:00 | 194 | Tasnim | 41 | 20:00
63 | Gollamari | 104 | 19:30 | 129 | Nabinagar | 100 | 18:00 | 195 | Thakurgaon | 118 | 19:00
64 | Gopalganj | 111 | 22:00 | 130 | Naogaon | 129 | 22:00 | 196 | Tongi | 143 | 19:00
65 | Gulshan | 134 | 14:00 | 131 | Narail | 59 | 22:00 | 197 | Ullahpara | 40 | 20:00
66 | Halishahar | 136 | 14:00 | 132 | Narinda | 72 | 18:30 | 198 | Ullon | 63 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 30-08-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15213.8 | 3678 |  | 19057.8
1:00 | 14333.83 | 3350 |  | 17834.83
2:00 | 14152.67 | 3322 |  | 17623.67
3:00 | 14199.56 | 3167 |  | 17509.56
4:00 | 14202.78 | 3085 |  | 17426.78
5:00 | 14081.74 | 2883 |  | 17094.74
6:00 | 14027.58 | 2665 |  | 16812.58
7:00 | 14070.56 | 2415 |  | 16594.56
8:00 | 13478.48 | 2692 |  | 16291.48
9:00 | 13527.06 | 2936 |  | 16595.06
10:00 | 13480.47 | 3102 |  | 16722.47
11:00 | 13647.1 | 3179 |  | 16969.1
12:00 | 13735.91 | 3590 |  | 17487.91
13:00 | 13703.08 | 3535 |  | 17397.08
14:00 | 13844.75 | 3451 |  | 17450.75
15:00 | 13514.06 | 3692 |  | 17372.06
16:00 | 13644.77 | 3639 |  | 17447.77
17:00 | 13719.44 | 3297 |  | 17164.44
18:00 | 14218.16 | 2539 |  | 16871.16
19:00 | 15508.48 | 2405 |  | 18021.48
19:30 | 15586.21 | 2401 |  | 18095.21
20:00 | 15696.7 | 2007 |  | 17793.7
21:00 | 15828.82 | 2393 |  | 18329.82
22:00 | 15627.17 | 1916 |  | 17629.39
23:00 | 15212.76 | 2538 |  | 17864.76
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 30-08-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 153 | 36 | 380 | 118 | 1440 | 640 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 105 | 36 | 212 | 116 | 1222 | 590
2:00 | 115 | 34 | 246 | 108 | 1310 | 606 |  | Import | 0
3:00 | 101 | 27 | 230 | 118 | 1240 | 584
4:00 | 99 | 29 | 200 | 110 | 1226 | 592 | Ishurdi-Ghorashal Ckt-2 | Export | 3370545.45
5:00 | 92 | 27 | 180 | 116 | 1128 | 562
6:00 | 86 | 22 | 130 | 80 | 1116 | 554 |  | Import | 0
7:00 | 89 | 18 | 180 | 140 | 1290 | 548
8:00 | 143 | 39 | 320 | 114 | 1594 | 642 | Sirajganj-Sreepur Ckt-1 | Export | 2001000
9:00 | 185 | 59 | 390 | 96 | 1752 | 704
10:00 | 191 | 47 | 430 | 120 | 1910 | 704 |  | Import | 0
11:00 | 175 | 36 | 410 | 140 | 1858 | 662
12:00 | 187 | 43 | 500 | 176 | 1842 | 690 | Sirajganj-Sreepur Ckt-2 | Export | 2011000
13:00 | 205 | 54 | 510 | 184 | 1916 | 738
14:00 | 207 | 61 | 510 | 188 | 1964 | 796 |  | Import | 0
15:00 | 176 | 44 | 420 | 148 | 1856 | 692
16:00 | 188 | 51 | 490 | 188 | 1884 | 728 | Gopalganj-Aminbazar Ckt-1 | Export | 18050000
17:00 | 179 | 52 | 470 | 204 | 1762 | 766
18:00 | 173 | 53 | 430 | 188 | 1718 | 772 |  | Import | 0
18:30 | 151 | 48 | 360 | 184 | 1536 | 726
19:00 | 142 | 42 | 370 | 176 | 1492 | 672 | Gopalganj-Aminbazar Ckt-2 | Export | 18090000
19:30 | 110 | 23 | 300 | 156 | 1336 | 592
20:00 | 100 | 16 | 310 | 144 | 1262 | 558 |  | Import | 0
21:00 | 100 | 14 | 310 | 150 | 1266 | 532
22:00 | 117 | 37 | 330 | 176 | 1282 | 594 |  | Total Export | 43522545.45
23:00 | 124 | 35 | 380 | 182 | 1386 | 570 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 30-08-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8455.92 | 6757.88 | 15213.8 | DAILY GENERATION CURVE
00:30 | 8337.375 | 6436.44 | 14773.815
01:00 | 8218.83 | 6115 | 14333.83 | 30-08-2026
01:30 | 8138.625 | 6104.625 | 14243.25
02:00 | 8058.42 | 6094.25 | 14152.67
02:30 | 8080.52 | 6095.595 | 14176.115
03:00 | 8102.62 | 6096.94 | 14199.56
03:30 | 8146.02 | 6055.15 | 14201.17
04:00 | 8189.42 | 6013.36 | 14202.78
04:30 | 8175.42 | 5966.84 | 14142.26
05:00 | 8161.42 | 5920.32 | 14081.74
05:30 | 8154.85 | 5899.81 | 14054.66
06:00 | 8148.28 | 5879.3 | 14027.58
06:30 | 8129.065 | 5920.005 | 14049.07
07:00 | 8109.85 | 5960.71 | 14070.56
07:30 | 7733.33 | 6041.19 | 13774.52
08:00 | 7356.81 | 6121.67 | 13478.48
08:30 | 7338.645 | 6164.125 | 13502.77
09:00 | 7320.48 | 6206.58 | 13527.06
09:30 | 7215.97 | 6287.795 | 13503.765
10:00 | 7111.46 | 6369.01 | 13480.47
10:30 | 7170.495 | 6393.29 | 13563.785
11:00 | 7229.53 | 6417.57 | 13647.1
11:30 | 7249.045 | 6442.46 | 13691.505
12:00 | 7268.56 | 6467.35 | 13735.91
12:30 | 7206.28 | 6513.215 | 13719.495
13:00 | 7144 | 6559.08 | 13703.08
13:30 | 7253.65 | 6520.265 | 13773.915
14:00 | 7363.3 | 6481.45 | 13844.75
14:30 | 7283.22 | 6396.185 | 13679.405
15:00 | 7203.14 | 6310.92 | 13514.06
15:30 | 7266.745 | 6312.67 | 13579.415
16:00 | 7330.35 | 6314.42 | 13644.77
16:30 | 7371.115 | 6310.99 | 13682.105
17:00 | 7411.88 | 6307.56 | 13719.44
17:30 | 7612.385 | 6356.415 | 13968.8
18:00 | 7812.89 | 6405.27 | 14218.16
18:30 | 8261.695 | 6601.625 | 14863.32
19:00 | 8710.5 | 6797.98 | 15508.48
19:30 | 8913 | 6673.21 | 15586.21
20:00 | 8927 | 6769.7 | 15696.7
20:30 | 8949.68 | 6813.08 | 15762.76 |  | Executive Engineer
21:00 | 8972.36 | 6856.46 | 15828.82 |  | Network Operation Division
21:30 | 8873.36 | 6854.635 | 15727.995
22:00 | 8774.36 | 6852.81 | 15627.17
22:30 | 8571.18 | 6848.785 | 15419.965
23:00 | 8368 | 6844.76 | 15212.76

## En-Curve
QF-LDC-12
Date | 30-08-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3537 | 1372 | 923 | 0 | 182 | 1293.68 | 222 | 4674 | 0 | 727.42 | 2075.7 | 165 | 0 | 42 | 3678 | DAILY ENERGY CURVE
00:30 | 3585 | 1394 | 927.5 | 0 | 177 | 1104.74 | 222 | 4672 | 0 | 660.42 | 1819.155 | 165 | 0 | 47 | 3514 | 30-08-2026
01:00 | 3633 | 1416 | 932 | 0 | 172 | 915.8 | 222 | 4670 | 0 | 593.42 | 1562.61 | 165 | 0 | 52 | 3350
01:30 | 3629 | 1408 | 932.5 | 0 | 174 | 907.925 | 220 | 4669.5 | 0 | 516.42 | 1577.405 | 165 | 0 | 43.5 | 3336 | Energy Generated | 344.533 |  | MKWHr
02:00 | 3625 | 1400 | 933 | 0 | 176 | 900.05 | 218 | 4669 | 0 | 439.42 | 1592.2 | 165 | 0 | 35 | 3322 | Energy not Served | 71.476 |  | MKWHr
02:30 | 3632.5 | 1415 | 933 | 0 | 172 | 901.395 | 218 | 4669 | 0 | 439.42 | 1597.3 | 165 | 0 | 33.5 | 3244.5 | Total Energy Requirement | 416.009 |  | MKWHr
03:00 | 3640 | 1430 | 933 | 0 | 168 | 902.74 | 218 | 4669 | 0 | 439.42 | 1602.4 | 165 | 0 | 32 | 3167
03:30 | 3672.5 | 1465.5 | 933 | 0 | 168 | 903.45 | 218 | 4669 | 0 | 429.42 | 1569.8 | 132.5 | 0 | 40 | 3126
04:00 | 3705 | 1501 | 933 | 0 | 168 | 904.16 | 218 | 4669 | 0 | 419.42 | 1537.2 | 100 | 0 | 48 | 3085
04:30 | 3678 | 1556.5 | 933 | 0 | 166 | 908.64 | 195 | 4669 | 0 | 443.42 | 1504.7 | 50 | 0 | 38 | 2984
05:00 | 3651 | 1612 | 933 | 0 | 164 | 913.12 | 172 | 4669 | 0 | 467.42 | 1472.2 | 0 | 0 | 28 | 2883
05:30 | 3637 | 1592 | 933 | 0 | 157 | 907.765 | 195 | 4669.5 | 4.775 | 476.42 | 1459.7 | 0 | 0 | 22.5 | 2774
06:00 | 3623 | 1572 | 933 | 0 | 150 | 902.41 | 218 | 4670 | 9.55 | 485.42 | 1447.2 | 0 | 0 | 17 | 2665
06:30 | 3658.5 | 1580.5 | 928 | 0 | 151 | 907.545 | 218.5 | 4627.5 | 64.405 | 486.92 | 1403.2 | 0 | 0 | 23 | 2540
07:00 | 3694 | 1589 | 923 | 0 | 152 | 912.68 | 219 | 4585 | 119.26 | 488.42 | 1359.2 | 0 | 0 | 29 | 2415
07:30 | 3623.5 | 1556 | 925.5 | 0 | 153 | 911.3 | 219.5 | 4328.5 | 197.1 | 472.42 | 1360.2 | 0 | 0 | 27.5 | 2553.5
08:00 | 3553 | 1523 | 928 | 0 | 154 | 909.92 | 220 | 4072 | 274.94 | 456.42 | 1361.2 | 0 | 0 | 26 | 2692
08:30 | 3584 | 1481.5 | 928 | 0 | 145 | 908.275 | 220 | 4049.5 | 360.875 | 443.92 | 1353.2 | 0 | 0 | 28.5 | 2814
09:00 | 3615 | 1440 | 928 | 0 | 136 | 906.63 | 220 | 4027 | 446.81 | 431.42 | 1345.2 | 0 | 0 | 31 | 2936
09:30 | 3539.5 | 1411 | 928 | 0 | 130 | 906.62 | 220 | 4050 | 523.025 | 410.42 | 1347.7 | 0 | 0 | 37.5 | 3019
10:00 | 3464 | 1382 | 928 | 0 | 124 | 906.61 | 220 | 4073 | 599.24 | 389.42 | 1350.2 | 0 | 0 | 44 | 3102
10:30 | 3490.5 | 1401 | 928 | 0 | 132 | 907.74 | 219.5 | 4148 | 585.525 | 370.92 | 1342.6 | 0 | 0 | 38 | 3140.5
11:00 | 3517 | 1420 | 928 | 0 | 140 | 908.87 | 219 | 4223 | 571.81 | 352.42 | 1335 | 0 | 0 | 32 | 3179
11:30 | 3579 | 1430.5 | 930.5 | 0 | 144 | 911.45 | 219 | 4224 | 582.745 | 287.21 | 1360.6 | 0 | 0 | 22.5 | 3384.5
12:00 | 3641 | 1441 | 933 | 0 | 148 | 914.03 | 219 | 4225 | 593.68 | 222 | 1386.2 | 0 | 0 | 13 | 3590
12:30 | 3570.5 | 1470 | 933 | 0 | 138 | 917.29 | 218.5 | 4227 | 620.005 | 221.5 | 1384.7 | 0 | 0 | 19 | 3562.5
13:00 | 3500 | 1499 | 933 | 0 | 128 | 920.55 | 218 | 4229 | 646.33 | 221 | 1383.2 | 0 | 0 | 25 | 3535
13:30 | 3491.5 | 1569.5 | 933.5 | 0 | 146 | 917.735 | 218 | 4231.5 | 585.48 | 266 | 1388.2 | 0 | 0 | 26.5 | 3493
14:00 | 3483 | 1640 | 934 | 0 | 164 | 914.92 | 218 | 4234 | 524.63 | 311 | 1393.2 | 0 | 0 | 28 | 3451
14:30 | 3480 | 1551.5 | 933.5 | 0 | 172 | 918.81 | 218.5 | 4232 | 394.895 | 354.5 | 1390.7 | 0 | 0 | 33 | 3571.5
15:00 | 3477 | 1463 | 933 | 0 | 180 | 922.7 | 219 | 4230 | 265.16 | 398 | 1388.2 | 0 | 0 | 38 | 3692
15:30 | 3525.5 | 1476 | 933 | 0 | 175 | 920.06 | 219 | 4318 | 242.255 | 353.5 | 1381.6 | 0 | 0 | 35.5 | 3665.5
16:00 | 3574 | 1489 | 933 | 0 | 170 | 917.42 | 219 | 4406 | 219.35 | 309 | 1375 | 0 | 0 | 33 | 3639
16:30 | 3575.5 | 1429 | 933 | 0 | 164 | 920.59 | 219 | 4447.5 | 164.415 | 324.5 | 1471.1 | 0 | 0 | 33.5 | 3468
17:00 | 3577 | 1369 | 933 | 0 | 158 | 923.76 | 219 | 4489 | 109.48 | 340 | 1567.2 | 0 | 0 | 34 | 3297
17:30 | 3608 | 1389.5 | 933 | 0 | 160 | 975.415 | 219 | 4524.5 | 60.685 | 398.5 | 1664.2 | 0 | 0 | 36 | 2918
18:00 | 3639 | 1410 | 933 | 0 | 162 | 1027.07 | 219 | 4560 | 11.89 | 457 | 1761.2 | 0 | 0 | 38 | 2539
18:30 | 3650 | 1412 | 933 | 0 | 166 | 1074.925 | 220 | 4716.5 | 5.945 | 538.5 | 2061.45 | 50 | 0 | 35 | 2472
19:00 | 3661 | 1414 | 933 | 0 | 170 | 1122.78 | 221 | 4873 | 0 | 620 | 2361.7 | 100 | 0 | 32 | 2405
19:30 | 3597 | 1329.5 | 933 | 0 | 172 | 1123.01 | 221 | 4924 | 0 | 635 | 2543.7 | 70 | 0 | 38 | 2401
20:00 | 3649 | 1388.5 | 933 | 0 | 178 | 1125.5 | 221 | 4921 | 0 | 628 | 2535.7 | 75 | 0 | 42 | 2007
20:30 | 3653.5 | 1395 | 933 | 0 | 173 | 1118.38 | 221 | 4919.5 | 0 | 635.5 | 2552.38 | 120 | 0 | 41.5 | 2200
21:00 | 3658 | 1401.5 | 933 | 0 | 168 | 1111.26 | 221 | 4918 | 0 | 643 | 2569.06 | 165 | 0 | 41 | 2393
21:30 | 3668.5 | 1398 | 932.5 | 0 | 171 | 1103.935 | 221 | 4923.5 | 0 | 642.5 | 2468.56 | 165 | 0 | 33.5 | 2154.5
22:00 | 3679 | 1394.5 | 932 | 0 | 174 | 1096.61 | 221 | 4929 | 0 | 642 | 2368.06 | 165 | 0 | 26 | 1916
22:30 | 3626 | 1357.5 | 932 | 0 | 175 | 1094.585 | 221 | 4925.5 | 0 | 619 | 2276.88 | 165 | 0 | 27.5 | 2227
23:00 | 3573 | 1320.5 | 932 | 0 | 176 | 1092.56 | 221 | 4922 | 0 | 596 | 2185.7 | 165 | 0 | 29 | 2538
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 30-08-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 376 | 03:00 | 363 | 14:00 | Madunaghat | 401 | 01:00 | 397 | 12:00
Amtali | 413 | 02:00 | 409 | 12:00 | Meghnaghat | 382 | 02:00 | 370 | 14:00
Ashuganj | 393 | 02:00 | 383 | 18:30 | Mirsorai | 400 | 02:00 | 393 | 14:00
Bhulta | 396 | 06:00 | 376 | 14:00 | Payra | 414 | 02:00 | 411 | 12:00
Bibiana | 383 | 07:00 | 375 | 18:00 | Rahanpur | 410 | 09:00 | 402 | 18:30
BIPTC | 405 | 07:00 | 397 | 20:00 | Rampal | 398 | 08:00 | 390 | 14:00
Bogura | 396 | 09:00 | 387 | 07:00
Gopalganj | 393 | 02:00 | 383 | 18:30
Kaliakoir | 371 | 07:00 | 352 | 18:00
Korerhat | 400 | 07:00 | 392 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 06:00 | 218 | 14:00 | Hasnabad | 226 | 04:00 | 215 | 13:00
AKSML | 237 | 07:00 | 231 | 22:00 | Hathazari | 238 | 07:00 | 234 | 12:00
Aminbazar | 230 | 02:00 | 219 | 14:00 | Ishurdi | 237 | 09:00 | 224 | 18:30
Ashuganj | 229 | 06:00 | 221 | 13:00 | Jhenaidah | 229 | 09:00 | 215 | 20:00
Ashuganj-400 | 229 | 06:00 | 221 | 13:00 | Kachua | 231 | 07:00 | 227 | 12:00
Baghabari | 233 | 01:00 | 226 | 19:30 | Kaliakoir | 230 | 01:00 | 216 | 18:30
Barapukuria | 227 | 00:00 | 222 | 18:30 | Keranigonj | 227 | 02:00 | 215 | 18:30
Barapukuria-230 | 227 | 00:00 | 222 | 18:30 | Khulna(S) | 228 | 02:00 | 220 | 20:00
Barapukuria(N) | 230 | 09:00 | 225 | 07:00 | Korerhat | 229 | 07:00 | 224 | 13:00
Barishal | 227 | 08:00 | 222 | 18:30 | Madunaghat | 239 | 00:00 | 236 | 12:00
Bheramara | 235 | 09:00 | 222 | 19:30 | Madunaghat-400 | 240 | 01:00 | 238 | 12:00
Bhulta | 226 | 06:00 | 213 | 14:00 | Maniknagar | 223 | 04:00 | 211 | 14:00
Bibiana | 223 | 03:00 | 217 | 18:30 | Meghnaghat | 235 | 03:00 | 222 | 14:00
BIPTC | 238 | 09:00 | 223 | 18:30 | Meghnaghat-400 | 227 | 02:00 | 216 | 13:00
Birulia | 230 | 07:00 | 218 | 14:00 | Mirsorai | 233 | 02:00 | 228 | 16:00
Bogura | 239 | 09:00 | 233 | 07:00 | Naogaon | 225 | 02:00 | 212 | 07:00
Bogura-400 | 239 | 04:00 | 233 | 07:00 | Purbasadipur | 225 | 09:00 | 219 | 20:00
Borhanuddin | 230 | 08:00 | 226 | 01:00 | Rajshahi | 234 | 02:00 | 223 | 18:30
BSRM | 229 | 01:00 | 225 | 14:00 | Rampal | 227 | 08:00 | 220 | 20:00
Charfasson | 229 | 02:00 | 226 | 21:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 230 | 07:00 | 226 | 12:00 | Rampura | 225 | 06:00 | 210 | 14:00
Cumilla(N) | 229 | 14:00 | 219 | 17:00 | Shikalbaha | 238 | 01:00 | 235 | 22:00
Faridpur | 223 | 09:00 | 216 | 20:00 | Shyampur | 226 | 02:00 | 210 | 19:30
Fenchuganj | 224 | 01:00 | 218 | 22:00 | Siddhirganj | 225 | 02:00 | 214 | 13:00
Feni | 230 | 23:00 | 222 | 18:30 | Sirajgonj | 237 | 02:00 | 232 | 07:00
Ghorashal | 230 | 01:00 | 220 | 16:00 | Sreepur | 225 | 02:00 | 217 | 17:00
Ghorashal-230 | 218 | 02:00 | 203 | 18:00 | Tongi | 220 | 04:00 | 203 | 17:00
Gopalganj | 223 | 03:00 | 218 | 18:30
GPH | 235 | 01:00 | 232 | 14:00
Haripur | 225 | 02:00 | 213 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 02:00 | 125 | 14:00 | Madaripur | 133 | 08:00 | 129 | 19:00
Agargaon | 135 | 02:00 | 126 | 14:00 | Madartek | 136 | 05:00 | 124 | 14:00
Agrabad | 138 | 12:00 | 134 | 13:00 | Madunaghat | 139 | 00:00 | 136 | 19:30
AKS | 135 | 14:00 | 131 | 01:00 | Magura | 137 | 08:00 | 128 | 21:00
Aminbazar | 132 | 04:00 | 124 | 14:00 | Mahasthangarh | 134 | 00:00 | 131 | 05:00
Amnura | 135 | 01:00 | 131 | 18:00 | Maijdee | 129 | 08:00 | 126 | 12:00
Ashuganj | 134 | 01:00 | 126 | 18:30 | Manikganj | 130 | 00:00 | 123 | 17:00
Ashuganj-230 | 135 | 01:00 | 130 | 13:00 | Maniknagar | 139 | 06:00 | 130 | 14:00
Bagerhat | 131 | 08:00 | 121 | 22:00 | Matarbari | 133 | 18:30 | 117 | 22:00
Bajitpur | 128 | 01:00 | 120 | 18:30 | Matuail | 134 | 04:00 | 126 | 14:00
Bakerganj | 133 | 15:00 | 129 | 20:00 | Metrorail_Motijheel | 139 | 06:00 | 130 | 14:00
Bakulia | 138 | 18:30 | 135 | 00:00 | Metrorail_Uttara | 133 | 04:00 | 119 | 18:30
Banani | 136 | 04:00 | 124 | 14:00 | Millgate | 134 | 01:00 | 120 | 18:30
Bangabhaban | 140 | 04:00 | 129 | 18:30 | Mirpur | 131 | 04:00 | 123 | 14:00
Barapukuria | 138 | 00:00 | 131 | 18:30 | Mirzapur | 132 | 00:00 | 124 | 17:00
Barguna | 133 | 08:00 | 128 | 22:00 | Mithapukur | 133 | 00:00 | 127 | 20:00
Barishal | 133 | 08:00 | 129 | 20:00 | MI_Cement | 133.7 | 06:00 | 125 | 14:00
Barishal-230 | 133 | 08:00 | 128 | 20:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroaulia | 138 | 07:00 | 135 | 11:00 | Mogbazar | 137 | 01:00 | 127 | 14:00
Baroirhat | 134 | 07:00 | 130 | 14:00 | Mongla | 130 | 08:00 | 121 | 21:00
Bashundhara | 136 | 02:00 | 118 | 18:30 | Motijheel | 140 | 04:00 | 129 | 18:30
BashundharaCement | 133 | 04:00 | 126 | 14:00 | Muktagacha | 131 | 00:00 | 119 | 16:00
Beanibazar | 124 | 00:00 | 121 | 15:00 | Munshiganj | 131 | 00:00 | 124 | 18:00
Benapole | 136 | 08:00 | 124 | 21:00 | Muradnagar | 130 | 07:00 | 122 | 18:30
Bhaluka | 133 | 09:00 | 123 | 13:00 | Mymensingh | 132 | 00:00 | 115 | 17:00
Bhandaria | 131 | 17:00 | 123 | 21:00 | Nabinagar | 132 | 07:00 | 120 | 18:30
Bhangura | 135 | 09:00 | 129 | 20:00 | Naogaon | 136 | 09:00 | 128 | 07:00
Bheramara | 139 | 09:00 | 130 | 19:30 | Narail | 138 | 02:00 | 127 | 21:00
Bheramara(GK) | 138 | 01:00 | 130 | 20:00 | Narinda | 139 | 06:00 | 130 | 14:00
Bhulta | 127 | 07:00 | 121 | 14:00 | Narshingdi | 130 | 23:00 | 120 | 14:00
Bhulta-400 | 130 | 03:00 | 122 | 14:00 | Natore | 136 | 02:00 | 130 | 20:00
Birulia | 135 | 07:00 | 128 | 14:00 | Nawabganj | 137 | 06:00 | 129 | 14:00
Bog-Sherpur | 136 | 09:00 | 131 | 21:00 | Netrakona | 123 | 09:00 | 112 | 17:00
Bogura | 137 | 00:00 | 134 | 05:00 | New | 135 | 01:00 | 122 | 14:00
Bogura-230 | 138 | 00:00 | 134 | 07:00 | Niamatpur | 136 | 10:00 | 130 | 18:30
Brahmanbaria | 129 | 01:00 | 124 | 22:00 | Noapara | 134 | 02:00 | 128 | 21:00
Cantonment | 134 | 02:00 | 125 | 14:00 | Pabna | 136 | 09:00 | 128 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandina | 132 | 08:00 | 127 | 18:30 | Palashbari | 131 | 09:00 | 120 | 06:00
Chandpur | 135 | 01:00 | 133 | 00:00 | Panchagarh | 135 | 02:00 | 130 | 19:00
Chandraghona | 139 | 12:00 | 136 | 20:00 | Patiya | 139 | 07:00 | 133 | 20:00
Chapai | 134 | 02:00 | 130 | 18:30 | Patnitala | 132 | 10:00 | 128 | 18:30
Charsaidpur | 133 | 01:00 | 125 | 18:00 | Patuakhali | 132 | 03:00 | 129 | 20:00
Chauddagram | 132 | 07:00 | 128 | 12:00 | Payra | 135 | 00:00 | 133 | 20:00
Chhatak | 122 | 01:00 | 117 | 19:30 | PHP | 133 | 02:00 | 130 | 12:00
Chowmuhani | 130 | 08:00 | 126 | 12:00 | Postogola | 135 | 03:00 | 127 | 14:00
Chuadanga | 136 | 08:00 | 126 | 21:00 | Pubail | 131 | 23:00 | 124 | 13:00
Coxsbazar | 133 | 11:00 | 118 | 20:00 | Purbachal | 136 | 02:00 | 124 | 14:00
Cumilla(N) | 132 | 05:00 | 127 | 18:30 | Purbasadipur | 136 | 01:00 | 132 | 20:00
Cumilla(S) | 132 | 08:00 | 124 | 15:00 | Rahanpur | 137 | 09:00 | 134 | 05:00
Daganbhuiyan | 132 | 08:00 | 128 | 14:00 | Rahanpur-400 | 137 | 02:00 | 134 | 18:30
Daudkandi | 129 | 07:00 | 120 | 18:30 | Rahim | 134 | 04:00 | 126 | 17:00
DhakaUniversity | 136 | 02:00 | 124 | 14:00 | Rajbari | 127 | 02:00 | 121 | 22:00
Dhamrai | 134 | 23:00 | 121 | 18:30 | Rajendrapur | 136 | 09:00 | 129 | 12:00
Dhanmondi | 138 | 02:00 | 125 | 14:00 | Rajshahi | 133 | 01:00 | 128 | 19:30
Dohazari | 137 | 18:30 | 128 | 20:00 | Rajshahi-230 | 134 | 01:00 | 128 | 18:30
Faridpur | 129 | 03:00 | 125 | 21:00 | Ramganj | 131 | 07:00 | 128 | 10:00
Fatullah | 135 | 06:00 | 126 | 14:00 | Rampur | 138 | 07:00 | 134 | 20:00
Fenchuganj | 132 | 01:00 | 128 | 18:30 | Rampura | 136 | 03:00 | 124 | 14:00
Feni | 132 | 01:00 | 129 | 16:00 | Rangamati | 139 | 07:00 | 135 | 14:00
Feni-230 | 132 | 01:00 | 129 | 12:00 | Rangpur | 132 | 00:00 | 126 | 20:00
Ghatail | 129 | 00:00 | 119 | 08:00 | Ruppur | 138 | 01:00 | 130 | 21:00
Ghorashal | 130 | 23:00 | 124 | 17:00 | Saidpur | 135 | 00:00 | 131 | 06:00
Goalpara | 138 | 02:00 | 131 | 22:00 | Santhia | 135 | 08:00 | 130 | 02:00
Gollamari | 136 | 08:00 | 131 | 20:00 | Satkhira | 132 | 02:00 | 124 | 22:00
Gopalganj | 134 | 02:00 | 129 | 20:00 | Satmasjid | 135 | 06:00 | 125 | 14:00
Gopalganj-400 | 133 | 00:00 | 130 | 18:30 | Savar | 132 | 07:00 | 123 | 18:00
Gulshan | 136 | 06:00 | 124 | 14:00 | SevenRings | 132 | 01:00 | 124 | 18:00
Halishahar | 138 | 01:00 | 135 | 12:00 | ShahCement | 133 | 01:00 | 125 | 18:00
Haripur | 134 | 02:00 | 125 | 18:30 | Shahjadpur | 136 | 09:00 | 135 | 00:00
HaripurSBU | 134 | 02:00 | 126 | 14:00 | Shahjibazar | 132 | 15:00 | 121 | 22:00
Hasnabad | 138 | 08:00 | 128 | 14:00 | Shahmirpur | 138 | 18:30 | 135 | 13:00
Hathazari | 138 | 01:00 | 136 | 13:00 | Shariatpur | 131 | 01:00 | 127 | 18:30
Hatirjheel | 136 | 02:00 | 125 | 14:00 | Sherpur | 133 | 00:00 | 114 | 06:00
Ishurdi | 140 | 09:00 | 132 | 18:30 | Shikalbaha | 127 | 07:00 | 124 | 03:00
Jaldhaka | 133 | 00:00 | 128 | 19:30 | Shikalbaha-230 | 139 | 01:00 | 136 | 19:30
Jamalpur | 136 | 00:00 | 118 | 08:00 | Shitalakhya | 133.7 | 06:00 | 125 | 14:00
Jashore | 136 | 08:00 | 125 | 21:00 | Sholosohor | 138 | 00:00 | 136 | 16:00
Jhenaidah | 139 | 08:00 | 130 | 20:00 | Shomvuganj | 123 | 07:00 | 115 | 18:30
Jhenaidah-230 | 140 | 09:00 | 129 | 22:00 | Shyampur | 134 | 04:00 | 127 | 14:00
Joydebpur | 130 | 23:00 | 122 | 13:00 | Shyampur-230 | 136 | 02:00 | 129 | 14:00
Joypurhat | 133 | 08:00 | 128 | 21:00 | Siddhirganj | 134 | 03:00 | 126 | 14:00
Juldah | 138 | 18:30 | 136 | 14:00 | Sirajganj | 131 | 02:00 | 126 | 20:00
Kabirpur | 134 | 00:00 | 117 | 17:00 | Sitakunda | 137 | 00:00 | 134 | 07:00
Kachua | 132 | 07:00 | 129 | 12:00 | Sonargaon | 131 | 02:00 | 123 | 18:30
Kaliakoir | 136 | 01:00 | 126 | 18:30 | Sreemongol | 128 | 01:00 | 122 | 22:00
Kaliganj | 138 | 08:00 | 130 | 20:00 | Sreepur | 137 | 06:00 | 129 | 13:00
Kallyanpur | 131 | 08:00 | 124 | 17:00 | Srinagar | 137 | 03:00 | 129 | 14:00
Kalurghat | 139 | 01:00 | 137 | 00:00 | SSM | 142 | 01:00 | 140 | 00:00
Kamrangirchar | 138 | 07:00 | 121 | 14:00 | Sunamganj | 121 | 08:00 | 116 | 18:30
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 125 | 07:00 | 122 | 18:30
Kasba | 128 | 01:00 | 122 | 18:30 | Sylhet_(South) | 126 | 01:00 | 120 | 15:00
Kazla | 139 | 04:00 | 130 | 14:00 | Tangail | 130 | 00:00 | 120 | 20:00
Keranigonj | 137 | 02:00 | 130 | 14:00 | Taraganj | 134 | 00:00 | 128 | 20:00
Khagrachori | 137 | 01:00 | 134 | 20:00 | Tasnim | 131 | 01:00 | 123 | 18:30
Khulna | 135 | 02:00 | 129 | 20:00 | Thakurgaon | 137 | 01:00 | 132 | 19:00
Khulna(S) | 137 | 02:00 | 131 | 21:00 | TK | 138 | 10:00 | 135 | 07:00
Khulshi | 135 | 01:00 | 133 | 16:00 | Tongi | 137 | 04:00 | 124 | 17:00
Kishoreganj | 127 | 06:00 | 118 | 18:30 | Ullahpara | 133 | 01:00 | 128 | 21:00
Kodda | 131 | 00:00 | 122 | 13:00 | Ullon | 136 | 04:00 | 124 | 14:00
Korerhat | 135 | 07:00 | 132 | 13:00 | Uttara | 133 | 02:00 | 120 | 14:00
KSRM | 139 | 07:00 | 135 | 03:00 | UttaraNew | 133 | 04:00 | 119 | 18:30
Kulaura | 130 | 01:00 | 126 | 22:00 | Zigatola | 138 | 07:00 | 130 | 14:00
Kurigram | 130 | 17:00 | 120 | 20:00
Kushtia | 137 | 08:00 | 129 | 21:00
Laksam | 131 | 01:00 | 129 | 00:00
Lakshmipur | 129 | 02:00 | 126 | 11:00
Lalbag | 137 | 06:00 | 129 | 14:00
Lalmonirhat | 128 | 18:00 | 125 | 01:00
Madanganj | 133 | 04:00 | 126 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 30-08-2026 | [28 empty] | Date: | 30-08-2026 | [28 empty] | Date: | 30-08-2026 | [28 empty] | Date: | 30-08-2026 | [28 empty] | Date: | 30-08-2026 | [18 empty] | Date: | 30-08-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [18 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 50 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 237 | 54 | 17 | 53 | 92 | 147 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 55 | 270 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 300 | 0 | 16 | 38 | 0 | 42 | 50 | 22 | 17 | 12 | 12 | 0 | 222 | 107 | 2 | 558 | 70 | 0 | 50 | 25.5 | 88 | 216 | 0 | 0 | 0 | 1224 | 0 | 15 | 0 | 320 | 172 | 275 | 51 | 0 | 187 | 0 | 74 | 133 | 190 | 0 | 17 | 104 | 182 | 8 | 0 | 22 | 270 | 400 | 366 | 40 | 0 | 148 | 0 | 16 | 0 | 84 | 0 | 142 | 0 | 126 | 17 | 86 | 0 | 164 | 0 | 0 | 0 | 4 | 8455.92 | 923 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 920 | 0 | 0 | 0 | 1293.68 | 0 | 32 | 0 | 55 | 70 | 0 | 100 | 28 | 52.2 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 46 | 115 | 0 | 63 | 0 | 165 | 0 | 0 | 0 | 0 | 48 | 200 | 116 | 220 | 0 | 1000 | 570 | 17 | 6757.88 | 15213.8 | 105.99
01:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 259 | 35 | 0 | 53 | 92 | 147 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 287 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 320 | 0 | 16 | 28 | 0 | 52 | 50 | 22 | 0 | 12 | 12 | 0 | 222 | 107 | 7 | 558 | 70 | 0 | 50 | 8 | 88 | 216 | 0 | 0 | 0 | 1224 | 0 | 23.41 | 0 | 270 | 240 | 310 | 51 | 0 | 210 | 0 | 72 | 134 | 189 | 0 | 19 | 105 | 172 | 8 | 0 | 22 | 265 | 400 | 367 | 40 | 0 | 148 | 0 | 16 | 0 | 84 | 0 | 143 | 0 | 126 | 0 | 58 | 0 | 68 | 0 | 0 | 0 | 6 | 8218.83 | 932 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 920 | 0 | 0 | 0 | 915.8 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 28 | 52.2 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 47 | 115 | 0 | 34 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 565 | 17 | 6115 | 14333.83 | 106.05
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 249 | 35 | 0 | 53 | 0 | 147 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 278 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 310 | 0 | 16 | 25 | 0 | 35 | 0 | 15 | 0 | 12 | 12 | 0 | 218 | 106 | 13 | 558 | 70 | 0 | 50 | 8 | 95 | 216 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 230 | 280 | 300 | 51 | 0 | 212 | 0 | 69 | 134 | 190 | 0 | 19 | 105 | 176 | 8 | 0 | 22 | 265 | 397 | 367 | 40 | 0 | 146 | 0 | 16 | 0 | 84 | 0 | 141 | 0 | 126 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 6 | 8058.42 | 933 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 920 | 0 | 0 | 0 | 900.05 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 28 | 52.2 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 47 | 115 | 0 | 34 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 565 | 17 | 6094.25 | 14152.67 | 106.1
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 259 | 35 | 0 | 53 | 0 | 147 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 290 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 320 | 0 | 16 | 24 | 0 | 32 | 0 | 15 | 0 | 12 | 12 | 0 | 218 | 107 | 24 | 558 | 70 | 0 | 50 | 8 | 105 | 216 | 0 | 0 | 0 | 1224 | 0 | 55.2 | 0 | 230 | 280 | 305 | 51 | 0 | 204 | 0 | 68 | 133 | 190 | 0 | 19 | 104 | 168 | 8 | 0 | 22 | 262 | 400 | 367 | 40 | 0 | 148 | 0 | 16 | 0 | 84 | 0 | 141 | 0 | 125 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 6 | 8102.62 | 933 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 920 | 0 | 0 | 0 | 902.74 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 28 | 52.2 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 47 | 115 | 0 | 34 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 565 | 17 | 6096.94 | 14199.56 | 106.11
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 280 | 35 | 0 | 53 | 0 | 98 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 35 | 314 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 360 | 0 | 16 | 24 | 0 | 48 | 0 | 15 | 0 | 12 | 12 | 0 | 218 | 109 | 28 | 558 | 70 | 0 | 50 | 8 | 105 | 217 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 230 | 280 | 335 | 51 | 0 | 206 | 0 | 52 | 133 | 190 | 0 | 19 | 104 | 168 | 8 | 0 | 22 | 264 | 392 | 382 | 40 | 0 | 152 | 0 | 16 | 0 | 84 | 0 | 141 | 0 | 125 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 6 | 8189.42 | 933 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 920 | 0 | 0 | 0 | 904.16 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 28 | 52.2 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 155 | 47 | 115 | 0 | 34 | 0 | 100 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 565 | 17 | 6013.36 | 14202.78 | 106.12
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 333 | 17 | 0 | 53 | 50 | 98 | 15 | 17 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 0 | 143.42 | 5 | 22 | 0 | 410 | 0 | 16 | 25 | 0 | 28 | 0 | 15 | 0 | 12 | 12 | 0 | 172 | 110 | 35 | 558 | 70 | 0 | 50 | 8 | 95 | 217 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 230 | 280 | 280 | 51 | 0 | 215 | 0 | 51 | 134 | 189 | 0 | 19 | 104 | 164 | 8 | 0 | 22 | 265 | 396 | 382 | 40 | 0 | 152 | 0 | 16 | 0 | 84 | 0 | 142 | 0 | 125 | 0 | 57 | 0 | 67 | 0 | 0 | 0 | 6 | 8161.42 | 933 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 920 | 0 | 0 | 0 | 913.12 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 26 | 52.2 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 156 | 46 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 200 | 116 | 220 | 0 | 1000 | 565 | 17 | 5920.32 | 14081.74 | 106.13
06:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 301 | 17 | 0 | 53 | 106 | 98 | 15 | 17 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 1 | 143.42 | 5 | 22 | 0 | 410 | 0 | 16 | 24 | 0 | 17 | 0 | 15 | 0 | 12 | 12 | 0 | 218 | 109 | 29 | 558 | 35 | 0 | 50 | 8 | 105 | 216 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 230 | 280 | 275 | 51 | 0 | 217 | 0 | 51 | 134 | 190 | 0 | 19 | 105 | 150 | 8 | 1 | 22 | 264 | 398 | 382 | 40 | 0 | 151 | 0 | 16 | 0 | 84 | 0 | 142 | 0 | 125 | 0 | 57 | 0.3 | 67 | 0 | 0 | 0.56 | 6 | 8148.28 | 933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 1 | 920 | 0 | 0 | 0 | 902.41 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 15 | 52.2 | 1.3 | 0 | 17 | 0 | 1.28 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.1 | 157 | 46 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 3 | 0.01 | 32 | 200 | 116 | 220 | 0 | 1000 | 565 | 17 | 5879.3 | 14027.58 | 106.14
07:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 267 | 17 | 0 | 34 | 109 | 98 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 316 | 0 | 0 | 6 | 143.42 | 5 | 22 | 0 | 470 | 0 | 16 | 25 | 0 | 29 | 0 | 15 | 0 | 12 | 12 | 0.32 | 219 | 103 | 24 | 558 | 16 | 0 | 50 | 8 | 94 | 217 | 0 | 0 | 0 | 1140 | 1 | 53 | 0 | 270 | 280 | 295 | 51 | 0 | 214 | 0 | 36 | 133 | 189 | 0 | 19 | 104 | 152 | 8 | 10 | 22 | 260 | 396 | 370 | 40 | 0 | 151 | 3 | 16 | 0 | 84 | 0 | 142 | 0 | 125 | 0 | 58 | 3.7 | 67 | 0 | 0.2 | 6.21 | 6 | 8109.85 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 13 | 920 | 0 | 0 | 0 | 912.68 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 15 | 52.2 | 10.55 | 22 | 17 | 0 | 7.38 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.69 | 157 | 45 | 115 | 6 | 34 | 0 | 0 | 0 | 1.2 | 28 | 0.01 | 32 | 200 | 116 | 220 | 0 | 1000 | 565 | 17 | 5960.71 | 14070.56 | 106.18
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 254 | 17 | 0 | 34 | 77 | 98 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 270 | 0 | 0 | 9 | 143.42 | 5 | 22 | 0 | 455 | 0 | 16 | 25 | 0 | 26 | 0 | 15 | 0 | 12 | 12 | 0.86 | 220 | 92 | 8 | 558 | 16 | 0 | 50 | 8 | 105 | 217 | 0 | 0 | 0 | 612 | 0 | 57 | 0 | 270 | 280 | 240 | 51 | 0 | 193 | 0 | 34 | 133 | 189 | 0 | 19 | 104 | 154 | 8 | 6 | 22 | 260 | 396 | 382 | 40 | 0 | 137 | 4 | 8 | 0 | 84 | 0 | 142 | 0 | 125 | 0 | 58 | 3.9 | 67 | 0 | 0.9 | 18.73 | 6 | 7356.81 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 41 | 920 | 0 | 0 | 0 | 909.92 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 15 | 52.2 | 12 | 42 | 17 | 0 | 28.11 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.74 | 157 | 45 | 115 | 13 | 34 | 0 | 0 | 0 | 3.5 | 90 | 0.2 | 32 | 200 | 117 | 220 | 0 | 1000 | 580 | 17 | 6121.67 | 13478.48 | 106.19
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 263 | 17 | 0 | 34 | 77 | 98 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 274 | 0 | 0 | 11 | 143.42 | 5 | 22 | 0 | 355 | 0 | 16 | 23 | 0 | 31 | 0 | 15 | 17 | 12 | 12 | 1.64 | 220 | 94 | 3 | 558 | 16 | 0 | 50 | 8 | 105 | 214 | 0 | 0 | 0 | 570 | 0 | 53 | 0 | 270 | 300 | 260 | 51 | 0 | 198 | 0 | 34 | 133 | 190 | 0 | 19 | 70 | 136 | 8 | 43 | 15 | 265 | 392 | 382 | 40 | 0 | 146 | 9 | 8 | 0 | 83 | 0 | 142 | 0 | 126 | 0 | 58 | 8.88 | 67 | 0 | 0.8 | 35.74 | 6 | 7320.48 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 57 | 920 | 0 | 0 | 0 | 906.63 | 0 | 32 | 0 | 0 | 4 | 0 | 0 | 15 | 52.2 | 16.86 | 79 | 17 | 0 | 25.99 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.06 | 154 | 45 | 115 | 24 | 34 | 0 | 0 | 0 | 5.3 | 124 | 0.54 | 32 | 200 | 117 | 220 | 0 | 1000 | 580 | 17 | 6206.58 | 13527.06 | 106.2
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 244 | 17 | 0 | 34 | 60 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 270 | 0 | 0 | 13 | 143.42 | 5 | 22 | 0 | 325 | 0 | 16 | 16 | 0 | 44 | 0 | 15 | 17 | 12 | 12 | 0.84 | 220 | 107 | 0 | 558 | 23 | 0 | 50 | 8 | 92 | 217 | 0 | 0 | 0 | 555 | 0 | 53 | 0 | 270 | 300 | 225 | 51 | 0 | 183 | 0 | 34 | 133 | 176 | 0 | 19 | 52 | 124 | 8 | 33 | 15 | 262 | 389 | 292 | 40 | 0 | 143 | 10 | 8 | 0 | 83 | 0 | 142 | 0 | 126 | 0 | 58 | 21.03 | 116 | 0 | 0.9 | 42.27 | 6 | 7111.46 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 79.47 | 1005 | 0 | 0 | 0 | 906.61 | 0 | 24 | 0 | 0 | 35 | 0 | 0 | 15 | 52.2 | 56.97 | 100 | 17 | 0 | 58.22 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.47 | 157 | 46 | 107 | 16 | 0 | 0 | 0 | 0 | 6.8 | 158 | 0.27 | 32 | 200 | 113 | 220 | 0 | 972 | 580 | 17 | 6369.01 | 13480.47 | 106.22
11:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 232 | 17 | 0 | 43 | 45 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 284 | 0 | 0 | 34 | 143.42 | 5 | 22 | 0 | 360 | 0 | 16 | 16 | 0 | 32 | 0 | 15 | 17 | 12 | 12 | 3.05 | 219 | 108 | 0 | 558 | 35 | 0 | 44 | 10 | 98 | 214 | 0 | 0 | 0 | 590 | 0 | 53 | 0 | 270 | 300 | 275 | 51 | 0 | 204 | 0 | 35 | 132 | 182 | 0 | 19 | 21 | 140 | 8 | 30 | 16 | 275 | 386 | 249 | 40 | 0 | 146 | 7 | 8 | 0 | 82 | 0 | 141 | 0 | 126 | 0 | 58 | 20 | 115 | 0 | 0 | 34.06 | 6 | 7229.53 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 46 | 1110 | 0 | 0 | 0 | 908.87 | 0 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 43 | 58.43 | 100 | 0 | 0 | 33.81 | 10 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.87 | 158 | 46 | 102 | 9 | 0 | 0 | 0 | 0 | 4.1 | 186 | 0.49 | 32 | 200 | 115 | 220 | 0 | 981 | 580 | 17 | 6417.57 | 13647.1 | 106.22
12:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 232 | 17 | 5 | 52 | 45 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 285 | 0 | 0 | 35 | 0 | 5 | 22 | 0 | 360 | 0 | 16 | 18 | 0 | 13 | 0 | 15 | 17 | 20 | 25 | 1.68 | 219 | 104 | 0 | 558 | 35 | 0 | 45 | 8 | 105 | 219 | 0 | 0 | 0 | 580 | 0 | 53 | 0 | 360 | 300 | 290 | 51 | 0 | 206 | 0 | 44 | 132 | 179 | 0 | 19 | 17 | 148 | 8 | 39 | 22 | 295 | 386 | 249 | 40 | 0 | 147 | 10 | 8 | 0 | 82 | 0 | 142 | 0 | 126 | 0 | 58 | 20.53 | 114 | 0 | 0.8 | 41.55 | 0 | 7268.56 | 933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 6.02 | 1115 | 1 | 0 | 0 | 914.03 | 0 | 31 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 64.84 | 110 | 0 | 0 | 63.72 | 12 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.34 | 165 | 45 | 109 | 38 | 0 | 0 | 0 | 0 | 1.1 | 156 | 0.1 | 32 | 200 | 115 | 220 | 0 | 982 | 580 | 17 | 6467.35 | 13735.91 | 106.22
13:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 267 | 17 | 17 | 51 | 45 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 30 | 0 | 5 | 22 | 0 | 390 | 0 | 16 | 24 | 0 | 25 | 0 | 15 | 17 | 24 | 25 | 1.6 | 218 | 102 | 0 | 558 | 35 | 0 | 45 | 8 | 95 | 219 | 0 | 0 | 0 | 580 | 0 | 53 | 0 | 325 | 300 | 265 | 51 | 0 | 208 | 0 | 34 | 91 | 174 | 0 | 19 | 17 | 128 | 8 | 7 | 22 | 290 | 382 | 218 | 36 | 0 | 146 | 10 | 8 | 0 | 81 | 0 | 141 | 0 | 128 | 0 | 58 | 20.35 | 114 | 0 | 2.4 | 56.65 | 0 | 7144 | 933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 92.73 | 1124 | 6 | 0 | 0 | 920.55 | 0 | 31 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 34.57 | 110 | 0 | 0 | 57.78 | 17 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.28 | 161 | 46 | 107 | 9 | 0 | 0 | 0 | 0 | 2.6 | 207 | 0.37 | 32 | 200 | 115 | 220 | 0 | 980 | 580 | 17 | 6559.08 | 13703.08 | 106.22
14:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 325 | 17 | 0 | 52 | 45 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 22 | 72 | 5 | 22 | 0 | 470 | 0 | 16 | 21 | 0 | 28 | 0 | 15 | 17 | 24 | 25 | 2.1 | 218 | 106 | 0 | 558 | 35 | 0 | 45 | 8 | 103 | 219 | 0 | 0 | 0 | 590 | 0 | 53 | 0 | 260 | 300 | 275 | 51 | 0 | 210 | 0 | 34 | 91 | 181 | 0 | 19 | 17 | 164 | 8 | 9 | 22 | 295 | 382 | 217 | 40 | 0 | 144 | 7 | 8 | 0 | 81 | 0 | 141 | 0 | 127 | 0 | 58 | 8.3 | 114 | 0 | 0 | 48.9 | 2 | 7363.3 | 934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 22.02 | 1127 | 13 | 0 | 0 | 914.92 | 0 | 31 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 47.27 | 91 | 0 | 0 | 41.61 | 32 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 5.9 | 160 | 46 | 108 | 6 | 0 | 0 | 0 | 0 | 0.9 | 212 | 0.63 | 32 | 200 | 115 | 220 | 0 | 983 | 570 | 17 | 6481.45 | 13844.75 | 106.22
15:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 274 | 17 | 0 | 52 | 60 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 275 | 0 | 0 | 13 | 140 | 5 | 22 | 0 | 340 | 0 | 16 | 18 | 0 | 38 | 0 | 15 | 17 | 24 | 25 | 0.84 | 219 | 107 | 0 | 558 | 35 | 0 | 43 | 8 | 100 | 218 | 0 | 0 | 0 | 580 | 0 | 53 | 0 | 230 | 300 | 255 | 51 | 0 | 217 | 0 | 34 | 93 | 179 | 0 | 19 | 17 | 180 | 8 | 9 | 22 | 295 | 382 | 241 | 40 | 0 | 146 | 8 | 8 | 0 | 83 | 0 | 142 | 0 | 127 | 0 | 58 | 5.9 | 114 | 0 | 1.9 | 23.5 | 6 | 7203.14 | 933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 49.84 | 1131 | 14 | 0 | 0 | 922.7 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 0 | 52.2 | 22.35 | 32 | 0 | 0 | 12.61 | 69 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.15 | 161 | 48 | 107 | 7 | 0 | 0 | 0 | 0 | 1 | 77 | 0.07 | 32 | 200 | 115 | 220 | 0 | 987 | 565 | 17 | 6310.92 | 13514.06 | 106.21
16:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 286 | 17 | 0 | 52 | 60 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 285 | 0 | 0 | 6 | 51 | 5 | 22 | 0 | 345 | 0 | 16 | 15 | 0 | 33 | 0 | 15 | 17 | 24 | 25 | 0.54 | 219 | 108 | 0 | 555 | 35 | 0 | 43 | 8 | 95 | 217 | 0 | 0 | 0 | 750 | 0 | 53 | 0 | 245 | 300 | 270 | 51 | 0 | 201 | 0 | 34 | 93 | 181 | 0 | 19 | 17 | 170 | 8 | 11 | 22 | 304 | 400 | 260 | 40 | 0 | 146 | 1 | 8 | 0 | 83 | 0 | 142 | 0 | 127 | 0 | 58 | 4.9 | 114 | 0 | 1.3 | 13.61 | 6 | 7330.35 | 933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 17.42 | 1135 | 16 | 0 | 0 | 917.42 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 0 | 43 | 30.29 | 55 | 0 | 0 | 8.61 | 123 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0.71 | 166 | 47 | 106 | 6 | 0 | 0 | 0 | 0 | 1.9 | 61 | 0.07 | 32 | 200 | 115 | 220 | 0 | 988 | 565 | 17 | 6314.42 | 13644.77 | 106.21
17:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 263 | 17 | 0 | 52 | 60 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 275 | 0 | 0 | 6 | 51 | 5 | 22 | 0 | 320 | 0 | 16 | 22 | 0 | 34 | 0 | 15 | 17 | 24 | 25 | 0.45 | 219 | 97 | 0 | 555 | 35 | 0 | 44 | 8 | 90 | 217 | 0 | 0 | 0 | 870 | 2 | 53 | 0 | 270 | 300 | 235 | 51 | 0 | 182 | 0 | 34 | 94 | 169 | 6 | 19 | 94 | 158 | 8 | 8 | 22 | 283 | 400 | 315 | 40 | 0 | 135 | 2 | 8 | 0 | 83 | 0 | 141 | 0 | 126 | 10 | 58 | 2.27 | 114 | 0 | 0.6 | 13.56 | 6 | 7411.88 | 933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 8.24 | 1128 | 22 | 0 | 0 | 923.76 | 0 | 31 | 0 | 35 | 35 | 0 | 0 | 0 | 52.2 | 5.49 | 15 | 0 | 0 | 12.78 | 143 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 1.16 | 161 | 47 | 108 | 4 | 67 | 0 | 0 | 0 | 0.8 | 27 | 0.13 | 32 | 200 | 116 | 180 | 0 | 958 | 570 | 17 | 6307.56 | 13719.44 | 106.2
18:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 269 | 17 | 0 | 52 | 60 | 97 | 15 | 17 | 54 | 0 | 0 | 0 | 0 | 0 | 35 | 277 | 0 | 0 | 1 | 51 | 5 | 22 | 0 | 320 | 0 | 16 | 24 | 0 | 38 | 17 | 15 | 17 | 50 | 50 | 0 | 219 | 108 | 0 | 555 | 35 | 0 | 44 | 8 | 99 | 217 | 0 | 0 | 0 | 970 | 0 | 65 | 0 | 260 | 300 | 255 | 51 | 0 | 187 | 0 | 35 | 93 | 177 | 27 | 19 | 102 | 162 | 0 | 0 | 22 | 270 | 400 | 377 | 40 | 0 | 143 | 0 | 8 | 0 | 83 | 0 | 141 | 0 | 126 | 17 | 58 | 0.28 | 114 | 0 | 0 | 0.61 | 6 | 7812.89 | 933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 2.37 | 1085 | 28 | 0 | 0 | 1027.07 | 0 | 31 | 0 | 55 | 43 | 0 | 0 | 0 | 52.2 | 1.04 | 0 | 21 | 0 | 1.18 | 139 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0.09 | 159 | 47 | 109 | 1 | 70 | 0 | 0 | 0 | 0.3 | 4 | 0.02 | 48 | 200 | 116 | 220 | 0 | 974 | 570 | 17 | 6405.27 | 14218.16 | 106.2
19:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 258 | 54 | 0 | 85 | 125 | 200 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 0 | 35 | 282 | 0 | 0 | 0 | 51 | 5 | 22 | 0 | 345 | 0 | 16 | 24 | 0 | 32 | 50 | 15 | 17 | 50 | 50 | 0 | 221 | 107 | 0 | 555 | 50 | 0 | 44 | 25.5 | 100 | 217 | 0 | 0 | 0 | 1172 | 0 | 138 | 0 | 230 | 300 | 270 | 51 | 0 | 217 | 0 | 85 | 93 | 179 | 27 | 19 | 101 | 170 | 0 | 0 | 22 | 260 | 400 | 394 | 40 | 0 | 143 | 0 | 8 | 0 | 83 | 0 | 141 | 0 | 126 | 17 | 88 | 0 | 162 | 0 | 0 | 0 | 6 | 8710.5 | 933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1070 | 33 | 0 | 0 | 1122.78 | 0 | 32 | 0 | 55 | 70 | 0 | 50 | 14 | 52.2 | 0 | 0 | 21 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 160 | 46 | 108 | 0 | 70 | 0 | 100 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1100 | 570 | 17 | 6797.98 | 15508.48 | 106.2
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 248 | 54 | 0 | 116 | 140 | 294 | 15 | 55 | 150 | 0 | 0 | 0 | 0 | 0 | 55 | 285 | 0 | 0 | 0 | 51 | 5.5 | 22 | 0 | 330 | 0 | 16 | 36 | 0 | 38 | 50 | 15 | 36 | 50 | 50 | 0 | 221 | 107 | 0 | 555 | 52 | 0 | 44 | 25.5 | 97 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 260 | 300 | 260 | 51 | 0 | 216 | 0 | 89 | 93 | 179 | 27 | 19 | 105 | 172 | 0 | 0 | 22 | 255 | 400 | 394 | 40 | 0 | 128 | 0 | 8 | 0 | 83 | 0 | 142 | 0 | 126 | 17 | 87 | 0 | 162 | 0 | 0 | 0 | 6 | 8913 | 933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1070 | 33 | 0 | 0 | 1123.01 | 0 | 32 | 0 | 55 | 70 | 0 | 50 | 14 | 52.2 | 0 | 0 | 21 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 159 | 46 | 108 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 180 | 0 | 1100 | 570 | 17 | 6673.21 | 15586.21
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 252 | 54 | 0 | 116 | 140 | 294 | 15 | 55 | 154 | 0 | 0 | 0 | 0 | 0 | 55 | 284 | 0 | 0 | 0 | 51 | 5.5 | 22 | 0 | 335 | 0 | 16 | 39 | 0 | 42 | 50 | 15 | 36 | 50 | 50 | 0 | 221 | 103 | 2 | 555 | 53 | 0 | 44 | 25.5 | 94 | 218 | 0 | 0 | 0 | 1224 | 0 | 147 | 0 | 250 | 300 | 260 | 51 | 0 | 216 | 0 | 89 | 94 | 172 | 28 | 19 | 103 | 178 | 0 | 0 | 15 | 257 | 400 | 394 | 40 | 0 | 134 | 0 | 8 | 0 | 83 | 0 | 142 | 0 | 126 | 17 | 87 | 0 | 162 | 0 | 0 | 0 | 6 | 8927 | 933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1070 | 33 | 0 | 0 | 1125.5 | 0 | 32 | 0 | 55 | 70 | 0 | 50 | 14 | 52.2 | 0 | 0 | 21 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 157 | 45 | 110 | 0 | 70 | 0 | 75 | 0 | 0 | 0 | 0 | 64 | 200 | 116 | 220 | 0 | 1100 | 570 | 17 | 6769.7 | 15696.7 | 106.2
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 248 | 54 | 0 | 116 | 139 | 294 | 15 | 55 | 152 | 0 | 0 | 0 | 0 | 0 | 55 | 281 | 0 | 0 | 0 | 51 | 5.5 | 22 | 0 | 330 | 0 | 16 | 43 | 0 | 41 | 50 | 15 | 54.36 | 50 | 50 | 0 | 221 | 106 | 2 | 555 | 55 | 0 | 44 | 25.5 | 97 | 219 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 230 | 300 | 260 | 51 | 0 | 217 | 0 | 89 | 96 | 177 | 28 | 19 | 100 | 168 | 0 | 0 | 15 | 259 | 400 | 394 | 40 | 0 | 147 | 0 | 15 | 0 | 83 | 0 | 142 | 0 | 126 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 6 | 8972.36 | 933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1070 | 33 | 0 | 0 | 1111.26 | 0 | 32 | 0 | 55 | 70 | 0 | 50 | 30 | 52.2 | 0 | 0 | 21 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 158 | 46 | 109 | 0 | 70 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 200 | 117 | 220 | 0 | 1100 | 565 | 17 | 6856.46 | 15828.82 | 106.2
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 268 | 54 | 0 | 88 | 140 | 114 | 15 | 55 | 148 | 0 | 0 | 0 | 0 | 0 | 55 | 295 | 0 | 0 | 0 | 51 | 5.5 | 22 | 0 | 365 | 0 | 16 | 41 | 0 | 26 | 50 | 15 | 54.36 | 50 | 50 | 0 | 221 | 99 | 2 | 555 | 53 | 0 | 48 | 25.5 | 103 | 218 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 220 | 300 | 285 | 51 | 0 | 210 | 0 | 88 | 96 | 186 | 28 | 19 | 102 | 174 | 0 | 0 | 15 | 257 | 400 | 394 | 40 | 0 | 147 | 0 | 16 | 0 | 22 | 0 | 141 | 0 | 126 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 6 | 8774.36 | 932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1070 | 34 | 0 | 0 | 1096.61 | 0 | 32 | 0 | 55 | 70 | 0 | 50 | 28 | 52.2 | 0 | 0 | 21 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 169 | 46 | 110 | 0 | 70 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 200 | 117 | 220 | 0 | 1100 | 565 | 17 | 6852.81 | 15627.17 | 106.2
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 244 | 54 | 0 | 82 | 90 | 114 | 15 | 55 | 152 | 0 | 0 | 0 | 0 | 0 | 55 | 275 | 0 | 0 | 0 | 51 | 5.5 | 22 | 0 | 320 | 0 | 16 | 24 | 0 | 29 | 50 | 15 | 17 | 50 | 50 | 0 | 221 | 92 | 4 | 555 | 53 | 0 | 50 | 25.5 | 99 | 220 | 0 | 0 | 0 | 1224 | 0 | 55 | 0 | 220 | 280 | 250 | 51 | 0 | 191 | 0 | 88 | 95 | 178 | 28 | 19 | 103 | 176 | 0 | 0 | 15 | 255 | 400 | 388 | 40 | 0 | 142 | 0 | 16 | 0 | 22 | 0 | 140 | 0 | 125 | 0 | 87 | 0 | 163 | 0 | 0 | 0 | 6 | 8368 | 932 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 1070 | 34 | 0 | 0 | 1092.56 | 0 | 32 | 0 | 55 | 70 | 0 | 50 | 13 | 52.2 | 0 | 0 | 21 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 160 | 48 | 112 | 0 | 70 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 200 | 117 | 220 | 0 | 1100 | 565 | 17 | 6844.76 | 15212.76 | 106.2
Total KWH | 0 | 1376640 | 671040 | 0 | 0 | 0 | 0 | 0 | 8668800 | 0 | 6689950 | 694080 | 55440 | 1465056 | 1721760 | 2995353 | 378660 | 705341 | 1972800 | 0 | 0 | 0 | 0 | 0 | 710330 | 6962521 | 0 | 0 | 188058 | 2322000 | 120000 | 522720 | 0 | 8893636.36 | 0 | 371345 | 598080 | 0 | 767040 | 353552 | 363984 | 388052 | 567360 | 582720 | 24281 | 5264822 | 2532509 | 187200 | 13440000 | 1062182 | 0 | 1142400 | 305582.4 | 2396181 | 5006414 | 0 | 0 | 0 | 22745452 | 2430 | 1649309 | 0 | 6321000 | 7299000 | 6818000 | 1236628 | 0 | 5072000 | 0 | 1323840 | 2694594 | 4386720 | 179760 | 454430 | 1816020 | 3852480 | 151589 | 235855 | 480336 | 6490000 | 9328800 | 8312000 | 947000 | 0 | 3498300 | 74418 | 276096 | 0 | 1841280 | 0 | 3383600 | 0 | 2731400 | 123120 | 1549200 | 116665 | 2577600 | 0 | 11600 | 327250 | 134640 | 190910301.76 | 22528000 | 0 | 0 | 168480 | 0 | 0 | 0 | 0 | 0 | 0 | 1868688 | 447840 | 24792730 | 283580 | 0 | 0 | 23198182 | 0 | 740074 | 0 | 406464 | 820032 | 0 | 347200 | 280732 | 1201368 | 358368 | 742750 | 295019 | 0 | 377088 | 1382091 | 0 | 0 | 0 | 0 | 0 | 9240145 | 0 | 34860 | 4017000 | 1093964 | 2704224 | 156048 | 825321 | 0 | 1360958 | 0 | 35778.12 | 1311120 | 3180 | 971232 | 4800000 | 2790000 | 5237870 | 0 | 24392727 | 13968000 | 441600 | 153622713.12 | 344533014.88