## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-09-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-09-2026 | during | 02-09-2026 | during | 02-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 407 | 413 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 12 | 55 | 55 | 0 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 290 | 290 | 335 | 335 | 300 | 300 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 35 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 120 | 149.36 | 149.36 | 45 | 142 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 5 | 4.6 | 33 | 33 | 5 | 5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 51 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 31 | 81 | 300 | 300 | 175 | 145 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 29 | 36 | 149 | 149 | 52 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 34 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 7 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 340 | 340 | 584 | 584 | 350 | 350 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 224 | 223 | 718 | 718 | 260 | 260 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 34 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Engine problem
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1655 | 2184.02 | 5206.16 | 5180.16 | 2016.42 | 2460.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 7 | 0 | 7 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 43 | 42 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 217 | 218 | 216 | 216 | 216 | 216 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 215 | 218 | 210 | 210 | 210 | 210 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 34 | 105 | 105 | 95 | 95 | FGMO
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 15 | 40 | 14 | 32 | 14 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 75 | 100 | 100 | 12 | 12 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 25 | 32 | 25 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 22 | 54 | 95.1 | 95.1 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.34 | 0 | 5.02 | 0 | 5.02 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 36 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 93 | 100 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 75 | 100 | 100 | 12 | 12 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 94 | 92 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 73 | 71 | 163 | 163 | 35 | 55 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1160 | 1120 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 50 | 30 | 5 | 6 | 5 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1130 | 1130 | 1150 | 1150 | 700 | 1130 | -
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3258.34 | 3426.5 | 4074.98 | 4139.96 | 2877.02 | 3461.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 204 | 190 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 280 | 280 | 350.01 | 350.01 | 280 | 280 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 320 | 275 | 342.01 | 342.01 | 270 | 270 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 230 | 300 | 393 | 393 | 300 | 300 | Gas shortage
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 53 | 110 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 22 | 29 | 32 | 32 | 32 | 32 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 85 | 163 | 163 | 91 | 91 | machine problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 190 | 190 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 132 | 170 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 47 | 52.2 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 103 | 105 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 73 | 113 | 113 | 9 | 18 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 33 | 89 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1830 | 2010.2 | 2764.44 | 2688.44 | 1866.25 | 1959.25
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-09-2026 | during | 02-09-2026 | during | 02-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 10 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.3 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 125 | 162 | 120 | 170 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 88 | 70 | 90 | 70 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 15.54 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 9 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 239.84 | 279 | 547.6 | 546.5 | 273.1 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 40 | 40 | 40 | 40 | machine problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 30 | 40 | 40 | 30 | 30 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 141 | 141 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 20 | 30 | 30 | 0 | 0 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 86 | 84 | 84 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 125 | 125 | 125 | 125 | 125 | 125 | ST under maint
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 16 | 16 | 16 | 16 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 270 | 341 | 341 | 270 | 270 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 372 | 331 | 370 | 390 | 390 | 390 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 400 | 400 | 383 | 383 | 383 | 383 | -
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1448 | 1452 | 1569 | 1589 | 1478 | 1478
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 929 | 871 | 1000 | 1000 | 950 | 950 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 30 | 105 | 105 | 0 | 34 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 67 | 105 | 105 | 67 | 67 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 25 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 150 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1050 | 1050 | 370 | 370 | 800 | 370 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 2004 | 2168 | 2690 | 2615 | 2477 | 2006
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1000 | 800 | 800 | 800 | 800 | 800 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 32 | 64 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 116 | 116 | 120 | 120 | 117 | 117 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 570 | 565 | 580 | 580 | 580 | 580 | machine problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 276 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.1 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2230.1 | 2026 | 2288 | 2287 | 2074 | 2105
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 8.64 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 40 | 39 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 14 | 25 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 128 | 128 | 214 | 214 | 130 | 130 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 291 | 250 | 413.79 | 413.79 | 300 | 300 | Gas shortage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 0 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 40 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 1.84 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 832.65 | 1314.79 | 1469.13 | 1469.13 | 800 | 800 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 40.12 | 0 | 63 | 0 | 63 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 62 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1505.45 | 2043.99 | 3270.04 | 3050.12 | 1675.12 | 1605.2
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 100 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 45 | 49 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 156 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 92 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.4 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 108 | 110 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 96 | 0 | 177.29 | 0 | 177.29 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 447.4 | 507 | 685.29 | 472 | 572.29 | 394
System Total |  |  |  |  | 28843.2 | 29158.791 | 14618.13 | 16096.71 | 23095.51 | 22568.18 | 15309.2 | 15758.37
Forecast Scenario (02-09-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15510 |  | 1757.2 |  | 17350
|  |  |  | 1:00 | 14490 |  | 2177.4 |  | 16770
|  |  |  | 2:00 | 14110 |  | 2196.5 |  | 16410
|  |  |  | 3:00 | 14060 |  | 1938.65 |  | 16090
|  |  |  | 4:00 | 14050 |  | 1642.6 |  | 15770
|  |  |  | 5:00 | 13940 |  | 1594.85 |  | 15610
|  |  |  | 6:00 | 13760 |  | 1298.8 |  | 15120
|  |  |  | 7:00 | 13630 |  | 1308.35 |  | 15000
|  |  |  | 8:00 | 13610 |  | 1136.45 |  | 14800
|  |  |  | 9:00 | 13570 |  | 1184.2 |  | 14810
|  |  |  | 10:00 | 13950 |  | 935.9 |  | 14930
|  |  |  | 11:00 | 14160 |  | 687.6 |  | 14880
|  |  |  | 12:00 | 14620 |  | 945.45 |  | 15610
|  |  |  | 13:00 | 14370 |  | 1480.25 |  | 15920
|  |  |  | 14:00 | 14250 |  | 1518.45 |  | 15840
|  |  |  | 15:00 | 14200 |  | 2053.25 |  | 16350
|  |  |  | 16:00 | 14080 |  | 1871.8 |  | 16040
|  |  |  | 17:00 | 14110 |  | 1652.15 |  | 15840
|  |  |  | 18:00 | 13830 |  | 1337 |  | 15230
|  |  |  | 18:30 | 14630 |  | 1465.925 |  | 16165
|  |  |  | 19:00 | 15430 |  | 1594.85 |  | 17100
|  |  |  | 19:30 | 15630 |  | 1680.8 |  | 17390
|  |  |  | 20:00 | 15440 |  | 1957.75 |  | 17490
|  |  |  | 21:00 | 15730 |  | 1938.65 |  | 17760
|  |  |  | 22:00 | 15780 |  | 1594.85 |  | 17450
|  |  |  | 23:00 | 15890 |  | 1594.85 |  | 17560
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 15610.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 17760.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15730.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 346.57 MKWHr. |  | 350 | 180 | 150 | 280 | 119 | 280 | 80 | 260 | 240 | 1939
*** This report is generated digitally from Operation Information System (OIS) at 10:11 hrs on 02-09-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-09-2026 | [28 empty] | Date: | 01-09-2026 | [28 empty] | Date: | 01-09-2026 | [28 empty] | Date: | 01-09-2026 | [28 empty] | Date: | 01-09-2026 | [17 empty] | Date: | 01-09-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 50 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 244 | 54 | 17 | 18 | 79 | 48 | 0 | 55 | 162 | 0 | 0 | 0 | 0 | 55 | 282 | 0 | 0 | 0 | 34 | 5 | 22 | 0 | 320 | 89 | 16 | 24 | 0 | 27 | 50 | 30 | 17 | 12 | 12 | 0 | 217 | 94 | 2 | 1080 | 53 | 0 | 45 | 25.5 | 88 | 219 | 0 | 0 | 0 | 1205 | 0 | 53 | 0 | 210 | 300 | 255 | 51 | 0 | 195 | 0 | 88 | 91 | 177 | 0 | 19 | 101 | 164 | 43 | 0 | 30 | 264 | 400 | 386 | 40 | 0 | 15 | 0 | 16 | 0 | 84 | 0 | 141 | 0 | 125 | 17 | 87 | 0 | 164 | 0 | 0 | 0 | 12 | 8711.5 | 882 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 239 | 0 | 15 | 0 | 1050 | 34 | 0 | 0 | 1009.49 | 0 | 46 | 0 | 55 | 70 | 0 | 101 | 28 | 52.2 | 0 | 0 | 22 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 154 | 48 | 108 | 0 | 49 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 116 | 220 | 0 | 1000 | 565 | 17 | 6797.69 | 15509.19 | 106.11
01:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 247 | 35 | 17 | 17 | 63 | 48 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 285 | 0 | 0 | 0 | 17 | 5 | 10 | 0 | 335 | 96 | 16 | 24 | 0 | 15 | 50 | 15 | 0 | 12 | 12 | 0 | 217 | 93 | 2 | 1080 | 53 | 0 | 50 | 8 | 58 | 219 | 0 | 0 | 0 | 1160 | 0 | 55 | 0 | 210 | 300 | 260 | 51 | 0 | 198 | 0 | 62 | 91 | 115 | 0 | 19 | 104 | 158 | 43 | 0 | 30 | 268 | 400 | 386 | 40 | 0 | 0 | 0 | 16 | 0 | 84 | 0 | 141 | 0 | 125 | 17 | 58 | 0 | 66 | 0 | 0 | 0 | 12 | 8116 | 929 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 238 | 0 | 15 | 0 | 1050 | 19 | 0 | 0 | 815.39 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 28 | 52.2 | 0 | 0 | 17 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 154 | 50 | 110 | 0 | 34 | 0 | 165 | 0 | 0 | 0 | 0 | 16 | 307 | 116 | 220 | 0 | 1000 | 560 | 17 | 6378.59 | 14494.59 | 106.1
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 248 | 35 | 17 | 17 | 63 | 32 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 290 | 0 | 0 | 0 | 17 | 5 | 22 | 0 | 330 | 92 | 16 | 24 | 0 | 23 | 50 | 15 | 0 | 12 | 12 | 0 | 217 | 106 | 2 | 1125 | 53 | 0 | 50 | 8 | 34 | 219 | 0 | 0 | 0 | 1160 | 0 | 53 | 0 | 210 | 300 | 265 | 51 | 0 | 199 | 0 | 51 | 91 | 105 | 0 | 19 | 103 | 150 | 43 | 0 | 31 | 268 | 400 | 386 | 40 | 0 | 0 | 0 | 16 | 0 | 84 | 0 | 141 | 0 | 125 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8135 | 929 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 17 | 0 | 0 | 825.29 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 21 | 52.2 | 0 | 0 | 17 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 150 | 50 | 107 | 0 | 34 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 307 | 116 | 220 | 0 | 1000 | 565 | 17 | 5972.49 | 14107.49 | 106.09
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 241 | 35 | 17 | 17 | 63 | 32 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 280 | 0 | 0 | 0 | 17 | 5 | 22 | 0 | 320 | 96 | 16 | 24 | 0 | 42 | 0 | 15 | 0 | 12 | 12 | 0 | 216 | 100 | 7 | 1125 | 53 | 0 | 50 | 8 | 34 | 219 | 0 | 0 | 0 | 1160 | 0 | 55 | 0 | 210 | 300 | 250 | 51 | 0 | 193 | 0 | 51 | 91 | 110 | 0 | 19 | 104 | 150 | 52.2 | 0 | 31 | 265 | 400 | 387 | 40 | 0 | 0 | 0 | 16 | 0 | 84 | 0 | 142 | 0 | 125 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8105.2 | 928 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 17 | 0 | 0 | 828.19 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 21 | 52.2 | 0 | 0 | 17 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 149 | 50 | 108 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 116 | 220 | 0 | 1000 | 565 | 17 | 5954.39 | 14059.59 | 106.08
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 240 | 35 | 17 | 17 | 63 | 32 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 275 | 0 | 0 | 0 | 17 | 5 | 22 | 0 | 320 | 85 | 16 | 24 | 0 | 60 | 0 | 15 | 0 | 12 | 12 | 0 | 215 | 92 | 15 | 1125 | 55 | 0 | 50 | 8 | 34 | 219 | 0 | 0 | 0 | 1160 | 0 | 53 | 0 | 210 | 300 | 245 | 51 | 0 | 188 | 0 | 51 | 91 | 101 | 0 | 19 | 103 | 154 | 52.2 | 0 | 31 | 265 | 400 | 387 | 40 | 0 | 0 | 0 | 16 | 0 | 84 | 0 | 141 | 0 | 125 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8089.2 | 928 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 17 | 0 | 0 | 826.59 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 14 | 52.2 | 0 | 0 | 17 | 0 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 153 | 50 | 110 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 117 | 220 | 0 | 1000 | 565 | 17 | 5965.79 | 14054.99 | 106.07
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 255 | 0 | 17 | 17 | 63 | 32 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 17 | 5 | 22 | 0 | 340 | 94 | 16 | 24 | 0 | 37 | 0 | 15 | 0 | 12 | 12 | 0 | 215 | 94 | 19 | 1125 | 53 | 0 | 50 | 8 | 34 | 219 | 0 | 0 | 0 | 1164 | 0 | 53 | 0 | 240 | 300 | 280 | 51 | 0 | 207 | 0 | 51 | 91 | 102 | 0 | 19 | 104 | 156 | 52.2 | 0 | 31 | 266 | 400 | 387 | 40 | 0 | 0 | 0 | 16 | 0 | 84 | 0 | 142 | 0 | 125 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8123.2 | 929 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 17 | 0 | 0 | 832.12 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 14 | 52.2 | 0 | 0 | 17 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 154 | 50 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 116 | 220 | 0 | 873 | 565 | 17 | 5820.32 | 13943.52 | 106.06
06:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 259 | 0 | 17 | 17 | 63 | 32 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 17 | 5 | 22 | 0 | 355 | 101 | 16 | 25 | 0 | 26 | 0 | 15 | 0 | 12 | 12 | 0 | 215 | 93 | 24 | 1125 | 40 | 0 | 50 | 8 | 34 | 219 | 0 | 0 | 0 | 1224 | 0 | 55 | 0 | 270 | 300 | 285 | 51 | 0 | 209 | 0 | 47 | 91 | 103 | 0 | 19 | 103 | 144 | 52.2 | 1 | 23 | 267 | 400 | 392 | 40 | 0 | 0 | 0 | 16 | 0 | 84 | 0 | 142 | 0 | 125 | 0 | 58 | 0.21 | 67 | 0 | 0 | 0.7 | 11 | 8195.11 | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 17 | 0 | 0 | 834.91 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 14 | 52.2 | 0.33 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 155 | 49 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 307 | 117 | 220 | 0 | 638 | 565 | 17 | 5564.45 | 13759.56 | 106.05
07:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 258 | 0 | 17 | 19 | 63 | 32 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 3 | 17 | 5 | 22 | 0 | 355 | 100 | 16 | 25 | 0 | 40 | 0 | 15 | 0 | 12 | 12 | 0.19 | 170 | 92 | 11 | 1125 | 36 | 0 | 50 | 8 | 34 | 219 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 270 | 300 | 285 | 51 | 0 | 208 | 0 | 17 | 90 | 103 | 0 | 19 | 104 | 136 | 52.2 | 4 | 23 | 266 | 399 | 387 | 40 | 0 | 0 | 1 | 16 | 0 | 84 | 0 | 141 | 0 | 125 | 0 | 58 | 1.6 | 67 | 0 | 0.1 | 6.6 | 9 | 8089.69 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1050 | 0 | 0 | 0 | 833.07 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 14 | 52.2 | 3.81 | 3 | 0 | 0 | 2.84 | 140 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0.38 | 156 | 49 | 108 | 1 | 0 | 0 | 0 | 0 | 0.5 | 5 | 0.01 | 0 | 307 | 117 | 220 | 0 | 609 | 565 | 17 | 5540.81 | 13630.5 | 106.04
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 255 | 0 | 17 | 17 | 30 | 32 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 5 | 17 | 5 | 22 | 0 | 330 | 100 | 16 | 24 | 0 | 27 | 0 | 15 | 0 | 12 | 12 | 0.94 | 170 | 94 | 0 | 1125 | 35 | 0 | 50 | 8 | 34 | 219 | 0 | 0 | 0 | 1224 | 3 | 53 | 0 | 270 | 300 | 280 | 51 | 0 | 199 | 0 | 17 | 91 | 102 | 0 | 19 | 103 | 146 | 52.2 | 9 | 23 | 261 | 400 | 387 | 40 | 0 | 0 | 2 | 0 | 0 | 81 | 0 | 144 | 0 | 125 | 0 | 58 | 2.5 | 67 | 0 | 0.3 | 9.22 | 12 | 7994.16 | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.98 | 1050 | 0 | 0 | 0 | 835.27 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 14 | 52.2 | 10.24 | 10 | 0 | 0 | 16.27 | 140 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 1.15 | 154 | 48 | 107 | 3 | 0 | 0 | 0 | 0 | 1.2 | 18 | 0.01 | 0 | 307 | 116 | 220 | 0 | 607 | 570 | 17 | 5618.32 | 13612.48 | 106.02
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 238 | 0 | 17 | 17 | 31 | 32 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 6 | 17 | 5 | 22 | 0 | 330 | 97 | 16 | 25 | 0 | 15 | 0 | 15 | 17 | 12 | 12 | 1.16 | 170 | 92 | 0 | 1130 | 35 | 0 | 44 | 8 | 34 | 217 | 0 | 0 | 0 | 1224 | 8 | 55 | 0 | 230 | 280 | 240 | 43 | 0 | 219 | 0 | 19 | 90 | 109 | 0 | 19 | 102 | 124 | 52.2 | 46 | 23 | 264 | 400 | 367 | 40 | 0 | 0 | 5 | 8 | 0 | 81 | 0 | 143 | 0 | 125 | 0 | 58 | 6.7 | 105 | 0 | 0.5 | 12.88 | 12 | 7939.44 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.77 | 1050 | 0 | 0 | 0 | 832.22 | 0 | 41 | 0 | 0 | 5 | 0 | 0 | 14 | 52.2 | 5.33 | 20 | 0 | 0 | 5.6 | 132 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0.59 | 156 | 49 | 106 | 8 | 0 | 0 | 0 | 0 | 0.7 | 72 | 0.03 | 0 | 307 | 110 | 220 | 0 | 607 | 570 | 17 | 5632.44 | 13571.88 | 106
10:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 214 | 17 | 17 | 17 | 31 | 32 | 0 | 6 | 35 | 0 | 0 | 0 | 0 | 5 | 284 | 0 | 0 | 2 | 17 | 5 | 22 | 0 | 330 | 85 | 16 | 25 | 0 | 26 | 0 | 15 | 17 | 12 | 25 | 3.25 | 217 | 94 | 0 | 1130 | 40 | 0 | 44 | 8 | 34 | 218 | 0 | 0 | 0 | 1140 | 4 | 53 | 0 | 230 | 280 | 255 | 43 | 0 | 194 | 0 | 34 | 90 | 187 | 0 | 19 | 97 | 122 | 52.2 | 44 | 22 | 268 | 400 | 320 | 40 | 0 | 0 | 7 | 8 | 0 | 81 | 0 | 141 | 0 | 125 | 0 | 58 | 5.4 | 115 | 0 | 0.9 | 9.4 | 12 | 7961.15 | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1050 | 0 | 0 | 0 | 832.6 | 0 | 40 | 0 | 0 | 34 | 0 | 0 | 14 | 43 | 47.23 | 93 | 0 | 0 | 19.82 | 132 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 2.23 | 156 | 50 | 106 | 13 | 0 | 0 | 0 | 0 | 3.8 | 191 | 0.1 | 0 | 307 | 117 | 180 | 0 | 713 | 570 | 17 | 5984.78 | 13945.93 | 105.99
11:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 218 | 17 | 17 | 17 | 16 | 32 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 17 | 290 | 0 | 0 | 5 | 17 | 5 | 18 | 0 | 330 | 91 | 16 | 24 | 0 | 38 | 0 | 15 | 17 | 24 | 25 | 4.4 | 217 | 92 | 0 | 1130 | 73 | 0 | 44 | 8 | 34 | 217 | 0 | 0 | 0 | 1160 | 10 | 53 | 0 | 230 | 280 | 280 | 43 | 0 | 200 | 0 | 34 | 90 | 189 | 0 | 17 | 96 | 126 | 52.2 | 59 | 22 | 270 | 400 | 352 | 40 | 0 | 0 | 8 | 8 | 0 | 84 | 0 | 141 | 0 | 125 | 0 | 67 | 15 | 125 | 0 | 1.5 | 13.25 | 12 | 8245.35 | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 1050 | 0 | 0 | 0 | 834.61 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 14 | 52.2 | 8.25 | 27 | 0 | 0 | 6.54 | 132 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 1.82 | 159 | 50 | 104 | 30 | 0 | 0 | 0 | 0 | 3 | 95 | 0.21 | 0 | 307 | 115 | 220 | 0 | 800 | 565 | 17 | 5916.63 | 14161.98 | 105.97
12:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 224 | 17 | 17 | 29 | 16 | 31 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 17 | 290 | 0 | 0 | 7 | 34 | 5 | 14 | 0 | 340 | 94 | 16 | 22 | 0 | 50 | 0 | 15 | 17 | 24 | 25 | 4.34 | 217 | 93 | 0 | 1130 | 73 | 0 | 43 | 8 | 34 | 215 | 0 | 0 | 0 | 1160 | 18 | 53 | 0 | 230 | 280 | 320 | 43 | 0 | 204 | 0 | 33 | 90 | 190 | 0 | 17 | 103 | 132 | 47 | 66 | 22 | 270 | 400 | 372 | 41 | 0 | 0 | 8 | 8 | 0 | 83 | 0 | 141 | 0 | 125 | 9 | 68 | 10 | 125 | 0 | 0.3 | 15.54 | 12 | 8431.18 | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1050 | 0 | 0 | 0 | 832.65 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 14 | 52.2 | 8.64 | 62 | 0 | 0 | 40.12 | 128 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 1.84 | 160 | 45 | 108 | 36 | 0 | 0 | 0 | 0 | 2.4 | 96 | 0.1 | 0 | 307 | 116 | 220 | 0 | 1000 | 570 | 17 | 6186.95 | 14618.13 | 105.97
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 230 | 17 | 17 | 34 | 16 | 32 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 10 | 34 | 5 | 22 | 0 | 360 | 92 | 16 | 24 | 0 | 43 | 0 | 15 | 17 | 24 | 25 | 3.27 | 217 | 92 | 0 | 1130 | 73 | 0 | 42 | 8 | 34 | 215 | 0 | 0 | 0 | 1160 | 13 | 55 | 0 | 230 | 280 | 310 | 43 | 0 | 200 | 0 | 33 | 85 | 190 | 0 | 17 | 103 | 136 | 43 | 44 | 28 | 270 | 396 | 367 | 41 | 0 | 0 | 3 | 16 | 0 | 83 | 0 | 141 | 0 | 125 | 17 | 68 | 11.21 | 126 | 0 | 0.6 | 16.02 | 12 | 8337.1 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 1050 | 4 | 0 | 0 | 835.76 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 14 | 52.2 | 18.53 | 13 | 0 | 0 | 7.99 | 127 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0.82 | 157 | 40 | 108 | 29 | 0 | 0 | 0 | 0 | 5.3 | 44 | 0.02 | 16 | 307 | 116 | 220 | 0 | 1000 | 570 | 17 | 6031.62 | 14368.72 | 105.95
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 227 | 17 | 17 | 17 | 16 | 32 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 17 | 285 | 0 | 0 | 15 | 34 | 5 | 22 | 0 | 330 | 90 | 16 | 24 | 0 | 22 | 0 | 15 | 17 | 24 | 25 | 3.75 | 217 | 93 | 0 | 1050 | 71 | 0 | 42 | 8 | 34 | 217 | 0 | 0 | 0 | 1195 | 13 | 53 | 0 | 230 | 280 | 260 | 43 | 0 | 198 | 0 | 34 | 85 | 190 | 1 | 17 | 103 | 146 | 43 | 15 | 29 | 265 | 396 | 331 | 41 | 0 | 0 | 4 | 16 | 0 | 83 | 0 | 140 | 0 | 125 | 17 | 68 | 7.5 | 124 | 0 | 1.1 | 25.08 | 12 | 8102.43 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1050 | 9 | 0 | 0 | 832.83 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 14 | 52.2 | 31.11 | 48 | 18 | 0 | 37.11 | 127 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 2.19 | 162 | 35 | 106 | 13 | 0 | 0 | 0 | 0 | 3.4 | 122 | 0.01 | 16 | 307 | 116 | 180 | 0 | 1000 | 570 | 17 | 6150.85 | 14253.28 | 105.9
15:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 209 | 17 | 17 | 17 | 16 | 32 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 17 | 290 | 0 | 0 | 20 | 34 | 4.6 | 22 | 0 | 330 | 87 | 16 | 25 | 0 | 47 | 0 | 15 | 17 | 24 | 25 | 1.45 | 217 | 92 | 0 | 1130 | 71 | 0 | 43 | 8 | 34 | 218 | 0 | 0 | 0 | 1120 | 8 | 53 | 0 | 230 | 280 | 270 | 43 | 0 | 179 | 0 | 34 | 86 | 190 | 9 | 19 | 102 | 150 | 52.2 | 5 | 29 | 264 | 400 | 331 | 41 | 0 | 0 | 3 | 16 | 0 | 83 | 5 | 141 | 0 | 125 | 17 | 67 | 13.4 | 124 | 0 | 0.2 | 10.38 | 12 | 8114.23 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 1050 | 12 | 0 | 0 | 828.7 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 14 | 52.2 | 25.07 | 45 | 23 | 0 | 6.25 | 128 | 0 | 0 | 0 | 0 | 0 | 268 | 0 | 0.55 | 162 | 47 | 105 | 33 | 0 | 0 | 0 | 0 | 2.1 | 142 | 0.07 | 16 | 260 | 116 | 180 | 0 | 1000 | 565 | 17 | 6089.94 | 14204.17 | 105.93
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 209 | 17 | 0 | 17 | 16 | 31 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 17 | 290 | 0 | 0 | 12 | 34 | 4.6 | 22 | 0 | 330 | 87 | 16 | 33 | 0 | 28 | 0 | 15 | 17 | 36 | 38 | 1.03 | 217 | 97 | 0 | 1130 | 71 | 0 | 43 | 8 | 34 | 218 | 0 | 0 | 0 | 1162 | 2 | 53 | 0 | 230 | 280 | 265 | 43 | 0 | 181 | 0 | 36 | 85 | 190 | 8 | 19 | 104 | 152 | 52.2 | 21 | 29 | 267 | 400 | 331 | 40 | 20 | 0 | 3 | 16 | 0 | 83 | 20 | 141 | 0 | 126 | 17 | 68 | 0.46 | 124 | 0 | 0 | 18.02 | 12 | 8194.31 | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1050 | 7 | 0 | 0 | 829.4 | 0 | 39 | 0 | 35 | 35 | 0 | 0 | 14 | 52.2 | 30.76 | 13 | 25 | 0 | 1.12 | 128 | 0 | 0 | 0 | 0 | 0 | 262 | 0 | 0.12 | 159 | 48 | 109 | 13 | 0 | 0 | 0 | 0 | 4.4 | 128 | 0.07 | 16 | 269 | 116 | 220 | 0 | 800 | 565 | 17 | 5884.07 | 14078.38 | 105.92
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 233 | 17 | 0 | 20 | 16 | 31 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 2 | 34 | 4.6 | 22 | 0 | 370 | 92 | 16 | 35 | 0 | 28 | 0 | 15 | 17 | 37 | 38 | 0.38 | 217 | 92 | 0 | 1130 | 71 | 0 | 42 | 8 | 34 | 215 | 0 | 0 | 0 | 1162 | 3 | 53 | 0 | 230 | 280 | 295 | 43 | 0 | 201 | 0 | 51 | 85 | 189 | 26 | 19 | 104 | 146 | 52.2 | 10 | 29 | 270 | 400 | 331 | 41 | 30 | 0 | 2 | 16 | 0 | 84 | 20 | 141 | 0 | 126 | 17 | 68 | 0.97 | 125 | 0 | 0.2 | 2.6 | 12 | 8330.95 | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0.44 | 1050 | 11 | 0 | 0 | 826.84 | 0 | 39 | 0 | 35 | 35 | 0 | 0 | 14 | 52.2 | 8.06 | 9 | 25 | 0 | 0.95 | 128 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 0.07 | 161 | 48 | 111 | 4 | 46 | 0 | 0 | 0 | 1.8 | 19 | 0.03 | 16 | 278 | 116 | 180 | 0 | 800 | 565 | 17 | 5781.39 | 14112.34 | 105.91
18:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 222 | 17 | 8 | 53 | 45 | 80 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 17 | 295 | 0 | 0 | 0 | 34 | 4.6 | 22 | 0 | 370 | 89 | 16 | 40 | 0 | 13 | 0 | 15 | 17 | 50 | 0 | 0 | 217 | 92 | 0 | 1130 | 73 | 0 | 43 | 8 | 34 | 217 | 0 | 0 | 0 | 1104 | 0 | 53 | 0 | 230 | 280 | 300 | 43 | 0 | 200 | 0 | 51 | 85 | 190 | 71 | 19 | 103 | 146 | 52.2 | 0 | 29 | 275 | 400 | 331 | 41 | 30 | 0 | 0 | 8 | 0 | 86 | 20 | 141 | 0 | 125 | 17 | 68 | 0.04 | 125 | 0 | 0 | 0 | 12 | 8524.84 | 870 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 1050 | 17 | 0 | 0 | 860.69 | 0 | 39 | 0 | 35 | 40 | 0 | 0 | 20 | 52.2 | 0.37 | 2 | 25 | 0 | 0.51 | 128 | 0 | 0 | 0 | 0 | 0 | 258 | 0 | 0.03 | 158 | 50 | 110 | 1 | 66 | 0 | 0 | 0 | 0.5 | 1 | 0 | 16 | 228 | 116 | 220 | 0 | 800 | 565 | 17 | 5796.3 | 14321.14 | 105.9
19:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 223 | 54 | 17 | 39 | 95 | 81 | 0 | 55 | 72 | 0 | 0 | 0 | 0 | 55 | 305 | 0 | 0 | 0 | 120 | 4.6 | 22 | 0 | 340 | 94 | 16 | 41 | 0 | 17 | 50 | 35 | 36 | 75 | 0 | 0 | 217 | 93 | 0 | 1080 | 71 | 0 | 43 | 12 | 34 | 217 | 0 | 0 | 0 | 1140 | 0 | 60 | 0 | 270 | 280 | 270 | 43 | 0 | 180 | 0 | 72 | 85 | 190 | 65 | 19 | 104 | 162 | 52.2 | 0 | 29 | 270 | 400 | 331 | 41 | 30 | 0 | 0 | 8 | 0 | 86 | 20 | 142 | 0 | 125 | 17 | 88 | 0 | 161 | 0 | 0 | 0 | 12 | 8922.8 | 871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 67 | 0 | 1050 | 25 | 0 | 0 | 1313.55 | 0 | 39 | 0 | 40 | 70 | 0 | 100 | 21 | 52.2 | 0 | 0 | 25 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 157 | 48 | 109 | 0 | 92 | 0 | 130 | 0 | 0 | 0 | 0 | 16 | 276 | 113 | 180 | 0 | 800 | 565 | 17 | 6706.75 | 15629.55 | 105.89
19:30 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 223 | 54 | 17 | 36 | 120 | 81 | 12 | 55 | 162 | 0 | 0 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 143.42 | 4.6 | 22 | 0 | 340 | 92 | 16 | 54 | 0 | 30 | 50 | 40 | 36 | 75 | 75 | 0 | 218 | 100 | 0 | 1130 | 71 | 0 | 42 | 25.5 | 34 | 218 | 0 | 0 | 0 | 1120 | 0 | 110 | 0 | 300 | 280 | 275 | 43 | 0 | 190 | 0 | 89 | 85 | 190 | 73 | 19 | 105 | 170 | 52.2 | 0 | 29 | 270 | 400 | 331 | 41 | 30 | 0 | 0 | 8 | 0 | 86 | 20 | 141 | 0 | 125 | 17 | 88 | 0 | 162 | 0 | 0 | 0 | 12 | 9351.72 | 871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 67 | 0 | 1050 | 30 | 0 | 0 | 1314.79 | 0 | 39 | 0 | 40 | 70 | 0 | 100 | 25 | 52.2 | 0 | 0 | 25 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 156 | 49 | 110 | 0 | 92 | 0 | 100 | 0 | 0 | 0 | 0 | 32 | 276 | 116 | 220 | 0 | 800 | 565 | 17 | 6744.99 | 16096.71
20:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 227 | 54 | 17 | 35 | 144 | 81 | 7 | 55 | 162 | 0 | 0 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 143.42 | 4.6 | 22 | 0 | 340 | 90 | 16 | 53 | 0 | 14 | 50 | 43 | 36 | 75 | 76 | 0 | 218 | 104 | 2 | 1130 | 75 | 0 | 42 | 25.5 | 34 | 218 | 0 | 0 | 0 | 1166 | 0 | 150 | 0 | 300 | 280 | 290 | 43 | 0 | 194 | 0 | 89 | 85 | 183 | 74 | 19 | 103 | 176 | 52.2 | 0 | 29 | 268 | 400 | 341 | 41 | 30 | 0 | 0 | 16 | 0 | 86 | 20 | 141 | 0 | 125 | 17 | 88 | 0 | 165 | 0 | 0 | 0 | 12 | 9479.72 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 67 | 0 | 1037 | 34 | 0 | 0 | 1311.62 | 0 | 39 | 0 | 43 | 70 | 0 | 100 | 30 | 52.2 | 0 | 0 | 25 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 155 | 49 | 110 | 0 | 21 | 0 | 100 | 0 | 0 | 0 | 0 | 32 | 271 | 117 | 220 | 0 | 800 | 565 | 17 | 6615.82 | 16095.54 | 105.88
21:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 223 | 54 | 17 | 37 | 145 | 81 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 143.42 | 4.6 | 22 | 0 | 320 | 87 | 16 | 55 | 0 | 9 | 50 | 30 | 54.36 | 75 | 76 | 0 | 218 | 105 | 3 | 1130 | 73 | 0 | 42 | 25.5 | 34 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 300 | 280 | 240 | 43 | 0 | 189 | 0 | 89 | 86 | 180 | 73 | 19 | 104 | 162 | 52.2 | 0 | 29 | 270 | 400 | 342 | 41 | 30 | 0 | 0 | 16 | 0 | 86 | 20 | 141 | 0 | 125 | 0 | 88 | 0 | 165 | 0 | 0 | 0 | 12 | 9448.08 | 774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 67 | 0 | 924 | 38 | 0 | 0 | 1307 | 0 | 40 | 0 | 65 | 70 | 0 | 100 | 30 | 52.2 | 0 | 0 | 25 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 247 | 0 | 0 | 157 | 47 | 105 | 0 | 60 | 0 | 100 | 0 | 0 | 0 | 0 | 32 | 294 | 117 | 220 | 0 | 900 | 565 | 17 | 6631.2 | 16079.28 | 105.87
22:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 236 | 54 | 17 | 36 | 145 | 81 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 55 | 302 | 0 | 0 | 0 | 143.42 | 4.6 | 22 | 0 | 345 | 91 | 16 | 55 | 0 | 22 | 50 | 30 | 54.36 | 75 | 76 | 0 | 218 | 104 | 3 | 1130 | 71 | 0 | 43 | 25.5 | 34 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 300 | 280 | 260 | 43 | 0 | 200 | 0 | 88 | 91 | 190 | 73 | 19 | 104 | 160 | 52.2 | 0 | 29 | 265 | 395 | 355 | 41 | 30 | 0 | 0 | 16 | 0 | 86 | 20 | 141 | 0 | 125 | 11 | 88 | 0 | 164 | 0 | 0 | 0 | 12 | 9568.08 | 775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 880 | 37 | 0 | 0 | 1292.94 | 0 | 40 | 0 | 55 | 70 | 0 | 100 | 28 | 52.2 | 0 | 0 | 25 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 247 | 0 | 0 | 157 | 50 | 95 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 277 | 117 | 180 | 0 | 900 | 565 | 17 | 6287.14 | 15855.22 | 105.86
23:00 | 0 | 105 | 51 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 223 | 54 | 17 | 36 | 145 | 81 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 55 | 288 | 0 | 0 | 0 | 143.42 | 4.5 | 22 | 0 | 320 | 95 | 16 | 47 | 0 | 24 | 50 | 30 | 17 | 75 | 76 | 0 | 219 | 106 | 2 | 1130 | 71 | 0 | 43 | 25.5 | 34 | 217 | 0 | 0 | 0 | 1224 | 0 | 115 | 0 | 300 | 280 | 230 | 43 | 0 | 187 | 0 | 88 | 91 | 191 | 73 | 19 | 104 | 164 | 52.2 | 0 | 24 | 265 | 400 | 360 | 41 | 30 | 0 | 0 | 11 | 0 | 86 | 20 | 141 | 0 | 125 | 35 | 88 | 0 | 164 | 0 | 0 | 0 | 12 | 9429.62 | 870 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 850 | 37 | 0 | 0 | 1275.47 | 0 | 40 | 0 | 55 | 70 | 0 | 100 | 28 | 52.2 | 0 | 0 | 25 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 158 | 48 | 95 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 269 | 115 | 220 | 0 | 900 | 565 | 17 | 6363.67 | 15793.29 | 105.85
Total KWH | 0 | 1430179 | 688032 | 0 | 0 | 0 | 0 | 0 | 9637200 | 0 | 5928600 | 585432 | 402120 | 585792 | 1437600 | 1072385 | 72040 | 600923 | 1762560 | 0 | 0 | 0 | 0 | 599168 | 7120594 | 0 | 0 | 84307 | 1210800 | 114600 | 494280 | 0 | 8156818.18 | 2225564 | 375109 | 779856 | 0 | 714240 | 377131 | 448224 | 392175 | 742080 | 641280 | 21719 | 5107916 | 2261526 | 107040 | 26930909.09 | 1482036 | 0 | 1101600 | 295241.4 | 874836 | 5192934 | 0 | 0 | 0 | 28396361 | 78300 | 1634254 | 0 | 6111000 | 7329200 | 6876000 | 1104156 | 0 | 4977000 | 0 | 1249920 | 2105812 | 3787200 | 487200 | 457960 | 2519400 | 3533760 | 1196112 | 323255 | 651552 | 6400000 | 9501300 | 8755000 | 962000 | 230280 | 0 | 48030 | 317856 | 0 | 2011200 | 184608 | 3243000 | 0 | 3734740 | 291240 | 1627200 | 71467 | 2700000 | 0 | 6950 | 155060 | 286320 | 205399539.67 | 21586182 | 0 | 0 | 108480 | 0 | 0 | 0 | 0 | 741687 | 0 | 452448 | 173260 | 24567280 | 344544 | 0 | 0 | 22659942 | 0 | 877428 | 0 | 414624 | 820704 | 0 | 623200 | 400123 | 1229808 | 168696 | 337570 | 293360 | 0 | 131248 | 3178182 | 0 | 0 | 0 | 0 | 0 | 6774545 | 0 | 11460 | 3903000 | 1134109 | 2661623 | 173919 | 705446 | 0 | 599287.5 | 0 | 33775.32 | 929520 | 775 | 277728 | 7135000 | 2790000 | 5217870 | 0 | 20453460 | 14011636.36 | 435600 | 146357520.18 | 351757059.85

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 01-09-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14618.13 | MW | 12:00 Hr. | Energy Generated |  |  | 351.7571 |  | MKWHr.
| Day Peak Demand |  |  | 16287.13 | MW | 12:00 Hr. | Energy Unserverd |  |  | 31.239 |  | MKWHr.
| Evening Peak Generation |  |  | 16096.71 | MW | 19:30 Hr. | Energy Demand |  |  | 382.9961 |  | MKWHr.
| Evening Peak Demand |  |  | 16855.71 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32 |  | °C
| Minimum Generation of the Day |  |  | 13571.88 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 849.81 |  | MMCFD
| Maximum Generation of the Day |  |  | 16096.71 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 7.5738 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.4521 | 0 | 10.447 | 0 | 0 | 0.084307 | 0 | 0 | 41.9834 | Gas | 119.0138 | Gas | 409289972.5606
| Chattogram Zone |  |  | 5.3 | 55.3273 | 11.9967 | 0 | 5.1079 | 0.10002 | 0 | 0.71424 | 78.5461 | Coal | 126.5318 | Coal | 893080960.9617
| Cumilla Zone |  |  | 28.9611 | 0 | 11.5256 | 0 | 0 | 0.32326 | 3.5338 | 0 | 44.3438 | HFO | 48.5192 | HFO | 979244424.872
| Mymensingh Zone |  |  | 0 | 0 | 4.9048 | 0 | 0 | 0.23348 | 0 | 0 | 5.1382 | HSD | 1.341 | HSD | 33488075.4
| Sylhet Zone |  |  | 35.34 | 0 | 0 | 0 | 0 | 0.04803 | 0 | 0 | 35.388 | Hydro | 5.1079 | Hydro | 510791.6
| Khulna Zone |  |  | 0 | 24.5673 | 0.90547 | 0.74169 | 0 | 0.17326 | 21.5862 | 0 | 47.9739 | Solar | 2.7493 | Solar | 44818711.2752
| Barishal Zone |  |  | 8.0079 | 41.6001 | 0.71333 | 0 | 0 | 0.000775 | 0 | 0 | 50.3221 | Import | 47.7799 | Import | 293192830.5
| Rajshahi Zone |  |  | 9.9527 | 0 | 4.6592 | 0 | 0 | 0.64897 | 22.6599 | 0 | 37.9209 | Wind | 0.71424 | Wind | 10506470.4
| Rangpur Zone |  |  | 0 | 5.0371 | 3.3671 | 0.59929 | 0 | 1.1372 | 0 | 0 | 10.1407
| Total |  |  | 119.0138 | 126.5318 | 48.5192 | 1.341 | 5.1079 | 2.7493 | 47.7799 | 0.71424 | 351.7571
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 409289972.5606 |  | Hydro | 510791.6
|  |  |  | Coal | 893080960.9617 |  | Solar | 44818711.2752
|  |  |  | HFO | 979244424.872 |  | Import | 293192830.5
|  |  |  | HSD | 33488075.4 |  | Wind | 10506470.4
[5 empty] | Total: | 266,41,32,237 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5862 | Peak Hr Flow | 871.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33382036.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.6599 | Peak Hr Flow | 1314.79 MW at 19:30 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1655 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.5338 | Peak Hr Flow | 170.00 MW at 19:30 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2139 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.7799 | Peak Hr Flow | 2355.79 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 171 |  | 6159
|  |  |  | Chattogram |  | 9 |  | 1520
|  |  |  | Cumilla |  | 69 |  | 1486
|  |  |  | Mymensingh |  | 319 |  | 1455
|  |  |  | Sylhet |  | 31 |  | 698
|  |  |  | Khulna |  | 58 |  | 1905
|  |  |  | Barishal |  | 0 |  | 461
|  |  |  | Rajshahi |  | 48 |  | 1618
|  |  |  | Rangpur |  | 21 |  | 1004
|  |  |  | Total |  | 726 |  | 16306
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 54
|  |  |  | Total Unavailable Capacity |  |  |  | 354
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:16 | Mirpur 132/33kV S/S Reserve Bus is restored.
|  | 08:17 | Mirpur 132/33kV S/S T2 HT is restored.
|  | 08:23 | Mirpur 132/33kV S/S T2 LT is restored.
| 08:50 | 09:21 | Daudkandi-Sonargaon 132 kV Ckt-2 Tripped from Sonargaon 132/33kV end showing Line
Distance Relay (21L) relays. and from Daudkandi 132/33kV end showing Dist trip c , Remote
CBF , ZONE-1 , 11.69KM. relays.
| 09:52 | 20:53 | Baghabari-Bangura 132 kV Ckt-2 Project Work S/D from Bhangura 132/33kV end Due to SuS
work
| 10:02 | 17:08 | KSRM 132/33kV S/S Transformer-02 HT Scheduled S/D Due to 33 KV BUS Maintenance
| 10:05 | 17:05 | KSRM 132/33kV S/S Transformer-03 HT Scheduled S/D Due to 33 KV Bus Maintenance
| 10:52 | 11:54 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Forced S/D Due to Rights of Way.
| 10:52 | 11:59 | Kasba 132/33kV S/S TR-2 HT Scheduled S/D Due to shutdown tacken by pbs for redhot
maintenance
| 10:52 | 11:59 | Kasba 132/33kV S/S TR-2 LT Scheduled S/D Due to shutdown tacken by pbs for redhot | [7 empty] | 17.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 11:08 |  | Birulia 230/132kV S/S ATR-3 LT Project Work S/D Due to For Transformer troubleshooting
and checking of ATR-3 due to Tripped showing: ATR SELF Protection Operated. SUDDEN OIL
Pressure Trip, Lockout operated(K861, K8612, K862,K8622) in SAS Panel on 31.08.2026 at
16:36.
| 11:08 |  | Birulia 230/132kV S/S ATR-3 HT Project Work S/D Due to For Transformer troubleshooting
and checking of ATR-3 due to Tripped showing: ATR SELF Protection Operated. SUDDEN OIL
Pressure Trip, Lockout operated(K861, K8612, K862,K8622) in SAS Panel on 31.08.2026 at
16:36.
| 12:00 |  | Day Peak Generation: 14618 MW.
| 13:41 | 15:22 | BIPTC S/S 10CF13 Forced S/D
|  | 14:40 | Halishahar-Julda 132kV Ckt-1 is restored.
| 15:05 |  | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 Tripped from Bogura 230/132kV end showing Relay
Model: SEl-311C Distance Protection : Zone 1 DIR. Over Current Earth Fault Fault Type
A-G Fault Current: 27182A relays Due to Bad Weather & Thundering and from Bog-Sherpur
132/33kV end showing Distance Protection P443, Overcurrent Protection P132 relays Due to
Fault in Bogura 230/132 KV Grid Substation
| 15:26 | 16:15 | Ashuganj-Brahmanbaria 132kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end.
| 16:19 | 16:59 | Ashuganj-Brahmanbaria 132kV Ckt-1 Forced S/D from Brahmanbaria 132/33kV end. | [7 empty] | 20.0MW load
interrup.
Brahmanbaria
132/33kV end
| 17:20 | 18:48 | Chandina-Cumilla(N) 132 kV Ckt-2 Project Work S/D from Chandina 132/33kV end Due to
Project Work at Cumilla North end
|  | 17:56 | Fenchuganj-Sreemangal 132kV Ckt-1 is restored.
| 04:12 |  | Ishurdi 230/132kV S/S 230/132 kV T-03 HT Tripped showing R Phase,Y Phase,B
phase,Mechanical Trip relays.
| 04:12 |  | Ishurdi 230/132kV S/S 230/132 kV T-03 LT Tripped showing Mechanical Trip(R,Y,B) relays.
| 06:16 | 07:16 | Gollamari 132/33kV S/S Tr-2 LT Scheduled S/D Due to Due to hotspot maintenance work.
| 06:17 | 07:16 | Gollamari 132/33kV S/S Tr-2 HT Scheduled S/D Due to Due to hotspot maintenance work.
| 07:07 |  | Fenchuganj-Sreemangal 132kV Ckt-1 Project Work S/D from Sreemongol 132/33kV end Due to
G2G Project Work and from Fenchuganj 230/132/33kV end Due to G2G project work
| 07:34 |  | Purbasadipur 230/132/33kV S/S TR-4 LT Forced S/D Due to Red hot maintenance at 33 kV BUS | [7 empty] | 52.0MW load
|  |  | Coupler DS. | [7 empty] | interrup.
| 07:35 |  | Purbasadipur 230/132/33kV S/S TR-4 HT Forced S/D Due to Red hot maintenance at 33 kV BUS | [7 empty] | 52.0MW load
|  |  | Coupler DS. | [7 empty] | interrup.
| 07:35 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Forced S/D from Naogaon 132/33kV end Due to 132 kV
bogura-sherpur ckt-2 jumper loop maintenance at Bogura S/S end and from Bogura 230/132kV
end Due to Jumper loop connection of Sherpur Ckt.-2
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-09-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 413 | 9637200 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 12 | 72040 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 290 | 7120594 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 585432 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 120 | 1437600 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 600923 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 599168 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 4.6 | 114600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 494280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 51 | 688032 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 81 | 1072385 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 36 | 585792 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1430179 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1762560 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 84307 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 402120 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 340 | 8156818.18 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 223 | 5928600 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 1210800 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2184.02 | 41983430.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 295241.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 78300 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 42 | 1101600 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 218 | 5107916 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 218 | 5192934 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 874836 | FGMO
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 448224 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 377131 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 75 | 742080 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 107040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 54 | 779856 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21719 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 375109 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 36 | 392175 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 100 | 2261526 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 75 | 641280 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 92 | 2225564 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 71 | 1482036 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1120 | 28396361 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 30 | 714240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1130 | 26930909.09 | GT-2 U/M
Chattogram Area Total |  |  |  |  | 4885.967 | 3426.5 | 78546077.49
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 190 | 4977000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 280 | 7329200 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 275 | 6876000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 300 | 6111000 | Gas shortage
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 1104156 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 110 | 1634254 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 651552 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2105812 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 190 | 3787200 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 170 | 3533760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1196112 | Liquid fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 457960 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 105 | 2519400 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 73 | 487200 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 1249920 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 323255 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 2010.2 | 44343781
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 71467 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 162 | 2700000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1627200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 155060 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 286320 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 291240 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 279 | 5138237
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 48030 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 962000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 230280 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 141 | 3243000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 184608 | Machine Problem
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2011200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 125 | 3734740 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 317856 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 6400000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 331 | 8755000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9501300 | -
Sylhet Area Total |  |  |  |  | 2325 | 1452 | 35388014
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 871 | 21586182 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 108480 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 30 | 344544 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 452448 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 173260 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 150 | 741687 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1050 | 24567280 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 2168 | 47973881
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 800 | 20453460 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 277728 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 116 | 2790000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 565 | 14011636.36 | machine problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5217870 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 435600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 276 | 7135000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 775 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2026 | 50322069.36
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 168696 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 39 | 877428 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 400123 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 128 | 3178182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 250 | 6774545 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 293360 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1229808 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 623200 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 820704 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 40 | 414624 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 11460 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1314.79 | 22659942 | Coal shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 131248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 337570 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2043.99 | 37920890
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 100 | 599287.5 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1134109 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 156 | 3903000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 705446 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 33775.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 110 | 2661623 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 173919 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 929520 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 507 | 10140679.82
Eastern Grid Total |  |  |  |  | 17427.666 | 9351.72 | 205399539.67
Western Grid Total |  |  |  |  | 11731.125 | 6744.99 | 146357520.18
National Grid Total |  |  |  |  | 29158.791 | 16096.71 | 351757059.85
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-09-2026
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10719.38 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4860.6 | MW
i) Dhaka area |  |  | 5988.48 |  | MW | i) Khulna area |  |  |  | 1847 | MW
ii) Chattogram area |  |  | 1510.9 |  | MW | ii) Barishal area |  |  |  | 461 | MW
iii) Cumilla area |  |  | 1417 |  | MW | iii) Rajshahi area |  |  |  | 1569.6 | MW
iv) Mymensingh area |  |  | 1136 |  | MW | iv) Rangpur area |  |  |  | 983 | MW
v) Sylhet area |  |  | 667 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15579.98 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | HaripurSBU | 149 | 20:00 | 133 | Narshingdi | 194 | 21:00 | 199 | Uttara | 97 | 18:30
2 | AKSML | 135.2 | 10:00 | 68 | Hasnabad | 99 | 10:00 | 134 | Natore | 158 | 23:00 | 200 | UttaraNew | 59 | 00:00
3 | Aftabnagar | 44 | 00:00 | 69 | Hathazari | 100 | 20:00 | 135 | Nawabganj | 58.8 | 21:00 | 201 | Zigatola | 94 | 00:00
4 | Agargaon | 117 | 13:00 | 70 | Hatirjheel | 75 | 11:00 | 136 | Netrakona | 120 | 23:00
5 | Agrabad | 66 | 10:00 | 71 | Ishurdi | 84 | 19:30 | 137 | New | 90.2 | 09:00
6 | Amnura | 32 | 00:00 | 72 | Jaldhaka | 83 | 19:30 | 138 | Niamatpur | 70 | 00:00
7 | Ashuganj | 89 | 02:00 | 73 | Jamalpur | 126 | 22:00 | 139 | Noapara | 45 | 21:00
8 | BSRM | 202 | 16:00 | 74 | Jashore | 148 | 19:00 | 140 | PHP | 10 | 00:00
9 | Bagerhat | 89 | 21:00 | 75 | Jhenaidah | 88 | 20:00 | 141 | Pabna | 102 | 19:00
10 | Bajitpur | 90 | 20:00 | 76 | Joydebpur | 174 | 19:00 | 142 | Palashbari | 126 | 00:00
11 | Bakerganj | 14 | 00:00 | 77 | Joypurhat | 59 | 21:00 | 143 | Panchagarh | 70 | 19:00
12 | Bakulia | 95 | 18:00 | 78 | Juldah | 18 | 12:00 | 144 | Patiya | 20 | 15:00
13 | Banani | 56 | 12:00 | 79 | KSRM | 15 | 14:00 | 145 | Patnitala | 33 | 00:00
14 | Bangabhaban | 17 | 11:00 | 80 | Kabirpur | 259 | 19:30 | 146 | Patuakhali | 72 | 19:00
15 | Barapukuria | 64 | 08:00 | 81 | Kachua | 102 | 23:00 | 147 | Payra | 36 | 22:00
16 | Barguna | 22 | 19:00 | 82 | Kaliganj | 39 | 19:00 | 148 | Postogola | 67 | 13:00
17 | Barishal | 96 | 19:00 | 83 | Kallyanpur | 129 | 00:00 | 149 | Pubail | 45 | 19:30
18 | Barishal-230 | 102 | 19:00 | 84 | Kalurghat | 43 | 17:00 | 150 | Purbachal | 21 | 00:00
19 | Baroaulia | 60 | 16:00 | 85 | Kamrangirchar | 80 | 13:00 | 151 | Purbasadipur | 128 | 00:00
20 | Baroirhat | 62 | 23:00 | 86 | Kaptai | N/A | N/A | 152 | Rahanpur | 42 | 21:00
21 | Bashundhara | 232 | 12:00 | 87 | Kasba | 42 | 20:00 | 153 | Rahim | 55 | 09:00
22 | BashundharaCement | 5 | 23:00 | 88 | Kazla | 117 | 13:00 | 154 | Rajbari | 89 | 21:00
23 | Beanibazar | 80 | 20:00 | 89 | Keranigonj | 87 | 18:30 | 155 | Rajendrapur | 133 | 19:30
24 | Benapole | 62 | 19:30 | 90 | Khagrachori | 34 | 19:30 | 156 | Rajshahi | 111 | 23:00
25 | Bhaluka | 173 | 22:00 | 91 | Khulna | 60 | 19:00 | 157 | Rajshahi-230 | 104 | 00:00
26 | Bhandaria | 58 | 22:00 | 92 | Khulshi | 204 | 18:30 | 158 | Ramganj | 116 | 19:30
27 | Bhangura | 38 | 19:30 | 93 | Kishoreganj | 135 | 21:00 | 159 | Rampur | 44 | 20:00
28 | Bheramara(GK) | 72 | 19:30 | 94 | Kodda | 318 | 22:00 | 160 | Rangamati | 16 | 18:30
29 | Bhulta | 232 | 21:00 | 95 | Kulaura | 61 | 19:30 | 161 | Rangpur | 135 | 18:30
30 | Bog-Sherpur | 70 | 00:00 | 96 | Kurigram | 72 | 19:30 | 162 | Ruppur | 4.4 | 15:00
31 | Bogura | 201 | 00:00 | 97 | Kushtia | 159 | 19:30 | 163 | SSM | 0 | 00:00
32 | Borhanuddin | 82 | 23:00 | 98 | Laksam | 35 | 23:00 | 164 | Saidpur | 101 | 09:00
33 | Brahmanbaria | 146 | 20:00 | 99 | Lakshmipur | 54 | 23:00 | 165 | Santhia | 36 | 19:00
34 | Cantonment | 138 | 12:00 | 100 | Lalbag | 80 | 14:00 | 166 | Satkhira | 127 | 19:00
35 | Chandina | 18 | 00:00 | 101 | Lalmonirhat | 58 | 19:30 | 167 | Satmasjid | 107 | 13:00
36 | Chandpur | 86 | 21:00 | 102 | MI_Cement | 16.3 | 21:00 | 168 | Savar | 210 | 16:00
37 | Chandraghona | 34 | 19:00 | 103 | Madanganj | 42 | 00:00 | 169 | SevenRings | 21.34 | 11:00
38 | Chapai | 73 | 22:00 | 104 | Madaripur | 109 | 23:00 | 170 | ShahCement | 25 | 18:00
39 | Charfasson | 35 | 22:00 | 105 | Madartek | 96 | 00:00 | 171 | Shahjadpur | 88 | 20:00
40 | Charsaidpur | 39 | 00:00 | 106 | Madunaghat | 56 | 19:00 | 172 | Shahjibazar | 134 | 21:00
41 | Chauddagram | 76 | 22:00 | 107 | Magura | 71 | 19:30 | 173 | Shahmirpur | 58 | 21:00
42 | Chhatak | 40 | 19:00 | 108 | Mahasthangarh | 80 | 23:00 | 174 | Shariatpur | 101 | 21:00
43 | Chowmuhani | 155 | 21:00 | 109 | Maijdee | 39 | 23:00 | 175 | Sherpur | 150 | 18:30
44 | Chuadanga | 121 | 19:00 | 110 | Manikganj | 144 | 20:00 | 176 | Shikalbaha | 38 | 00:00
45 | Coxsbazar | 138 | 20:00 | 111 | Maniknagar | 81 | 13:00 | 177 | Shitalakhya | 77.4 | 12:00
46 | Cumilla(N) | 152 | 13:00 | 112 | Matarbari | 57 | 18:30 | 178 | Sholosohor | 48 | 17:00
47 | Cumilla(S) | 178 | 20:00 | 113 | Matuail | 78 | 09:00 | 179 | Shomvuganj | 41 | 20:00
48 | Daganbhuiyan | 36 | 22:00 | 114 | Metrorail_Motijheel | 38 | 15:00 | 180 | Shyampur | 176 | 13:00
49 | Daudkandi | 138 | 21:00 | 115 | Metrorail_Uttara | 0 | 00:00 | 181 | Siddhirganj | 136 | 12:00
50 | DhakaUniversity | 90 | 12:00 | 116 | Millgate | 104 | 12:00 | 182 | Sirajganj | 118 | 20:00
51 | Dhamrai | 98 | 22:00 | 117 | Mirpur | 153 | 13:00 | 183 | Sitakunda | 14 | 18:30
52 | Dhanmondi | 109 | 13:00 | 118 | Mirsorai | 38 | 00:00 | 184 | Sonargaon | 148 | 23:00
53 | Dohazari | 109 | 22:00 | 119 | Mirzapur | 46 | 21:00 | 185 | Sreemongol | 86 | 21:00
54 | Faridpur | 185 | 00:00 | 120 | Mithapukur | 70 | 18:00 | 186 | Sreepur | 135 | 19:30
55 | Fatullah | 116 | 12:00 | 121 | Modern | N/A | N/A | 187 | Srinagar | 47.8 | 22:00
56 | Fenchuganj | 45 | 20:00 | 122 | Mogbazar | 65.8 | 13:00 | 188 | Sunamganj | 63 | 20:00
57 | Feni | 107 | 18:30 | 123 | Mongla | 47 | 09:00 | 189 | Sylhet | 132 | 18:30
58 | GPH | 1 | 00:00 | 124 | Motijheel | 54 | 13:00 | 190 | Sylhet_(South) | 69 | 21:00
59 | Ghatail | 91 | 20:00 | 125 | Muktagacha | 45 | 15:00 | 191 | TK | 0 | 00:00
60 | Ghorashal | 0 | 00:00 | 126 | Munshiganj | 116 | 23:00 | 192 | Tangail | 164 | 19:30
61 | Ghorashal-230 | 114 | 19:30 | 127 | Muradnagar | 60 | 20:00 | 193 | Taraganj | 34 | 20:00
62 | Goalpara | 39 | 13:00 | 128 | Mymensingh | 148 | 19:30 | 194 | Tasnim | 40 | 00:00
63 | Gollamari | 106 | 19:30 | 129 | Nabinagar | 110 | 20:00 | 195 | Thakurgaon | 111 | 00:00
64 | Gopalganj | 120 | 19:30 | 130 | Naogaon | 112 | 19:30 | 196 | Tongi | 145 | 19:30
65 | Gulshan | 122 | 11:00 | 131 | Narail | 62 | 19:00 | 197 | Ullahpara | 38 | 20:00
66 | Halishahar | 144.5 | 12:00 | 132 | Narinda | 78 | 13:00 | 198 | Ullon | 45 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-09-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15509.19 | 2533 |  | 18156.18
1:00 | 14494.59 | 2376 |  | 16977.59
2:00 | 14107.49 | 2364 |  | 16577.49
3:00 | 14059.59 | 2240 |  | 16400.59
4:00 | 14054.99 | 1822 |  | 15958.99
5:00 | 13943.52 | 1609 |  | 15624.52
6:00 | 13759.56 | 1510 |  | 15337.56
7:00 | 13630.5 | 1398 |  | 15091.5
8:00 | 13612.48 | 1393 |  | 15068.48
9:00 | 13571.88 | 1657 |  | 15303.88
10:00 | 13945.93 | 1235 |  | 15236.93
11:00 | 14161.98 | 1138 |  | 15350.98
12:00 | 14618.13 | 1597 |  | 16287.13
13:00 | 14368.72 | 1390 |  | 15821.72
14:00 | 14253.28 | 1476 |  | 15795.28
15:00 | 14204.17 | 1547 |  | 15821.17
16:00 | 14078.38 | 872 |  | 14989.38
17:00 | 14112.34 | 475 |  | 14608.34
18:00 | 14321.14 | 523 |  | 14868.14
19:00 | 15629.55 | 839 |  | 16506.55
19:30 | 16096.71 | 726 |  | 16855.71
20:00 | 16095.54 | 279 |  | 16387.54
21:00 | 16079.28 | 192 |  | 16280.28
22:00 | 15855.22 | 194 |  | 16058.22
23:00 | 15793.29 | 580 |  | 16399.29
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 01-09-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8711.5 | 6797.69 | 15509.19 | DAILY GENERATION CURVE
00:30 | 8413.75 | 6588.14 | 15001.89
01:00 | 8116 | 6378.59 | 14494.59 | 01-09-2026
01:30 | 8125.5 | 6175.54 | 14301.04
02:00 | 8135 | 5972.49 | 14107.49
02:30 | 8120.1 | 5963.44 | 14083.54
03:00 | 8105.2 | 5954.39 | 14059.59
03:30 | 8097.2 | 5960.09 | 14057.29
04:00 | 8089.2 | 5965.79 | 14054.99
04:30 | 8106.2 | 5893.055 | 13999.255
05:00 | 8123.2 | 5820.32 | 13943.52
05:30 | 8159.155 | 5692.385 | 13851.54
06:00 | 8195.11 | 5564.45 | 13759.56
06:30 | 8142.4 | 5552.63 | 13695.03
07:00 | 8089.69 | 5540.81 | 13630.5
07:30 | 8041.925 | 5579.565 | 13621.49
08:00 | 7994.16 | 5618.32 | 13612.48
08:30 | 7966.8 | 5625.38 | 13592.18
09:00 | 7939.44 | 5632.44 | 13571.88
09:30 | 7950.295 | 5808.61 | 13758.905
10:00 | 7961.15 | 5984.78 | 13945.93
10:30 | 8103.25 | 5950.705 | 14053.955
11:00 | 8245.35 | 5916.63 | 14161.98
11:30 | 8338.265 | 6051.79 | 14390.055
12:00 | 8431.18 | 6186.95 | 14618.13
12:30 | 8384.14 | 6109.285 | 14493.425
13:00 | 8337.1 | 6031.62 | 14368.72
13:30 | 8219.765 | 6091.235 | 14311
14:00 | 8102.43 | 6150.85 | 14253.28
14:30 | 8108.33 | 6120.395 | 14228.725
15:00 | 8114.23 | 6089.94 | 14204.17
15:30 | 8154.27 | 5987.005 | 14141.275
16:00 | 8194.31 | 5884.07 | 14078.38
16:30 | 8262.63 | 5832.73 | 14095.36
17:00 | 8330.95 | 5781.39 | 14112.34
17:30 | 8427.895 | 5788.845 | 14216.74
18:00 | 8524.84 | 5796.3 | 14321.14
18:30 | 8723.82 | 6251.525 | 14975.345
19:00 | 8922.8 | 6706.75 | 15629.55
19:30 | 9351.72 | 6744.99 | 16096.71
20:00 | 9479.72 | 6615.82 | 16095.54
20:30 | 9463.9 | 6623.51 | 16087.41 |  | Executive Engineer
21:00 | 9448.08 | 6631.2 | 16079.28 |  | Network Operation Division
21:30 | 9508.08 | 6459.17 | 15967.25
22:00 | 9568.08 | 6287.14 | 15855.22
22:30 | 9498.85 | 6325.405 | 15824.255
23:00 | 9429.62 | 6363.67 | 15793.29

## En-Curve
QF-LDC-12
Date | 01-09-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3569 | 1262 | 882 | 0 | 164 | 1009.49 | 217 | 5409 | 0 | 538 | 2027.7 | 404 | 0 | 27 | 2533 | DAILY ENERGY CURVE
00:30 | 3552 | 1259.5 | 905.5 | 0 | 161 | 912.44 | 217 | 5385 | 0 | 440.5 | 1744.45 | 403.5 | 0 | 21 | 2454.5 | 01-09-2026
01:00 | 3535 | 1257 | 929 | 0 | 158 | 815.39 | 217 | 5361 | 0 | 343 | 1461.2 | 403 | 0 | 15 | 2376
01:30 | 3548 | 1261 | 929 | 0 | 154 | 820.34 | 217 | 5384 | 0 | 328.5 | 1423.7 | 216.5 | 0 | 19 | 2370 | Energy Generated | 351.7571 |  | MKWHr
02:00 | 3561 | 1265 | 929 | 0 | 150 | 825.29 | 217 | 5407 | 0 | 314 | 1386.2 | 30 | 0 | 23 | 2364 | Energy not Served | 31.239 |  | MKWHr
02:30 | 3575.5 | 1257.5 | 928.5 | 0 | 150 | 826.74 | 216.5 | 5406.5 | 0 | 289 | 1385.8 | 15 | 0 | 32.5 | 2302 | Total Energy Requirement | 382.9961 |  | MKWHr
03:00 | 3590 | 1250 | 928 | 0 | 150 | 828.19 | 216 | 5406 | 0 | 264 | 1385.4 | 0 | 0 | 42 | 2240
03:30 | 3589.5 | 1253.5 | 928 | 0 | 152 | 827.39 | 215.5 | 5408 | 0 | 260.5 | 1371.9 | 0 | 0 | 51 | 2031
04:00 | 3589 | 1257 | 928 | 0 | 154 | 826.59 | 215 | 5410 | 0 | 257 | 1358.4 | 0 | 0 | 60 | 1822
04:30 | 3647 | 1277 | 928.5 | 0 | 155 | 829.355 | 215 | 5349 | 0 | 257 | 1292.9 | 0 | 0 | 48.5 | 1715.5
05:00 | 3705 | 1297 | 929 | 0 | 156 | 832.12 | 215 | 5288 | 0 | 257 | 1227.4 | 0 | 0 | 37 | 1609
05:30 | 3732.5 | 1309.5 | 929 | 0 | 150 | 833.515 | 215 | 5200.5 | 1.125 | 235 | 1213.9 | 0 | 0 | 31.5 | 1559.5
06:00 | 3760 | 1322 | 929 | 0 | 144 | 834.91 | 215 | 5113 | 2.25 | 213 | 1200.4 | 0 | 0 | 26 | 1510
06:30 | 3756.5 | 1314.5 | 929.5 | 0 | 140 | 833.99 | 192.5 | 5099 | 18.64 | 213 | 1164.4 | 0 | 0 | 33 | 1454
07:00 | 3753 | 1307 | 930 | 0 | 136 | 833.07 | 170 | 5085 | 35.03 | 213 | 1128.4 | 0 | 0 | 40 | 1398
07:30 | 3747 | 1275.5 | 929.5 | 0 | 141 | 834.17 | 170 | 5085 | 81.92 | 196.5 | 1127.4 | 0 | 0 | 33.5 | 1395.5
08:00 | 3741 | 1244 | 929 | 0 | 146 | 835.27 | 170 | 5085 | 128.81 | 180 | 1126.4 | 0 | 0 | 27 | 1393
08:30 | 3670.5 | 1237 | 928.5 | 0 | 135 | 833.745 | 170 | 5089 | 166.035 | 185.5 | 1155.9 | 0 | 0 | 21 | 1525
09:00 | 3600 | 1230 | 928 | 0 | 124 | 832.22 | 170 | 5093 | 203.26 | 191 | 1185.4 | 0 | 0 | 15 | 1657
09:30 | 3545 | 1200 | 928.5 | 0 | 123 | 832.41 | 193.5 | 5104.5 | 333.195 | 217 | 1261.3 | 0 | 0 | 20.5 | 1446
10:00 | 3490 | 1170 | 929 | 0 | 122 | 832.6 | 217 | 5116 | 463.13 | 243 | 1337.2 | 0 | 0 | 26 | 1235
10:30 | 3520 | 1191.5 | 929 | 0 | 124 | 833.605 | 217 | 5168.5 | 390.55 | 261 | 1386.8 | 0 | 0 | 32 | 1186.5
11:00 | 3550 | 1213 | 929 | 0 | 126 | 834.61 | 217 | 5221 | 317.97 | 279 | 1436.4 | 0 | 0 | 38 | 1138
11:30 | 3600 | 1218.5 | 929 | 0 | 129 | 833.63 | 217 | 5321.5 | 359.625 | 287.5 | 1450.3 | 0 | 0 | 44 | 1367.5
12:00 | 3650 | 1224 | 929 | 0 | 132 | 832.65 | 217 | 5422 | 401.28 | 296 | 1464.2 | 0 | 0 | 50 | 1597
12:30 | 3635.5 | 1245 | 913 | 0 | 134 | 834.205 | 217 | 5418 | 324.02 | 246.5 | 1479.7 | 0 | 0 | 46.5 | 1493.5
13:00 | 3621 | 1266 | 897 | 0 | 136 | 835.76 | 217 | 5414 | 246.76 | 197 | 1495.2 | 0 | 0 | 43 | 1390
13:30 | 3566 | 1227 | 897 | 0 | 141 | 834.295 | 217 | 5391.5 | 312.505 | 206.5 | 1485.7 | 0 | 0 | 32.5 | 1433
14:00 | 3511 | 1188 | 897 | 0 | 146 | 832.83 | 217 | 5369 | 378.25 | 216 | 1476.2 | 0 | 0 | 22 | 1476
14:30 | 3511.5 | 1179.3 | 897 | 0 | 148 | 830.765 | 217 | 5351.5 | 356.86 | 218.5 | 1483.8 | 0 | 0 | 34.5 | 1511.5
15:00 | 3512 | 1170.6 | 897 | 0 | 150 | 828.7 | 217 | 5334 | 335.47 | 221 | 1491.4 | 0 | 0 | 47 | 1547
15:30 | 3525 | 1192.1 | 896.5 | 0 | 151 | 829.05 | 217 | 5258.5 | 292.725 | 221.5 | 1520.4 | 0 | 0 | 37.5 | 1209.5
16:00 | 3538 | 1213.6 | 896 | 0 | 152 | 829.4 | 217 | 5183 | 249.98 | 222 | 1549.4 | 0 | 0 | 28 | 872
16:30 | 3571.5 | 1227.6 | 896 | 0 | 149 | 828.12 | 217 | 5188.5 | 157.24 | 238 | 1594.4 | 0 | 0 | 28 | 673.5
17:00 | 3605 | 1241.6 | 896 | 0 | 146 | 826.84 | 217 | 5194 | 64.5 | 254 | 1639.4 | 0 | 0 | 28 | 475
17:30 | 3603.5 | 1255.6 | 883 | 0 | 146 | 843.765 | 217 | 5139.5 | 34.975 | 333.5 | 1739.4 | 0 | 0 | 20.5 | 499
18:00 | 3602 | 1269.6 | 870 | 0 | 146 | 860.69 | 217 | 5085 | 5.45 | 413 | 1839.4 | 0 | 0 | 13 | 523
18:30 | 3596 | 1232.6 | 870.5 | 0 | 154 | 1087.12 | 217 | 5100.5 | 2.725 | 575 | 1984.9 | 140 | 0 | 15 | 681
19:00 | 3590 | 1195.6 | 871 | 0 | 162 | 1313.55 | 217 | 5116 | 0 | 737 | 2130.4 | 280 | 0 | 17 | 839
19:30 | 3633 | 1235.6 | 871 | 0 | 170 | 1314.79 | 218 | 5146 | 0 | 794.42 | 2433.9 | 250 | 0 | 30 | 726
20:00 | 3652 | 1247.6 | 822 | 0 | 176 | 1311.62 | 218 | 5173 | 0 | 826.42 | 2404.9 | 250 | 0 | 14 | 279
20:30 | 3628.5 | 1237.1 | 798 | 0 | 169 | 1309.31 | 218 | 5207 | 0 | 820.92 | 2438.08 | 250 | 0 | 11.5 | 235.5
21:00 | 3605 | 1226.6 | 774 | 0 | 162 | 1307 | 218 | 5241 | 0 | 815.42 | 2471.26 | 250 | 0 | 9 | 192
21:30 | 3633 | 1223.1 | 774.5 | 0 | 161 | 1299.97 | 218 | 5212 | 0 | 814.42 | 2490.76 | 125 | 0 | 15.5 | 193
22:00 | 3661 | 1219.6 | 775 | 0 | 160 | 1292.94 | 218 | 5183 | 0 | 813.42 | 2510.26 | 0 | 0 | 22 | 194
22:30 | 3634 | 1217.55 | 822.5 | 0 | 162 | 1284.205 | 218.5 | 5163.5 | 0 | 814.92 | 2484.08 | 0 | 0 | 23 | 387
23:00 | 3607 | 1215.5 | 870 | 0 | 164 | 1275.47 | 219 | 5144 | 0 | 816.42 | 2457.9 | 0 | 0 | 24 | 580
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 01-09-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 147 | 71 | 340 | 192 | 1428 | 720 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 144 | 71 | 280 | 204 | 1442 | 714
2:00 | 117 | 66 | 240 | 202 | 1212 | 682 |  | Import | 0
3:00 | 116 | 64 | 250 | 200 | 1194 | 662
4:00 | 116 | 61 | 250 | 198 | 1212 | 662 | Ishurdi-Ghorashal Ckt-2 | Export | 3322036.36
5:00 | 114 | 64 | 230 | 206 | 1078 | 702
6:00 | 117 | 67 | 240 | 212 | 958 | 716 |  | Import | 0
7:00 | 117 | 67 | 224 | 206 | 924 | 732
8:00 | 134 | 73 | 268 | 200 | 1106 | 780 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 166 | 83 | 366 | 202 | 1282 | 826
10:00 | 189 | 85 | 440 | 220 | 1462 | 832 |  | Import | 0
11:00 | 167 | 86 | 374 | 232 | 1386 | 870
12:00 | 165 | 87 | 328 | 240 | 1482 | 878 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 149 | 79 | 320 | 220 | 1446 | 858
14:00 | 165 | 78 | 390 | 230 | 1584 | 894 |  | Import | 0
15:00 | 171 | 89 | 402 | 230 | 1512 | 854
16:00 | 166 | 86 | 362 | 214 | 1386 | 902 | Gopalganj-Aminbazar Ckt-1 | Export | 15010000
17:00 | 155 | 89 | 334 | 224 | 1344 | 918
18:00 | 138 | 75 | 346 | 234 | 1322 | 858 |  | Import | 0
18:30 | 162 | 81 | 404 | 246 | 1396 | 854
19:00 | 153 | 63 | 376 | 170 | 1398 | 804 | Gopalganj-Aminbazar Ckt-2 | Export | 15050000
19:30 | 129 | 51 | 326 | 212 | 1200 | 752
20:00 | 127 | 54 | 330 | 208 | 1144 | 750 |  | Import | 0
21:00 | 114 | 55 | 316 | 230 | 1078 | 752
22:00 | 95 | 49 | 256 | 204 | 934 | 704 |  | Total Export | 33382036.36
23:00 | 136 | 62 | 344 | 220 | 1092 | 754 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 01-09-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 367 | 04:00 | 264 | 02:00 | Madunaghat | 394 | 00:00 | 389 | 13:00
Amtali | 411 | 05:00 | 407 | 13:00 | Meghnaghat | 372 | 03:00 | 360 | 12:00
Ashuganj | 394 | 4:00 | 379 | 13:00 | Mirsorai | 394 | 11:00 | 383 | 12:00
Bhulta | 383 | 03:00 | 367 | 12:00 | Payra | 413 | 06:00 | 409 | 13:00
Bibiana | 376 | 04:00 | 370 | 16:00 | Rahanpur | 410 | 09:00 | 401 | 19:30
BIPTC | 406 | 05:00 | 398 | 19:00 | Rampal | 394 | 08:00 | 385 | 12:00
Bogura | 396 | 09:00 | 385 | 19:30
Gopalganj | 387 | 08:00 | 378 | 12:00
Kaliakoir | 375 | 06:00 | 343 | 14:00
Korerhat | 388 | 01:00 | 382 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 03:00 | 211 | 12:00 | Hasnabad | 220 | 03:00 | 209 | 12:00
AKSML | 231 | 06:00 | 225 | 12:00 | Hathazari | 231 | 00:00 | 227 | 12:00
Aminbazar | 225 | 04:00 | 212 | 12:00 | Ishurdi | 235 | 09:00 | 225 | 19:30
Ashuganj | 222 | 08:00 | 215 | 13:00 | Jhenaidah | 227 | 08:00 | 215 | 19:30
Ashuganj-400 | 222 | 08:00 | 215 | 13:00 | Kachua | 225 | 19:00 | 219 | 12:00
Baghabari | 232 | 08:00 | 224 | 19:30 | Kaliakoir | 220 | 03:00 | 209 | 12:00
Barapukuria | 227 | 09:00 | 222 | 22:00 | Keranigonj | 221 | 04:00 | 209 | 12:00
Barapukuria-230 | 227 | 09:00 | 222 | 22:00 | Khulna(S) | 225 | 09:00 | 218 | 22:00
Barapukuria(N) | 229 | 09:00 | 226 | 07:00 | Korerhat | 222 | 02:00 | 218 | 12:00
Barishal | 225 | 09:00 | 220 | 22:00 | Madunaghat | 236 | 03:00 | 232 | 11:00
Bheramara | 234 | 09:00 | 223 | 19:30 | Madunaghat-400 | 236 | 00:00 | 233 | 12:00
Bhulta | 218 | 03:00 | 208 | 12:00 | Maniknagar | 218 | 05:00 | 205 | 12:00
Bibiana | 214 | 03:00 | 211 | 12:00 | Meghnaghat | 225 | 03:00 | 216 | 11:00
BIPTC | 236 | 08:00 | 224 | 19:30 | Meghnaghat-400 | 221 | 04:00 | 211 | 12:00
Birulia | 223 | 04:00 | 211 | 12:00 | Mirsorai | 227 | 04:00 | 223 | 12:00
Bogura | 239 | 09:00 | 233 | 22:00 | Naogaon | 228 | 18:00 | 213 | 22:00
Bogura-400 | 239 | 18:00 | 233 | 19:30 | Purbasadipur | 225 | 09:00 | 219 | 22:00
Borhanuddin | 228 | 08:00 | 224 | 22:00 | Rajshahi | 234 | 09:00 | 223 | 19:30
BSRM | 223 | 02:00 | 219 | 12:00 | Rampal | 225 | 09:00 | 217 | 12:00
Charfasson | 229 | 11:00 | 225 | 22:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 223 | 04:00 | 219 | 12:00 | Rampura | 218 | 04:00 | 206 | 12:00
Cumilla(N) | 218 | 01:00 | 211 | 12:00 | Shikalbaha | 235 | 04:00 | 231 | 12:00
Faridpur | 220 | 09:00 | 214 | 21:00 | Shyampur | 228 | 07:00 | 208 | 12:00
Fenchuganj | 214 | 02:00 | 210 | 18:30 | Siddhirganj | 220 | 06:00 | 209 | 12:00
Feni | 221 | 04:00 | 216 | 12:00 | Sirajgonj | 236 | 09:00 | 231 | 12:00
Ghorashal | 220 | 00:00 | 215 | 12:00 | Sreepur | 219 | 00:00 | 214 | 12:00
Ghorashal-230 | 210 | 03:00 | 196 | 12:00 | Tongi | 211 | 01:00 | 195 | 11:00
Gopalganj | 220 | 08:00 | 215 | 12:00
GPH | 232 | 10:00 | 226 | 11:00
Haripur | 218 | 04:00 | 208 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 132 | 02:00 | 124 | 12:00 | Madaripur | 131 | 09:00 | 128 | 11:00
Agargaon | 131 | 03:00 | 122 | 12:00 | Madartek | 132 | 04:00 | 125 | 11:00
Agrabad | 135 | 23:00 | 129 | 11:00 | Madunaghat | 136 | 00:00 | 134 | 11:00
AKS | 132 | 19:30 | 128 | 15:00 | Magura | 136 | 08:00 | 127 | 19:30
Aminbazar | 130 | 04:00 | 119 | 12:00 | Mahasthangarh | 136 | 18:00 | 130 | 04:00
Amnura | 135 | 09:00 | 131 | 19:30 | Maijdee | 126 | 18:00 | 123 | 12:00
Ashuganj | 130 | 01:00 | 123 | 12:00 | Manikganj | 123 | 19:30 | 115 | 11:00
Ashuganj-230 | 131 | 02:00 | 128 | 11:00 | Maniknagar | 134 | 03:00 | 125 | 13:00
Bagerhat | 127 | 09:00 | 120 | 22:00 | Matarbari | 124 | 23:00 | 114 | 18:30
Bajitpur | 124 | 00:00 | 117 | 21:00 | Matuail | 130 | 14:00 | 122 | 12:00
Bakerganj | 133 | 09:00 | 128 | 19:00 | Metrorail_Motijheel | 134 | 03:00 | 125 | 13:00
Bakulia | 135 | 00:00 | 130 | 18:00 | Metrorail_Uttara | 132 | 07:00 | 114 | 12:00
Banani | 132 | 03:00 | 124 | 12:00 | Millgate | 126 | 03:00 | 115 | 12:00
Bangabhaban | 134 | 03:00 | 126 | 12:00 | Mirpur | 127 | 00:00 | 119 | 12:00
Barapukuria | 138 | 09:00 | 132 | 06:00 | Mirzapur | 127 | 09:00 | 120 | 14:00
Barguna | 132 | 08:00 | 127 | 22:00 | Mithapukur | 133 | 09:00 | 129 | 02:00
Barishal | 130 | 10:00 | 127 | 12:00 | MI_Cement | 130 | 04:00 | 119 | 12:00
Barishal-230 | 131 | 09:00 | 127 | 22:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 134 | 00:00 | 131 | 11:00 | Mogbazar | 134 | 05:00 | 125 | 12:00
Baroirhat | 129 | 00:00 | 127 | 12:00 | Mongla | 126 | 08:00 | 121 | 21:00
Bashundhara | 131 | 23:00 | 115 | 12:00 | Motijheel | 134 | 03:00 | 126 | 12:00
BashundharaCement | 127 | 01:00 | 120 | 20:00 | Muktagacha | 127 | 09:00 | 116 | 08:00
Beanibazar | 121 | 02:00 | 116 | 19:30 | Munshiganj | 126 | 00:00 | 120 | 12:00
Benapole | 135 | 08:00 | 121 | 19:30 | Muradnagar | 124 | 02:00 | 118 | 12:00
Bhaluka | 129 | 19:00 | 122 | 21:00 | Mymensingh | 126 | 09:00 | 110 | 21:00
Bhandaria | 129 | 07:00 | 121 | 22:00 | Nabinagar | 123 | 03:00 | 116 | 12:00
Bhangura | 132 | 07:00 | 128 | 11:00 | Naogaon | 137 | 18:00 | 128 | 22:00
Bheramara | 137 | 08:00 | 131 | 19:30 | Narail | 136 | 06:00 | 126 | 19:30
Bheramara(GK) | 137 | 01:00 | 131 | 19:30 | Narinda | 134 | 03:00 | 125 | 13:00
Bhulta | 123 | 07:00 | 118 | 11:00 | Narshingdi | 125 | 05:00 | 116 | 11:00
Bhulta-400 | 126 | 09:00 | 118 | 12:00 | Natore | 136 | 09:00 | 130 | 19:30
Birulia | 130 | 03:00 | 123 | 12:00 | Nawabganj | 132 | 02:00 | 126 | 12:00
Bog-Sherpur | 135 | 09:00 | 130 | 19:30 | Netrakona | 121 | 00:00 | 108 | 21:00
Bogura | 139 | 18:00 | 134 | 04:00 | New | 127 | 04:00 | 117 | 12:00
Bogura-230 | 139 | 18:00 | 135 | 02:00 | Niamatpur | 136 | 18:00 | 130 | 22:00
Brahmanbaria | 125 | 09:00 | 120 | 21:00 | Noapara | 132 | 09:00 | 127 | 12:00
Cantonment | 130 | 02:00 | 122 | 12:00 | Pabna | 135 | 09:00 | 129 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chandina | 127 | 02:00 | 123 | 12:00 | Palashbari | 133 | 18:00 | 127 | 12:00
Chandpur | 132 | 00:00 | 129 | 07:00 | Panchagarh | 137 | 09:00 | 131 | 22:00
Chandraghona | 136 | 00:00 | 134 | 12:00 | Patiya | 134 | 22:00 | 130 | 18:30
Chapai | 134 | 00:00 | 131 | 19:00 | Patnitala | 135 | 18:00 | 128 | 22:00
Charsaidpur | 127 | 01:00 | 118 | 13:00 | Patuakhali | 132 | 09:00 | 128 | 00:00
Chauddagram | 127 | 01:00 | 124 | 12:00 | Payra | 134 | 01:00 | 132 | 22:00
Chhatak | 120 | 07:00 | 113 | 19:30 | PHP | 129 | 00:00 | 126 | 12:00
Chowmuhani | 126 | 18:00 | 123 | 12:00 | Postogola | 131 | 03:00 | 123 | 12:00
Chuadanga | 135 | 09:00 | 124 | 19:30 | Pubail | 124 | 18:00 | 116 | 15:00
Coxsbazar | 129 | 12:00 | 117 | 18:00 | Purbachal | 131 | 02:00 | 123 | 12:00
Cumilla(N) | 127 | 02:00 | 122 | 12:00 | Purbasadipur | 136 | 09:00 | 132 | 22:00
Cumilla(S) | 130 | 06:00 | 123 | 12:00 | Rahanpur | 137 | 09:00 | 133 | 21:00
Daganbhuiyan | 127 | 00:00 | 125 | 12:00 | Rahanpur-400 | 137 | 09:00 | 134 | 19:30
Daudkandi | 123 | 04:00 | 115 | 21:00 | Rahim | 128 | 02:00 | 122 | 12:00
DhakaUniversity | 132 | 04:00 | 125 | 12:00 | Rajbari | 125 | 08:00 | 120 | 21:00
Dhamrai | 124 | 00:00 | 118 | 12:00 | Rajendrapur | 132 | 09:00 | 126 | 12:00
Dhanmondi | 132.5 | 04:00 | 124 | 12:00 | Rajshahi | 134 | 09:00 | 128 | 19:30
Dohazari | 130 | 02:00 | 126 | 12:00 | Rajshahi-230 | 135 | 09:00 | 128 | 19:30
Faridpur | 128 | 09:00 | 124 | 19:30 | Ramganj | 127 | 00:00 | 124 | 08:00
Fatullah | 131 | 04:00 | 121 | 12:00 | Rampur | 134 | 04:00 | 130 | 11:00
Fenchuganj | 128 | 09:00 | 124 | 18:30 | Rampura | 132 | 04:00 | 124 | 12:00
Feni | 129 | 02:00 | 125 | 12:00 | Rangamati | 135 | 06:00 | 133 | 11:00
Feni-230 | 128 | 00:00 | 125 | 12:00 | Rangpur | 132 | 09:00 | 126 | 20:00
Ghatail | 122 | 15:00 | 117 | 01:00 | Ruppur | 138 | 15:00 | 130 | 19:30
Ghorashal | 126 | 18:30 | 118 | 12:00 | Saidpur | 135 | 09:00 | 131 | 03:00
Goalpara | 135 | 09:00 | 130 | 12:00 | Santhia | 135 | 07:00 | 129 | 19:30
Gollamari | 134 | 08:00 | 129 | 12:00 | Satkhira | 132 | 09:00 | 125 | 12:00
Gopalganj | 130 | 09:00 | 126 | 12:00 | Satmasjid | 130 | 03:00 | 122 | 12:00
Gopalganj-400 | 131 | 09:00 | 128 | 12:00 | Savar | 128 | 03:00 | 118 | 12:00
Gulshan | 131 | 05:00 | 124 | 12:00 | SevenRings | 126 | 02:00 | 119 | 13:00
Halishahar | 135 | 22:00 | 129 | 11:00 | ShahCement | 127 | 01:00 | 121 | 12:00
Haripur | 129 | 04:00 | 122 | 12:00 | Shahjadpur | 136 | 04:00 | 132 | 13:00
HaripurSBU | 128 | 01:00 | 123 | 11:00 | Shahjibazar | 124 | 00:00 | 120 | 21:00
Hasnabad | 130 | 00:00 | 122 | 12:00 | Shahmirpur | 136 | 00:00 | 133 | 11:00
Hathazari | 136 | 19:30 | 133 | 11:00 | Shariatpur | 130 | 09:00 | 125 | 19:30
Hatirjheel | 132 | 03:00 | 124 | 12:00 | Sherpur | 129 | 19:30 | 112 | 01:00
Ishurdi | 139 | 09:00 | 131 | 19:30 | Shikalbaha | 125 | 00:00 | 122 | 14:00
Jaldhaka | 133 | 09:00 | 128 | 22:00 | Shikalbaha-230 | 136 | 05:00 | 133 | 13:00
Jamalpur | 132 | 19:30 | 116 | 03:00 | Shitalakhya | 130 | 04:00 | 119 | 12:00
Jashore | 136 | 08:00 | 120 | 21:00 | Sholosohor | 135 | 00:00 | 130 | 12:00
Jhenaidah | 138 | 08:00 | 129 | 19:30 | Shomvuganj | 120 | 00:00 | 114 | 12:00
Jhenaidah-230 | 139 | 08:00 | 129 | 19:30 | Shyampur | 130 | 08:00 | 123 | 12:00
Joydebpur | 123 | 18:30 | 114 | 15:00 | Shyampur-230 | 131 | 01:00 | 124 | 12:00
Joypurhat | 135 | 18:00 | 129 | 22:00 | Siddhirganj | 128 | 01:00 | 123 | 12:00
Juldah | 136 | 22:00 | 132 | 15:00 | Sirajganj | 131 | 09:00 | 125 | 19:30
Kabirpur | 127 | 03:00 | 112 | 12:00 | Sitakunda | 134 | 00:00 | 132 | 12:00
Kachua | 137 | 02:00 | 126 | 05:00 | Sonargaon | 124 | 00:00 | 119 | 11:00
Kaliakoir | 130 | 06:00 | 123 | 11:00 | Sreemongol | 125 | 06:00 | 119 | 21:00
Kaliganj | 137 | 07:00 | 128 | 19:30 | Sreepur | 133 | 00:00 | 127 | 21:00
Kallyanpur | 128 | 02:00 | 119 | 12:00 | Srinagar | 133 | 07:00 | 126 | 12:00
Kalurghat | 136 | 08:00 | 133 | 13:00 | SSM | 140 | 20:00 | 136 | 12:00
Kamrangirchar | 133 | 03:00 | 116 | 12:00 | Sunamganj | 118 | 09:00 | 111 | 19:30
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 124 | 04:00 | 120 | 00:00
Kasba | 123 | 01:00 | 117 | 12:00 | Sylhet_(South) | 122 | 01:00 | 119 | 18:30
Kazla | 134 | 04:00 | 125 | 13:00 | Tangail | 124 | 09:00 | 118 | 12:00
Keranigonj | 134 | 03:00 | 126 | 12:00 | Taraganj | 133 | 09:00 | 129 | 22:00
Khagrachori | 134 | 02:00 | 132 | 11:00 | Tasnim | 125 | 01:00 | 120 | 11:00
Khulna | 134 | 09:00 | 128 | 12:00 | Thakurgaon | 138 | 09:00 | 133 | 02:00
Khulna(S) | 135 | 09:00 | 130 | 12:00 | TK | 137 | 09:00 | 133 | 12:00
Khulshi | 133 | 05:00 | 128 | 12:00 | Tongi | 130 | 01:00 | 119 | 11:00
Kishoreganj | 124 | 09:00 | 114 | 21:00 | Ullahpara | 133 | 09:00 | 127 | 21:00
Kodda | 125 | 18:00 | 114 | 15:00 | Ullon | 132 | 23:00 | 124 | 12:00
Korerhat | 131 | 01:00 | 128 | 11:00 | Uttara | 128 | 04:00 | 115 | 15:00
KSRM | 137 | 19:30 | 130 | 12:00 | UttaraNew | 132 | 07:00 | 114 | 12:00
Kulaura | 127 | 09:00 | 123 | 18:30 | Zigatola | 133 | 03:00 | 126 | 12:00
Kurigram | 130 | 10:00 | 123 | 22:00
Kushtia | 137 | 09:00 | 128 | 19:30
Laksam | 128 | 18:00 | 125 | 12:00
Lakshmipur | 125 | 18:00 | 122 | 12:00
Lalbag | 133 | 03:00 | 126 | 12:00
Lalmonirhat | 130 | 07:00 | 124 | 00:00
Madanganj | 127 | 01:00 | 122 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division