## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: July 2026
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2026-07-01 |  | 2026-06-01 |  | 2025-07-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 16716.67 | 2026-07-02 | 16193.27 | 2026-06-25 | 16794 | 2025-07-23 | 17200.79 | 2026-05-20
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr.
2 | Minimum Generation (MW) | 11329.86 | 2026-07-10 | 11665.13 | 2026-06-19 | 9799.07 | 2025-07-25 | 11665.13 | 2026-06-19
|  |  | 08:00 Hr. |  | 10:00 Hr. |  | 6:00 |  | 10:00 Hr.
3 | Maximum Evening Peak Generation (MW) | 16716.67 | 2026-07-02 | 16193.27 | 2026-06-25 | 16794 | 2025-07-23 | 17200.79 | 2026-05-20
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr.
4 | Maximum Day Peak Generation (MW) | 15327.46 | 2026-07-02 | 14920 | 2026-06-30 | 14859 | 2025-07-23 | 15418.78 | 2026-05-20
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 Hr.
5 | Maximum Evening Peak Demand (MW) Estimated | 17266.7 | 2026-07-26 | 18354.59 | 2026-06-28 | 17099.14 | 2025-07-23 | 18354.59 | 2026-06-28
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 Hr.
6 | Average Generation (MW) at Evening Peak | 15613.7248 |  | 15362.4037 |  | 14953.5771 |  | 15373.711 | Sep-2025
7 | Average Generation (MW) at Day Peak | 14076.9597 |  | 14030.2117 |  | 13322.5084 |  | 14030.2117 | Jun-2026
8 | Maximum Power Import from India, BIPTC (MW) | 951 | 2026-07-09 | 976 | 2026-06-15 | 976 | 2025-07-01 | 981 | 2025-06-20
|  |  | 11:30 |  | 9:30 |  | 15:00 |  | 02:00:00
9 | Maximum Power Import from Tripura, India (MW) | 197 | 2026-07-04 | 194 | 2026-06-23 | 64 | 2025-07-13 | 213 | 2026-04-22
|  |  | 16:00 |  | 19:00 |  | 20:00 |  | 16:00:00
10 | Maximum Load Shed (MW) at Evening Peak | 2335 | 2026-07-29 | 2874 | 2026-06-27 | 812 | 2025-07-21 | 4395 | 2022-10-04
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14798.75 | 2026-07-29 | 15298.25 | 2026-06-27 | 15152.08 | 2025-07-21 | 16531.26 | 2026-05-21
|  |  | 21:00 Hr. |  | 21:00 Hr. |  | 21:00 |  | 21:00 Hr.
12 | Minimum Load Shed (MW) at Evening Peak | 30 | 2026-07-10 | 44 | 2026-06-21 | 0 | 2025-07-04 | 54 | 44788
|  |  | 21:00 Hr. |  |  |  | 21:00 | - | 21:00:00
13 | Generation During Min. Load Shed (MW) at Evening Peak | 14358.07 | 2026-07-10 | 14649.64 | 2026-06-21 | 13879 | 2025-07-04 | 15064.21 | 45905
|  |  | 21:00 Hr. |  |  |  | 21:00 | - | 21:00:00
14 | Maximum Load Shed (MW) at Day Peak | 1949 | 2026-07-30 | 2620 | 2026-06-21 | 190 | 2025-07-23 | 2675 | 45082
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | 12:00:00
15 | Generation During Max. Load Shed (MW) at Day Peak | 13611.74 | 2026-07-30 | 14398.75 | 2026-06-21 | 14859 | 2025-07-23 | 14859 | 45861
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | 12:00:00
16 | Minimum Load Shed (MW) at Day Peak | 15 | 2026-07-17 | 9 | 2026-06-10 | 0 | 2025-07-04 | 90 | 46090
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | 12:00 Hr.
17 | Generation During Min. Load Shed (MW) at Day Peak | 12954.44 | 2026-07-17 | 13966.46 | 2026-06-10 | 12021 | 2025-07-04 | 13966.46 | 46183
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 | - | 12:00 Hr.
18 | Nos. of Days Load Shed at Evening Peak | 31 |  | 30 |  | 24 |  | 31 | Aug-2022
19 | Nos. of Days Load Shed at Day Peak | 28 |  | 29 |  | 4 |  | 30 | Aug-2022
20 | Gross Generation of BPDB (MKWH) | 1143.3569 |  | 995.0699 |  | 1285.2058 |  | 3805.7195 | Sep-2019
21 | Station Use of BPDB (MKWH) | 26.7217 |  | 20.0516 |  | 114.435 |  | 206.7694 | Apr-2024
22 | Net Generation of BPDB (MKWH) | 1116.6352 |  | 975.0183 |  | 1170.7708 |  | 3681.055 | Sep-2019
23 | Net Generation of IPP (MKWH) | 2754.1536 |  | 2617.3181 |  | 3008.2106 |  | 6375.85 | Jul-2024
23b | Net Generation by Generation Companies | 4886.0001 |  | 4739.8645 |  | 2817.8548 |  | 4739.8645 | Jun-2026
24 | Net Generation of REB (MKWH) | 48.4553 |  | 53.7875 |  | 48.2102 |  | 171.4948 | Aug-2019
25 | Net Generation of Rental Power Plant (MKWH) | 90.0345 |  | 82.2671 |  | 135.6626 |  | 793.0297 | Jul-2018
26 | Total Net Generation (MKHWh) (Excluding Import) | 8895.2786 |  | 8468.2556 |  | 7180.7089 |  | 8626.1194 | Sep-2025
27 | Energy Generation by Gas (MKWH) | 3659.1497 |  | 3745.8602 |  | 4241.0786 |  | 4815.0058 | Jul-2021
28 | Energy Generation by Diesel (MKWH) | 9.5006 |  | 3.465 |  | 0.018 |  | 736.5643 | Jul-2018
29 | Energy Generation by Furnace Oil (MKWH) | 1077.9349 |  | 1014.0995 |  | 1124.286 |  | 2402.1611 | Jul-2022
30 | Energy Generation by Hydro (MKWH) | 128.8827 |  | 54.5607 |  | 148.0037 |  | 162.1321 | Aug-2025
31 | Energy Generation by Solar (MKWH) | 105.8874 |  | 114.6082 |  | 99.5917 |  | 149.0391 | Apr-2025
31b | Energy Generation by Wind (MKWH) | 20.4389 |  | 5.5723 |  | 14.5906 |  | 14.5906 | Jul-2025
32 | Energy Generation by Coal (MKWH) | 3920.2061 |  | 3550.1413 |  | 2943.4421 |  | 3550.1413 | Jun-2026
33 | Enegry Import from India (MKWH) | 1693.3611 |  | 1755.2156 |  | 1545.2637 |  | 1755.2156 | Jun-2026
34 | Monthly Load Factor (%) | 85.3709 |  | 87.8696 |  | 80.9643 |  | 92.6177 | Aug-2022

## QF-LDC-22
QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: July 2026
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 16716.67 | 2026-07-02 | 21:00 Hr.
Generation Period
| Dhaka | MW | 5769.29
| Chattogram | MW | 1636.3
| Cumilla | MW | 1571
| Mymensingh | MW | 1209
| Sylhet | MW | 685
a) | Total supply in East zone | MW | 10870.59
| Khulna | MW | 1888
| Barisal | MW | 526
| Rajshahi | MW | 1684.6
| Rangpur | MW | 1148
b) | Total supply in West zone | MW | 5246.6
c) | Total supply in both zone ( a+b) | MW | 16117.19
Ref: | 27.21.0000.603.16.087.20.987 | Date: 16/08/2026
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month: July 2026
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Maximum power Export through EWI/ NO-1
| a) Ishurdi end | AMPS | 628 | 2026-07-04 | 11:00
|  | MW | 240
| b) Ghorashal end | AMPS | 116 | 2026-07-14 | 21:00
|  | MW | 18
18 | Maximum power Import through EWI/ NO-1 |  |  | -
| a) Ishurdi end | AMPS | 114 | 2026-07-14 | 21:00
|  | MW | 18
| b) Ghorashal end | AMPS | 632 | 2026-07-04 | 11:00
|  | MW | 211
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ishurdi end | MWh | 4285.527 | 2026-07-09 | N/A
| b) Ghorashal end | MWh | 43.59 | 2026-07-14
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 43.49 | 2026-07-14
| b) Ghorashal end | MWh | 3951.27 | 2026-07-09 | N/A
21 | Total Energy Export through EWI/ NO-1
| a) Ishurdi end | MWh | 106096.0745
| b) Ghorashal end | MWh | 99.9287
22 | Total Energy Import through EWI/ NO-1
| a) Ishurdi end | MWh | 97.0182
| b) Ghorashal end | MWh | 102913.1922
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Maximum power Export through EWI/ NO-2
| a) Sirajganj end | AMPS | 1780 | 2026-07-11
|  | MW | 704
| b) Sreepur end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
25 | Maximum power Import through EWI/ NO-2 |  | - | -
| a) Sirajganj end | AMPS | 0 | N/A | N/A
|  | MW | 0 | N/A | N/A
| b) Sreepur end | AMPS | 1760 | 2026-07-11 | -
|  | MW | 677
26 | Daily Maximum Energy Export through EWI/NO-2
| a) Sirajganj end | MWh | 6998 | 2026-07-11 | -
| b) Sreepur end | MWh | 0 | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Sirajganj end | MWh | 0 | - | -
| b) Sreepur end | MWh | 12870 | 2026-07-11 | -
28 | Total Energy Export through EWI/ NO-2
| a) Sirajganj end | MWh | 345560 | - | -
| b) Sreepur end | MWh | 0 | - | -
29 | Total Energy Import through EWI/ NO-2
| a) Sirajganj end | MWh | 0 | - | -
| b) Sreepur end | MWh | 334724 | - | -
30 | Transmission loss of EWI/ NO-2 | % | 3.14% | - | -
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 3676 | 2026-07-09 | 0:00
|  | MW | 2348
| b) Aminbazar end | AMPS | 0
|  | MW | 0
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | 0
|  | MW | 0
| b) Aminbazar end | AMPS | 3666 | 2026-07-09 | 0:00
|  | MW | 2346
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 48150 | 2026-07-09 | N/A
| a) Aminbazar end | MWh | 0
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0 | - | N/A
| a) Aminbazar end | MWh | 47973 | 2026-07-09
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 1307220
| b) Aminbazar end (ckt-1 ) | MWh | 0
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | 0
| b) Aminbazar end (ckt-2 ) | MWh | 1301743
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.419
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: July 2026
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka 132/33kV | 01. Transformer- 01 | 2026-07-12 02:42 | 2026-07-12 02:55 | 0.0090278 | T | Tripped | 50 | 10.8333 | Power interruption
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-07-12 02:42 | 2026-07-12 02:55 | 0.0090278 | T | Tripped | 50 | 10.8333 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2026-07-25 12:27 | 2026-07-25 13:13 | 0.031944 | T | 33kV Boroibari feeder earth fault. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 230/132 kV T-1 | 2026-07-07 09:54 | 2026-07-07 10:39 | 0.03125 | T | Due to problem at 109-89B DS | 237 | 177.75 | Power interruption
Sreepur 230/132/33kV | 230/132 kV T-2 | 2026-07-07 09:54 | 2026-07-07 10:48 | 0.0375 | T | Due to problem at 109-89B DS. | 237 | 213.3 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-1 | 2026-07-31 07:20 | 2026-07-31 07:55 | 0.024306 | T | Earth Fault | 60 | 35 | Power interruption
Bajitpur 132/33kV | Tr-2(414T) | 2026-07-23 14:22 | 2026-07-23 15:19 | 0.039583 | E/O | High temperature maintenance | 20 | 19 | Power interruption
Bhaluka 132/33kV | 03. Transformer-03 | 2026-07-28 11:56 | 2026-07-28 12:43 | 0.032639 | E/O | 33 kv Y phase Bushing red hot minimize | 0 | 0 | No interruption
Joydebpur 132/33kV | GT-4 | 2026-07-25 10:58 | 2026-07-25 11:20 | 0.015278 | E/O | Oil Leakage Maintenance | 20 | 7.3333 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-07-08 17:08 | 2026-07-08 18:45 | 0.067361 | E/O | 33 kV Feeder red hot maintenance | 80 | 129.3333 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2026-07-21 22:28 | 2026-07-22 01:13 | 0.11458 | E/O | 33 kV Riser Connection to the 33 kV Bus | 70 | 192.5 | Power interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2026-07-04 15:02 | 2026-07-04 16:50 | 0.075 | E/O | 33 kv jumper repair work by pbs | 60 | 108 | Power interruption
|  |  | Total : | 0.4875 |  | Unserved Energy: |  | 903.8833
Dhaka (South) Grid Circle :
Ghorashal 230kV | TARFO-2 | 2026-07-14 12:17 | 2026-07-14 12:55 | 0.026389 | T | WTI & OTI | 101 | 63.9667 | Power interruption
Ghorashal 230kV | TARFO-2 | 2026-07-24 01:47 | 2026-07-24 04:21 | 0.10694 | T | Post Insulator flasing and bus Ds. | 80 | 205.3333 | Power interruption
Hasnabad 132/33kV | 33kv Main Bus | 2026-07-09 01:59 | 2026-07-09 02:37 | 0.026389 | T | Nawabganj-2 33Kv feeder fault. | 46 | 29.1333 | Power interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 | 2026-07-09 01:59 | 2026-07-09 02:37 | 0.026389 | T | Nawabganj -2 33kv feeder fault | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2026-07-09 01:59 | 2026-07-09 02:37 | 0.026389 | T | Over current, Earth fault. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2026-07-10 11:58 | 2026-07-10 12:10 | 0.0083333 | T | Nowabganj-2 33 kv load side R phase conductor broke down | 28 | 5.6 | Power interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 | 2026-07-10 11:58 | 2026-07-10 12:10 | 0.0083333 | T | Nowabganj-2 33kv feeder load side R Phase conductor broke down | 28 | 5.6 | Power interruption
Hasnabad 230/132kV | AUTO TR-1 | 2026-07-01 18:41 | 2026-07-01 20:27 | 0.073611 | T | false signal. | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-1 | 2026-07-02 06:08 | 2026-07-02 09:28 | 0.13889 | T | unknown | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-1 | 2026-07-02 12:10 | 2026-07-02 21:05 | 0.37153 | T | Tripped | 0 | 0 | No interruption
Maniknagar 230/132kV | Auto Transformer-01(705T) | 2026-07-22 02:18 | 2026-07-22 02:37 | 0.013194 | T | Over Current (W1,W2 TOC I2BLC) | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-1 | 2026-07-13 00:52 | 2026-07-13 01:32 | 0.027778 | T | 33 kv PT blast of khusumhati feeder. | 25 | 16.6667 | Power interruption
Nawabganj 132/33kV | TR-2 | 2026-07-13 00:52 | 2026-07-13 04:21 | 0.14514 | T | 33 kv PT blast of khusumhati feeder. | 25 | 87.0833 | Power interruption
Madanganj 132/33kV | GT-1 | 2026-07-25 14:39 | 2026-07-25 21:44 | 0.29514 | E/O | 33kv busbar faulty sound occuring | 0 | 0 | No interruption
Maniknagar 230/132kV | Auto Transformer-02 (715T) | 2026-07-22 21:18 | 2026-07-23 01:07 | 0.15903 | E/O | Red hot Repaire. | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-1 | 2026-07-11 18:10 | 2026-07-11 19:07 | 0.039583 | E/O | PBS Red hot | 30 | 28.5 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-07-26 15:28 | 2026-07-26 16:26 | 0.040278 | E/O | PBS 33KV Everest Feeder bypass blade changing | 55 | 53.1667 | Power interruption
|  |  | Total : | 1899-12-31 12:48 |  | Unserved Energy: |  | 495.05
Chattogram Grid Circle :
Bakulia 132/33kV | T-1 (402T) | 2026-07-16 18:44 | 2026-07-17 10:32 | 0.65833 | T | 33 kv feeder trip by O/C . | 0 | 0 | No interruption
Coxsbazar 132/33kV | T3 | 2026-07-26 12:58 | 2026-07-26 13:38 | 0.027778 | T | 33kv Teknaf feeder, 33kv Sador switching feeder O/C fault | 58 | 38.6667 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2026-07-09 13:23 | 2026-07-09 13:40 | 0.011806 | T | Due to Bandarban 33 KV feeder . | 11 | 3.1167 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2026-07-17 20:35 | 2026-07-17 20:50 | 0.010417 | T | Due to Banderban 33kv Loop Broken. | 73 | 18.25 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2026-07-21 10:43 | 2026-07-21 10:59 | 0.011111 | T | Bandarban 33kv Feeder O/C & E/F | 55 | 14.6667 | Power interruption
Dohazari 132/33kV | Power Transformer -T-1 | 2026-07-24 21:29 | 2026-07-24 21:41 | 0.0083333 | T | Due to Banshkhali 33 KV feeder O/C & E/F | 35 | 7 | Power interruption
GPH 230/33kV | Transformer-01(D05) | 2026-07-10 04:06 | 2026-07-10 09:07 | 0.20903 | T | prv trip | 0 | 0 | No interruption
Juldah 132/33kV | 133/33 KV T-2 416T | 2026-07-10 07:29 | 2026-07-10 08:40 | 0.049306 | T |  | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2026-07-09 04:41 | 2026-07-09 15:13 | 0.43889 | T | B-phase cable blust at LT side. | 0 | 0 | No interruption
Sitakunda 132/33kV | TRAFO-2 | 2026-07-05 19:04 | 2026-07-05 20:09 | 0.045139 | T | Over Current , EARTH Fault | 26 | 28.1667 | Power interruption
Coxsbazar 132/33kV | 405T-T1 | 2026-07-07 12:25 | 2026-07-07 13:12 | 0.032639 | E/O | Bus shutdown for kolatoli-2 3kV post inhalator sparking | 20 | 15.6667 | Power interruption
Coxsbazar 132/33kV | 415T-T2 | 2026-07-07 12:25 | 2026-07-07 13:13 | 0.033333 | E/O | Kolatoli _2 33kV post inhalator sparking | 20 | 16 | Power interruption
Halishahar 132/33kV | 425T(TR-3) | 2026-07-26 16:32 | 2026-07-26 17:14 | 0.029167 | E/O | 33 KV PDB incomer transfomer T-03 R-phase cable faulty work. | 10 | 7 | Power interruption
KSRM 132/33kV | Transformer-02 | 2026-07-18 09:38 | 2026-07-18 14:47 | 0.21458 | E/O | red hot maintenance. check every junction point., cleaning. | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2026-07-08 15:24 | 2026-07-08 15:57 | 0.022917 | E/O | Pdb incomer -3 ct joint red hot. | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2026-07-09 00:29 | 2026-07-09 00:52 | 0.015972 | E/O | PDB red hot maintenance in their CT section. | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-02(516T) | 2026-07-19 09:50 | 2026-07-19 10:47 | 0.039583 | E/O | High temperature maintenance | 0 | 0 | No interruption
Khagrachori 132/33kV | TR-1 | 2026-07-12 17:14 | 2026-07-12 17:54 | 0.027778 | E/O | Emergency shutdown on TR-01 for removing red hot at 33 kV CT(B-ph) | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-1(507T) | 2026-07-09 11:14 | 2026-07-09 20:34 | 0.38889 | E/O | Due to Noapara feeder maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | TR-1(507T) | 2026-07-09 23:11 | 2026-07-10 00:17 | 0.045833 | E/O |  | 0 | 0 | No interruption
Sitakunda 132/33kV | TRAFO-1 | 2026-07-31 10:05 | 2026-07-31 11:53 | 0.075 | E/O | PDB End Isolator and ACR Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 09:30 |  | Unserved Energy: |  | 148.5333
Cumilla Grid Circle :
Chowmuhani 230/132/33kV | TR1-415T | 2026-07-15 13:30 | 2026-07-15 13:53 | 0.015972 | T | Short ckt at 33 kV Bus | 50 | 19.1667 | Power interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-07-15 13:30 | 2026-07-15 13:45 | 0.010417 | T | Short ckt at 33 kV Bus | 50 | 12.5 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2026-07-07 07:16 | 2026-07-07 07:26 | 0.0069444 | T | 33Kv feeder fault | 30 | 5 | Power interruption
Cumilla(S) 132/33kV | TR-4 | 2026-07-07 07:16 | 2026-07-07 07:26 | 0.0069444 | T | 33Kv Feeder Fault | 30 | 5 | Power interruption
Cumilla(S) 132/33kV | TR-3 | 2026-07-19 14:23 | 2026-07-19 14:43 | 0.013889 | T | 33 KV Donaitori feeder fault(PDB) | 40 | 13.3333 | Power interruption
Cumilla(S) 132/33kV | TR-4 | 2026-07-19 14:23 | 2026-07-19 14:43 | 0.013889 | T | 33 KV Donaotori feeder fault(PDB) | 40 | 13.3333 | Power interruption
Fenchuganj 230/132/33kV | TR-01 | 2026-07-29 06:57 | 2026-07-29 08:21 | 0.058333 | T |  | 10 | 14 | Power interruption
Fenchuganj 230/132/33kV | TR-01 | 2026-07-29 16:05 | 2026-07-29 16:21 | 0.011111 | T | Earth Fault | 12 | 3.2 | Power interruption
Fenchuganj 230/132/33kV | TR-01 | 2026-07-29 16:40 | 2026-07-29 16:49 | 0.00625 | T | Earth Fault | 12 | 1.8 | Power interruption
Feni 132/33kV | T-1(405T) | 2026-07-13 17:04 | 2026-07-13 18:11 | 0.046528 | T | Due to BPDB sultanpur 33kv feeder | 42 | 46.9 | Power interruption
Feni 132/33kV | T-1(405T) | 2026-07-16 08:20 | 2026-07-16 08:35 | 0.010417 | T | 33KV feeder fault | 32 | 8 | Power interruption
Kulaura 132/33kV | TR-1 AB | 2026-07-30 18:28 | 2026-07-30 18:50 | 0.015278 | T | 33KV PBS feeder fault | 20 | 7.3333 | Power interruption
Ramganj 132/33kV | Transformer -02 | 2026-07-08 19:21 | 2026-07-08 19:27 | 0.0041667 | T | Oil temp. high trip | 30 | 3 | Power interruption
Sylhet 132/33kV | T2 | 2026-07-30 19:28 | 2026-07-30 19:31 | 0.0020833 | T | over current c phase. | 60 | 3 | Power interruption
Chowmuhani 230/132/33kV | TR3 | 2026-07-13 21:28 | 2026-07-14 00:59 | 0.14653 | E/O | 33kV T2-T3 BUS Section DS loop maintenance | 40 | 140.6667 | Power interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-07-15 17:28 | 2026-07-15 19:01 | 0.064583 | E/O | 33 kv bus loop maintenance work | 40 | 62 | Power interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-07-15 20:10 | 2026-07-15 21:10 | 0.041667 | E/O | TR3 33 kv Y bushing red hot maintenence | 40 | 40 | Power interruption
Chowmuhani 230/132/33kV | TR3-435T | 2026-07-17 10:30 | 2026-07-17 11:59 | 0.061806 | E/O | Primary B-phase red hot maintenance | 25 | 37.0833 | Power interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2026-07-19 14:04 | 2026-07-19 15:18 | 0.051389 | E/O | 33 KV Feeder Line DS red hot maintenance | 12 | 14.8 | Power interruption
Lakshmipur 132/33kV | Transformer-2 | 2026-07-10 12:34 | 2026-07-10 16:39 | 0.17014 | E/O | Redhot Maintenance Work. | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-1 | 2026-07-10 17:09 | 2026-07-10 18:23 | 0.051389 | E/O | Redhot work Maintenance. | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-2 | 2026-07-17 22:11 | 2026-07-18 00:59 | 0.11667 | E/O | Red Hot maintenance | 0 | 0 | No interruption
Lakshmipur 132/33kV | Transformer-1 | 2026-07-18 01:07 | 2026-07-18 03:12 | 0.086806 | E/O | Red Hot Maintenance | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-02 | 2026-07-28 18:49 | 2026-07-28 20:27 | 0.068056 | E/O | Red hot maintenance . | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 01:57 |  | Unserved Energy: |  | 450.1167
Khulna Grid Circle :
Barguna 132/33kV | Transformer-1 | 2026-07-02 03:18 | 2026-07-02 03:42 | 0.016667 | T | Barguna BREB-1 (barguna pbs) feeder fault ( there is a fire at the substation). | 10 | 4 | Power interruption
Barguna 132/33kV | Transformer-2 | 2026-07-02 03:18 | 2026-07-02 03:42 | 0.016667 | T | Barguna BREB-1 (barguna pbs) feeder fault ( there is a fire at the substation). | 10 | 4 | Power interruption
Barguna 132/33kV | Transformer-2 | 2026-07-07 18:45 | 2026-07-07 19:58 | 0.050694 | T | BREB -1, 33 kV Feeder PT blast | 0 | 0 | No interruption
Barguna 132/33kV | Transformer-1 | 2026-07-07 18:45 | 2026-07-07 18:59 | 0.0097222 | T | BREB -1, 33 kV Feeder PT blast | 0 | 0 | No interruption
Barishal 132/33kV | T-1 (405T) | 2026-07-16 10:03 | 2026-07-16 10:14 | 0.0076389 | T | 33kV Dopdapia-2 (WZPDCL) feeder fault-E/F | 53 | 9.7167 | Power interruption
Barishal 132/33kV | T-2 (415T) | 2026-07-16 10:03 | 2026-07-16 10:14 | 0.0076389 | T | 33kV Dopdapia-2 (WZPDCL) feeder fault-E/F | 33 | 6.05 | Power interruption
Barishal 230/132kV | T-4 | 2026-07-03 11:32 | 2026-07-03 12:40 | 0.047222 | T | 33kv korapur feeder fault | 34 | 38.5333 | Power interruption
Barishal 230/132kV | T-5 | 2026-07-03 11:32 | 2026-07-03 11:56 | 0.016667 | T | 33Kv korapur feeder fault | 34 | 13.6 | Power interruption
Barishal 230/132kV | T-4 | 2026-07-21 06:21 | 2026-07-21 06:46 | 0.017361 | T | Over current Tripping due to 33kv Sarupkhathi-2 feeder fault. | 36 | 15 | Power interruption
Barishal 230/132kV | T-5 | 2026-07-21 06:21 | 2026-07-21 06:44 | 0.015972 | T | Over current tripping due to 33kv Sarupkathi-2 feeder fault | 36 | 13.8 | Power interruption
Goalpara 132/33kV | T-6 | 2026-07-01 07:42 | 2026-07-01 11:13 | 0.14653 | T |  | 0 | 0 | No interruption
Gopalganj 132/33kV | T2 | 2026-07-10 05:45 | 2026-07-10 06:15 | 0.020833 | T | Reb-7 feeder fault. (Loop damaged) | 15 | 7.5 | Power interruption
Gopalganj 132/33kV | T1 | 2026-07-10 05:46 | 2026-07-10 06:15 | 0.020139 | T | REB-7 feeder fault.(loop damaged) | 15 | 7.25 | Power interruption
Khulna (C) | TR-1 425T | 2026-07-27 07:07 | 2026-07-27 07:31 | 0.016667 | T | For 33kv satkhira feeder | 10 | 4 | Power interruption
Khulna (C) | Tr-3 405T | 2026-07-28 12:38 | 2026-08-02 13:15 | 1900-01-04 00:37 | T | TR3 132/33KV under ground cable Burn. | 0 | 0 | No interruption
Madaripur 132/33kV | T2-415T | 2026-07-21 07:35 | 2026-07-21 08:01 | 0.018056 | T | Tripped | 61 | 26.4333 | Power interruption
Madaripur 132/33kV | T1-405T | 2026-07-21 07:35 | 2026-07-21 08:05 | 0.020833 | T | Tripped | 0 | 0 | No interruption
Mongla 132/33kV | T-1 | 2026-07-03 18:59 | 2026-07-03 19:15 | 0.011111 | T | Tripped | 7 | 1.8667 | Power interruption
Rajbari 132/33kV | Transformer-2 | 2026-07-08 13:23 | 2026-07-08 13:33 | 0.0069444 | T | 33kV Binodpur wz feeder fault. | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-1 | 2026-07-08 13:23 | 2026-07-08 13:34 | 0.0076389 | T | 33kV Binodpur wz feeder fault. | 0 | 0 | No interruption
Satkhira 132/33kV | Transformer-2 (T-2) | 2026-07-24 07:59 | 2026-07-24 12:55 | 0.20556 | T | Trip for PRD | 0 | 0 | No interruption
Barishal 230/132kV | T-5 | 2026-07-20 21:13 | 2026-07-20 23:02 | 0.075694 | E/O | 33 kV Mehendiganj Feeder red hot maintenance work by PBS | 46 | 83.5667 | Power interruption
Benapole 132/33kV | Transformer-1(406T) | 2026-07-16 06:08 | 2026-07-16 08:37 | 0.10347 | E/O | 33 KV Incomer-1 source DS R-phase Red hot maintenance. | 0 | 0 | No interruption
Benapole 132/33kV | Transformer-1(406T) | 2026-07-30 06:34 | 2026-07-30 09:26 | 0.11944 | E/O | Tr-1 NIFPS Fire extinguishing system signal remove. | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-1 | 2026-07-18 13:01 | 2026-07-18 14:09 | 0.047222 | E/O | oil leakage maintenance work by G2G. | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-1 | 2026-07-15 10:09 | 2026-07-15 10:44 | 0.024306 | E/O | Emergency Maintenance On DS -403M. | 0 | 0 | No interruption
Noapara 132/33kV | T-1 | 2026-07-27 18:09 | 2026-07-27 19:03 | 0.0375 | E/O | 33kv buss shutdown due to reb-3 jamper loop out. | 0 | 0 | No interruption
Noapara 132/33kV | Bus Section-1 | 2026-07-27 18:17 | 2026-07-27 19:01 | 0.030556 | E/O | 33kv buss shutdown due to reb-3 jamper loop out. | 25 | 18.3333 | Power interruption
|  |  |  | 1900-01-05 03:28 |  | Unserved Energy: |  | 253.65
HVDC Grid Circle :
BIPTC | 20D09C 20MVA | 2026-07-01 13:50 | 2026-07-01 16:34 | 0.11389 | T | Tripped by Buccholz Relay | 0 | 0 | No interruption
BIPTC | Block-01, Trafo-01 | 2026-07-01 13:50 | 2026-07-01 16:34 | 0.11389 | T | Tripped for it's Source (20 MVA Trafo) Trip | 0 | 0 | No interruption
BIPTC | Block-02, Trafo-01 | 2026-07-01 13:50 | 2026-07-01 16:34 | 0.11389 | T | Tripped for it's Source (20 MVA Trafo) Trip | 0 | 0 | No interruption
BIPTC | 20D10A 20MVA | 2026-07-02 06:20 | 2026-07-02 10:28 | 0.17222 | T | Tripped By PRV | 0 | 0 | No interruption
BIPTC | Block-02, Trafo-02 | 2026-07-02 06:20 | 2026-07-02 10:28 | 0.17222 | T | Tripped by Source Trip | 0 | 0 | No interruption
BIPTC | Block-01, Trafo-02 | 2026-07-02 06:20 | 2026-07-02 10:28 | 0.17222 | T | Tripped by Source Trip | 0 | 0 | No interruption
BIPTC | 10CF14 | 2026-07-04 10:15 | 2026-07-04 13:18 | 0.12708 | T | ACF C1 unbalence 60/61 | 0 | 0 | No interruption
BIPTC | 20DF44 | 2026-07-08 06:25 | 2026-07-08 12:41 | 0.26111 | T |  | 0 | 0 | No interruption
BIPTC | 20DF24 | 2026-07-10 16:24 | 2026-07-12 12:39 | 1899-12-31 20:15 | T |  | 0 | 0 | No interruption
BIPTC | 10CF16 | 2026-07-11 02:35 | 2026-07-11 12:24 | 0.40903 | T | Tripped by C1 Unbalance CPR04. | 0 | 0 | No interruption
BIPTC | 20DF24 | 2026-07-17 15:45 | 2026-07-19 10:43 | 1899-12-31 18:58 | T | Impedence 21R trip | 0 | 0 | No interruption
Bheramara(GK) 132/33kV | TR-1 | 2026-07-31 06:28 | 2026-07-31 07:00 | 0.022222 | T | fault due to 33kv Douloatpur feeder | 0 | 0 | No interruption
Bheramara(GK) 132/33kV | TR-2 | 2026-07-31 06:28 | 2026-07-31 07:00 | 0.022222 | T | Fault due to 33KV Douloatpur Feeder | 0 | 0 | No interruption
Ishurdi 132/33kV | 132/33 kV T-3 | 2026-07-27 19:15 | 2026-07-27 19:30 | 0.010417 | T |  | 25 | 6.25 | Power interruption
Jashore 132/33kV | T-1 | 2026-07-13 11:59 | 2026-07-13 12:30 | 0.021528 | T | 33 Kv Feeder Fault (new town feeder) Of WZPDCL . | 45 | 23.25 | Power interruption
Jashore 132/33kV | T-2 | 2026-07-13 11:59 | 2026-07-13 12:30 | 0.021528 | T | 33 Kv Feeder Fault (new town feeder) Of WZPDCL . | 45 | 23.25 | Power interruption
Jashore 132/33kV | Cap. Bank-1 | 2026-07-13 11:59 | 2026-07-13 21:00 | 0.37569 | T |  | 0 | 0 | No interruption
Pabna 132/33kV | T-1 | 2026-07-28 17:28 | 2026-07-28 17:38 | 0.0069444 | T | 33 KV Pailanpur Trip ( O/C+ E/F) | 35 | 5.8333 | Power interruption
Shahjadpur 132/33kV | T-2(415T) | 2026-07-04 18:48 | 2026-07-04 21:45 | 0.12292 | T | 33kv Bera-Faridpur feeder OC & EF -এ ট্রিপ করায় 132 kv T-2 X-Former LV(OC & EF) -এ ট্রিপ করে । | 0 | 0 | No interruption
BIPTC | 20DF11 | 2026-07-23 14:47 | 2026-07-23 15:34 | 0.032639 | E/O | Shutdow is taken for cleaning grass and weeds inside the filter bank | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-07-05 21:06 | 2026-07-05 21:43 | 0.025694 | E/O | Red hot | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-07-11 22:32 | 2026-07-11 22:59 | 0.01875 | E/O | Red hot | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-07-12 14:53 | 2026-07-12 18:04 | 0.13264 | E/O | 33 kv PBS feeder red hot remove | 12 | 38.2 | Power interruption
Jashore 132/33kV | T-1 | 2026-07-02 05:42 | 2026-07-02 08:10 | 0.10278 | E/O | Redhot Maintanance | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-3 | 2026-07-11 07:30 | 2026-07-11 09:36 | 0.0875 | E/O | For, Maintainance of 33kv 'R' phase Redhot at CB input side. | 0 | 0 | No interruption
Jhenaidah 132/33kV | Transformer T-2 | 2026-07-18 06:40 | 2026-07-18 09:35 | 0.12153 | E/O | 33kv T2A DS TO BUS LOOP CHANGE WORK. | 0 | 0 | No interruption
Kushtia 132/33kV | T-3 | 2026-07-03 10:17 | 2026-07-03 11:12 | 0.038194 | E/O | 33kv Kumarkhali feeder source side red hot maintenance | 15 | 13.75 | Power interruption
Kushtia 132/33kV | T-1 | 2026-07-03 10:18 | 2026-07-03 11:11 | 0.036806 | E/O | 33 kv kumarkhali feeder red hot maintenance | 0 | 0 | No interruption
Kushtia 132/33kV | T-1 | 2026-07-05 09:25 | 2026-07-05 10:07 | 0.029167 | E/O | Old power cable remove from auxiliary transformer | 0 | 0 | No interruption
Kushtia 132/33kV | T-2 | 2026-07-08 21:53 | 2026-07-09 00:14 | 0.097917 | E/O | Mazompur 33 kv fedeer's bus D/S red hot maintenance | 26.5 | 62.275 | Power interruption
Kushtia 132/33kV | T-3 | 2026-07-28 15:10 | 2026-07-28 16:17 | 0.046528 | E/O | Red Hot maintenance By PBS | 10 | 11.1667 | Power interruption
Shahjadpur 132/33kV | T-3(425T) | 2026-07-05 15:52 | 2026-07-05 17:35 | 0.071528 | E/O | Maintenance work for nesco | 35 | 60.0833 | Power interruption
Shahjadpur 132/33kV | T-3(425T) | 2026-07-05 20:00 | 2026-07-05 20:30 | 0.020833 | E/O | Red hot maintenance work. | 20 | 10 | Power interruption
|  |  | Total : | 1900-01-05 18:08 |  | Unserved Energy: |  | 254.0583
Bogura Grid Circle:
Joypurhat 132/33kV | Transformer T-4 (437 T) | 2026-07-09 13:13 | 2026-07-09 18:19 | 0.2125 | T | P R D Trip | 0 | 0 | No interruption
Natore 132/33kV | TR-1 (405 T) | 2026-07-06 23:41 | 2026-07-08 13:23 | 1899-12-31 13:42 | T | Tripped | 0 | 0 | No interruption
Natore 132/33kV | TR-2 (415 T) | 2026-07-06 23:41 | 2026-07-07 06:48 | 0.29653 | T | Tripped | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-07-01 20:31 | 2026-07-01 21:09 | 0.026389 | T | 33 kV PBS Side Auxiliary transformer flushing. | 21 | 13.3 | Power interruption
Palashbari 132/33kV | TR1-414T | 2026-07-30 21:15 | 2026-07-30 21:55 | 0.027778 | T | chatra 33kv feeder fault | 35 | 23.3333 | Power interruption
Palashbari 132/33kV | TR2-404T | 2026-07-30 21:15 | 2026-07-30 21:30 | 0.010417 | T | chatra 33 Kv Feeder Fault | 35 | 8.75 | Power interruption
Rajshahi 230/132/33kV | 132/33 kV T-01 (406T) | 2026-07-16 16:27 | 2026-07-16 17:14 | 0.032639 | T | Nesco feeder faulty | 50 | 39.1667 | Power interruption
Rajshahi 230/132/33kV | 132/33 kV T-02 (416T) | 2026-07-16 16:27 | 2026-07-16 17:15 | 0.033333 | T | Nesco feeder faulty | 50 | 40 | Power interruption
Sirajganj 132/33kV | T3-(435) | 2026-07-27 17:24 | 2026-07-27 17:59 | 0.024306 | T | 33kv Economic zone (pbs) feeder CT and CB Blast. | 20 | 11.6667 | Power interruption
Sirajganj 132/33kV | T4-(445) | 2026-07-27 17:24 | 2026-07-27 17:59 | 0.024306 | T | Economic zone 33 kv feeder (pbs) CB and CT Blast. | 20 | 11.6667 | Power interruption
Barapukuria 230/132/33kV | 132/33 KV T-5, 424T | 2026-07-21 10:17 | 2026-07-21 11:53 | 0.066667 | E/O | emergency maintenance 33kv DS | 0 | 0 | No interruption
Chapai 132/33kV | T-2 (415T) | 2026-07-08 13:16 | 2026-07-08 15:10 | 0.079167 | E/O | Section bus DS maintenance. | 38 | 72.2 | Power interruption
Chapai 132/33kV | T-3 (425T) | 2026-07-08 13:16 | 2026-07-08 15:57 | 0.11181 | E/O | Section bus DS maintenance | 0 | 0 | No interruption
Chapai 132/33kV | T-4 (435T) | 2026-07-13 17:05 | 2026-07-13 18:37 | 0.063889 | E/O | High temperature, Maintenance | 7 | 10.7333 | Power interruption
Kurigram 132/33kV | Transformer T-1 (Tr-403T) | 2026-07-28 11:01 | 2026-07-28 11:43 | 0.029167 | E/O | LT Bushing Redhot maintenance of Transformer T-1 | 0 | 0 | No interruption
Mithapukur 132/33kV | TR-2 (414T) | 2026-07-03 11:24 | 2026-07-03 15:19 | 0.16319 | E/O | 33 kv TR-2 isolator er insulator maintenance work. | 20 | 78.3333 | Power interruption
Mithapukur 132/33kV | TR-2 (414T) | 2026-07-16 08:34 | 2026-07-16 09:29 | 0.038194 | E/O | Red hot | 20 | 18.3333 | Power interruption
Naogaon 132/33kV | T-2 33kV BUS | 2026-07-10 08:16 | 2026-07-10 10:37 | 0.097917 | E/O | Red hot maintenance. | 10 | 23.5 | Power interruption
Natore 132/33kV | TR-4 (435 T) | 2026-07-12 00:07 | 2026-07-12 00:50 | 0.029861 | E/O | Emergency maintenance | 15 | 10.75 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-07-10 21:18 | 2026-07-10 22:44 | 0.059722 | E/O | Hot Spot maintenance. | 0 | 0 | No interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-07-12 14:48 | 2026-07-12 16:21 | 0.064583 | E/O | T1 33kv pbs bus redhot maintenance. | 17 | 26.35 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-07-19 16:16 | 2026-07-19 18:02 | 0.073611 | E/O | Porsha 33 Kv feeder red hot maintenance. | 16 | 28.2667 | Power interruption
Niamatpur 132/33kV | Transformer-1(407T) | 2026-07-22 17:28 | 2026-07-22 18:43 | 0.052083 | E/O | Emergency maintenance | 24 | 30 | Power interruption
Niamatpur 132/33kV | Bus-1 | 2026-07-27 07:42 | 2026-07-27 11:00 | 0.1375 | E/O | Emergency maintenance | 0 | 0 | No interruption
Palashbari 132/33kV | TR2-404T | 2026-07-06 07:39 | 2026-07-06 08:41 | 0.043056 | E/O | Red hot Maintenance | 0 | 0 | No interruption
Palashbari 132/33kV | TR2-404T | 2026-07-07 17:30 | 2026-07-07 18:06 | 0.025 | E/O | Emergency maintenance | 20 | 12 | Power interruption
Palashbari 132/33kV | TR1-414T | 2026-07-07 20:20 | 2026-07-07 21:10 | 0.034722 | E/O | Red hot | 30 | 25 | Power interruption
Palashbari 132/33kV | TR2-404T | 2026-07-07 20:20 | 2026-07-07 21:10 | 0.034722 | E/O | Red hot | 30 | 25 | Power interruption
Palashbari 132/33kV | TR2-404T | 2026-07-12 14:35 | 2026-07-12 15:56 | 0.05625 | E/O | Raizer Maintenance | 60 | 81 | Power interruption
Palashbari 132/33kV | TR2-404T | 2026-07-15 14:42 | 2026-07-15 16:07 | 0.059028 | E/O | T2 33 kv bus Red hot maintenance | 60 | 85 | Power interruption
Palashbari 132/33kV | TR1-414T | 2026-07-31 14:28 | 2026-07-31 15:29 | 0.042361 | E/O | red hot maintenance | 20 | 20.3333 | Power interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2026-07-16 00:23 | 2026-07-16 00:49 | 0.018056 | E/O | 33 KV Bus DS Maintenance Work By NPBS-2 | 15 | 6.5 | Power interruption
Rajshahi 132/33kV | Transformer T-3 (425T) | 2026-07-16 15:01 | 2026-07-16 16:10 | 0.047917 | E/O | Broken clam change | 0 | 0 | No interruption
Rajshahi 132/33kV | 33 kV T-3 Bus | 2026-07-16 15:01 | 2026-07-16 16:12 | 0.049306 | E/O | Broken clamp change | 10 | 11.8333 | Power interruption
Sirajganj 132/33kV | T4-(445) | 2026-07-14 09:30 | 2026-07-14 10:59 | 0.061806 | E/O | 33 KV Economic Zone feeder Bus DS Red hot. ( T-4 33kv Bus ). DS bolt replacement at Economic Zone feeder. | 0 | 0 | No interruption
Taraganj 132/33kV | TR-03 (404T) | 2026-07-18 14:41 | 2026-07-18 15:48 | 0.046528 | E/O | Red hot HT Bushing | 0 | 0 | No interruption
Taraganj 132/33kV | TR-03 (404T) | 2026-07-19 12:59 | 2026-07-19 15:16 | 0.095139 | E/O | Loose bushing Connection rectification (33KV Side) | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 22:34 |  | Unserved Energy: |  | 713.0167
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-21 08:07 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: July 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka 132/33kV | Sreepur Ckt- 01 | 2026-07-07 09:46 | 2026-07-07 12:04 | 0.095833 | T | Sripur side problem | 123 | 282.9 | Power interruption
Bhaluka 132/33kV | Sreepur Ckt- 02 | 2026-07-07 09:46 | 2026-07-07 12:04 | 0.095833 | T | Sripur side problem | 123 | 282.9 | Power interruption
Bhaluka 132/33kV | Sreepur Ckt- 01 | 2026-07-12 02:42 | 2026-07-12 02:54 | 0.0083333 | T | Thundering | 123 | 24.6 | Power interruption
Kabirpur 132/33kV | Tongi-2 | 2026-07-17 15:10 | 2026-07-17 15:32 | 0.015278 | T | Tripped | 0 | 0 | No interruption
Shomvuganj 400/132kV | Shambhuganj-Kishoreganj Ckt-2 | 2026-07-01 00:01 | 2026-07-01 00:01 | 0 | T | Tripped | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-1 | 2026-07-12 02:41 | 2026-07-12 02:53 | 0.0083333 | T | Diff. Optd | 115 | 23 | Power interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-2 | 2026-07-19 17:20 | 2026-07-21 15:20 | 1899-12-31 22:00 | T | THUNDER. | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-1 | 2026-07-04 15:04 | 2026-07-04 21:21 | 0.26181 | E/O | Emergency Maintenance | 0 | 0 | No interruption
Netrakona 132/33kV | Mymensingh-Netrokona Ckt-1 | 2026-07-04 13:23 | 2026-07-04 15:23 | 0.083333 | E/O | For high Temperature to Line DS | 0 | 0 | No interruption
Shomvuganj 400/132kV | Shambhuganj-Kishoreganj Ckt-2 | 2026-07-01 00:28 | 2026-07-02 03:16 | 1899-12-31 02:48 | E/O | Emergency Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 14:27 |  | Unserved Energy: |  | 613.4
Dhaka (South) Grid Circle :
Haripur 230/132kV | Ullon (Maniknagar-2) | 2026-07-05 08:22 | 2026-07-05 08:53 | 0.021528 | T | Tripped | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Bhulta-1 | 2026-07-08 09:53 | 2026-07-08 09:55 | 0.0013889 | T | Tripped | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Bhulta-2 | 2026-07-08 09:53 | 2026-07-08 10:57 | 0.044444 | T | Tripped | 0 | 0 | No interruption
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2026-07-07 00:28 | 2026-07-07 01:28 | 0.041667 | T | Tripped | 40 | 40 | Power interruption
Maniknagar 132/33kV | Motijheel Ckt-2 | 2026-07-22 02:18 | 2026-07-22 02:18 | 0 | T | unkown | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-1 | 2026-07-23 15:21 | 2026-07-23 15:57 | 0.025 | T | 400kV Korerhat ckt-1 Tripped by Line Differential and DTT. | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2026-07-27 07:41 | 2026-07-27 07:41 | 0 | T | Unknown | 0 | 0 | No interruption
Siddhirganj 132/33kV | Ullon 1 | 2026-07-01 10:16 | 2026-07-01 16:12 | 0.24722 | T | Due to line Fault. | 0 | 0 | No interruption
Siddhirganj 132/33kV | Ullon 1 | 2026-07-13 15:21 | 2026-07-13 15:56 | 0.024306 | T | Due to line fault. | 0 | 0 | No interruption
Madanganj 132/33kV | Madanganj-Fatullah 132KV Ckt | 2026-07-16 14:56 | 2026-07-16 16:34 | 0.068056 | E/O | DS finger maintenance work | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2026-07-11 13:38 | 2026-07-18 13:37 | 1900-01-05 23:59 | E/O | Emergency Shutdown by NLDC( Fire incedent on Mogbazar ss) | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2026-07-22 07:29 | 2026-07-27 07:41 | 1900-01-04 00:12 | E/O | Order by NLDC | 0 | 0 | No interruption
Rampura 230/132kV | Ullon-02 | 2026-07-27 10:15 | 2026-07-27 10:15 | 0 | E/O | U/G Cable IR Test. | 0 | 0 | No interruption
Rampura 230/132kV | Moghbazar-01 | 2026-07-11 13:37 | 2026-07-19 15:15 | 1900-01-07 01:38 | E/O | Emergency Shutdown by NLDC( Fire incedent on Mogbazar ss) | 0 | 0 | No interruption
Siddhirganj 132/33kV | Ullon 1 | 2026-07-01 12:10 | 2026-07-01 16:12 | 0.16806 | E/O | Due to line fault (Distance Relay, B-phase, Zone-1) & Repair of T-connector & short loop conductor connection of B-phase of T-Point (between 667M and 666M No. DS of Diameter). | 0 | 0 | No interruption
Siddhirganj 132/33kV | Haripur 1 | 2026-07-15 21:36 | 2026-07-15 21:36 | 0 | E/O | Red hot | 0 | 0 | No interruption
|  |  | Total : | 1900-01-19 17:13 |  | Unserved Energy: |  | 40
Chattogram Grid Circle :
Bakulia 132/33kV | Bakalia-Modern Ckt | 2026-07-11 02:50 | 2026-07-11 03:28 | 0.026389 | T | Bakali khulshi cKt-02 Trip Due to Heavy thunder & rain | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Sikalbaha ckt-1 | 2026-07-07 12:23 | 2026-07-07 12:45 | 0.015278 | T | Stormy weather | 0 | 0 | No interruption
Dohazari 132/33kV | Dohazari-Cox's Bazar ckt-2 | 2026-07-09 03:57 | 2026-07-09 11:19 | 0.30694 | T | Landslide with tree at Hill due to Heavy rainfall. | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Khulshi-Ckt.-3 | 2026-07-25 12:01 | 2026-07-25 13:43 | 0.070833 | T | Transient fault | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-07-23 15:21 | 2026-07-23 15:57 | 0.025 | T | Shunt Reactor Work | 0 | 0 | No interruption
Patiya 132/33kV | Patiya-Dohazari Ckt-01 | 2026-07-07 12:24 | 2026-07-07 12:42 | 0.0125 | T | 21-zone 2 B ph EF | 31 | 9.3 | Power interruption
Juldah 132/33kV | 132 KV Julda-Sikalbaha | 2026-07-30 00:16 | 2026-07-30 16:25 | 0.67292 | E/O | Red-Hot Issue | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-Hathazari-1 | 2026-07-04 13:34 | 2026-07-04 14:51 | 0.053472 | E/O | Emergency Tree Trimming. | 0 | 0 | No interruption
Rangamati 132/33kV | Khagrachari Ckt-02 | 2026-07-11 16:50 | 2026-07-11 21:38 | 0.2 | E/O | Rangamati Khagrachari Ckt-02 taken emergency shutdown due to Signal of Trip Ckt -1 fault in the panel. | 0 | 0 | No interruption
Rangamati 132/33kV | Khagrachari Ckt-02 | 2026-07-12 11:55 | 2026-07-12 17:27 | 0.23056 | E/O | Khagrachari ckt-02 shut down due to checking the trip ckt-1 fault and operation by NLDC at 11:55 AM. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 14:44 |  | Unserved Energy: |  | 9.3
Cumilla Grid Circle :
Chhatak 132/33kV | Sylhet 01 | 2026-07-03 04:26 | 2026-07-03 04:40 | 0.0097222 | T | trip at sylhet end | 34 | 7.9333 | Power interruption
Chhatak 132/33kV | Sylhet 02 | 2026-07-03 04:26 | 2026-07-03 04:47 | 0.014583 | T | Trip at sylhet end | 52 | 18.2 | Power interruption
Chhatak 132/33kV | Sylhet 02 | 2026-07-03 06:43 | 2026-07-03 06:53 | 0.0069444 | T | Trip at Sylhet end | 50 | 8.3333 | Power interruption
Cumilla(S) 132/33kV | Cumilla North-2 | 2026-07-05 09:58 | 2026-07-05 12:31 | 0.10625 | T | Tripped | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-02 | 2026-07-21 04:19 | 2026-07-21 16:52 | 0.52292 | T | LA blast of Sreemangal Grid. | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal - Shahjibazar circuit-1 | 2026-07-21 04:19 | 2026-07-21 04:40 | 0.014583 | T | Due to the LA blast in Sreemangal-Shahjibazar circuit 2 | 0 | 0 | No interruption
Sreemongol 132/33kV | sreemangal-Shahjibazar circuit-2 | 2026-07-21 04:19 | 2026-07-21 16:50 | 0.52153 | T | R phase LA blast. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2026-07-03 04:28 | 2026-07-03 04:40 | 0.0083333 | T | Distance Protection Operated | 35 | 7 | Power interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-07-03 04:28 | 2026-07-03 04:46 | 0.0125 | T | Distance Protection Operated | 50 | 15 | Power interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-07-03 06:44 | 2026-07-03 06:53 | 0.00625 | T | Distance protection operated | 40 | 6 | Power interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2026-07-28 09:18 | 2026-07-31 16:15 | 1900-01-02 06:57 | T | Tripped | 0 | 0 | No interruption
Bibiana 400/230kV | Bibi-Fen Ckt-II | 2026-07-25 18:01 | 2026-07-26 01:17 | 0.30278 | E/O | Disconnected Switch Flashing | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2026-07-03 08:53 | 2026-07-03 12:16 | 0.14097 | E/O | Emergency Maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-1 | 2026-07-05 22:22 | 2026-07-06 04:09 | 0.24097 | E/O | Emergency Maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Shahjibazar Circuit-2 | 2026-07-05 22:25 | 2026-07-06 04:09 | 0.23889 | E/O | Emergency Maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2026-07-07 12:11 | 2026-07-07 14:52 | 0.11181 | E/O | Emergency Maint.work | 35 | 93.9167 | Power interruption
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-2 | 2026-07-07 12:16 | 2026-07-07 14:53 | 0.10903 | E/O | Emergency Maint.work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 132KV Cumilla(N)-Kachua Ckt-1 | 2026-07-15 10:37 | 2026-07-15 12:45 | 0.088889 | E/O | Emergency Maint.work | 0 | 0 | No interruption
Kachua 230/132/33kV | Cumilla North CKT | 2026-07-15 10:40 | 2026-07-15 12:40 | 0.083333 | E/O | CT oil leakage | 0 | 0 | No interruption
Sreemongol 132/33kV | sreemangal-Shahjibazar circuit-2 | 2026-07-21 04:24 | 2026-07-21 16:50 | 0.51806 | E/O | R phase LA blast | 0 | 0 | No interruption
Sreemongol 132/33kV | sreemangal-Shahjibazar circuit-2 | 2026-07-21 04:45 | 2026-07-21 16:50 | 0.50347 | E/O | LA Blust | 0 | 0 | No interruption
|  |  | Total : | 1900-01-05 20:26 |  | Unserved Energy: |  | 156.3833
Khulna Grid Circle :
Khulna(S) 230/132kV | Capacitor Bank 1 & 2 | 2026-07-15 07:17 | 2026-07-16 13:14 | 1899-12-31 05:57 | T | Capacitor Bank CT Blast (R Phase) | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-2 (L-2) | 2026-07-09 17:02 | 2026-07-09 17:59 | 0.039583 | E/O | Order by ALDC,Khulna | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-2 (L-2) | 2026-07-10 11:48 | 2026-07-10 12:00 | 0.0083333 | E/O | Emergency Maint.work | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 07:06 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-1 | 2026-07-12 07:23 | 2026-07-12 11:38 | 0.17708 | T |  | 0 | 0 | No interruption
Jhenaidah 132/33kV | Jhenaidah-Magura, 132kV Circuit-1(L7) | 2026-07-01 08:29 | 2026-07-01 08:53 | 0.016667 | T | Thundering. | 35 | 14 | Power interruption
Jhenaidah 132/33kV | Jhenaidah-Magura 132kV Circuit-2(L6) | 2026-07-01 08:29 | 2026-07-01 08:54 | 0.017361 | T | Thundering. | 35 | 14.5833 | Power interruption
Magura 132/33kV | Jhenaidah Ckt. -1 | 2026-07-01 08:52 | 2026-07-01 08:54 | 0.0013889 | T | Thundering. | 0 | 0 | No interruption
Magura 132/33kV | Jhenaidah Ckt. - 2 | 2026-07-01 08:52 | 2026-07-01 08:58 | 0.0041667 | T | Thundering. | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Shahjadpur Line | 2026-07-12 06:59 | 2026-07-12 09:38 | 0.11042 | T | Tripped | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Pabna | 2026-07-12 06:59 | 2026-07-12 09:38 | 0.11042 | T | Heavy thunderstorm. | 0 | 0 | No interruption
Bheramara 230/132kV | GTG (NW) | 2026-07-19 10:34 | 2026-07-20 13:11 | 1899-12-31 02:37 | E/O | Concrete slub for cable tray reinstallation | 0 | 0 | No interruption
Bheramara 230/132kV | STG (NW) | 2026-07-19 10:36 | 2026-07-20 12:55 | 1899-12-31 02:19 | E/O | Concrete slub for cable tray reinstallation | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 15:26 |  | Unserved Energy: |  | 28.5833
Bogura Grid Circle:
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt1 | 2026-07-29 20:18 | 2026-07-31 10:51 | 1899-12-31 14:33 | T | Tropped | 0 | 0 | No interruption
Chapai 132/33kV | Chapai Rahanpur ckt 1 | 2026-07-08 21:15 | 2026-07-08 21:47 | 0.022222 | T | Heavy Thundering | 0 | 0 | No interruption
Joypurhat 132/33kV | Patnitola Ckt.-1 | 2026-07-26 23:56 | 2026-07-27 00:47 | 0.035417 | T | Thandaring | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Kurigram-Lalmonirhat | 2026-07-03 13:11 | 2026-07-03 13:42 | 0.021528 | T | Tripped | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Rangpur-Lalmonirhat | 2026-07-03 13:13 | 2026-07-03 14:24 | 0.049306 | T | রংপুর - লালমনিরহাট ১৩২ কেভি লাইন রংপুর প্রান্তে ট্রিপ করে কিন্তু লালমনিরহাট প্রান্তে ব্রেকার চালু ছিল। পরবর্তীতে ALDC, Bogura পরামর্শে CB OFF করা হয়। | 30 | 35.5 | Power interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-2 | 2026-07-11 09:34 | 2026-07-11 10:46 | 0.05 | T | Weather related and Lighting. | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2026-07-03 13:08 | 2026-07-03 14:24 | 0.052778 | T | Trip Circuit Supervision RY | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Barapukuria-1 | 2026-07-29 20:18 | 2026-07-31 10:50 | 1899-12-31 14:32 | T | Heavy rain and wind flow. | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Teesta Solar-1 | 2026-07-20 02:57 | 2026-07-20 04:32 | 0.065972 | T | Zone-1 Phase-A & B | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Teesta Solar-2 | 2026-07-20 02:57 | 2026-07-20 04:34 | 0.067361 | T | Zone-1 Phase A & B | 0 | 0 | No interruption
Sirajganj 132/33kV | Solar Park 1 | 2026-07-09 05:55 | 2026-07-09 10:01 | 0.17083 | T | Thunderstorm | 0 | 0 | No interruption
Barapukuria 230/132/33kV | Rangpur 132 KV Ckt1 | 2026-07-30 09:24 | 2026-07-31 10:51 | 1899-12-31 01:27 | E/O | SOTF Fault | 0 | 0 | No interruption
Lalmonirhat 132/33kV | Rangpur-Lalmonirhat | 2026-07-12 12:58 | 2026-07-12 14:28 | 0.0625 | E/O | Rangpur grid side redhot work | 0 | 0 | No interruption
Niamatpur 132/33kV | 132kV Rahanpur Ckt-1 | 2026-07-27 07:43 | 2026-07-27 10:56 | 0.13403 | E/O | Rahanpur Ckt-01 & Bus-01 required to shutdown due to Rahanpur Ckt-01 ( DS Nut & Bolt ) Red-hot emergency maintenance. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 00:06 |  | Unserved Energy: |  | 35.5
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Transmission lines : |  |  |  | 1900-02-09 17:28 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:July 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | 230kV Transformer-1 ( 705T1) | 2026-07-03 08:40 | 2026-07-03 12:36 | 3:56 | S/O | O/C & E/F Relay Replacement | 0 | 0 | No interruption
Aminbazar 400/230/132kV | 230/132kv Tr-01 | 2026-07-15 05:58 | 2026-07-15 08:10 | 2:12 | S/O | Read Hot maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Bus-2 (400kV) | 2026-07-28 09:24 | 2026-07-28 14:13 | 4:49 | S/O | Bus diff. Protection & stability testing | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Bus-1 (400kV) | 2026-07-30 09:54 | 2026-07-30 14:53 | 4:59 | S/O | Bus diff. protection and stability testing for IDRNP project. | 0 | 0 | No interruption
Bajitpur 132/33kV | 132 kV Bus-1 | 2026-07-22 14:18 | 2026-07-22 15:50 | 1:32 | S/O | Maint.work | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-2(414T) | 2026-07-22 14:22 | 2026-07-22 15:46 | 1:24 | S/O | Maint.work | 0 | 0 | No interruption
Bajitpur 132/33kV | Tr-1(404T) | 2026-07-22 15:59 | 2026-07-22 16:45 | 0:46 | S/O | Maint.work | 0 | 0 | No interruption
Bajitpur 132/33kV | 132 kV Bus-1 | 2026-07-28 14:36 | 2026-07-28 15:39 | 1:03 | S/O | Due to132 KV Bus coupler Bus-1 DS(B phase) Clamp maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | Bus A | 2026-07-10 14:54 | 2026-07-10 17:15 | 2:21 | S/O | Maint.work | 0 | 0 | No interruption
Bhaluka 132/33kV | 02. Transformer- 02 | 2026-07-12 15:08 | 2026-07-12 17:03 | 1:55 | S/O | clamp change | 20 | 38.3333 | Power interruption
Bhaluka 132/33kV | Bus A | 2026-07-15 06:10 | 2026-07-15 08:57 | 2:47 | S/O | High temperature maintenance work | 0 | 0 | No interruption
Bhaluka 132/33kV | Bus B | 2026-07-28 06:59 | 2026-07-28 12:40 | 5:41 | S/O | for red-hot | 0 | 0 | No interruption
Dhamrai 132/33kV | Transformer-2 | 2026-07-01 10:04 | 2026-07-01 14:21 | 4:17 | S/O | Red hot maintenances by PBS | 40 | 171.3333 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-07-10 10:22 | 2026-07-10 11:52 | 1:30 | S/O | Red hot maintenance of 33 kV Goari feeder Source side | 70 | 105 | Power interruption
Kabirpur 132/33kV | XFR, T-2 | 2026-07-19 15:23 | 2026-07-19 17:39 | 2:16 | S/O | Red Hot maintanence of 33 kV kashimpur-2 feeder | 85 | 192.6667 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2026-07-22 14:47 | 2026-07-22 16:31 | 1:44 | S/O | DPBS-1 Shutdown for Red hot maintenance. | 54 | 93.6 | Power interruption
Kabirpur 132/33kV | XFR, T-3 | 2026-07-27 14:16 | 2026-07-27 16:43 | 2:27 | S/O | High temperature maintenance. | 60 | 147 | Power interruption
Kabirpur 132/33kV | XFR, T-I | 2026-07-28 07:25 | 2026-07-28 09:30 | 2:05 | S/O | Red Hot maintanence of 33 kV kaliakair feeder. | 90 | 187.5 | Power interruption
Kaliakoir 400/230/132kV | 400/132kV TR-3 | 2026-07-08 10:15 | 2026-07-08 18:59 | 8:44 | S/O | SAS, DFDR | 50 | 436.6667 | Power interruption
Kaliakoir 400/230/132kV | 400/132kV TR-3 | 2026-07-31 07:27 | 2026-07-31 12:38 | 5:11 | S/O | DFDR Commissioning. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2026-07-31 09:01 | 2026-07-31 11:59 | 2:58 | S/O | DCRM Test for CB. | 0 | 0 | No interruption
Kodda 132/33kV | Tr-2 (416T) | 2026-07-04 07:44 | 2026-07-04 16:57 | 9:13 | S/O | 33kv LDS change | 25 | 230.4167 | Power interruption
Kodda 132/33kV | Tr-1 (406T) | 2026-07-06 13:11 | 2026-07-06 14:21 | 1:10 | S/O | Red hot maintenance | 0 | 0 | No interruption
Kodda 132/33kV | Bus-1 | 2026-07-21 09:07 | 2026-07-21 13:07 | 4:00 | S/O | Work By PBS Bus-2 DS change of L-19 | 0 | 0 | No interruption
Kodda 132/33kV | Bus-2 | 2026-07-21 09:08 | 2026-07-21 13:07 | 3:59 | S/O | Work By PBS. Bus-2 DS change of L-19 | 70 | 278.8333 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2026-07-23 16:40 | 2026-07-23 17:58 | 1:18 | S/O | 132/33kV GT-3 X-Former LT Side Y-Phase Bushing Clamp Redhot Remove. | 25 | 32.5 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) | 2026-07-24 10:10 | 2026-07-24 16:30 | 6:20 | S/O | 132/33kV X-Former GT-4 33kV Side Redhot Remove. | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) | 2026-07-26 10:14 | 2026-07-26 17:03 | 6:49 | S/O | Project work | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus B | 2026-07-09 13:38 | 2026-07-09 18:50 | 5:12 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-1 (404T) | 2026-07-09 14:06 | 2026-07-09 17:40 | 3:34 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-3 (424T) | 2026-07-09 17:45 | 2026-07-09 19:50 | 2:05 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-2 (414T) | 2026-07-30 06:25 | 2026-07-30 08:50 | 2:25 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-3 (424T) | 2026-07-31 06:32 | 2026-07-31 06:32 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus A | 2026-07-31 07:15 | 2026-07-31 09:59 | 2:44 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus B | 2026-07-31 10:45 | 2026-07-31 14:37 | 3:52 | S/O | Maint.work | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2026-07-14 14:13 | 2026-07-14 16:50 | 2:37 | S/O | Rajendrapur-Sreepur Bay Extention Work. | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2026-07-15 10:49 | 2026-07-15 17:34 | 6:45 | S/O | Maint.work | 0 | 0 | No interruption
Rajendrapur 132/33kV | MTR-2 | 2026-07-16 13:38 | 2026-07-16 18:15 | 4:37 | S/O | Sreepur Bay extension work. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 | 2026-07-17 08:22 | 2026-07-17 10:07 | 1:45 | S/O | Red hot removed work. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 | 2026-07-17 10:20 | 2026-07-17 12:28 | 2:08 | S/O | Red hot | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-1 | 2026-07-06 10:09 | 2026-07-06 16:46 | 6:37 | S/O | Project Work (PSDC), jack bus Loop connection | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-1 | 2026-07-12 12:12 | 2026-07-12 18:36 | 6:24 | S/O | Project work PSDC due to loop connection | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-2 | 2026-07-21 09:29 | 2026-07-21 09:29 | 0:00 | S/O | 132 kV Transformer-02 shifting by PSDC | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-1 | 2026-07-30 13:17 | 2026-07-30 15:24 | 2:07 | S/O | PTR-3 Project Work | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-2 | 2026-07-31 07:36 | 2026-07-31 09:11 | 1:35 | S/O | Project Work | 0 | 0 | No interruption
Tangail 132/33kV | Tr-3 | 2026-07-17 08:22 | 2026-07-17 10:23 | 2:01 | S/O | Red-hot of BUS section-3 Loop of PBS 33kV Feeder. | 20 | 40.3333 | Power interruption
|  |  | Total : | 1900-01-05 09:54 |  | Unserved Energy: |  | 1954.1833
Dhaka (South) Grid Circle :
Bhulta 132/33kV | GT2 | 2026-07-03 14:46 | 2026-07-03 17:05 | 2:19 | S/O | GT- 2 transformer HT bushing top terminal & LT side link cable maintenance for Hot spot. | 0 | 0 | No interruption
Bhulta 132/33kV | GT2 | 2026-07-16 07:18 | 2026-07-16 16:18 | 9:00 | S/O | The changes of GT-02 HT bushing Top Terminal shaft | 60 | 540 | Power interruption
Bhulta 400/230/132kV | 400kV Bus-1 | 2026-07-29 12:11 | 2026-07-29 16:54 | 4:43 | S/O | Due to rectify DS alignment problem. | 0 | 0 | No interruption
Haripur 230/132kV | Bus-2 | 2026-07-01 08:22 | 2026-07-01 14:57 | 6:35 | S/O | Temperature Correction work. | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Reserve Bus Sec-2 | 2026-07-02 11:57 | 2026-07-02 16:24 | 4:27 | S/O | Busbar Protection Work. | 0 | 0 | No interruption
Haripur 230/132kV | Auto TR-3 | 2026-07-19 08:26 | 2026-07-19 11:45 | 3:19 | S/O | High temperature maintenance . | 0 | 0 | No interruption
Hasnabad 132/33kV | 132kV Main Bus | 2026-07-03 06:25 | 2026-07-03 12:31 | 6:06 | S/O | Red hot maintenance work of Shitalakkhya ckt main bus D/S & ATR-1 main bus D/S. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132kV Reserve Bus | 2026-07-03 12:35 | 2026-07-03 12:35 | 0:00 | S/O | AutoTR-3 Reserve Bus D/S red hot maintenance work. | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Main Bus | 2026-07-16 15:14 | 2026-07-16 17:06 | 1:52 | S/O | Temperature rise | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 | 2026-07-16 15:17 | 2026-07-16 17:38 | 2:21 | S/O | Temperature rise | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-1 | 2026-07-03 06:18 | 2026-07-03 08:28 | 2:10 | S/O | 132 kv main bus D/S mainance by 132kv S/S. | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-3 | 2026-07-03 08:35 | 2026-07-03 16:21 | 7:46 | S/O | maintenance work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-1 | 2026-07-27 07:17 | 2026-07-27 08:17 | 1:00 | S/O | High temperature maintenance work. | 0 | 0 | No interruption
Meghnaghat 400/230kV | 230kV BUS Section 02 | 2026-07-30 13:40 | 2026-07-30 16:34 | 2:54 | S/O | 230 kv old ss work | 0 | 0 | No interruption
Meghnaghat 400/230kV | ATR -03 | 2026-07-31 09:44 | 2026-07-31 18:50 | 9:06 | S/O | For fire fighting work | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-2 | 2026-07-17 06:57 | 2026-07-17 10:57 | 4:00 | S/O | Shifting of 33/0.4 kv auxiliary -02transformer and 33 kv bus pt | 25 | 100 | Power interruption
Munshiganj 132/33kV | Transformer-1 | 2026-07-20 06:15 | 2026-07-20 10:40 | 4:25 | S/O | Shifting of 33/.4 KV Auxiliary -01 and 33KV bus PT | 30 | 132.5 | Power interruption
Munshiganj 132/33kV | Transformer-1 | 2026-07-22 06:25 | 2026-07-22 08:04 | 1:39 | S/O | Shifting of 33/0.4kv Auxiliary T01 | 30 | 49.5 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2026-07-24 06:40 | 2026-07-24 08:20 | 1:40 | S/O |  | 25 | 41.6667 | Power interruption
Munshiganj 132/33kV | Transformer-2 | 2026-07-27 06:38 | 2026-07-27 22:24 | 15:46 | S/O | 33KV CT Change and Related Different types of Maintenance work | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-1 | 2026-07-28 07:13 | 2026-07-28 19:23 | 12:10 | S/O | 33 kv CT replacement work | 0 | 0 | No interruption
Munshiganj 132/33kV | Transformer-1 | 2026-07-29 06:45 | 2026-07-30 00:12 | 17:27 | S/O | 33 KV CB Replacement work. | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2026-07-16 15:24 | 2026-07-16 17:04 | 1:40 | S/O | T-4 BUS DS-1 NUT-BOLTS HOTSPOTS MAINTENANCE WORK | 0 | 0 | No interruption
Narshingdi 132/33kV | T-4 | 2026-07-18 22:55 | 2026-07-18 23:37 | 0:42 | S/O | T4 Transformer এর Hasnabad 33kV Feeder R-Phase Red hot Maintenance Work. | 35 | 24.5 | Power interruption
Nawabganj 132/33kV | TR-2 | 2026-07-24 07:14 | 2026-07-24 13:07 | 5:53 | S/O | 33kv Bus-02 shutdown for PT changing of kushumhati feeder. | 20 | 117.6667 | Power interruption
Sonargaon 132/33kV | Tr-1 | 2026-07-10 09:12 | 2026-07-12 06:28 | 45:16 | S/O | Transformer Oil centrifuge purpose. | 20 | 905.3333 | Power interruption
Srinagar 132/33kV | Tr-02 | 2026-07-25 20:20 | 2026-07-25 22:26 | 2:06 | S/O | Red hot maintenance at Tr-02 LT side Y-phase. | 15 | 31.5 | Power interruption
Srinagar 132/33kV | Tr-01 | 2026-07-25 22:45 | 2026-07-25 23:39 | 0:54 | S/O | Red hot maintenance by Pbs. | 20 | 18 | Power interruption
|  |  | Total : | 1900-01-06 09:16 |  | Unserved Energy: |  | 1960.6667
Chattogram Grid Circle :
BSRM 230/33kV | 230/33 kV Transformer-2 (125/140 MVA) | 2026-07-02 10:46 | 2026-07-16 13:01 | 338:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
BSRM 230/33kV | 230/33 kV Transformer-1 (125/140 MVA) | 2026-07-22 12:40 | 2026-07-22 12:40 | 0:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bakulia 132/33kV | T-4 (432T) | 2026-07-13 12:10 | 2026-07-13 16:11 | 4:01 | S/O | AVR Testing | 0 | 0 | No interruption
Coxsbazar 132/33kV | 415T-T2 | 2026-07-09 05:46 | 2026-07-10 07:58 | 26:12 | S/O | Project work | 5 | 131 | Power interruption
Coxsbazar 132/33kV | 405T-T1 | 2026-07-10 09:25 | 2026-07-10 18:20 | 8:55 | S/O | project work | 5 | 44.5833 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2026-07-03 17:56 | 2026-07-03 19:22 | 1:26 | S/O | Due to keranihut 33kv red hot Maintenance | 62 | 88.8667 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2026-07-18 00:24 | 2026-07-18 03:07 | 2:43 | S/O | bandarban 33kv loop intermittence. | 60 | 163 | Power interruption
Dohazari 132/33kV | Power Transformer -T-1 | 2026-07-18 05:30 | 2026-07-18 06:50 | 1:20 | S/O | Due to bashkhali 33kv isolator maintenance | 6 | 8 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2026-07-22 16:40 | 2026-07-22 17:47 | 1:07 | S/O | Dohazari PDB 33kv bus isolator Maintenance. | 56 | 62.5333 | Power interruption
Dohazari 132/33kV | Power Transformer -T-1 | 2026-07-25 00:51 | 2026-07-25 01:36 | 0:45 | S/O | Due to Banshkhali 33 KV feeder BUS DS maintenance . | 25 | 18.75 | Power interruption
Dohazari 132/33kV | Power Transformer -T-2 | 2026-07-28 22:30 | 2026-07-29 00:19 | 1:49 | S/O | keranihut ds redhot maintenance. | 53 | 96.2833 | Power interruption
Hathazari 230/132/33kV | 230KV MAIN BUS-02 | 2026-07-20 09:46 | 2026-07-20 16:24 | 6:38 | S/O | G2G project work. | 0 | 0 | No interruption
Hathazari 230/132/33kV | 230KV MAIN BUS-01 | 2026-07-21 08:27 | 2026-07-21 16:31 | 8:04 | S/O |  | 0 | 0 | No interruption
KSRM 132/33kV | Transformer-01 | 2026-07-25 11:35 | 2026-07-25 15:43 | 4:08 | S/O | for 33 KV Incoming CT Oil Leakage maintenance | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) | 2026-07-19 15:30 | 2026-07-19 17:23 | 1:53 | S/O | Cable termination | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7103T) | 2026-07-01 11:41 | 2026-07-01 18:07 | 6:26 | S/O | Project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7103T) | 2026-07-07 10:38 | 2026-07-07 19:47 | 9:09 | S/O | Due to project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7103T) | 2026-07-08 09:21 | 2026-07-08 18:01 | 8:40 | S/O | Project Work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-2(7203T)-Three Ph | 2026-07-09 09:36 | 2026-07-09 18:02 | 8:26 | S/O | Project Work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-07-12 10:29 | 2026-07-12 17:25 | 6:56 | S/O | Project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-07-13 09:01 | 2026-07-13 17:48 | 8:47 | S/O | Project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7303T)-Three Ph | 2026-07-14 11:30 | 2026-07-14 18:51 | 7:21 | S/O | Due to project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-07-22 09:40 | 2026-07-22 21:21 | 11:41 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-2(7203T)-Three Ph | 2026-07-23 10:18 | 2026-07-23 21:02 | 10:44 | S/O | Project work (DFDR) | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7103T) | 2026-07-25 10:01 | 2026-07-25 19:47 | 9:46 | S/O | DFDR work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-3(7303T)-Three Ph | 2026-07-26 09:27 | 2026-07-26 18:34 | 9:07 | S/O | DFDR work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-07-28 13:24 | 2026-07-28 15:52 | 2:28 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | ATR-4(7403T) | 2026-07-30 11:18 | 2026-07-30 17:23 | 6:05 | S/O | CAF/DFDR | 0 | 0 | No interruption
Patiya 132/33kV | TRAFO-01 | 2026-07-14 10:18 | 2026-07-14 12:19 | 2:01 | S/O | Corrective maintenance | 6 | 12.1 | Power interruption
Patiya 132/33kV | TRAFO-01 | 2026-07-17 08:25 | 2026-07-17 11:55 | 3:30 | S/O | Red hot corrective maintenance | 7 | 24.5 | Power interruption
|  |  | Total : | 1900-01-20 14:23 |  |  |  | 649.6167
Cumilla Grid Circle :
Chandina 132/33kV | TR-3 | 2026-07-03 09:14 | 2026-07-03 17:08 | 7:54 | S/O | 132/33 kV TR-2 HT Scheduled S/D due to Due to cumilla pbs-1 has their maintenance work in the switchyard. | 0 | 0 | No interruption
Chandina 132/33kV | TR-2 | 2026-07-03 09:41 | 2026-07-03 15:43 | 6:02 | S/O | 132/33 kV TR-2 HT Scheduled S/D due to Due to cumilla pbs-1 has their maintenance work in the switchyard. | 0 | 0 | No interruption
Chandpur 132/33kV | 422T(T-5) | 2026-07-29 11:02 | 2026-07-29 16:12 | 5:10 | S/O | OLTC oil change | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-1 | 2026-07-22 08:08 | 2026-07-22 09:33 | 1:25 | S/O | Red hot maintenance at 33KV bus-01. | 35 | 49.5833 | Power interruption
Chhatak 132/33kV | T-1 | 2026-07-02 14:41 | 2026-07-02 17:37 | 2:56 | S/O | 33KV Doarabazar PBS Feeder DS maintenance work. | 15 | 44 | Power interruption
Chhatak 132/33kV | T-1 | 2026-07-24 06:12 | 2026-07-24 11:26 | 5:14 | S/O | 33kv Doara bazar feeder DS Maintanance | 12 | 62.8 | Power interruption
Chowmuhani 230/132/33kV | TR2-425T | 2026-07-10 08:29 | 2026-07-10 08:29 | 0:00 | S/O | Panel replacement. | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Transformer-1 | 2026-07-21 11:14 | 2026-07-21 13:50 | 2:36 | S/O | 33KV Bus DS Maintenance Of transformer -01 | 0 | 0 | No interruption
Feni 132/33kV | T-2(415T) | 2026-07-01 12:49 | 2026-07-01 15:46 | 2:57 | S/O | 132kV Bus coupler GCB Y & B Phase Red hot Maintenance | 0 | 0 | No interruption
Kachua 230/132/33kV | ATR-1 | 2026-07-09 14:57 | 2026-07-09 21:52 | 6:55 | S/O | AVR Test. | 0 | 0 | No interruption
Kachua 230/132/33kV | ATR-2 | 2026-07-11 14:07 | 2026-07-11 18:03 | 3:56 | S/O | AVR testing | 0 | 0 | No interruption
Kasba 132/33kV | TR-2 | 2026-07-12 21:48 | 2026-07-12 23:02 | 1:14 | S/O | shutdown taken by pbs for DS Isolator Red hot. | 0 | 0 | No interruption
Kasba 132/33kV | TR-2 | 2026-07-25 09:24 | 2026-07-25 10:51 | 1:27 | S/O | Kasba-2 feeder 33kV side DS isolator maintenace by PBS | 0 | 0 | No interruption
Kasba 132/33kV | TR-2 | 2026-07-30 00:48 | 2026-07-30 01:30 | 0:42 | S/O | shutdown tacken by pbs for load side redhot maintenance | 15 | 10.5 | Power interruption
Kulaura 132/33kV | TR-1 AB | 2026-07-31 07:47 | 2026-07-31 09:21 | 1:34 | S/O | PBS bus DS redhot maintenance | 24 | 37.6 | Power interruption
Lakshmipur 132/33kV | MAIN BUS-2 | 2026-07-30 16:11 | 2026-07-30 18:31 | 2:20 | S/O | To fixing SCADA Integration work via Project(CNEEC). | 0 | 0 | No interruption
Maijdee 132/33kV | Tr-02 | 2026-07-02 16:20 | 2026-07-02 17:11 | 0:51 | S/O | Maintanance the Red Hot condition at the source side of the 33kv ABS of BREB. | 0 | 0 | No interruption
Maijdee 132/33kV | Tr-02 | 2026-07-07 11:01 | 2026-07-07 11:48 | 0:47 | S/O | TR 02 auxiliary transformer fuse is blown. | 0 | 0 | No interruption
Maijdee 132/33kV | Tr-02 | 2026-07-08 13:16 | 2026-07-08 13:34 | 0:18 | S/O | For the replacement of the Auxiliary Transformer-02 fuse. | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 | 2026-07-18 00:32 | 2026-07-18 02:57 | 2:25 | S/O | Red Hot Maintanance. | 16 | 38.6667 | Power interruption
Maijdee 132/33kV | TR-01 | 2026-07-21 12:01 | 2026-07-21 23:13 | 11:12 | S/O | TR-01 33kV BREB DS Replace & Others Maintenance work | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 | 2026-07-22 12:23 | 2026-07-22 20:21 | 7:58 | S/O | TR-01 S/D for BREB 33 kV DS REPLACE & Other Maintenance Work. | 0 | 0 | No interruption
Maijdee 132/33kV | TR-01 | 2026-07-26 11:50 | 2026-07-26 20:34 | 8:44 | S/O | BREB 33KV Red Hot Maintenance and Others Work. | 0 | 0 | No interruption
Maijdee 132/33kV | Tr-02 | 2026-07-29 14:56 | 2026-07-29 19:12 | 4:16 | S/O | TR-02 OVER CURRENT RELAY CHANGE BY PROJECT (CNTIC) | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-01 | 2026-07-19 10:20 | 2026-07-20 20:44 | 34:24 | S/O | PBS 33 KV PT Replacement work | 0 | 0 | No interruption
Ramganj 132/33kV | Transformer -02 | 2026-07-10 14:45 | 2026-07-10 15:45 | 1:00 | S/O | OTI Alarm Checking | 15 | 15 | Power interruption
Ramganj 132/33kV | Transformer -02 | 2026-07-12 15:04 | 2026-07-12 16:59 | 1:55 | S/O | OTI Alarm cheking | 15 | 28.75 | Power interruption
Shahjibazar 132/33kV | TR-06 | 2026-07-11 13:46 | 2026-07-11 15:00 | 1:14 | S/O | 33 Kv Bus Redhot Maintenence by PDB | 50 | 61.6667 | Power interruption
Shahjibazar 132/33kV | TR-06 | 2026-07-14 07:11 | 2026-07-14 09:18 | 2:07 | S/O | 33 Kv CT Redhot Maintenence | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 | 2026-07-28 21:30 | 2026-07-28 22:14 | 0:44 | S/O | Oil Leakage | 50 | 36.6667 | Power interruption
Shahjibazar 132/33kV | TR-06 | 2026-07-30 07:33 | 2026-07-30 10:56 | 3:23 | S/O | Tr-06 Maintenance for Oil Leakage. | 0 | 0 | No interruption
Sylhet_(South) 132/33kV | Trafo-1 | 2026-07-15 14:01 | 2026-07-15 16:26 | 2:25 | S/O | Red hot maintenance Work. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 16:05 |  |  |  | 385.2333
Khulna Grid Circle :
Barguna 132/33kV | Transformer-1 | 2026-07-07 22:49 | 2026-07-08 01:19 | 2:30 | S/O | Flashing maintenance at T1A DS-1 | 0 | 0 | No interruption
Barguna 132/33kV | Transformer-2 | 2026-07-08 01:50 | 2026-07-08 03:10 | 1:20 | S/O | Flashing maintenance at T2-A D/S-1 | 0 | 0 | No interruption
Barishal 132/33kV | T-2 (415T) | 2026-07-26 17:18 | 2026-07-26 18:50 | 1:32 | S/O | WZPDCL Maintenance work. | 20 | 30.6667 | Power interruption
Barishal 230/132kV | T-5 | 2026-07-11 06:36 | 2026-07-11 09:40 | 3:04 | S/O | Hot spot maintenance | 20 | 61.3333 | Power interruption
Barishal 230/132kV | T-5 | 2026-07-17 06:18 | 2026-07-17 09:15 | 2:57 | S/O | 33 kV Nobogram feeder source DS repair. | 42 | 123.9 | Power interruption
Barishal 230/132kV | T-5 | 2026-07-21 15:33 | 2026-07-21 19:07 | 3:34 | S/O | 33 কেভি সরুপকাঠি -২ ফিডারের রেড হড | 24 | 85.6 | Power interruption
Barishal 230/132kV | ATR-1 | 2026-07-25 15:23 | 2026-07-25 18:00 | 2:37 | S/O | Maintenance of tap changer motor | 0 | 0 | No interruption
Bhandaria 132/33kV | Transformer-1 | 2026-07-12 12:01 | 2026-07-12 14:30 | 2:29 | S/O | 33 kV Bus PT cable Change. | 20 | 49.6667 | Power interruption
Faridpur 132/33kV | Transformer-1 | 2026-07-16 06:03 | 2026-07-16 10:05 | 4:02 | S/O | Red hot | 10 | 40.3333 | Power interruption
Faridpur 132/33kV | Transformer-2 | 2026-07-18 06:50 | 2026-07-18 08:03 | 1:13 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | ATR-1 | 2026-07-21 09:55 | 2026-07-21 12:20 | 2:25 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-2 | 2026-07-28 02:07 | 2026-07-28 02:42 | 0:35 | S/O | Maint.work | 70 | 40.8333 | Power interruption
Goalpara 132/33kV | Bus 1 | 2026-07-03 08:58 | 2026-07-03 17:30 | 8:32 | S/O | Maintenance works. | 0 | 0 | No interruption
Gopalganj 132/33kV | T2 | 2026-07-12 16:41 | 2026-07-12 18:52 | 2:11 | S/O | 33kv bus section DS maintenance | 20 | 43.6667 | Power interruption
Gopalganj 400/132kV | ATR-02 | 2026-07-29 12:58 | 2026-07-29 14:38 | 1:40 | S/O | 3rd Harmonic current measure | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-07-26 06:15 | 2026-07-26 09:01 | 2:46 | S/O | Maint. Work of south ckt-2 main bus DS. | 0 | 0 | No interruption
Khulna (C) | Tr-3 405T | 2026-07-27 07:35 | 2026-07-27 09:41 | 2:06 | S/O | Due to read-hot maintenance | 0 | 0 | No interruption
Khulna (C) | Tr-2 415 T | 2026-07-27 10:57 | 2026-07-27 12:18 | 1:21 | S/O | for temperature reduce | 0 | 0 | No interruption
Khulna (C) | TR-1 425T | 2026-07-27 15:15 | 2026-07-27 17:18 | 2:03 | S/O | 33 kv Bus Section 1 Satkhira Feeder Post insulator maintenance Y phase. | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-2 | 2026-07-09 17:04 | 2026-07-09 17:55 | 0:51 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-1 | 2026-07-10 07:32 | 2026-07-10 11:30 | 3:58 | S/O | Busbar DS Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-3 | 2026-07-10 07:32 | 2026-07-10 11:32 | 4:00 | S/O | Busbar DS Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-2 | 2026-07-10 07:47 | 2026-07-10 11:56 | 4:09 | S/O | Busbar DS Maintenance | 0 | 0 | No interruption
Madaripur 132/33kV | T1-405T | 2026-07-05 07:56 | 2026-07-05 09:28 | 1:32 | S/O | High Temperature maintenance 33 kv bus section -1 | 25 | 38.3333 | Power interruption
Narail 132/33kV | TR1 (403-T) | 2026-07-24 07:30 | 2026-07-24 09:28 | 1:58 | S/O | Red hot maintenance | 24 | 47.2 | Power interruption
Payra 400/132/33kV | 132/33 kV Transformer-04 | 2026-07-20 08:58 | 2026-07-20 18:07 | 9:09 | S/O | Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | 132/33 kV Transformer-04 | 2026-07-21 06:32 | 2026-07-21 16:03 | 9:31 | S/O | Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-02 12:05 |  | Unserved Energy : |  | 561.5333
HVDC Grid Circle
BIPTC | 20D09C 20MVA | 2026-07-06 08:25 | 2026-07-06 11:43 | 3:18 | S/O | For corrective maintenance. 230/33kV Aux. Trafo-01 | 0 | 0 | No interruption
BIPTC | 20D10A 20MVA | 2026-07-15 10:09 | 2026-07-15 12:06 | 1:57 | S/O | 20MVA (230/33kV) Auxiliary Transformer 2 | 0 | 0 | No interruption
BIPTC | 20DF22 | 2026-07-23 11:41 | 2026-07-23 12:11 | 0:30 | S/O | Maintenance | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) | 2026-07-17 21:02 | 2026-07-17 21:32 | 0:30 | S/O | Redhot at 33kV incomer CB Clamp of Tr-1 | 20 | 10 | Power interruption
Bhangura 132/33kV | Tr-2(413T) | 2026-07-17 21:33 | 2026-07-17 21:53 | 0:20 | S/O | Redhot at 33kV incomer CB of Tr-2 | 15 | 5 | Power interruption
Bhangura 132/33kV | Tr-1(403T) | 2026-07-27 17:15 | 2026-07-27 18:02 | 0:47 | S/O | Redhot removal | 10 | 7.8333 | Power interruption
Ishurdi 230/132kV | 230 kV Bus 2 | 2026-07-18 11:28 | 2026-07-18 12:52 | 1:24 | S/O | 23 KV ISD-Ghorasal-2's different equipments clamp changing | 0 | 0 | No interruption
Kushtia 132/33kV | 132 KV Bus-A | 2026-07-09 12:16 | 2026-07-09 15:13 | 2:57 | S/O | Maintenance | 0 | 0 | No interruption
Kushtia 132/33kV | T-2 | 2026-07-24 08:46 | 2026-07-24 11:36 | 2:50 | S/O | Wzpdcl 33kv mozompur feeder bus isolator clamp change | 15 | 42.5 | Power interruption
Kushtia 132/33kV | T-3 | 2026-07-24 12:01 | 2026-07-24 16:21 | 4:20 | S/O | DWZTGE project work for newly meherpur bay | 0 | 0 | No interruption
Kushtia 132/33kV | 132 KV Bus-A | 2026-07-24 12:20 | 2026-07-24 12:20 | 0:00 | S/O | DWZTGE project work for newly meherpur bay | 0 | 0 | No interruption
|  |  | Total : | 0.78681 |  | Unserved Energy : |  | 65.3333
Bogura Grid Circle:
Barapukuria 230/132/33kV | 132/33 KV T-3, 404T | 2026-07-29 07:02 | 2026-07-29 09:46 | 2:44 | S/O | 33KV coal mine feeder conductor stringing work | 25 | 68.3333 | Power interruption
Bog-Sherpur 132/33kV | Transformer-1 (404T) | 2026-07-15 14:23 | 2026-07-15 17:00 | 2:37 | S/O | 33 kv bus red hot maintenance. shutdown for PBS | 40 | 104.6667 | Power interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) | 2026-07-15 17:06 | 2026-07-15 18:56 | 1:50 | S/O | 33 kv bus red hot maintenance. Shutdown for PBS | 11 | 20.1667 | Power interruption
Bogura 230/132kV | T-01 | 2026-07-07 11:18 | 2026-07-07 13:22 | 2:04 | S/O | auxiliary x-former installation | 0 | 0 | No interruption
Bogura 230/132kV | T-01 | 2026-07-10 10:54 | 2026-07-10 15:50 | 4:56 | S/O | Auxiliary Transformer work | 0 | 0 | No interruption
Bogura 230/132kV | T-01 | 2026-07-12 10:30 | 2026-07-12 20:57 | 10:27 | S/O | red-hot maintenance | 0 | 0 | No interruption
Bogura 230/132kV | T-01 | 2026-07-14 14:26 | 2026-07-14 18:11 | 3:45 | S/O | Auxiliary transformer Oil Centrifuging. | 0 | 0 | No interruption
Bogura 230/132kV | T-01 | 2026-07-16 16:09 | 2026-07-16 17:32 | 1:23 | S/O | Maint.work | 0 | 0 | No interruption
Bogura 230/132kV | T-02 | 2026-07-28 10:05 | 2026-07-28 20:07 | 10:02 | S/O | Auxiliary Transformer Installation | 0 | 0 | No interruption
Joypurhat 132/33kV | Transformer T-3 (427 T) | 2026-07-20 16:21 | 2026-07-20 18:31 | 2:10 | S/O | Red hot Maintenance work is doing by Joypurhat PBS | 13 | 28.1667 | Power interruption
Joypurhat 132/33kV | Transformer T-4 (437 T) | 2026-07-20 16:21 | 2026-07-20 19:09 | 2:48 | S/O | Red hot Maintenance work is doing by Joypurhat PBS | 13 | 36.4 | Power interruption
Mahasthangarh 132/33kV | 416T MTR 2 | 2026-07-17 07:11 | 2026-07-17 13:00 | 5:49 | S/O | 33 kv Durgapur feeder DS change | 28 | 162.8667 | Power interruption
Mithapukur 132/33kV | TR-2 (414T) | 2026-07-25 13:48 | 2026-07-25 16:35 | 2:47 | S/O | incomer -2 DS maintenance | 16 | 44.5333 | Power interruption
Naogaon 132/33kV | 230kV Bus A | 2026-07-16 13:29 | 2026-07-21 12:43 | 119:14 | S/O | Naogaon-Bigura ckt-1&2 230 kV Bay Interlock checking. | 0 | 0 | No interruption
Naogaon 132/33kV | 230kV Bus B | 2026-07-16 13:29 | 2026-07-21 12:56 | 119:27 | S/O | Naogaon-Bigura ckt-1&2 230 kV Bay Interlock checking. | 0 | 0 | No interruption
Naogaon 132/33kV | T-4 | 2026-07-29 07:23 | 2026-07-29 09:53 | 2:30 | S/O | Old Bay Dismentle work | 0 | 0 | No interruption
Naogaon 132/33kV | T-3 | 2026-07-29 09:50 | 2026-07-29 11:45 | 1:55 | S/O | old bay dismentle work | 0 | 0 | No interruption
Natore 132/33kV | TR-2 (415 T) | 2026-07-08 13:54 | 2026-07-09 00:20 | 10:26 | S/O | Maintenance work at 33KV C.B | 0 | 0 | No interruption
Natore 132/33kV | TR-2 (415 T) | 2026-07-08 14:34 | 2026-07-09 00:02 | 9:28 | S/O | Maintenance work at 33KV C.B | 0 | 0 | No interruption
Natore 132/33kV | TR-1 (405 T) | 2026-07-09 06:44 | 2026-07-09 09:36 | 2:52 | S/O | Maint.work | 0 | 0 | No interruption
Natore 132/33kV | TR-2 (415 T) | 2026-07-09 06:44 | 2026-07-09 09:38 | 2:54 | S/O | Maint.work | 0 | 0 | No interruption
Natore 132/33kV | TR-4 (435 T) | 2026-07-11 08:30 | 2026-07-11 10:22 | 1:52 | S/O | 33 KV Bus work ( actual interruption 19 MW due to bad weather) | 34 | 63.4667 | Power interruption
Natore 132/33kV | 132 KV MAIN BUS | 2026-07-14 06:15 | 2026-07-14 08:22 | 2:07 | S/O | Maint.work | 120 | 254 | Power interruption
Natore 132/33kV | TR-1 (405 T) | 2026-07-18 06:32 | 2026-07-18 08:20 | 1:48 | S/O | For 33 kV Bus Red hot maintenance work | 32.5 | 58.5 | Power interruption
Natore 132/33kV | TR-2 (415 T) | 2026-07-18 06:32 | 2026-07-18 08:21 | 1:49 | S/O | For 33 kV Bus Red hot maintenance work | 32.5 | 59.0417 | Power interruption
Natore 132/33kV | TR-1 (405 T) | 2026-07-23 06:33 | 2026-07-23 08:32 | 1:59 | S/O | Maint.work | 29 | 57.5167 | Power interruption
Natore 132/33kV | TR-2 (415 T) | 2026-07-23 06:33 | 2026-07-23 08:32 | 1:59 | S/O | Maint.work | 29 | 57.5167 | Power interruption
Purbasadipur 230/132/33kV | AIS Old T-4 Transformer | 2026-07-13 15:58 | 2026-07-13 17:12 | 1:14 | S/O | Red hot on 33kv Nesco feeder | 10 | 12.3333 | Power interruption
Rangpur 132/33kV | T-2 (404T) | 2026-07-06 05:48 | 2026-07-06 09:43 | 3:55 | S/O | Maint.work | 25 | 97.9167 | Power interruption
Rangpur 132/33kV | 132KV Bus A | 2026-07-12 10:38 | 2026-07-12 14:50 | 4:12 | S/O | Clamp Change. | 0 | 0 | No interruption
Rangpur 132/33kV | 33KV Bus | 2026-07-17 07:09 | 2026-07-17 10:27 | 3:18 | S/O | Replacement of 33kv DS | 50 | 165 | Power interruption
Saidpur 132/33kV | TR-3 (424T) | 2026-07-24 06:43 | 2026-07-24 12:41 | 5:58 | S/O | 33 kV loop change of golahat 33kV feeder. | 12 | 71.6 | Power interruption
Thakurgaon 132/33kV | 33kV Bus | 2026-07-14 07:35 | 2026-07-14 07:55 | 0:20 | S/O | 33kV Bus Section-2 with T-2 HT & LT Side, Baliadangi, Neckmorad, Goalpara, Pirgonj, REB, Thakurgaon Sadar, Golapganj. RPC-1. | 50 | 16.6667 | Power interruption
|  |  | Total : | 1900-01-13 16:39 |  | Unserved Energy : |  | 1378.6917
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1441:15 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:July 2026
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Gopalganj-1 | 2026-07-03 07:21 | 2026-07-03 08:16 | 0:55 | S/O | Setting change by SPMD | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Gopalganj-2 | 2026-07-03 08:20 | 2026-07-03 08:57 | 0:37 | S/O | Setting change by SPMD | 0 | 0 | No interruption
Bajitpur 132/33kV | Ashuganj Ckt-2 | 2026-07-02 13:20 | 2026-07-02 16:04 | 2:44 | S/O | Due to high temperature reduce maintenance at line DS | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-2 | 2026-07-28 13:29 | 2026-07-28 14:31 | 1:02 | S/O | Due to Line DS B Phase clamp Maintenance | 0 | 0 | No interruption
Bajitpur 132/33kV | Kishoreganj Ckt-1 | 2026-07-28 14:40 | 2026-07-28 15:37 | 0:57 | S/O | Due To Line DS (RYB) Phase clamp maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-07-09 07:10 | 2026-07-09 19:11 | 12:01 | S/O | Bhaluka-Mymensingh 400KV line stringing work. | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2026-07-09 07:11 | 2026-07-09 19:11 | 12:00 | S/O | Bhaluka-Mymensingh 400KV line Stringing work. | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 01 | 2026-07-09 10:58 | 2026-07-09 18:29 | 7:31 | S/O | Clamp changing | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-07-10 09:34 | 2026-07-10 17:21 | 7:47 | S/O | Mymensingh Bhaluka 400 KV line stringing work | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2026-07-10 09:34 | 2026-07-10 17:21 | 7:47 | S/O | Mymensingh Bhaluka 400 KV line stringing work | 0 | 0 | No interruption
Bhaluka 132/33kV | Sreepur Ckt- 02 | 2026-07-10 10:14 | 2026-07-10 17:20 | 7:06 | S/O | Clamp changing | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 01 | 2026-07-15 06:09 | 2026-07-15 09:05 | 2:56 | S/O | High temperature maintenance work | 0 | 0 | No interruption
Bhaluka 132/33kV | Mymensingh Ckt- 02 | 2026-07-28 06:24 | 2026-07-28 11:23 | 4:59 | S/O | Clamp Change different point at B-bus DS | 0 | 0 | No interruption
Bhaluka 132/33kV | BR Powergen Ckt- 02 | 2026-07-28 06:52 | 2026-07-28 13:35 | 6:43 | S/O | Maint.work | 0 | 0 | No interruption
Kabirpur 132/33kV | Manikganj-1 | 2026-07-15 14:50 | 2026-07-15 17:33 | 2:43 | S/O | High temperature maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-1 | 2026-07-17 06:32 | 2026-07-17 09:22 | 2:50 | S/O | Shutdown taken by SouthWest Transmission Grid Expansion Project | 0 | 0 | No interruption
Kabirpur 132/33kV | Tongi-2 | 2026-07-17 09:48 | 2026-07-17 11:42 | 1:54 | S/O | Shutdown taken by South west transmission grid expansion project | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-2 | 2026-07-06 13:11 | 2026-07-06 17:17 | 4:06 | S/O | By instruction NLDC | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-1 | 2026-07-10 06:37 | 2026-07-10 08:29 | 1:52 | S/O | High temperature mitigation work of 132 kv Kishorganj -Mymensingh ckt -01 R phase line DS to line connector T - clamp | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-1 | 2026-07-24 06:13 | 2026-07-24 15:31 | 9:18 | S/O | Shambhuganj project work. | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-2 | 2026-07-24 06:57 | 2026-07-24 14:56 | 7:59 | S/O | Shambhuganj project work. | 0 | 0 | No interruption
Kishoreganj 132/33kV | Bajitpur Ckt-2 | 2026-07-28 13:28 | 2026-07-28 14:31 | 1:03 | S/O | Work at Bajitpur substation. | 0 | 0 | No interruption
Kishoreganj 132/33kV | Bajitpur Ckt-1 | 2026-07-28 14:38 | 2026-07-28 15:38 | 1:00 | S/O | Work at Bajitpur substation end. | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2026-07-21 09:03 | 2026-07-22 19:03 | 34:00 | S/O | Project development Work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Netrakona Ckt-1 | 2026-07-04 13:26 | 2026-07-04 15:21 | 1:55 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-1 | 2026-07-09 07:05 | 2026-07-09 19:13 | 12:08 | S/O | Maint.work | 40 | 485.3333 | Power interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-2 | 2026-07-09 07:06 | 2026-07-09 19:13 | 12:07 | S/O | Maint.work | 40 | 484.6667 | Power interruption
Mymensingh 132/33kV | Mymensingh-RPCL Ckt-1 | 2026-07-09 12:30 | 2026-07-09 19:36 | 7:06 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Netrakona Ckt-1 | 2026-07-09 14:01 | 2026-07-09 20:06 | 6:05 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Kishoreganj Ckt-1 | 2026-07-10 06:32 | 2026-07-10 08:29 | 1:57 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Kishoreganj Ckt-1 | 2026-07-10 06:32 | 2026-07-10 08:29 | 1:57 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-1 | 2026-07-10 09:34 | 2026-07-10 17:26 | 7:52 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-2 | 2026-07-10 09:35 | 2026-07-10 17:30 | 7:55 | S/O | Maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-RPCL Ckt-2 | 2026-07-23 14:21 | 2026-07-23 16:13 | 1:52 | S/O | NLDC AE. | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Kishoreganj Ckt-1 | 2026-07-24 06:10 | 2026-07-24 15:33 | 9:23 | S/O | PGNS (G2G) project works. | 70 | 656.8333 | Power interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-2 | 2026-07-28 06:25 | 2026-07-28 11:26 | 5:01 | S/O | Maint.work | 0 | 0 | No interruption
Shomvuganj 400/132kV | Shambhuganj-Kishoreganj Ckt-2 | 2026-07-06 13:20 | 2026-07-06 17:19 | 3:59 | S/O | Maint.work | 0 | 0 | No interruption
Shomvuganj 400/132kV | Shambhuganj-Kishoreganj Ckt-2 | 2026-07-24 06:55 | 2026-07-24 13:56 | 7:01 | S/O | G2G Project work | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-1 | 2026-07-09 11:08 | 2026-07-09 18:31 | 7:23 | S/O | NLDC instruction | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Valuka Ckt-2 | 2026-07-10 10:20 | 2026-07-10 17:17 | 6:57 | S/O | taken by NLDC for bhaluka end works | 0 | 0 | No interruption
Sreepur 230/132/33kV | Sreepur-Ashuganj Ckt-1 | 2026-07-12 23:53 | 2026-07-13 19:16 | 19:23 | S/O | shutdown Taken Ashuganj | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-1 | 2026-07-02 11:04 | 2026-07-02 12:51 | 1:47 | S/O | Suspension clamp maintenance work. | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-1 | 2026-07-17 06:34 | 2026-07-17 09:23 | 2:49 | S/O | Maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Kabirpur Ckt-2 | 2026-07-17 09:55 | 2026-07-17 11:40 | 1:45 | S/O | Maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Basundhara Ckt-2 | 2026-07-21 10:46 | 2026-07-21 15:20 | 4:34 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-10 08:46 |  | Unserved Energy: |  | 1626.8333
Dhaka (South) Grid Circle :
Bhulta 400/230/132kV | 400kV Ashuganj-01 | 2026-07-28 09:41 | 2026-07-28 10:29 | 0:48 | S/O | Shutdown taken by NLDC for project Work. | 0 | 0 | No interruption
Bhulta 400/230/132kV | 400kV Ashuganj-02 | 2026-07-28 10:32 | 2026-07-28 18:29 | 7:57 | S/O | Shutdown Taken by NLDC For project work | 0 | 0 | No interruption
Bhulta 400/230/132kV | 230kV Ghorashal-01 | 2026-07-31 08:48 | 2026-07-31 18:07 | 9:19 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230/132kV | 230kV Horipur-02 | 2026-07-13 06:50 | 2026-07-14 01:48 | 18:58 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230/132kV | 230kV Horipur-01 | 2026-07-15 06:32 | 2026-07-15 19:11 | 12:39 | S/O | Maint.work | 0 | 0 | No interruption
Bhulta 400/230/132kV | 132kV Narsingdi | 2026-07-30 12:26 | 2026-07-30 15:04 | 2:38 | S/O | Maint.work | 104 | 273.8667 | Power interruption
Haripur 230/132kV | 230kV Bhulta-2 | 2026-07-13 06:49 | 2026-07-14 01:47 | 18:58 | S/O | Relay Replacement Work. | 0 | 0 | No interruption
Haripur 230/132kV | 230kV Bhulta-1 | 2026-07-15 06:33 | 2026-07-15 19:11 | 12:38 | S/O | Relay Replacement work at Haripur. | 0 | 0 | No interruption
Haripur 230/132kV | Siddhirganj-1 | 2026-07-15 21:40 | 2026-07-16 00:17 | 2:37 | S/O | From Siddhirganj end. | 0 | 0 | No interruption
Haripur 230/132kV | HPL-2 | 2026-07-24 11:25 | 2026-07-24 14:19 | 2:54 | S/O | Multifuntional Meter Changing work | 0 | 0 | No interruption
Hasnabad 132/33kV | Keraniganj-2 (Pre- Aourahati) | 2026-07-03 16:37 | 2026-07-03 16:37 | 0:00 | S/O | Maint.work | 0 | 0 | No interruption
Hasnabad 132/33kV | Shitallakhya | 2026-07-03 05:57 | 2026-07-03 11:52 | 5:55 | S/O | Red hot maintenance work. | 0 | 0 | No interruption
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2026-07-07 15:45 | 2026-07-07 18:25 | 2:40 | S/O | Jumper suspension insulator broken aat 93 No. Tower | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Lalbagh Ckt. 3 | 2026-07-04 08:41 | 2026-07-04 16:06 | 7:25 | S/O | Maintenance work at Lalbagh end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 132 kV Sreenagar Ckt. 1 | 2026-07-27 08:51 | 2026-07-27 10:06 | 1:15 | S/O | High temp. maintenance work. | 0 | 0 | No interruption
Meghnaghat 230/132kV | Bus2 | 2026-07-30 13:30 | 2026-07-30 16:38 | 3:08 | S/O | maintanence work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-2 | 2026-07-07 11:01 | 2026-07-07 19:57 | 8:56 | S/O | Korerhat SS will do the maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-2 | 2026-07-08 09:11 | 2026-07-08 18:22 | 9:11 | S/O | Requested by korerhat | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-2 | 2026-07-09 09:10 | 2026-07-09 18:25 | 9:15 | S/O | Maint.work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-1 | 2026-07-11 09:56 | 2026-07-11 18:20 | 8:24 | S/O | Requested by korerhat | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-1 | 2026-07-12 10:38 | 2026-07-12 17:44 | 7:06 | S/O | requested bt korerhat | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-1 | 2026-07-13 09:08 | 2026-07-13 17:58 | 8:50 | S/O | Maint.work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-2 | 2026-07-19 09:27 | 2026-07-19 20:09 | 10:42 | S/O | Taken by korerhat | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-2 | 2026-07-20 09:36 | 2026-07-20 18:42 | 9:06 | S/O | Requested by NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-1 | 2026-07-21 09:49 | 2026-07-21 21:29 | 11:40 | S/O | Project work purpose. | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-1 | 2026-07-22 09:48 | 2026-07-22 21:46 | 11:58 | S/O | For korerhat ss project work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Korerhat 400KV Ckt-1 | 2026-07-30 10:19 | 2026-07-30 18:35 | 8:16 | S/O | taken by korerhat | 0 | 0 | No interruption
Shyampur 230/132kV | 132 kV Fatullah-2(E05) | 2026-07-06 13:31 | 2026-07-06 17:03 | 3:32 | S/O | Maintenance work at 132/33kV Fatullah Grid Sub-station (DPDC) | 0 | 0 | No interruption
Srinagar 132/33kV | Keraniganj-01 | 2026-07-27 08:50 | 2026-07-27 10:06 | 1:16 | S/O | Maintenance by Keraniganj Grid SS | 0 | 0 | No interruption
|  |  | Total : | 1900-01-08 02:01 |  | Unserved Energy: |  | 273.8667
Chattogram Grid Circle :
Baroirhat 132/33kV | Feni-1 | 2026-07-28 08:35 | 2026-07-28 12:25 | 3:50 | S/O | Maint.work | 0 | 0 | No interruption
Baroirhat 132/33kV | Hat-2 | 2026-07-29 08:32 | 2026-07-29 10:32 | 2:00 | S/O | Maint.work | 0 | 0 | No interruption
Baroirhat 132/33kV | Hat-1 | 2026-07-29 11:03 | 2026-07-29 12:46 | 1:43 | S/O | Maint.work | 0 | 0 | No interruption
Baroirhat 132/33kV | PHP | 2026-07-10 08:12 | 2026-07-10 17:06 | 8:54 | S/O | PHP Substation Work | 0 | 0 | No interruption
Baroirhat 132/33kV | PHP | 2026-07-28 12:35 | 2026-07-28 17:36 | 5:01 | S/O | Maint.work | 0 | 0 | No interruption
GPH 230/33kV | HATHAZARI | 2026-07-15 09:45 | 2026-07-15 11:50 | 2:05 | S/O | Gas Refill | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Khulshi-Ckt.-3 | 2026-07-26 09:04 | 2026-07-26 22:39 | 13:35 | S/O | Hali-khulshi ckt line checking (R-Ph) | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Ananda Bazar Ckt-1 | 2026-07-31 08:18 | 2026-07-31 14:15 | 5:57 | S/O | Due to OPGW Cable fault inspection in 4-Ckt Tower 1&11 CEpz area. | 0 | 0 | No interruption
Halishahar 132/33kV | Halishahar-Khulshi-Ckt.-3 | 2026-07-31 08:32 | 2026-07-31 14:14 | 5:42 | S/O | Due to OPGW Cable fault inspection in 4-Ckt Tower 1 &11 CEpz area | 0 | 0 | No interruption
Hathazari 230/132/33kV | GPH-01 | 2026-07-15 09:47 | 2026-07-15 11:50 | 2:03 | S/O | Sf6 Gas meter problem | 0 | 0 | No interruption
Hathazari 230/132/33kV | Raojan-01 | 2026-07-20 09:42 | 2026-07-20 13:37 | 3:55 | S/O | G2G project work | 0 | 0 | No interruption
Hathazari 230/132/33kV | Raojan-02 | 2026-07-20 09:46 | 2026-07-20 09:46 | 0:00 | S/O | G2G project work | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-07-23 08:20 | 2026-07-23 17:46 | 9:26 | S/O | To removing building near transmission line. | 0 | 0 | No interruption
Juldah 132/33kV | 132 KV Julda-Halishahar | 2026-07-29 08:24 | 2026-07-29 18:41 | 10:17 | S/O | for the demolition of the building within the right of way | 0 | 0 | No interruption
Korerhat 400/230/132kV | Feni -2 | 2026-07-06 08:57 | 2026-07-06 12:11 | 3:14 | S/O | Project work on feni side | 0 | 0 | No interruption
Korerhat 400/230/132kV | Feni -1 | 2026-07-06 12:44 | 2026-07-06 15:12 | 2:28 | S/O | Project work feni end | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-2 | 2026-07-07 10:59 | 2026-07-07 20:10 | 9:11 | S/O | Due to project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-2 | 2026-07-08 09:13 | 2026-07-08 18:21 | 9:08 | S/O | Project Work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-2 | 2026-07-09 09:11 | 2026-07-09 18:25 | 9:14 | S/O | Project Work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Madunaghat-1 | 2026-07-09 09:26 | 2026-07-09 16:55 | 7:29 | S/O | Project Work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-07-11 09:59 | 2026-07-11 18:19 | 8:20 | S/O | Project Work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-07-12 10:41 | 2026-07-12 17:43 | 7:02 | S/O | Project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-07-13 09:09 | 2026-07-13 17:58 | 8:49 | S/O | Project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-2 | 2026-07-19 09:33 | 2026-07-19 20:08 | 10:35 | S/O | Project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-2 | 2026-07-20 09:51 | 2026-07-20 18:43 | 8:52 | S/O | Project work (shunt reactor) | 0 | 0 | No interruption
Korerhat 400/230/132kV | Chowmuhani-1 | 2026-07-20 10:07 | 2026-07-20 18:52 | 8:45 | S/O | Project work (DFDR) | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-07-21 08:48 | 2026-07-21 21:23 | 12:35 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-07-22 09:47 | 2026-07-22 21:48 | 12:01 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Madunaghat-1 | 2026-07-27 13:31 | 2026-07-27 16:43 | 3:12 | S/O | For project work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Meghnaghat-1 | 2026-07-30 10:44 | 2026-07-30 18:35 | 7:51 | S/O | Shunt reactor /DFDR | 0 | 0 | No interruption
Korerhat 400/230/132kV | Feni -2 | 2026-07-30 10:57 | 2026-07-30 17:44 | 6:47 | S/O | DFDR Work | 0 | 0 | No interruption
Korerhat 400/230/132kV | Chowmuhani-3 | 2026-07-30 11:07 | 2026-07-30 18:47 | 7:40 | S/O | DFDR WORK | 0 | 0 | No interruption
Korerhat 400/230/132kV | Hathajari-1 | 2026-07-19 09:14 | 2026-07-19 19:26 | 10:12 | S/O | Project work | 0 | 0 | No interruption
Madunaghat 400/230kV | Madunaghat-Meghnaghat 400kV Ckt.-1 | 2026-07-09 09:28 | 2026-07-09 17:52 | 8:24 | S/O | SD taken by Korerhat 400kV Grid SS | 0 | 0 | No interruption
|  |  | Total : | 1900-01-08 20:17 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Brahmanbaria 132/33kV | Brahmanbaria-Ashugonj Circuit-1 | 2026-07-17 06:29 | 2026-07-17 07:08 | 0:39 | S/O | S/D taken by NLDC | 0 | 0 | No interruption
Chhatak 132/33kV | Sylhet 02 | 2026-07-07 08:57 | 2026-07-07 12:17 | 3:20 | S/O | For 132kV Sylhet Circuit-2 Relay Testing work. | 15 | 50 | Power interruption
Chhatak 132/33kV | Sylhet 01 | 2026-07-07 12:20 | 2026-07-07 13:16 | 0:56 | S/O |  | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Lakshmipur-02 | 2026-07-29 11:39 | 2026-07-30 10:10 | 22:31 | S/O | Shutdown taken by Lakshmipur substation for project work. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Korerhat-03 | 2026-07-30 11:02 | 2026-07-30 18:48 | 7:46 | S/O | Shutdown Taken by Korerhat 400/230 kV Substation. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Lakshmipur-01 | 2026-07-30 12:20 | 2026-07-30 14:10 | 1:50 | S/O | Project Work. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Maijdee-02 | 2026-07-30 12:36 | 2026-07-30 13:43 | 1:07 | S/O | Project Work. | 0 | 0 | No interruption
Chowmuhani 230/132/33kV | Lakshmipur-02 | 2026-07-30 14:19 | 2026-07-30 16:02 | 1:43 | S/O | Project Work. | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-2 | 2026-07-05 09:21 | 2026-07-05 12:17 | 2:56 | S/O | Feni 230 KV S/S project work. | 0 | 0 | No interruption
Daganbhuiyan 132/33kV | Feni Ckt-1 | 2026-07-05 12:48 | 2026-07-05 15:07 | 2:19 | S/O | project work at feni 230kv s/s. | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-1 | 2026-07-14 09:22 | 2026-07-14 15:49 | 6:27 | S/O | For project work at bus section. | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-2 | 2026-07-14 09:24 | 2026-07-14 15:50 | 6:26 | S/O | For project work at bus section. | 0 | 0 | No interruption
Daudkandi 132/33kV | Titas 50 MW Power Plant Line | 2026-07-14 09:28 | 2026-07-14 15:23 | 5:55 | S/O | For project work at bus section. | 0 | 0 | No interruption
Daudkandi 132/33kV | Main | 2026-07-14 10:55 | 2026-07-14 15:10 | 4:15 | S/O | For project work at bus section. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Bibiyana-2 | 2026-07-25 18:09 | 2026-07-26 01:21 | 7:12 | S/O | Bibiyana SS end work. | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-1 | 2026-07-05 09:11 | 2026-07-05 12:33 | 3:22 | S/O | 230 KV grid side project Work | 0 | 0 | No interruption
Feni 132/33kV | Feni Ckt-2 | 2026-07-05 12:38 | 2026-07-05 15:22 | 2:44 | S/O | 230kv grid end project work | 0 | 0 | No interruption
Feni 132/33kV | PHP (ISML) Ckt | 2026-07-10 08:18 | 2026-07-10 17:00 | 8:42 | S/O | PHP end maintenance work | 0 | 0 | No interruption
Feni 132/33kV | Barayerhat Ckt | 2026-07-28 08:34 | 2026-07-28 12:26 | 3:52 | S/O | Baroiarhat End RedHot Maintenance | 0 | 0 | No interruption
Feni 230/132kV | Feni-1 | 2026-07-05 09:09 | 2026-07-05 12:08 | 2:59 | S/O | Installation OPGW TT to gantry | 0 | 0 | No interruption
Feni 230/132kV | Feni-2 | 2026-07-05 12:37 | 2026-07-05 15:21 | 2:44 | S/O | OPGW Earthing installation. | 0 | 0 | No interruption
Feni 230/132kV | Cumilla(North)-1 | 2026-07-06 08:32 | 2026-07-06 11:57 | 3:25 | S/O | Shield wire instillation | 0 | 0 | No interruption
Feni 230/132kV | Korerhat-2 | 2026-07-06 08:32 | 2026-07-06 11:57 | 3:25 | S/O | Shield wire instillation | 0 | 0 | No interruption
Feni 230/132kV | Korerhat-1 | 2026-07-06 12:21 | 2026-07-06 15:08 | 2:47 | S/O | Shield wire instillation | 0 | 0 | No interruption
Feni 230/132kV | Cumilla(North)-2 | 2026-07-06 12:21 | 2026-07-06 15:14 | 2:53 | S/O | Shield wire instillation | 0 | 0 | No interruption
Feni 230/132kV | Chauddagram-1 | 2026-07-06 15:36 | 2026-07-06 17:30 | 1:54 | S/O | Shield wire instillation | 0 | 0 | No interruption
Feni 230/132kV | Feni-4 | 2026-07-06 15:41 | 2026-07-06 17:39 | 1:58 | S/O | Shield wire instillation | 0 | 0 | No interruption
Feni 230/132kV | Chauddagram-2 | 2026-07-06 17:41 | 2026-07-06 19:23 | 1:42 | S/O | Shield wire instillation | 0 | 0 | No interruption
Feni 230/132kV | Feni-3 | 2026-07-06 17:44 | 2026-07-06 19:42 | 1:58 | S/O | After work clearance given | 0 | 0 | No interruption
Feni 230/132kV | Korerhat-2 | 2026-07-30 10:53 | 2026-07-30 17:44 | 6:51 | S/O | DFDR testing at Korerhat SS end. | 0 | 0 | No interruption
Feni 230/132kV | Dagonbhuyan-2 | 2026-07-05 09:21 | 2026-07-05 12:17 | 2:56 | S/O | Installation OPGW TT to gantry | 0 | 0 | No interruption
Feni 230/132kV | Dagonbhuyan-1 | 2026-07-05 12:46 | 2026-07-05 15:07 | 2:21 | S/O | OPGW Earthing installation. | 0 | 0 | No interruption
Kachua 230/132/33kV | Laksam CKT-1 | 2026-07-06 12:03 | 2026-07-06 18:30 | 6:27 | S/O | SAS signal test | 0 | 0 | No interruption
Kachua 230/132/33kV | Laksam CKT-2 | 2026-07-07 10:14 | 2026-07-07 19:45 | 9:31 | S/O | For checking SAS signal. | 0 | 0 | No interruption
Kachua 230/132/33kV | Laksam CKT-1 | 2026-07-08 10:12 | 2026-07-08 15:40 | 5:28 | S/O | SAS signal checking by spmd | 0 | 0 | No interruption
Kachua 230/132/33kV | Laksam CKT-2 | 2026-07-08 15:41 | 2026-07-08 18:50 | 3:09 | S/O | SAS signal checking by SPMD | 0 | 0 | No interruption
Kachua 230/132/33kV | Laksam CKT-2 | 2026-07-10 15:04 | 2026-07-11 20:01 | 28:57 | S/O | to resolve the Pole Discrepancy fault. | 0 | 0 | No interruption
Lakshmipur 132/33kV | Lakshmipur-Chowmuhani Circuit 2 | 2026-07-06 12:17 | 2026-07-06 16:18 | 4:01 | S/O | Chowmuhani-Lakshmipur Ckt-02 Shutdown taken for project work. | 0 | 0 | No interruption
Lakshmipur 132/33kV | Lakshmipur-Chowmuhani Circuit 2 | 2026-07-29 11:25 | 2026-07-29 19:27 | 8:02 | S/O | Scada Integration Project Work | 0 | 0 | No interruption
Lakshmipur 132/33kV | Lakshmipur-Chowmuhani Circuit 1 | 2026-07-30 12:20 | 2026-07-30 14:17 | 1:57 | S/O | Lakshmipur-Chowmuhani Circuit-1 has taken Shutdown to fix Scada Integration work via Project(CNEEC). | 0 | 0 | No interruption
Lakshmipur 132/33kV | Lakshmipur-Chowmuhani Circuit 2 | 2026-07-30 14:19 | 2026-07-30 16:02 | 1:43 | S/O | Lakshmipur-Chowmuhani Circuit-2 has taken Shutdown to fix Scada Integration work via Project(CNEEC). | 0 | 0 | No interruption
Maijdee 132/33kV | Chowmuhoni-Maijdee ckt -02 | 2026-07-30 12:35 | 2026-07-30 13:42 | 1:07 | S/O | project work | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-01 | 2026-07-29 09:00 | 2026-07-29 17:35 | 8:35 | S/O | D/S maintenance work | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-B.Baria Ckt-02 | 2026-07-30 10:07 | 2026-07-30 16:50 | 6:43 | S/O | E/S Maintenance Work | 0 | 0 | No interruption
Shahjibazar 132/33kV | SPCL 86 MW | 2026-07-05 09:25 | 2026-07-05 15:28 | 6:03 | S/O | 86MW plant maitenance work. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-2 | 2026-07-07 08:57 | 2026-07-07 12:15 | 3:18 | S/O | relay test | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2026-07-07 12:24 | 2026-07-07 13:15 | 0:51 | S/O | Relay testing . | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2026-07-28 09:45 | 2026-07-31 16:15 | 78:30 | S/O | CB fault | 0 | 0 | No interruption
|  |  | Total : | 1900-01-11 18:17 |  | Unserved Energy: |  | 50
Khulna Grid Circle :
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-07-07 09:38 | 2026-07-07 12:37 | 2:59 | S/O | Bagerhat bhandaria line red hot maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-07-12 16:43 | 2026-07-12 18:12 | 1:29 | S/O | CT R phase clamp overheat maintenance work | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Goalpara Line | 2026-07-16 06:30 | 2026-07-16 07:12 | 0:42 | S/O | Bagerhat-Goalpara, Gollamari-Gopalganj line conductor tapping. | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Goalpara Line | 2026-07-16 10:24 | 2026-07-16 18:51 | 8:27 | S/O | Maint.work | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat-Goalpara Line | 2026-07-18 15:13 | 2026-07-18 17:43 | 2:30 | S/O | Maint.work | 0 | 0 | No interruption
Bagerhat 132/33kV | Bagerhat- Bhandaria | 2026-07-20 11:29 | 2026-07-20 12:21 | 0:52 | S/O | Tree trimming work of Tower 9-10 span of 132kv Bagerhat -Bhandaria Line. | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2026-07-12 16:44 | 2026-07-12 18:11 | 1:27 | S/O | Shutdown taken from Bagerhat SS | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2026-07-12 19:33 | 2026-07-16 17:52 | 94:19 | S/O | Shutdown by ALDC | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-2 | 2026-07-14 07:09 | 2026-07-14 10:20 | 3:11 | S/O | Red hot maintenance work | 0 | 0 | No interruption
Barishal 132/33kV | 132kv Bhandaria ckt | 2026-07-20 11:30 | 2026-07-20 12:20 | 0:50 | S/O | Shutdown by ALDC | 0 | 0 | No interruption
Barishal 230/132kV | Barishal ckt-02 | 2026-07-14 07:09 | 2026-07-14 10:19 | 3:10 | S/O | DS maintenance | 0 | 0 | No interruption
Bhandaria 132/33kV | Bagerhat (L3) | 2026-07-07 09:39 | 2026-07-07 12:31 | 2:52 | S/O | Maint.work | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-1 | 2026-07-30 09:48 | 2026-07-30 17:44 | 7:56 | S/O | Project work at Gopalganj ss end. | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2026-07-30 09:55 | 2026-07-30 17:45 | 7:50 | S/O | Project work at Gopalganj ss end | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-1 | 2026-07-31 08:02 | 2026-07-31 17:17 | 9:15 | S/O | Tower crossing | 0 | 0 | No interruption
Faridpur 132/33kV | 230kV Faridpur-Gopalganj CKT-2 | 2026-07-31 08:03 | 2026-07-31 17:18 | 9:15 | S/O | Tower crossing | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Bagerhat | 2026-07-16 06:32 | 2026-07-16 07:12 | 0:40 | S/O | Goalpara-Bagerhat line -1 to gopalgonj- Gollamari ckt -1 Crossing point joint ( between tower no 61-62 ) | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Bagerhat | 2026-07-16 10:25 | 2026-07-16 10:25 | 0:00 | S/O | Tapping work for Goalpara-Bagerhat Circuit-1 and Garlamari-Gopalgong Circuit-1 | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-NWPGCL | 2026-07-03 08:44 | 2026-07-03 17:33 | 8:49 | S/O | Maintanance works. | 0 | 0 | No interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2026-07-01 13:26 | 2026-07-01 16:34 | 3:08 | S/O | Shutdown taken by DWZTGEP. | 0 | 0 | No interruption
Gollamari 132/33kV | E07 Gollamari-Gopalgonj Line - 2 | 2026-07-01 13:26 | 2026-07-01 16:05 | 2:39 | S/O | Shutdown taken by DWZTGEP. | 0 | 0 | No interruption
Gollamari 132/33kV | E01 Gollamari-Gopalgonj Line - 1 | 2026-07-11 08:41 | 2026-07-11 08:41 | 0:00 | S/O | DWZTGEP project work at 42 No Tower | 0 | 0 | No interruption
Gollamari 132/33kV | E07 Gollamari-Gopalgonj Line - 2 | 2026-07-11 08:42 | 2026-07-18 17:51 | 177:09 | S/O | DWZTGEP project work at 42 No Tower | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-1 | 2026-07-03 07:23 | 2026-07-03 08:14 | 0:51 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-2 | 2026-07-03 08:21 | 2026-07-03 08:55 | 0:34 | S/O | SPMD work | 0 | 0 | No interruption
Gopalganj 400/132kV | 132kV Madaripur Ckt-4 | 2026-07-04 11:26 | 2026-07-04 13:00 | 1:34 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Aminbazar Ckt-1 | 2026-07-04 15:02 | 2026-07-04 21:15 | 6:13 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-01 | 2026-07-30 09:54 | 2026-07-30 17:44 | 7:50 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-02 | 2026-07-30 09:55 | 2026-07-30 17:45 | 7:50 | S/O | Maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-01 | 2026-07-31 08:03 | 2026-07-31 17:19 | 9:16 | S/O | ,Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 230kV Faridpur CKT-02 | 2026-07-31 08:04 | 2026-07-31 17:20 | 9:16 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV | 400kV Rooppur | 2026-07-04 15:10 | 2026-07-05 14:18 | 23:08 | S/O | Maint.work | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Noapara-1 | 2026-07-13 16:08 | 2026-07-13 17:23 | 1:15 | S/O | R & B Phase Red Hot Maintenance. | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Noapara-1 | 2026-07-26 06:21 | 2026-07-26 08:58 | 2:37 | S/O | S/D for south ckt-02 bus DS maintenance work. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- Noapara-2 | 2026-07-26 06:21 | 2026-07-26 09:00 | 2:39 | S/O | S/D for south ckt-02 bus DS maintenance work. | 0 | 0 | No interruption
Khulna (C) | North-WestCkt-1 | 2026-07-26 06:23 | 2026-07-26 09:06 | 2:43 | S/O | S/D for south ckt-02 bus DS maintenance work. | 0 | 0 | No interruption
Khulna (C) | North- West Ckt-2 | 2026-07-26 06:23 | 2026-07-26 09:06 | 2:43 | S/O | S/D for south ckt-02 bus DS maintenance work. | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -2 | 2026-07-05 14:43 | 2026-07-05 16:41 | 1:58 | S/O | Hot spot maint. Work. | 27 | 53.1 | Power interruption
Khulna (C) | 132 kV Central- South -1 | 2026-07-10 07:11 | 2026-07-10 11:31 | 4:20 | S/O | Emergency maintenance | 13 | 56.3333 | Power interruption
Khulna (C) | 132 kV Central- South -2 | 2026-07-10 07:26 | 2026-07-10 11:32 | 4:06 | S/O | Emergency maintenance | 13 | 53.3 | Power interruption
Khulna (C) | 132 kV Central- South -1 | 2026-07-26 06:24 | 2026-07-26 17:55 | 11:31 | S/O | Maint. Work of South ckt-2 main bus DS | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-2 | 2026-07-05 14:42 | 2026-07-05 16:41 | 1:59 | S/O | ALDC Instruction | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-2 | 2026-07-09 17:03 | 2026-07-09 17:58 | 0:55 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2026-07-10 06:55 | 2026-07-10 11:38 | 4:43 | S/O | Busbar DS Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2026-07-10 07:09 | 2026-07-10 11:34 | 4:25 | S/O | Busbar DS Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-1 | 2026-07-10 07:12 | 2026-07-10 11:40 | 4:28 | S/O | Busbar DS Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Gallamari Ckt-2 | 2026-07-10 07:12 | 2026-07-10 11:41 | 4:29 | S/O | Busbar DS Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-2 | 2026-07-10 07:25 | 2026-07-10 11:34 | 4:09 | S/O | Busbar DS Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV | Satkhira Ckt-1 | 2026-07-18 10:23 | 2026-07-18 16:26 | 6:03 | S/O | Maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2026-07-26 06:25 | 2026-07-26 17:55 | 11:30 | S/O | Project Work at Central SS end. | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 1 | 2026-07-13 16:01 | 2026-07-13 17:25 | 1:24 | S/O | According to ALDC's Instruction. | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 1 | 2026-07-26 06:20 | 2026-07-26 08:58 | 2:38 | S/O | Maint.work | 0 | 0 | No interruption
Noapara 132/33kV | khulna central - 2 | 2026-07-26 06:21 | 2026-07-26 09:00 | 2:39 | S/O | Maint.work | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-2 | 2026-07-01 06:04 | 2026-07-01 19:08 | 13:04 | S/O | Operation by ALDC | 0 | 0 | No interruption
Patuakhali 132/33kV | PAYRA-PATUAKHALI CKT-2 | 2026-07-21 06:41 | 2026-07-21 15:40 | 8:59 | S/O | Payra grid end side red hot maintenance. | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-02 | 2026-07-01 06:05 | 2026-07-01 19:07 | 13:02 | S/O | High temperature maintenance | 0 | 0 | No interruption
Payra 400/132/33kV | Payra Patuakhali Line-02 | 2026-07-21 06:41 | 2026-07-21 15:40 | 8:59 | S/O | High temperature maintenance | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2026-07-10 06:54 | 2026-07-10 11:39 | 4:45 | S/O | Maint.work | 0 | 0 | No interruption
Satkhira 132/33kV | Khulna South-1 (L-1) | 2026-07-18 10:23 | 2026-07-18 16:27 | 6:04 | S/O | Maint.work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-22 02:08 |  | Unserved Energy: |  | 162.7333
HVDC Grid Circle :
BIPTC | Baharampur-3 | 2026-07-30 10:26 | 2026-07-30 12:25 | 1:59 | S/O | Shutdown is taken from baharampur end. | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2026-07-30 14:46 | 2026-07-30 16:59 | 2:13 | S/O | Shutdown taken from Berhampore End. | 0 | 0 | No interruption
Baghabari 230/132kV | Baghabari-Roppur 230kV Ckt-1 | 2026-07-31 09:58 | 2026-07-31 17:30 | 7:32 | S/O | SCADA Integration & Commissioning এর Live CRP side Cable Termination কাজের জন্য। | 0 | 0 | No interruption
Bheramara 230/132kV | Kushtia 1 | 2026-07-04 09:16 | 2026-07-04 14:51 | 5:35 | S/O | Project work | 0 | 0 | No interruption
Bheramara 230/132kV | Kushtia 2 | 2026-07-14 11:33 | 2026-07-25 14:58 | 267:25 | S/O | Erection and Stringing Work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-1 | 2026-07-14 06:12 | 2026-07-14 08:21 | 2:09 | S/O | natore grid redhot maintenance work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-2 | 2026-07-14 06:13 | 2026-07-14 08:22 | 2:09 | S/O | natore grid redhot maintenance work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2026-07-24 08:34 | 2026-07-24 13:11 | 4:37 | S/O | Maint.work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Kaliganj Ckt-2 | 2026-07-08 15:56 | 2026-07-08 18:26 | 2:30 | S/O | Measurement of Jumparing in Moheshpur Grid | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Kaliganj Ckt-2 | 2026-07-09 16:37 | 2026-07-09 17:53 | 1:16 | S/O | Maint.work | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah2-Kaliganj Ckt-2 | 2026-07-15 16:27 | 2026-07-15 17:55 | 1:28 | S/O | As per order of aldc | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia -Bheramara-1 | 2026-07-04 09:15 | 2026-07-04 14:50 | 5:35 | S/O | Maint.work | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia-Bheramara-2 | 2026-07-14 11:25 | 2026-07-14 11:25 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia-Jhenaidah-2 | 2026-07-21 13:22 | 2026-07-21 17:44 | 4:22 | S/O | DWZTGE project work | 0 | 0 | No interruption
Ullahpara 132/33kV | 132 KV Sirajgonj Ckt-1 | 2026-07-11 13:26 | 2026-07-11 20:21 | 6:55 | S/O | Dummy OPGW Connection | 0 | 0 | No interruption
Ullahpara 132/33kV | Shahjadpur Ckt | 2026-07-11 14:33 | 2026-07-11 20:21 | 5:48 | S/O | Dummy OPGW Connection | 0 | 0 | No interruption
Ullahpara 132/33kV | Baghabari ckt | 2026-07-11 15:00 | 2026-07-11 17:55 | 2:55 | S/O | Dummy OPGW Connection | 0 | 0 | No interruption
Ullahpara 132/33kV | 132 KV Sirajgonj Ckt-2 | 2026-07-11 17:55 | 2026-07-11 20:21 | 2:26 | S/O | Dummy OPGW Connection | 0 | 0 | No interruption
|  |  | Total : | 1900-01-12 14:54 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura 132/33kV | Natore-1 | 2026-07-14 06:12 | 2026-07-14 08:41 | 2:29 | S/O | from natore end and 132kv s/s end | 0 | 0 | No interruption
Bogura 132/33kV | Natore-2 | 2026-07-14 06:12 | 2026-07-14 08:42 | 2:30 | S/O | from natore end and 132kv s/s end | 0 | 0 | No interruption
Naogaon 132/33kV | Naogaon-Niamatpur Ckt-2 | 2026-07-29 08:11 | 2026-07-30 21:32 | 37:21 | S/O | Project works om Niamatpur Grid | 0 | 0 | No interruption
Niamatpur 132/33kV | 132 kV Naogaon ckt-2 | 2026-07-29 08:11 | 2026-07-30 21:31 | 37:20 | S/O | Patnitola s/s work | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | EPVTL-1 | 2026-07-20 09:58 | 2026-07-20 17:44 | 7:46 | S/O | RTU Interconnection work | 0 | 0 | No interruption
Purbasadipur 230/132/33kV | EPVTL-2 | 2026-07-21 09:41 | 2026-07-21 18:03 | 8:22 | S/O | RTU work in EPVTL side | 0 | 0 | No interruption
Rahanpur 400/132kV | Rahanpur-Niamatpur 132 KV Line Ckt-01 | 2026-07-27 07:45 | 2026-07-27 10:57 | 3:12 | S/O | Due to maintainance work at Niyamatpur side | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Natore-1 | 2026-07-14 06:15 | 2026-07-14 08:35 | 2:20 | S/O | Natore grid substation was taken Shutdown for 132 KV Busbar Maintenance Work. | 0 | 0 | No interruption
Rajshahi 132/33kV | 132 kV Natore-2 | 2026-07-14 06:15 | 2026-07-14 13:02 | 6:47 | S/O | Natore grid substation was taken Shutdown for 132 KV Busbar Maintenance Work. | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Lalmonirhat | 2026-07-12 12:58 | 2026-07-12 14:27 | 1:29 | S/O | Maint.work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Confidence-1 | 2026-07-12 11:25 | 2026-07-12 12:45 | 1:20 | S/O | Clamp Change. | 0 | 0 | No interruption
Sirajganj 132/33kV | Ullapara -1 | 2026-07-11 14:24 | 2026-07-11 20:23 | 5:59 | S/O | Telecommunication work by TRTUD Bogura at Ullapara S/S End. All operations have been conducted by the instruction of ALDC Bogura. | 0 | 0 | No interruption
Sirajganj 132/33kV | Ullapara -2 | 2026-07-11 17:56 | 2026-07-11 20:23 | 2:27 | S/O | Telecommunication work by TRTUD Bogura at Ullapara S/S End. All operations have been conducted by the instruction of ALDC Bogura. | 0 | 0 | No interruption
Thakurgaon 132/33kV | Thakurgaon-EPV Ckt-1 | 2026-07-22 10:05 | 2026-07-22 17:30 | 7:25 | S/O | Work at EPVTL CRP. | 0 | 0 | No interruption
Thakurgaon 132/33kV | Thakurgaon-EPV Ckt-2 | 2026-07-23 09:39 | 2026-07-23 17:32 | 7:53 | S/O | EMA Power Plant Work in RTU Control Pannel. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-04 14:40 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-03-25 09:03 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:July 2026
| Area | Previous Month (June' 2026) |  |  |  | Current Month (July'2026)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 30 | 13 | 44 | 87 | 13 | 9 | 91 | 113
2 | Dhaka (South) Grid Circle. | 16 | 7 | 59 | 82 | 22 | 11 | 57 | 90
3 | Chattogram Grid Circle. | 11 | 11 | 41 | 63 | 16 | 15 | 64 | 95
4 | Cumilla Grid Circle. | 31 | 20 | 58 | 109 | 25 | 20 | 80 | 125
5 | Khulna Grid Circle. | 39 | 22 | 73 | 134 | 22 | 9 | 86 | 117
6 | HVDC Grid Circle | 5 | 16 | 26 | 47 | 26 | 16 | 29 | 71
7 | Bogura Grid Circle. | 26 | 13 | 34 | 73 | 21 | 30 | 48 | 99
8 | Others
9 | Total | 158 | 102 | 335 | 595 | 145 | 110 | 455 | 710
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month: July 2026
| Area | Previous Month (June' 2026) |  |  |  | Current Month (July '2026)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 1054.5 | 91 | 352.42 | 1497.92 | 1061.12 | 456.17 | 3581.01 | 5098.3
2 | Dhaka (South) Grid Circle. | 425.16 | - | 3271.29 | 3696.45 | 453.38 | 81.67 | 2234.54 | 2769.59
3 | Chattogram Grid Circle. | 57.5 | 181.83 | 298.7 | 538.03 | 119.17 | 38.67 | 649.62 | 807.46
4 | Cumilla Grid Circle. | 650.55 | 290.83 | 866.12 | 1807.5 | 218.04 | 388.47 | 435.23 | 1041.74
5 | Khulna Grid Circle. | 312.77 | 71.33 | 1100.85 | 1484.95 | 151.75 | 101.9 | 724.26 | 977.91
6 | HVDC Grid Circle | 13.07 | 128.92 | 104.23 | 246.22 | 87.16 | 195.47 | 65.33 | 347.96
7 | Bogura Grid Circle. | 201.5 | 21.35 | 56.83 | 279.68 | 183.38 | 565.13 | 1378.69 | 2127.2
8 | Others | bar: Energy unserved ( MWH ) due to Total
9 | Total | 2715.05 | 785.26 | 6050.44 | 9550.75 | 2274 | 1827.48 | 9068.68 | 13170.16
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:July 2026
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 10 | 12 | 22 | 3 | 4 | 15 | 2858.06
2 | Dhaka (South) | 5031.6 | 9 | 10 | 19 | 2 | 7 | 10 | 2455.71
3 | Chattogram | 2042 | 9 | 10 | 19 | 4 | 5 | 10 | 798.15
4 | Cumilla | 2981 | 19 | 10 | 29 | 12 | 4 | 13 | 835.35
5 | Khulna | 2434 | 15 | 10 | 25 | 12 | 2 | 11 | 815.18
6 | HVDC | 5954.3 | 10 | 4 | 14 | 5 | 4 | 5 | 319.39
7 | Bogura | 3145.6 | 24 | 18 | 42 | 3 | 11 | 28 | 2091.71
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 10173.55
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 98.97%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | HVDC | 99.99%
6 | Bogura | 99.99%
7 | Cumilla | 99.99% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:July 2026
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 4 | 3 | 7 | 2 |  | 5 | 2240.23
2 | Dhaka (South) | 990.29 | - | 1 | 1 | 2 | - | 1 | 1 | 313.87
3 | Chattogram | 917 | - | 1 | - | 1 | 1 | - | - | 9.3
4 | Cumilla | 1648.16 | - | 7 | 1 | 8 | 6 | - | 2 | 206.38
5 | Khulna | 1238.4 | - | - | 3 | 3 | - | - | 3 | 162.73
6 | HVDC | 1325 | - | 2 | - | 2 | 2 | - | - | 28.5833
7 | Bogura | 1803.3 |  | 1 | - | 1 | - | - | 1 | 35.5
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 2996.5933
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 99.99%
6 | Bogura | 99.99%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:July 2026
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2026-07-01 | 53 | - | 15 | 27 hr 02 min | 1 | 2 hr 41 min
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:July 2026
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Bajitpur 132/33kV | 1 | 0:57 | 19
Barapukuria 230/132/33kV | 1 | 2:44 | 68.3333
Barguna 132/33kV | 2 | 0:48 | 8
Barishal 132/33kV | 3 | 1:54 | 46.4333
Barishal 230/132kV | 8 | 13:44 | 435.3333
Bhaluka 132/33kV | 6 | 7:09 | 650.4
Bhandaria 132/33kV | 1 | 2:29 | 49.6667
Bhangura 132/33kV | 4 | 4:48 | 61.0333
Bheramara(GK) 132/33kV | 0 | 0:00 | 0
Bhulta 132/33kV | 1 | 9:00 | 540
Bhulta 400/230/132kV | 1 | 2:38 | 273.8667
Bog-Sherpur 132/33kV | 2 | 4:27 | 124.8333
Brahmanbaria 132/33kV | 1 | 2:41 | 93.9167
Chapai 132/33kV | 2 | 3:26 | 82.9333
Chauddagram 132/33kV | 1 | 1:25 | 49.5833
Chhatak 132/33kV | 6 | 12:15 | 191.2667
Chowmuhani 230/132/33kV | 6 | 8:11 | 311.4167
Coxsbazar 132/33kV | 5 | 37:22 | 245.9167
Cumilla(S) 132/33kV | 4 | 1:00 | 36.6667
Daganbhuiyan 132/33kV | 1 | 1:14 | 14.8
Dhamrai 132/33kV | 1 | 4:17 | 171.3333
Dohazari 132/33kV | 10 | 10:10 | 480.4667
Faridpur 132/33kV | 2 | 4:37 | 81.1667
Fenchuganj 230/132/33kV | 3 | 1:49 | 19
Feni 132/33kV | 2 | 1:22 | 54.9
Ghorashal 230kV | 2 | 3:12 | 269.3
Gopalganj 132/33kV | 3 | 3:10 | 58.4167
Halishahar 132/33kV | 1 | 0:42 | 7
Hasnabad 132/33kV | 4 | 2:02 | 80.3333
Ishurdi 132/33kV | 1 | 0:15 | 6.25
Jashore 132/33kV | 2 | 1:02 | 46.5
Jhenaidah 132/33kV | 2 | 0:49 | 28.5833
Joydebpur 132/33kV | 1 | 0:22 | 7.3333
Joypurhat 132/33kV | 2 | 4:58 | 64.5667
Kabirpur 132/33kV | 7 | 14:24 | 1047.6
Kaliakoir 400/230/132kV | 1 | 8:44 | 436.6667
Kasba 132/33kV | 1 | 0:42 | 10.5
Khulna (C) | 4 | 10:48 | 166.7333
Kodda 132/33kV | 2 | 13:12 | 509.25
Kulaura 132/33kV | 2 | 1:56 | 44.9333
Kushtia 132/33kV | 4 | 7:13 | 129.6917
Lalmonirhat 132/33kV | 1 | 1:11 | 35.5
Madaripur 132/33kV | 2 | 1:58 | 64.7667
Magura 132/33kV | 0 | 0:00 | 0
Mahasthangarh 132/33kV | 1 | 5:49 | 162.8667
Maijdee 132/33kV | 1 | 2:25 | 38.6667
Manikganj 132/33kV | 1 | 1:18 | 32.5
Maniknagar 132/33kV | 1 | 0:00 | 0
Mithapukur 132/33kV | 3 | 7:37 | 141.2
Mongla 132/33kV | 1 | 0:16 | 1.8667
Munshiganj 132/33kV | 5 | 12:41 | 352.1667
Mymensingh 132/33kV | 3 | 33:38 | 1626.8333
Naogaon 132/33kV | 1 | 2:21 | 23.5
Narail 132/33kV | 1 | 1:58 | 47.2
Narshingdi 132/33kV | 1 | 0:42 | 24.5
Natore 132/33kV | 7 | 12:17 | 560.7917
Nawabganj 132/33kV | 3 | 10:02 | 221.4167
Niamatpur 132/33kV | 4 | 5:12 | 97.9167
Noapara 132/33kV | 1 | 0:44 | 18.3333
Pabna 132/33kV | 1 | 0:10 | 5.8333
Palashbari 132/33kV | 8 | 6:58 | 280.4167
Patiya 132/33kV | 3 | 5:49 | 45.9
Purbasadipur 230/132/33kV | 1 | 1:14 | 12.3333
Rajbari 132/33kV | 0 | 0:00 | 0
Rajshahi 132/33kV | 2 | 1:37 | 18.3333
Rajshahi 230/132/33kV | 2 | 1:35 | 79.1667
Ramganj 132/33kV | 3 | 3:01 | 46.75
Rangpur 132/33kV | 2 | 7:13 | 262.9167
Saidpur 132/33kV | 1 | 5:58 | 71.6
Shahjadpur 132/33kV | 2 | 2:13 | 70.0833
Shahjibazar 132/33kV | 2 | 1:58 | 98.3333
Sirajganj 132/33kV | 2 | 1:10 | 23.3333
Sitakunda 132/33kV | 1 | 1:05 | 28.1667
Sonargaon 132/33kV | 2 | 46:14 | 958.5
Sreepur 230/132/33kV | 5 | 4:14 | 557.05
Srinagar 132/33kV | 2 | 3:00 | 49.5
Sylhet 132/33kV | 4 | 0:42 | 31
Tangail 132/33kV | 1 | 2:01 | 40.3333
Thakurgaon 132/33kV | 1 | 0:20 | 16.6667
| 195 | 410:39 | 13170.1667
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: July 2026
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 21 | 2026-07-31 18:30
2 | AKSML | 169.2 | 2026-07-07 03:00
3 | Aftabnagar | 50 | 2026-07-04 19:30
4 | Agargaon | 131 | 2026-07-15 13:00
5 | Agrabad | 84 | 2026-07-04 19:00
6 | Amnura | 39 | 2026-07-08 13:00
7 | Ashuganj | 108 | 2026-07-02 00:00
8 | BSRM | 206 | 2026-07-07 05:00
9 | Bagerhat | 97 | 2026-07-09 21:00
10 | Bajitpur | 104 | 2026-07-03 19:30
11 | Bakerganj | 16.4 | 2026-07-01 20:00
12 | Bakulia | 105 | 2026-07-04 20:00
13 | Banani | 111.7 | 2026-07-10 21:00
14 | Bangabhaban | 21 | 2026-07-02 11:00
15 | Barapukuria | 82 | 2026-07-15 22:00
16 | Barguna | 24 | 2026-07-01 21:00
17 | Barishal | 114 | 2026-07-03 13:00
18 | Barishal-230 | 120 | 2026-07-12 19:30
19 | Baroaulia | 65 | 2026-07-05 21:00
20 | Baroirhat | 78 | 2026-07-26 23:00
21 | Bashundhara | 231 | 2026-07-04 19:00
22 | BashundharaCement | 13 | 2026-07-07 14:00
23 | Beanibazar | 94 | 2026-07-04 19:00
24 | Benapole | 80 | 2026-07-18 19:30
25 | Bhaluka | 181 | 2026-07-08 19:30
26 | Bhandaria | 66 | 2026-07-21 19:30
27 | Bhangura | 45 | 2026-07-17 22:00
28 | Bheramara(GK) | 75 | 2026-07-04 19:30
29 | Bhulta | 255 | 2026-07-22 18:00
30 | Bog-Sherpur | 88 | 2026-07-02 22:00
31 | Bogura | 199 | 2026-07-15 23:00
32 | Borhanuddin | 83 | 2026-07-03 23:00
33 | Brahmanbaria | 157 | 2026-07-03 19:30
34 | Cantonment | 144 | 2026-07-04 15:00
35 | Chandina | 47 | 2026-07-03 22:00
36 | Chandpur | 96 | 2026-07-04 20:00
37 | Chandraghona | 39 | 2026-07-28 23:00
38 | Chapai | 90 | 2026-07-04 23:00
39 | Charfasson | 35 | 2026-07-01 23:00
40 | Charsaidpur | 48 | 2026-07-29 10:00
41 | Chauddagram | 86 | 2026-07-03 23:00
42 | Chhatak | 46 | 2026-07-01 00:00
43 | Chowmuhani | 172 | 2026-07-02 20:00
44 | Chuadanga | 129 | 2026-07-08 21:00
45 | Coxsbazar | 154 | 2026-07-02 19:00
46 | Cumilla(N) | 160 | 2026-07-14 23:00
47 | Cumilla(S) | 197 | 2026-07-04 16:00
48 | Daganbhuiyan | 57 | 2026-07-28 16:00
49 | Daudkandi | 156 | 2026-07-14 23:00
50 | DhakaUniversity | 104 | 2026-07-29 13:00
51 | Dhamrai | 110 | 2026-07-03 21:00
52 | Dhanmondi | 126.3 | 2026-07-05 13:00
53 | Dohazari | 118 | 2026-07-03 20:00
54 | Faridpur | 193 | 2026-07-28 21:00
55 | Fatullah | 112 | 2026-07-28 15:00
56 | Fenchuganj | 53 | 2026-07-01 00:00
57 | Feni | 125 | 2026-07-04 21:00
58 | GPH | 82 | 2026-07-02 01:00
59 | Ghatail | 101 | 2026-07-05 19:30
60 | Ghorashal | 0 | 2026-07-01 00:00
61 | Ghorashal-230 | 112 | 2026-07-16 04:00
62 | Goalpara | 39 | 2026-07-05 01:00
63 | Gollamari | 120 | 2026-07-05 00:00
64 | Gopalganj | 128 | 2026-07-04 22:00
65 | Gulshan | 126 | 2026-07-06 12:00
66 | Halishahar | 125 | 2026-07-26 18:00
67 | HaripurSBU | 162 | 2026-07-12 10:00
68 | Hasnabad | 105 | 2026-07-26 17:00
69 | Hathazari | 99 | 2026-07-02 19:30
70 | Hatirjheel | 106 | 2026-07-19 13:00
71 | Ishurdi | 91 | 2026-07-26 20:00
72 | Jaldhaka | 103 | 2026-07-04 22:00
73 | Jamalpur | 150 | 2026-07-04 21:00
74 | Jashore | 167 | 2026-07-04 21:00
75 | Jhenaidah | 109 | 2026-07-04 19:30
76 | Joydebpur | 183 | 2026-07-21 19:30
77 | Joypurhat | 80 | 2026-07-04 22:00
78 | Juldah | 22 | 2026-07-01 13:00
79 | KSRM | 51 | 2026-07-08 12:00
80 | Kabirpur | 276 | 2026-07-26 19:00
81 | Kachua | 108 | 2026-07-04 19:30
82 | Kaliganj | 43 | 2026-07-15 00:00
83 | Kallyanpur | 156 | 2026-07-03 12:00
84 | Kalurghat | 45 | 2026-07-14 12:00
85 | Kamrangirchar | 88 | 2026-07-29 13:00
86 | Kaptai | N/A | N/A
87 | Kasba | 49 | 2026-07-27 22:00
88 | Kazla | 129 | 2026-07-29 13:00
89 | Keranigonj | 96 | 2026-07-04 19:30
90 | Khagrachori | 42 | 2026-07-15 19:00
91 | Khulna | 74 | 2026-07-12 12:00
92 | Khulshi | 215 | 2026-07-11 15:00
93 | Kishoreganj | 154 | 2026-07-03 22:00
94 | Kodda | 319 | 2026-07-19 20:00
95 | Kulaura | 64 | 2026-07-14 19:00
96 | Kurigram | 80 | 2026-07-05 19:30
97 | Kushtia | 171 | 2026-07-28 21:00
98 | Laksam | 39 | 2026-07-14 23:00
99 | Lakshmipur | 51 | 2026-07-29 19:00
100 | Lalbag | 84 | 2026-07-23 13:00
101 | Lalmonirhat | 80 | 2026-07-26 20:00
102 | MI_Cement | 18.1 | 2026-07-18 15:00
103 | Madanganj | 50 | 2026-07-27 21:00
104 | Madaripur | 134 | 2026-07-04 23:00
105 | Madartek | 94 | 2026-07-05 00:00
106 | Madunaghat | 63 | 2026-07-14 15:00
107 | Magura | 76 | 2026-07-04 20:00
108 | Mahasthangarh | 128 | 2026-07-29 01:00
109 | Maijdee | 49 | 2026-07-01 19:30
110 | Manikganj | 158 | 2026-07-08 21:00
111 | Maniknagar | 89 | 2026-07-28 14:00
112 | Matarbari | 61 | 2026-07-31 19:30
113 | Matuail | 83 | 2026-07-04 15:00
114 | Metrorail_Motijheel | 43 | 2026-07-05 10:00
115 | Metrorail_Uttara | 18 | 2026-07-15 10:00
116 | Millgate | 119 | 2026-07-04 15:00
117 | Mirpur | 190 | 2026-07-03 13:00
118 | Mirsorai | 53 | 2026-07-06 11:00
119 | Mirzapur | 56 | 2026-07-01 19:30
120 | Mithapukur | 91 | 2026-07-13 20:00
121 | Modern | N/A | N/A
122 | Mogbazar | 108.5 | 2026-07-04 15:00
123 | Mongla | 57 | 2026-07-13 12:00
124 | Motijheel | 54 | 2026-07-15 13:00
125 | Muktagacha | 46 | 2026-07-04 13:00
126 | Munshiganj | 129 | 2026-07-04 22:00
127 | Muradnagar | 58 | 2026-07-03 22:00
128 | Mymensingh | 200 | 2026-07-04 19:30
129 | Nabinagar | 120 | 2026-07-14 12:00
130 | Naogaon | 164 | 2026-07-04 21:00
131 | Narail | 65 | 2026-07-14 23:00
132 | Narinda | 90 | 2026-07-18 13:00
133 | Narshingdi | 203 | 2026-07-01 20:00
134 | Natore | 173 | 2026-07-04 20:00
135 | Nawabganj | 73 | 2026-07-04 22:00
136 | Netrakona | 147 | 2026-07-04 07:00
137 | New | 90 | 2026-07-26 12:00
138 | Niamatpur | 100 | 2026-07-04 22:00
139 | Noapara | 55 | 2026-07-27 21:00
140 | PHP | 15 | 2026-07-06 15:00
141 | Pabna | 116 | 2026-07-04 20:00
142 | Palashbari | 150 | 2026-07-04 22:00
143 | Panchagarh | 73 | 2026-07-02 19:30
144 | Patiya | 12.1 | 2026-07-04 21:00
145 | Patnitala | 0 | 2026-07-01 00:00
146 | Patuakhali | 75 | 2026-07-14 22:00
147 | Payra | 38 | 2026-07-02 23:00
148 | Postogola | 68 | 2026-07-04 19:00
149 | Pubail | 49 | 2026-07-07 09:00
150 | Purbachal | 33 | 2026-07-02 13:00
151 | Purbasadipur | 161 | 2026-07-04 23:00
152 | Rahanpur | 50 | 2026-07-04 23:00
153 | Rahim | 58 | 2026-07-28 08:00
154 | Rajbari | 95 | 2026-07-04 20:00
155 | Rajendrapur | 130 | 2026-07-23 02:00
156 | Rajshahi | 151 | 2026-07-01 00:00
157 | Rajshahi-230 | 113 | 2026-07-16 13:00
158 | Ramganj | 126 | 2026-07-04 19:00
159 | Rampur | 58 | 2026-07-21 12:00
160 | Rangamati | 20 | 2026-07-02 19:00
161 | Rangpur | 160 | 2026-07-26 19:30
162 | Ruppur | 17 | 2026-07-24 13:00
163 | SSM | 11 | 2026-07-28 07:00
164 | Saidpur | 123 | 2026-07-04 19:30
165 | Santhia | 42 | 2026-07-04 21:00
166 | Satkhira | 147 | 2026-07-04 22:00
167 | Satmasjid | 134 | 2026-07-04 14:00
168 | Savar | 234 | 2026-07-14 15:00
169 | SevenRings | 19.08 | 2026-07-30 17:00
170 | ShahCement | 37 | 2026-07-02 16:00
171 | Shahjadpur | 91 | 2026-07-14 20:00
172 | Shahjibazar | 148 | 2026-07-15 21:00
173 | Shahmirpur | 64 | 2026-07-16 01:00
174 | Shariatpur | 102 | 2026-07-03 23:00
175 | Sherpur | 180 | 2026-07-04 21:00
176 | Shikalbaha | 34 | 2026-07-27 11:00
177 | Shitalakhya | 87.5 | 2026-07-04 16:00
178 | Sholosohor | 52 | 2026-07-04 15:00
179 | Shomvuganj | 50 | 2026-07-30 19:00
180 | Shyampur | 188 | 2026-07-02 12:00
181 | Siddhirganj | 143 | 2026-07-29 16:00
182 | Sirajganj | 132 | 2026-07-26 20:00
183 | Sitakunda | 37 | 2026-07-14 19:30
184 | Sonargaon | 164 | 2026-07-07 12:00
185 | Sreemongol | 101 | 2026-07-05 00:00
186 | Sreepur | 140 | 2026-07-20 12:00
187 | Srinagar | 57.8 | 2026-07-04 21:00
188 | Sunamganj | 65 | 2026-07-24 19:00
189 | Sylhet | 146 | 2026-07-15 14:00
190 | Sylhet_(South) | 86 | 2026-07-04 22:00
191 | TK | 28 | 2026-07-02 19:30
192 | Tangail | 206 | 2026-07-03 20:00
193 | Taraganj | 35 | 2026-07-31 19:00
194 | Tasnim | 48 | 2026-07-08 12:00
195 | Thakurgaon | 127 | 2026-07-04 22:00
196 | Tongi | 177 | 2026-07-16 11:00
197 | Ullahpara | 45 | 2026-07-14 19:30
198 | Ullon | 80 | 2026-07-17 13:00
199 | Uttara | 111 | 2026-07-29 13:00
200 | UttaraNew | 59 | 2026-07-04 19:30
201 | Zigatola | 113 | 2026-07-16 14:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: July 2026
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 6136.76 | 2026-07-06 | 12:00
Chattogram | 1764 | 2026-07-04 | 15:00
Cumilla | 1640 | 2026-07-14 | 23:00
Mymensingh | 1234 | 2026-07-03 | 20:00
Sylhet | 731 | 2026-07-03 | 21:00
Khulna | 1959 | 2026-07-04 | 23:00
Barishal | 537.8 | 2026-07-02 | 23:00
Rajshahi | 1779.4 | 2026-07-04 | 20:00
Rangpur | 1204 | 2026-07-04 | 23:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July 2026
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 392 | 2026-07-06 22:00 | 345 | 2026-07-28 11:00
2 | Amtali | 400 | 414 | 2026-07-10 08:00 | 400 | 2026-07-02 22:00
3 | Ashuganj | 400 | N/A | N/A | N/A | N/A
4 | Bhulta | 400 | 409 | 2026-07-12 07:00 | 352 | 2026-07-28 11:00
5 | Bibiana | 400 | 386 | 2026-07-01 06:00 | 362 | 2026-07-26 11:00
6 | BIPTC | 400 | 409 | 2026-07-15 03:00 | 389 | 2026-07-05 00:00
7 | Bogura | 400 | 392 | 2026-07-10 17:00 | 358 | 2026-07-18 20:00
8 | Gopalganj | 400 | 397 | 2026-07-10 08:00 | 366 | 2026-07-26 19:30
9 | Kaliakoir | 400 | 373 | 2026-07-10 08:00 | 318 | 2026-07-22 20:00
10 | Korerhat | 400 | 400 | 2026-07-10 09:00 | 371 | 2026-07-28 11:00
11 | Madunaghat | 400 | 400 | 2026-07-31 02:00 | 377 | 2026-07-04 12:00
12 | Meghnaghat | 400 | 392 | 2026-07-17 18:30 | 349 | 2026-07-28 11:00
13 | Mirsorai | 400 | 234 | 2026-07-15 05:00 | 216 | 2026-07-02 12:00
14 | Payra | 400 | 416 | 2026-07-10 08:00 | 403 | 2026-07-02 13:00
15 | Rahanpur | 400 | 409 | 2026-07-10 17:00 | 380 | 2026-07-26 19:30
16 | Rampal | 400 | 404 | 2026-07-10 08:00 | 328 | 2026-07-06 00:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 236 | 2026-07-10 08:00 | 206 | 2026-07-26 11:00
2 | AKSML | 230 | 238 | 2026-07-25 02:00 | 216 | 2026-07-02 11:00
3 | Aminbazar | 230 | 237 | 2026-07-10 17:00 | 207 | 2026-07-26 11:00
4 | Ashuganj | 230 | 235 | 2026-07-10 10:00 | 206 | 2026-07-27 15:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 236 | 2026-07-06 18:30 | 213 | 2026-07-25 19:00
7 | Barapukuria | 230 | 227 | 2026-07-10 17:00 | 208 | 2026-07-25 21:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 230 | 2026-07-09 06:00 | 213 | 2026-07-02 23:00
10 | Bheramara | 230 | 235 | 2026-07-13 06:00 | 205 | 2026-07-02 21:00
11 | Bhulta | 230 | 237 | 2026-07-12 07:00 | 203 | 2026-07-27 12:00
12 | Bibiana | 230 | 225 | 2026-07-10 08:00 | 207 | 2026-07-27 15:00
13 | BIPTC | 230 | 237 | 2026-07-10 05:00 | 205 | 2026-07-26 19:30
14 | Bogura | 230 | 245 | 2026-07-10 17:00 | 222 | 2026-07-26 19:30
15 | Bogura-400 | 230 | 245 | 2026-07-10 10:00 | 224 | 2026-07-03 00:00
16 | Borhanuddin | 230 | 232 | 2026-07-09 06:00 | 219 | 2026-07-02 23:00
17 | BSRM | 230 | 230 | 2026-07-09 06:00 | 212 | 2026-07-02 11:00
18 | Charfasson | 230 | 233 | 2026-07-09 05:00 | 219 | 2026-07-02 23:00
19 | Chowmuhani | 230 | 229 | 2026-07-12 23:00 | 210 | 2026-07-01 00:00
20 | Cumilla(N) | 230 | 231 | 2026-07-10 09:00 | 205 | 2026-07-28 11:00
21 | Faridpur | 230 | 227 | 2026-07-10 17:00 | 205 | 2026-07-02 23:00
22 | Fenchuganj | 230 | 228 | 2026-07-10 10:00 | 208 | 2026-07-27 15:00
23 | Feni | 230 | 228 | 2026-07-10 10:00 | 208 | 2026-07-27 11:00
24 | Ghorashal | 230 | 238 | 2026-07-10 17:00 | 210 | 2026-07-25
25 | Ghorashal-230 | 230 | 224 | 2026-07-04 20:00 | 188 | 2026-07-26 11:00
26 | Gopalganj | 230 | 228 | 2026-07-10 18:00 | 208 | 2026-07-02 22:00
27 | GPH | 230 | 236 | 2026-07-04 20:00 | 216 | 2026-07-02 11:00
28 | Haripur | 230 | 236 | 2026-07-10 18:00 | 204 | 2026-07-27 12:00
29 | Hasnabad | 230 | 238 | 2026-07-21 07:00 | 204 | 2026-07-28 11:00
30 | Hathazari | 230 | 238 | 2026-07-07 17:00 | 216 | 2026-07-02 11:00
31 | Ishurdi | 230 | 237 | 2026-07-17 15:00 | 206 | 2026-07-26 19:30
32 | Jhenaidah | 230 | 232 | 2026-07-10 10:00 | 196 | 2026-07-26 19:30
33 | Kachua | 230 | 230 | 2026-07-15 06:00 | 210 | 2026-07-22 23:00
34 | Kaliakoir | 230 | 233 | 2026-07-10 08:00 | 203 | 2026-07-26 11:00
35 | Keranigonj | 230 | 235 | 2026-07-10 08:00 | 204 | 2026-07-27 10:00
36 | Khulna(S) | 230 | 238 | 2026-07-10 10:00 | 202 | 2026-07-03 22:00
37 | Korerhat | 230 | 233 | 2026-07-13 07:00 | 211 | 2026-07-02 11:00
38 | Madunaghat | 230 | 241 | 2026-07-07 16:00 | 215 | 2026-07-15 20:00
39 | Madunaghat-400 | 230 | 242 | 2026-07-07 20:00 | 220 | 2026-07-02 12:00
40 | Maniknagar | 230 | 235 | 2026-07-10 18:00 | 201 | 2026-07-27 12:00
41 | Meghnaghat | 230 | 242 | 2026-07-10 10:00 | 210 | 2026-07-28 11:00
42 | Meghnaghat-400 | 230 | 238 | 2026-07-10 18:00 | 205 | 2026-07-26 11:00
43 | Mirsorai | 230 | N/A | N/A | N/A | N/A
44 | Naogaon | 230 | 231 | 2026-07-05 14:00 | 198 | 2026-07-02 21:00
45 | Purbasadipur | 230 | 225 | 2026-07-09 17:00 | 203 | 2026-07-30 10:00
46 | Rajshahi | 230 | 235 | 2026-07-06 18:30 | 202 | 2026-07-01 22:00
47 | Rampal | 230 | 233 | 2026-07-10 08:00 | 205 | 2026-07-02 19:30
48 | Rampur | 230 | N/A | N/A | N/A | N/A
49 | Rampura | 230 | 236 | 2026-07-12 07:00 | 201 | 2026-07-28 11:00
50 | Shikalbaha | 230 | 241 | 2026-07-08 17:00 | 218 | 2026-07-02 11:00
51 | Shyampur | 230 | 236 | 2026-07-10 10:00 | 204 | 2026-07-28 11:00
52 | Siddhirganj | 230 | 238 | 2026-07-10 16:00 | 204 | 2026-07-27 12:00
53 | Sirajgonj | 230 | 242 | 2026-07-10 09:00 | 224 | 2026-07-25 14:00
54 | Sreepur | 230 | 232 | 2026-07-07 10:00 | 206 | 2026-07-27 09:00
54 | Tongi | 230 | 224 | 2026-07-25 04:00 | 191 | 2026-07-27 09:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 141 | 2026-07-09 06:00 | 120 | 2026-07-04 12:00
2 | Agargaon | 132 | 139 | 2026-07-09 06:00 | 119 | 2026-07-26 11:00
3 | Agrabad | 132 | 138 | 2026-07-07 14:00 | 122 | 2026-07-01 11:00
4 | AKS | 132 | 136 | 2026-07-07 14:00 | 122 | 2026-07-02 11:00
5 | Aminbazar | 132 | 135 | 2026-07-10 17:00 | 116 | 2026-07-26 11:00
6 | Amnura | 132 | 139 | 2026-07-14 18:00 | 117 | 2026-07-18 21:00
7 | Ashuganj | 132 | 138 | 2026-07-21 07:00 | 118 | 2026-07-27 10:00
8 | Ashuganj-230 | 132 | 139 | 2026-07-18 21:00 | 123 | 2026-07-27 10:00
9 | Bagerhat | 132 | 135 | 2026-07-09 05:00 | 108 | 2026-07-16 13:00
10 | Bajitpur | 132 | 130 | 2026-07-04 20:00 | 114 | 2026-07-22 22:00
11 | Bakerganj | 132 | 133 | 2026-07-09 05:00 | 122 | 2026-07-04 22:00
12 | Bakulia | 132 | 140 | 2026-07-08 20:00 | 122 | 2026-07-02 11:00
13 | Banani | 132 | 141 | 2026-07-04 05:00 | 119 | 2026-07-04 12:00
14 | Bangabhaban | 132 | 139 | 2026-07-10 18:00 | 114 | 2026-07-27 12:00
0 | Barapukuria | 132 | 139 | 2026-07-29 11:00 | 121 | 2026-07-25 19:30
16 | Barguna | 132 | 134 | 2026-07-09 06:00 | 121 | 2026-07-02 23:00
17 | Barishal | 132 | 133 | 2026-07-09 05:00 | 120 | 2026-07-04 23:00
18 | Barishal-230 | 132 | 134 | 2026-07-09 06:00 | 121 | 2026-07-04 23:00
19 | Baroaulia | 132 | 139 | 2026-07-08 14:00 | 125 | 2026-07-01 11:00
20 | Baroirhat | 132 | 133 | 2026-07-09 05:00 | 122 | 2026-07-02 11:00
21 | Bashundhara | 132 | 141 | 2026-07-10 08:00 | 112 | 2026-07-04 14:00
22 | BashundharaCement | 132 | 138 | 2026-07-12 05:00 | 119 | 2026-07-26 11:00
23 | Beanibazar | 132 | 127 | 2026-07-09 06:00 | 112 | 2026-07-13 15:00
24 | Benapole | 132 | 140 | 2026-07-08 18:00 | 108 | 2026-07-19 21:00
25 | Bhaluka | 132 | 134 | 2026-07-04 20:00 | 108 | 2026-07-07 10:00
26 | Bhandaria | 132 | 133 | 2026-07-09 05:00 | 106 | 2026-07-01 00:00
27 | Bhangura | 132 | 136 | 2026-07-10 17:00 | 121 | 2026-07-01 00:00
28 | Bheramara | 132 | 138 | 2026-07-10 10:00 | 119 | 2026-07-03 22:00
29 | Bheramara(GK) | 132 | 138 | 2026-07-20 17:00 | 118 | 2026-07-03 22:00
30 | Bhulta | 132 | 138 | 2026-07-11 06:00 | 117 | 2026-07-04 12:00
31 | Bhulta-400 | 132 | 130 | 2026-07-29 04:00 | 119 | 2026-07-27 13:00
32 | Bog-Sherpur | 132 | 138 | 2026-07-08 18:30 | 123 | 2026-07-03 00:00
33 | Bogura | 132 | 140 | 2026-07-08 18:00 | 126 | 2026-07-02 23:00
34 | Bogura-230 | 132 | 141 | 2026-07-08 18:30 | 126 | 2026-07-03 00:00
35 | Brahmanbaria | 132 | 132 | 2026-07-10 09:00 | 114 | 2026-07-07 13:00
36 | Cantonment | 132 | 139 | 2026-07-10 08:00 | 118 | 2026-07-28 11:00
37 | Chandina | 132 | 134 | 2026-07-09 06:00 | 117 | 2026-07-28 11:00
39 | Chandpur | 132 | 134 | 2026-07-08 19:30 | 119 | 2026-07-01 02:00
40 | Chandraghona | 132 | 140 | 2026-07-07 17:00 | 126 | 2026-07-02 11:00
41 | Chapai | 132 | 135 | 2026-07-10 18:00 | 123 | 2026-07-01 22:00
42 | Charsaidpur | 132 | 138 | 2026-07-12 07:00 | 119 | 2026-07-25 13:00
43 | Chauddagram | 132 | 132 | 2026-07-10 09:00 | 119 | 2026-07-22 23:00
44 | Chhatak | 132 | 126 | 2026-07-08 08:00 | 107 | 2026-07-13 15:00
45 | Chowmuhani | 132 | 129 | 2026-07-09 05:00 | 117 | 2026-07-01 00:00
46 | Chuadanga | 132 | 140 | 2026-07-10 07:00 | 107 | 2026-07-18 19:00
47 | Coxsbazar | 132 | 132 | 2026-07-30 19:00 | 109 | 2026-07-01 19:00
48 | Cumilla(N) | 132 | 134 | 2026-07-10 18:00 | 118 | 2026-07-28 11:00
49 | Cumilla(S) | 132 | 136 | 2026-07-05 09:00 | 119 | 2026-07-03 15:00
50 | Daganbhuiyan | 132 | 131 | 2026-07-09 07:00 | 119 | 2026-07-01 22:00
51 | Daudkandi | 132 | 131 | 2026-07-10 18:00 | 114 | 2026-07-14 12:00
52 | DhakaUniversity | 132 | 141 | 2026-07-04 05:00 | 120 | 2026-07-04 12:00
53 | Dhamrai | 132 | 138 | 2026-07-10 18:00 | 111 | 2026-07-04 14:00
54 | Dhanmondi | 132 | 142 | 2026-07-04 05:00 | 120 | 2026-07-23 01:00
55 | Dohazari | 132 | 138 | 2026-07-30 08:00 | 118 | 2026-07-01 11:00
56 | Faridpur | 132 | 131 | 2026-07-10 06:00 | 118 | 2026-07-02 23:00
57 | Fatullah | 132 | 143 | 2026-07-10 18:30 | 117 | 2026-07-25 13:00
58 | Fenchuganj | 132 | 134 | 2026-07-09 06:00 | 121 | 2026-07-27 15:00
59 | Feni | 132 | 131 | 2026-07-09 03:00 | 121 | 2026-07-01 11:00
60 | Feni-230 | 132 | 132 | 2026-07-09 06:00 | 120 | 2026-07-28 11:00
61 | Ghatail | 132 | 133 | 2026-07-25 23:00 | 109 | 2026-07-21 19:30
62 | Ghorashal | 132 | 133 | 2026-07-10 18:00 | 115 | 2026-07-25 14:00
63 | Goalpara | 132 | 140 | 2026-07-10 06:00 | 118 | 2026-07-01 22:00
64 | Gollamari | 132 | 138 | 2026-07-09 06:00 | 118 | 2026-07-02 20:00
65 | Gopalganj | 132 | 135 | 2026-07-09 05:00 | 117 | 2026-07-03 22:00
66 | Gopalganj-400 | 132 | 134 | 2026-07-09 06:00 | 118 | 2026-07-09 17:00
67 | Gulshan | 132 | 140 | 2026-07-04 05:00 | 120 | 2026-07-04 12:00
68 | Halishahar | 132 | 140 | 2026-07-07 14:00 | 124 | 2026-07-01 11:00
69 | Haripur | 132 | 139 | 2026-07-12 07:00 | 120 | 2026-07-26 11:00
70 | HaripurSBU | 132 | 138 | 2026-07-10 18:00 | 120 | 2026-07-26 11:00
71 | Hasnabad | 132 | 141 | 2026-07-10 18:00 | 119 | 2026-07-02 13:00
72 | Hathazari | 132 | 140 | 2026-07-08 22:00 | 125 | 2026-07-01 03:00
73 | Hatirjheel | 132 | 141 | 2026-07-04 05:00 | 120 | 2026-07-04 12:00
74 | Ishurdi | 132 | 140 | 2026-07-10 10:00 | 121 | 2026-07-26 19:30
75 | Jaldhaka | 132 | 135 | 2026-07-08 04:00 | 117 | 2026-07-25 19:30
76 | Jamalpur | 132 | 134 | 2026-07-26 14:00 | 109 | 2026-07-19 02:00
77 | Jashore | 132 | 141 | 2026-07-08 18:00 | 111 | 2026-07-03 22:00
78 | Jhenaidah | 132 | 142 | 2026-07-14 09:00 | 110 | 2026-07-02 21:00
79 | Jhenaidah-230 | 132 | 141 | 2026-07-06 18:00 | 116 | 2026-07-26 19:30
80 | Joydebpur | 132 | 136 | 2026-07-04 20:00 | 109 | 2026-07-02 12:00
81 | Joypurhat | 132 | 138 | 2026-07-08 18:30 | 116 | 2026-07-19 00:00
82 | Juldah | 132 | 139 | 2026-07-07 14:00 | 123 | 2026-07-01 11:00
83 | Kabirpur | 132 | 138 | 2026-07-04 20:00 | 109 | 2026-07-07 11:00
84 | Kachua | 132 | 131 | 2026-07-08 19:30 | 119 | 2026-07-22 23:00
85 | Kaliakoir | 132 | 140 | 2026-07-10 18:00 | 117 | 2026-07-04 14:00
86 | Kaliganj | 132 | 141 | 2026-07-08 18:00 | 115 | 2026-07-26 19:30
87 | Kallyanpur | 132 | 136 | 2026-07-12 19:30 | 115 | 2026-07-28 13:00
88 | Kalurghat | 132 | 140 | 2026-07-08 18:00 | 126 | 2026-07-02 12:00
89 | Kamrangirchar | 132 | 141 | 2026-07-09 05:00 | 113 | 2026-07-04 12:00
90 | Kaptai | 132 | N/A | N/A | N/A | N/A
91 | Kasba | 132 | 131 | 2026-07-09 06:00 | 114 | 2026-07-25 13:00
92 | Kazla | 132 | 139 | 2026-07-12 08:00 | 113 | 2026-07-28 13:00
93 | Keranigonj | 132 | 142 | 2026-07-09 06:00 | 120 | 2026-07-25 13:00
94 | Khagrachori | 132 | 138 | 2026-07-07 15:00 | 124 | 2026-07-01 11:00
95 | Khulna | 132 | 138 | 2026-07-10 06:00 | 118 | 2026-07-01 22:00
96 | Khulna(S) | 132 | 145 | 2026-07-10 10:00 | 118 | 2026-07-01 22:00
97 | Khulshi | 132 | 138 | 2026-07-07 16:00 | 122 | 2026-07-01 11:00
98 | Kishoreganj | 132 | 129 | 2026-07-04 20:00 | 111 | 2026-07-27 19:00
99 | Kodda | 132 | 138 | 2026-07-04 05:00 | 115 | 2026-07-26 11:00
100 | Korerhat | 132 | 135 | 2026-07-10 09:00 | 123 | 2026-07-01 00:00
101 | KSRM | 132 | 140 | 2026-07-08 18:00 | 124 | 2026-07-01 11:00
102 | Kulaura | 132 | 133 | 2026-07-09 06:00 | 120 | 2026-07-27 14:00
103 | Kurigram | 132 | 133 | 2026-07-08 08:00 | 110 | 2026-07-05 00:00
104 | Kushtia | 132 | 136 | 2026-07-10 09:00 | 113 | 2026-07-03 22:00
105 | Laksam | 132 | 131 | 2026-07-31 07:00 | 118 | 2026-07-02 11:00
106 | Lakshmipur | 132 | 129 | 2026-07-09 06:00 | 116 | 2026-07-01 00:00
107 | Lalbag | 132 | 141 | 2026-07-09 05:00 | 113 | 2026-07-04 13:00
108 | Lalmonirhat | 132 | 129 | 2026-07-09 06:00 | 110 | 2026-07-05 02:00
109 | Madanganj | 132 | 138 | 2026-07-12 05:00 | 119 | 2026-07-26 11:00
110 | Madaripur | 132 | 132 | 2026-07-17 10:00 | 120 | 2026-07-02 22:00
111 | Madartek | 132 | 140 | 2026-07-09 06:00 | 120 | 2026-07-04 12:00
112 | Madunaghat | 132 | 141 | 2026-07-08 18:00 | 117 | 2026-07-03 15:00
113 | Magura | 132 | 139 | 2026-07-21 18:00 | 105 | 2026-07-03 22:00
114 | Mahasthangarh | 132 | 137 | 2026-07-08 18:00 | 121 | 2026-07-02 23:00
115 | Maijdee | 132 | 128 | 2026-07-07 18:00 | 117 | 2026-07-01 00:00
116 | Manikganj | 132 | 134 | 2026-07-12 07:00 | 108 | 2026-07-05 01:00
117 | Maniknagar | 132 | 139 | 2026-07-10 18:00 | 114 | 2026-07-27 12:00
118 | Matarbari | 132 | 135 | 2026-07-07 13:00 | 107 | 2026-07-01 19:00
119 | Matuail | 132 | 138.5 | 2026-07-12 07:00 | 119 | 2026-07-26 11:00
120 | Metrorail_Motijheel | 132 | 139 | 2026-07-10 17:00 | 114 | 2026-07-28 11:00
121 | Metrorail_Uttara | 132 | 136 | 2026-07-17 18:30 | 110 | 2026-07-25 16:00
122 | Millgate | 132 | 136 | 2026-07-04 04:00 | 112 | 2026-07-04 13:00
123 | Mirpur | 132 | 134 | 2026-07-12 07:00 | 115 | 2026-07-26 11:00
124 | Mirzapur | 132 | 133 | 2026-07-10 10:00 | 116 | 2026-07-27 10:00
125 | Mithapukur | 132 | 136 | 2026-07-08 08:00 | 112 | 2026-07-05 08:00
126 | MI_Cement | 132 | 139.7 | 2026-07-10 18:00 | 117 | 2026-07-25 13:00
127 | Modern | 132 | N/A | N/A | N/A | N/A
128 | Mogbazar | 132 | 143 | 2026-07-09 05:00 | 122 | 2026-07-04 12:00
129 | Mongla | 132 | 133 | 2026-07-10 05:00 | 109 | 2026-07-16 13:00
130 | Motijheel | 132 | 139 | 2026-07-10 18:00 | 114 | 2026-07-27 12:00
131 | Muktagacha | 132 | 130 | 2026-07-07 16:00 | 111 | 2026-07-23 19:00
132 | Munshiganj | 132 | 137 | 2026-07-12 07:00 | 118 | 2026-07-26 11:00
133 | Muradnagar | 132 | 131 | 2026-07-09 06:00 | 115 | 2026-07-25 13:00
134 | Mymensingh | 132 | 131 | 2026-07-26 14:00 | 106 | 2026-07-01 00:00
135 | Nabinagar | 132 | 137 | 2026-07-09 04:00 | 111 | 2026-07-04 12:00
136 | Naogaon | 132 | 139 | 2026-07-08 18:30 | 120 | 2026-07-01 22:00
137 | Narail | 132 | 139 | 2026-07-17 09:00 | 100 | 2026-07-03 22:00
139 | Narinda | 132 | 8 | 2026-07-28 08:00 | 8 | 2026-07-28 08:00
140 | Narshingdi | 132 | 132 | 2026-07-04 20:00 | 111 | 2026-07-25 13:00
141 | Natore | 132 | 137 | 2026-07-14 18:00 | 118 | 2026-07-02 22:00
142 | Nawabganj | 132 | 141 | 2026-07-09 06:00 | 120 | 2026-07-22 12:00
143 | Netrakona | 132 | 124 | 2026-07-04 20:00 | 100 | 2026-07-09 19:30
144 | New | 132 | 140 | 2026-07-04 20:00 | 114 | 2026-07-04 14:00
145 | Niamatpur | 132 | 139 | 2026-07-12 17:00 | 122 | 2026-07-02 21:00
146 | Noapara | 132 | 137 | 2026-07-10 06:00 | 113 | 2026-07-03 22:00
147 | Pabna | 132 | 137 | 2026-07-24 18:00 | 119 | 2026-07-02 21:00
148 | Palashbari | 132 | 133 | 2026-07-08 07:00 | 115 | 2026-07-25 23:00
149 | Panchagarh | 132 | 142 | 2026-07-28 19:00 | 125 | 2026-07-03 00:00
150 | Patiya | 132 | 139 | 2026-07-07 13:00 | 123 | 2026-07-01 11:00
151 | Patnitala | 132 | 136 | 2026-07-08 18:00 | 113 | 2026-07-01 00:00
152 | Patuakhali | 132 | 133 | 2026-07-16 10:00 | 122 | 2026-07-01 22:00
153 | Payra | 132 | 136 | 2026-07-09 05:00 | 129 | 2026-07-18 22:00
154 | PHP | 132 | 132 | 2026-07-08 19:30 | 122 | 2026-07-01 00:00
155 | Postogola | 132 | 141 | 2026-07-10 08:00 | 119 | 2026-07-27 10:00
156 | Pubail | 132 | 137 | 2026-07-04 20:00 | 111 | 2026-07-28 14:00
157 | Purbachal | 132 | 141 | 2026-07-09 06:00 | 120 | 2026-07-04 12:00
158 | Purbasadipur | 132 | 137 | 2026-07-09 17:00 | 123 | 2026-07-02 23:00
159 | Rahanpur | 132 | 138 | 2026-07-10 09:00 | 126 | 2026-07-06 22:00
160 | Rahanpur-400 | 132 | 137 | 2026-07-10 17:00 | 127 | 2026-07-05 23:00
161 | Rahim | 132 | 137 | 2026-07-10 19:00 | 120 | 2026-07-02 12:00
162 | Rajbari | 132 | 130 | 2026-07-20 09:00 | 114 | 2026-07-02 23:00
163 | Rajendrapur | 132 | 137 | 2026-07-04 20:00 | 113 | 2026-07-27 10:00
164 | Rajshahi | 132 | 135 | 2026-07-21 18:30 | 115 | 2026-07-01 00:00
165 | Rajshahi-230 | 132 | 135 | 2026-07-23 18:00 | 117 | 2026-07-01 22:00
166 | Ramganj | 132 | 132 | 2026-07-12 16:00 | 115 | 2026-07-18 21:00
167 | Rampur | 132 | 139 | 2026-07-07 19:30 | 123 | 2026-07-01 11:00
168 | Rampura | 132 | 141 | 2026-07-09 06:00 | 120 | 2026-07-04 12:00
169 | Rangamati | 132 | 139 | 2026-07-08 19:30 | 124 | 2026-07-02 12:00
170 | Rangpur | 132 | 135 | 2026-07-08 08:00 | 115 | 2026-07-25 19:30
171 | Ruppur | 132 | 139 | 2026-07-24 17:00 | 121 | 2026-07-01 22:00
172 | Saidpur | 132 | 136 | 2026-07-08 14:00 | 120 | 2026-07-25 19:30
173 | Santhia | 132 | 137 | 2026-07-06 14:00 | 122 | 2026-07-02 21:00
174 | Satkhira | 132 | 144 | 2026-07-10 10:00 | 108 | 2026-07-03 22:00
175 | Satmasjid | 132 | 142 | 2026-07-24 00:00 | 118 | 2026-07-19 13:00
176 | Savar | 132 | 134 | 2026-07-12 06:00 | 113 | 2026-07-26 11:00
177 | SevenRings | 132 | 137 | 2026-07-04 20:00 | 114 | 2026-07-27 10:00
178 | ShahCement | 132 | 138 | 2026-07-12 07:00 | 119 | 2026-07-02 12:00
179 | Shahjadpur | 132 | 140 | 2026-07-10 17:00 | 126 | 2026-07-02 00:00
180 | Shahjibazar | 132 | 134 | 2026-07-20 12:00 | 114 | 2026-07-22 22:00
181 | Shahmirpur | 132 | 140 | 2026-07-31 00:00 | 125 | 2026-07-01 11:00
182 | Shariatpur | 132 | 133 | 2026-07-09 06:00 | 117 | 2026-07-02 23:00
183 | Sherpur | 132 | 131 | 2026-07-08 20:00 | 106 | 2026-07-19 06:00
184 | Shikalbaha | 132 | 129 | 2026-07-31 00:00 | 115 | 2026-07-01 11:00
185 | Shikalbaha-230 | 132 | 140 | 2026-07-07 14:00 | 125 | 2026-07-01 10:00
186 | Shitalakhya | 132 | 139.7 | 2026-07-10 18:00 | 117 | 2026-07-25 13:00
187 | Sholosohor | 132 | 139 | 2026-07-07 17:00 | 124 | 2026-07-02 12:00
188 | Shomvuganj | 132 | 125 | 2026-07-09 06:00 | 108 | 2026-07-30 19:00
189 | Shyampur | 132 | 140 | 2026-07-10 08:00 | 119 | 2026-07-22 12:00
190 | Shyampur-230 | 132 | 142 | 2026-07-09 07:00 | 117 | 2026-07-23 11:00
191 | Siddhirganj | 132 | 138 | 2026-07-10 18:00 | 120 | 2026-07-04 11:00
192 | Sirajganj | 132 | 136 | 2026-07-10 10:00 | 119 | 2026-07-26 19:30
193 | Sitakunda | 132 | 139 | 2026-07-07 19:30 | 125 | 2026-07-02 11:00
194 | Sonargaon | 132 | 136 | 2026-07-12 07:00 | 117 | 2026-07-26 11:00
195 | Sreemongol | 132 | 131 | 2026-07-10 06:00 | 115 | 2026-07-27 15:00
196 | Sreepur | 132 | 137 | 2026-07-04 20:00 | 117 | 2026-07-27 09:00
197 | Srinagar | 132 | 141 | 2026-07-09 06:00 | 120 | 2026-07-22 12:00
198 | SSM | 132 | 142 | 2026-07-08 14:00 | 130 | 2026-07-01 00:00
199 | Sunamganj | 132 | 125 | 2026-07-09 07:00 | 107 | 2026-07-13 15:00
200 | Sylhet | 132 | 127 | 2026-07-09 06:00 | 114 | 2026-07-13 15:00
201 | Sylhet_(South) | 132 | 135 | 2026-07-17 23:00 | 115 | 2026-07-13 15:00
202 | Tangail | 132 | 129 | 2026-07-04 21:00 | 112 | 2026-07-06 21:00
203 | Taraganj | 132 | 135 | 2026-07-08 08:00 | 119 | 2026-07-25 19:30
204 | Tasnim | 132 | 139 | 2026-07-06 05:00 | 117 | 2026-07-26 11:00
205 | Thakurgaon | 132 | 141 | 2026-07-28 14:00 | 125 | 2026-07-03 00:00
206 | TK | 132 | 140 | 2026-07-08 21:00 | 126 | 2026-07-02 11:00
207 | Tongi | 132 | 140 | 2026-07-04 20:00 | 124 | 2026-07-01 15:00
208 | Ullahpara | 132 | 136 | 2026-07-09 05:00 | 120 | 2026-07-26 19:30
209 | Ullon | 132 | 140 | 2026-07-10 08:00 | 120 | 2026-07-04 12:00
210 | Uttara | 132 | 137 | 2026-07-04 05:00 | 110 | 2026-07-04 15:00
211 | UttaraNew | 132 | 137 | 2026-07-04 20:00 | 112 | 2026-07-04 12:00
212 | Zigatola | 132 | 142 | 2026-07-09 06:00 | 120 | 2026-07-22 12:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: July 2026
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 04-07-2026 | 10:00 | 423 | 226 | 92.2285
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 02-07-2026 | 12:00 | 418 | 215 | 90.3946
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 02-07-2026 | 12:00 | 418 | 215 | 90.3946
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 01-07-2026 | 01:00 | 0 | 0 | 0
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 09-07-2026 | 11:00 | 290 | 153 | 63.0549
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 09-07-2026 | 11:00 | 290 | 153 | 63.0549
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 01-07-2026 | 00:00 | 0 | 0 | 0
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 24-07-2026 | 20:00 | 261 | 69 | 51.9167
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 06-07-2026 | 22:00 | 423 | 108 | 58.2093
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 06-07-2026 | 22:00 | 423 | 108 | 58.2093
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 06-07-2026 | 22:00 | 423 | 108 | 58.2093
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 04-07-2026 | 21:00 | 160 | 71 | 53.8602
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 04-07-2026 | 21:00 | 160 | 71 | 53.8602
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 04-07-2026 | 21:00 | 160 | 71 | 53.8602
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 01-07-2026 | 19:00 | 209 | 65 | 29.1833
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 08-07-2026 | 05:00 | 356 | 170 | 75.8668
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 08-07-2026 | 05:00 | 356 | 170 | 75.8668
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 08-07-2026 | 18:30 | 296 | 51 | 92.4189
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 08-07-2026 | 18:30 | 296 | 51 | 92.4189
Madunaghat 400/230kV Grid Sub-Station | ATR-1 7006T | 400/230 | 750 | 19-07-2026 | 12:00 | 352 | 179 | 52.6532
Madunaghat 400/230kV Grid Sub-Station | ATR-2 7106T | 400/230 | 750 | 19-07-2026 | 12:00 | 352 | 179 | 52.6532
Madunaghat 400/230kV Grid Sub-Station | ATR-3 7206T | 400/230 | 750 | 19-07-2026 | 12:00 | 352 | 179 | 52.6532
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 31-07-2026 | 13:00 | 485 | 132 | 67.0189
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 31-07-2026 | 13:00 | 485 | 129 | 66.915
Meghnaghat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 750 | 15-07-2026 | 23:00 | 466 | 86 | 63.1826
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 14-07-2026 | 22:00 | 524 | 90 | 102.2448
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 14-07-2026 | 21:00 | 518 | 84 | 100.9167
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 19-07-2026 | 22:00 | 195 | 68 | 63.5435
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 19-07-2026 | 22:00 | 195 | 68 | 63.5435
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 04-07-2026 | 22:00 | 190 | 42 | 37.4205
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 04-07-2026 | 22:00 | 190 | 42 | 37.4205
Koerhat 400/230kV Grid Sub-Station | ATR-3 | 400/230 | 1000 | 22-07-2026 | 21:00 | 536 | 57 | 53.9022
Koerhat 400/132kV Grid Sub-Station | ATR-4 | 400/230 | 1000 | 01-07-2026 | 17:00 | 466 | 34 | 46.7239
Koerhat 400/132kV Grid Sub-Station | ATR-2 | 400/132 | 325 | 14-07-2026 | 16:00 | 122 | 8 | 37.6191
Koerhat 400/132kV Grid Sub-Station | ATR-3 | 400/132 | 325 | 23-07-2026 | 11:00 | 119 | 8 | 36.698
Mirsharai 400/230 kV Grid Sub-Station | ATR-1 | 400/230 | 1000 | 23-07-2026 | 13:00 | 111 | 47 | 12.054
Mirsharai 400/230 kV Grid Sub-Station | ATR-2 | 400/230 | 1000 | 15-07-2026 | 14:00 | 163 | 91 | 18.6682
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-1 | 400/230 | 325 |  |  |  |  | 0
Ashuganj 400/230 kV GIS Grid Sub-Station | Interbus-2 | 400/230 | 325 |  |  |  |  | 0
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 04-07-2026 | 15:00 | 199 | 86 | 72.2626
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 03-07-2026 | 12:00 | 230 | 83 | 81.506
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 03-07-2026 | 12:00 | 187 | 99 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 03-07-2026 | 12:00 | 187 | 99 | 83.2263
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 03-07-2026 | 12:00 | 187 | 99 | 83.2263
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 01-07-2026 | 01:00 | 200 | 115 | 76.9018
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 20-07-2026 | 08:00 | 260 | 74 | 90.1086
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 14-07-2026 | 19:30 | 210 | 47 | 71.7318
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 14-07-2026 | 19:30 | 157 | 40 | 72.0069
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 04-07-2026 | 18:30 | 156 | 48 | 72.5412
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 05-07-2026 | 00:00 | 113 | 46 | 54.224
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 04-07-2026 | 23:00 | 146 | 46 | 51.025
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 21-07-2026 | 11:00 | 116 | 25 | 39.5545
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 21-07-2026 | 11:00 | 116 | 25 | 39.5545
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 04-07-2026 | 21:00 | -155 | -30 | 70.1673
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 12-07-2026 | 00:00 | -177 | -43 | 80.9548
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 06-07-2026 | 21:00 | 166 | 51 | 77.1812
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 12-07-2026 | 20:00 | 170 | 73 | 82.227
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 12-07-2026 | 20:00 | 232 | 74 | 81.172
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 12-07-2026 | 20:00 | 232 | 74 | 81.172
Naogaon 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | - | - | - | - | #VALUE!
Naogaon 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | - | - | - | - | #VALUE!
Naogaon 230/132kV Grid Sub-Station | ATR-3 | 230/132 | 300 | - | - | - | - | #VALUE!
Purbasadipur 230/132kV Grid Sub-Station | ATR-01 | 230/132 | 300 | 04-07-2026 | 20:00 | -129 | -17 | 43.3718
Purbasadipur 230/132kV Grid Sub-Station | ATR-02 | 230/132 | 300 | 04-07-2026 | 20:00 | -129 | -17 | 43.3718
Purbasadipur 230/132kV Grid Sub-Station | ATR-03 | 230/132 | 300 | 04-07-2026 | 20:00 | -129 | -17 | 43.3718
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 10-07-2026 | 19:30 | 101 | 54 | 50.902
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 10-07-2026 | 19:30 | 101 | 52 | 50.489
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 10-07-2026 | 19:30 | 107 | 52 | 52.8739
Chowmohani 230/132 kV Grid Sub-Station | ATR-01 | 230/132 | 350 | 19-07-2026 | 21:00 | 90 | 7 | 25.7919
Chowmohani 230/132 kV Grid Sub-Station | ATR-02 | 230/132 | 350 | 19-07-2026 | 21:00 | 90 | 7 | 25.7919
Chowmohani 230/132 kV Grid Sub-Station | ATR-03 | 230/132 | 350 | 19-07-2026 | 21:00 | 90 | 7 | 25.7919
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 01-07-2026 | 01:00 | 222 | 101 | 81.2985
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 26-07-2026 | 22:00 | 254 | 74 | 88.1867
Feni 230/132 kV GIS Grid Sub-Station | ATR-1 | 230/132 | 300 | 03-07-2026 | 23:00 | 49 | 30 | 19.1514
Feni 230/132 kV GIS Grid Sub-Station | ATR-2 | 230/132 | 300 | 03-07-2026 | 23:00 | 49 | 30 | 19.1514
Feni 230/132 kV GIS Grid Sub-Station | ATR-3 | 230/132 | 300 | 03-07-2026 | 23:00 | 49 | 30 | 19.1514
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 04-07-2026 | 23:00 | 100 | 0 | 80
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 01-07-2026 | 00:00 | 0 | 0 | 0
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 19-07-2026 | 09:00 | 125 | 94 | 69.5112
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 19-07-2026 | 09:00 | 136 | 95 | 73.7309
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 21-07-2026 | 02:00 | 127 | 86 | 68.1683
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 16-07-2026 | 12:00 | 104 | 49 | 51.0956
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 16-07-2026 | 12:00 | 104 | 49 | 51.0956
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 16-07-2026 | 12:00 | 104 | 49 | 51.0956
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 10-06-2026 | 19:00 | 98 | 43 | 71.3458
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 01-07-2026 | 00:00 | 0 | 0 | 0
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 04-07-2026 | 14:00 | 98 | 44 | 71.6163
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 04-07-2026 | 14:00 | 98 | 44 | 71.6163
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 04-07-2026 | 20:00 | 113 | 44 | 53.8952
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 04-07-2026 | 20:00 | 113 | 44 | 53.8952
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 04-07-2026 | 20:00 | 111 | 42 | 52.7468
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 16-07-2026 | 19:30 | 225 | 60 | 77.6209
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 16-07-2026 | 19:30 | 225 | 60 | 77.6209
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 07-07-2026 | 15:00 | 262 | 52 | 89.0368
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 02-07-2026 | 19:30 | 142 | 62 | 51.6484
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 02-07-2026 | 19:30 | 142 | 62 | 51.6484
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 02-07-2026 | 19:30 | 142 | 62 | 51.6484
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 12-07-2026 | 20:00 | 176 | 54 | 81.8212
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 12-07-2026 | 20:00 | 176 | 54 | 81.8212
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 12-07-2026 | 20:00 | 230 | 61 | 79.3172
Madunaghat 230/132/33kV Grid Sub-Station | ATR-1(705T) | 230/132 | 300 | 04-07-2026 | 15:00 | 119 | 20 | 40.223
Madunaghat 230/132/33kV Grid Sub-Station | ATR-2(715T) | 230/132 | 300 | 04-07-2026 | 15:00 | 119 | 20 | 40.223
Madunaghat 230/132/33kV Grid Sub-Station | ATR-3(725T) | 230/132 | 300 | 04-07-2026 | 15:00 | 119 | 20 | 40.223
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 22-07-2026 | 22:00 | 214 | 76 | 75.6982
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 22-07-2026 | 18:00 | 193 | 61 | 67.4702
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 04-07-2026 | 21:00 | 120 | 12 | 40.1995
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 04-07-2026 | 21:00 | 120 | 12 | 40.1995
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-07-2026 | 00:00 | 1 | 0 | 0.33333
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-07-2026 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 28-07-2026 | 13:00 | 284 | 49 | 64.0436
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 28-07-2026 | 13:00 | 284 | 49 | 64.0436
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 28-07-2026 | 13:00 | 284 | 49 | 64.0436
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 14-07-2026 | 15:00 | 220 | 122 | 83.8544
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 14-07-2026 | 15:00 | 220 | 122 | 83.8544
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 30-07-2026 | 03:00 | 112 | 43 | 39.9903
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 07-07-2026 | 16:00 | 175 | 92 | 65.9031
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 01-07-2026 | 00:00 | 0 | 0 | 0
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 21-07-2026 | 08:00 | 198 | 15 | 66.1891
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 19-07-2026 | 19:00 | 261 | 114 | 94.9368
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 19-07-2026 | 19:00 | 261 | 114 | 94.9368
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 01-07-2026 | 11:00 | 150 | 65 | 72.6568
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 01-07-2026 | 15:00 | 145 | 60 | 69.7438
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 01-07-2026 | 15:00 | 145 | 60 | 69.7438
Tongi 230/132/33kV Grid Sub-Station | T-04 | 230/132 | 450 | 02-07-2026 | 11:00 | 290 | 120 | 69.7438
Bhulta 230/132kV Grid Sub-Station | TR1 | 230/132 | 300 | 19-07-2026 | 8:30 | 153.5 | 46 | 53.4148
Bhulta 230/132kV Grid Sub-Station | TR2 | 230/132 | 300 | 19-07-2026 | 8:30 | 153.5 | 46 | 53.4148
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: July 2026 |  |  |  | (For Evening Peak) | [10 empty] | Month: July 2026 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2026-07-01 | 16323.7 | 16835.7 | 490 | 21:00 Hr. | 54 | 0 | 20 | 416 | 0 | 0 | 0 | 0 | 0 | - | 2026-07-01 | 14658.25 | 15025.25 | 351 | 12:00 Hr. | 48 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | -
2026-07-02 | 16716.67 | 17232.67 | 494 | 21:00 Hr. | 67 | 0 | 14 | 280 | 34 | 99 | 0 | 0 | 0 | - | 2026-07-02 | 15327.46 | 15659.46 | 318 | 12:00 Hr. | 180 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | -
2026-07-03 | 16359.45 | 16653.45 | 281 | 21:00 Hr. | 45 | 0 | 0 | 215 | 21 | 0 | 0 | 0 | 0 | - | 2026-07-03 | 13980.55 | 14240.55 | 249 | 12:00 Hr. | 73 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | -
2026-07-04 | 16076.62 | 16826.62 | 718 | 19:30 Hr. | 208 | 0 | 23 | 342 | 19 | 48 | 3 | 2 | 73 | - | 2026-07-04 | 15213.62 | 15976.62 | 730 | 12:00 Hr. | 255 | 0 | 43 | 407 | 25 | 0 | 0 | 0 | 0 | -
2026-07-05 | 15821.76 | 16130.76 | 296 | 21:00 Hr. | 65 | 0 | 0 | 206 | 0 | 25 | 0 | 0 | 0 | - | 2026-07-05 | 14150.19 | 14228.19 | 75 | 12:00 Hr. | 70 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | -
2026-07-06 | 15631.39 | 15839.39 | 199 | 20:00 Hr. | 59 | 0 | 29 | 111 | 0 | 0 | 0 | 0 | 0 | - | 2026-07-06 | 14493.61 | 14493.61 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-07-07 | 15524 | 15662 | 132 | 20:00 Hr. | 32 | 0 | 18 | 82 | 0 | 0 | 0 | 0 | 0 | - | 2026-07-07 | 13862.45 | 14373.45 | 489 | 12:00 Hr. | 196 | 0 | 20 | 181 | 60 | 0 | 0 | 0 | 32 | -
2026-07-08 | 15376.01 | 15737.01 | 345 | 21:00 Hr. | 40 | 0 | 93 | 174 | 38 | 0 | 0 | 0 | 0 | - | 2026-07-08 | 14148.17 | 14199.17 | 49 | 12:00 Hr. | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-07-09 | 15407.51 | 15693.51 | 274 | 21:00 Hr. | 51 | 12 | 20 | 191 | 0 | 0 | 0 | 0 | 0 | - | 2026-07-09 | 13754.08 | 13950.08 | 188 | 12:00 Hr. | 95 | 15 | 24 | 54 | 0 | 0 | 0 | 0 | 0 | -
2026-07-10 | 14358.07 | 14389.07 | 30 | 21:00 Hr. | 14 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | - | 2026-07-10 | 12175.54 | 12175.54 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 0
2026-07-11 | 15324.78 | 15460.78 | 130 | 19:30 Hr. | 81 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | - | 2026-07-11 | 13859.4 | 13902.4 | 41 | 12:00 Hr. | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-07-12 | 15498.03 | 15694.49 | 188 | 19:30 Hr. | 0 | 0 | 0 | 180 | 0 | 8 | 0 | 0 | 0 | - | 2026-07-12 | 13422.39 | 13422.39 | 0 | 12:00 Hr. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-07-13 | 15527 | 15578 | 49 | 19:30 Hr. | 4 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | - | 2026-07-13 | 13613.22 | 13637.22 | 23 | 12:00 Hr. | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-07-14 | 16344.02 | 17054.02 | 679 | 21:00 Hr. | 198 | 0 | 0 | 259 | 78 | 134 | 0 | 10 | 0 | - | 2026-07-14 | 14786.67 | 14941.67 | 148 | 12:00 Hr. | 57 | 0 | 16 | 75 | 0 | 0 | 0 | 0 | 0 | -
2026-07-15 | 16029.58 | 17185.58 | 1106 | 21:00 Hr. | 219 | 83 | 118 | 259 | 98 | 218 | 0 | 58 | 53 | - | 2026-07-15 | 14831.45 | 15439.45 | 582 | 12:00 Hr. | 414 | 0 | 6 | 162 | 0 | 0 | 0 | 0 | 0 | -
2026-07-16 | 16315.45 | 16853.45 | 515 | 21:00 Hr. | 40 | 0 | 42 | 313 | 0 | 92 | 0 | 0 | 28 | - | 2026-07-16 | 14788.36 | 14878.23 | 86 | 12:00 Hr. | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2026-07-17 | 15047.09 | 15080.09 | 32 | 21:00 Hr. | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | - | 2026-07-17 | 12954.44 | 12970.44 | 15 | 12:00 Hr. | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | -
2026-07-18 | 15817.5 | 16355.5 | 515 | 21:00 Hr. | 15 | 0 | 20 | 428 | 0 | 52 | 0 | 0 | 0 | - | 2026-07-18 | 14178.41 | 14407.41 | 219 | 12:00 Hr. | 111 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | -
2026-07-19 | 15670.02 | 16130.02 | 440 | 19:30 Hr. | 159 | 0 | 24 | 257 | 0 | 0 | 0 | 0 | 0 | - | 2026-07-19 | 14696.1 | 14951.1 | 244 | 12:00 Hr. | 109 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | -
2026-07-20 | 15332.1 | 15511.1 | 171 | 19:30 Hr. | 7 | 0 | 26 | 138 | 0 | 0 | 0 | 0 | 0 | - | 2026-07-20 | 13990.44 | 14071.95 | 78 | 12:00 Hr. | 52 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | -
2026-07-21 | 15833.95 | 16189.95 | 341 | 20:00 Hr. | 25 | 0 | 31 | 285 | 0 | 0 | 0 | 0 | 0 | - | 2026-07-21 | 13992.75 | 14008.75 | 15 | 12:00 Hr. | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | -
2026-07-22 | 15384.75 | 15612.75 | 218 | 21:00 Hr. | 63 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | - | 2026-07-22 | 14290.4 | 14474.4 | 176 | 12:00 Hr. | 158 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | -
2026-07-23 | 15449.3 | 15672.3 | 213 | 19:30 Hr. | 64 | 0 | 22 | 89 | 38 | 0 | 0 | 0 | 0 | - | 2026-07-23 | 14107.12 | 14483.12 | 360 | 12:00 Hr. | 334 | 0 | 4 | 22 | 0 | 0 | 0 | 0 | 0 | -
2026-07-24 | 14450.72 | 14682.72 | 222 | 21:00 Hr. | 0 | 0 | 0 | 142 | 80 | 0 | 0 | 0 | 0 | - | 2026-07-24 | 12541.95 | 12735.95 | 186 | 12:00 Hr. | 58 | 0 | 35 | 77 | 16 | 0 | 0 | 0 | 0 | -
2026-07-25 | 15784.71 | 16692.71 | 869 | 20:00 Hr. | 161 | 0 | 8 | 353 | 207 | 101 | 2 | 0 | 37 | - | 2026-07-25 | 14007.39 | 14512.39 | 483 | 12:00 Hr. | 302 | 0 | 0 | 119 | 62 | 0 | 0 | 0 | 0 | -
2026-07-26 | 16080.7 | 17266.7 | 1135 | 21:00 Hr. | 286 | 0 | 18 | 648 | 84 | 99 | 0 | 0 | 0 | - | 2026-07-26 | 14388.39 | 15597.39 | 1157 | 12:00 Hr. | 741 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | -
2026-07-27 | 16080.45 | 16080.45 | 782 | 21:00 Hr. | 227 | 0 | 0 | 446 | 109 | 0 | 0 | 0 | 0 | - | 2026-07-27 | 14259.88 | 15077.88 | 783 | 12:00 Hr. | 487 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | -
2026-07-28 | 15636.28 | 17138.28 | 1437 | 21:00 Hr. | 120 | 116 | 133 | 411 | 235 | 174 | 32 | 146 | 70 | - | 2026-07-28 | 13996.92 | 15442.92 | 1384 | 12:00 Hr. | 568 | 55 | 190 | 424 | 140 | 0 | 0 | 7 | 0 | -
2026-07-29 | 14798.75 | 17238.75 | 2335 | 21:00 Hr. | 436 | 195 | 307 | 402 | 212 | 266 | 113 | 216 | 188 | - | 2026-07-29 | 14761.4 | 15929.4 | 1118 | 12:00 Hr. | 553 | 97 | 64 | 258 | 112 | 0 | 6 | 0 | 28 | -
2026-07-30 | 15322.59 | 16868.59 | 1479 | 21:00 Hr. | 234 | 66 | 201 | 311 | 103 | 249 | 45 | 185 | 85 | - | 2026-07-30 | 13611.74 | 15648.45 | 1949 | 12:00 Hr. | 629 | 139 | 168 | 177 | 155 | 252 | 94 | 246 | 89 | -
2026-07-31 | 14702.52 | 16286.52 | 1516 | 21:00 Hr. | 4 | 0 | 288 | 165 | 89 | 362 | 82 | 287 | 239 | - | 2026-07-31 | 13543.01 | 13923.01 | 364 | 12:00 Hr. | 68 | 0 | 0 | 2 | 0 | 163 | 0 | 0 | 131 | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: July 2026
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 16716.67 | 2026-07-02 | 21:00 Hr.
2 | Maximum Day Peak Genaration | MW | 15327.46 | 2026-07-02 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 17266.7 | 2026-07-26 | 21:00 Hr.
4 | Minimum Generation | MW | 11329.86 | 2026-07-10 | 08:00 Hr.
5 | Average of the daily evening peak Genaration | MW | 15613.7248 | - | -
6 | Average of the daily day peak Genaration | MW | 14076.9597 | - | -
7 | Maximum load shed (Evening Peak) | MW | 2335 | 2026-07-29 | 21:00 Hr.
8 | Minimum load shed | MW | 30 | 2026-07-10 | 21:00 Hr.
9 | Total nos. of load shed days | Day | 31 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 568.7419 | - | -
11 | Total Generation | MkWh | 10615.3615 | - | -
12 | Total Generation by BPDB | MkWh | 1143.3569 | % of total Gen. | 10.77%
13 | Total Generation by IPP | MkWh | 2754.1536 | '' | 25.94%
14 | A) Total Generation by Generation Companies | MkWh | 4886.0001 | '' | 46.03%
| B) Total Generation by REB | MkWh | 48.4553 | " | 0.4565%
| C) Total Generation by RENTAL | MkWh | 90.0345 | " | 0.8482%
| D) Total Imported from India (BIPTC) | MkWh | 630.216 | " | 5.937%
| E) Total Imported from Tripura, India (A.C) | MkWh | 100.4803 | " | 0.9466%
| F) Total Imported from Nepal | MkWh | 28.272 | " | 0.2663%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 934.3928 | " | 8.802%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3659.1497 | % of total Gen. | 34.47%
| B) Oil | MkWh | 1087.4355 | '' | 10.24%
| C) Hydro | MkWh | 128.8827 | '' | 1.214%
| D) Solar | MkWh | 105.8874 | '' | 0.9975%
| E) Coal | MkWh | 3920.2061 | '' | 36.93%
| F) BIPTC (Import from India) | MkWh | 630.216 | '' | 5.937%
| G) A.C (Import from Tripura, India) | MkWh | 100.4803 | '' | 0.9466%
| H) Total Imported from Nepal | MkWh | 28.272 | '' | 0.2663%
| I) Adani (Import from India) | MkWh | 934.3928 | '' | 8.802%
| J) Wind | MkWh | 20.4389 | '' | 0.1925%
16 | Maximun of the daily total Generation . | MkWh | 367.2367 | 2026-07-02
17 | Monthly Load factor | % | 85.3709 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 70979.7872 | - | -
| A) Gas | M.Taka | 12587.1647 | - | -
| B) Coal | M.Taka | 26241.8764 | - | -
| C) HFO | M.Taka | 19313.1247 | - | -
| D) HSD | M.Taka | 216.1286 | - | -
| E) Hydro | M.Taka | 197.5251 | - | -
| F) Solar | M.Taka | 1720.3945 | - | -
| G) Total Import | M.Taka | 10402.9172 | - | -
| H) Wind | M.Taka | 300.6559 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2707.501 | 2026-07-26
| A) Gas | M.Taka | 473.1821 | 2026-07-16
| B) Coal | M.Taka | 948.5595 | 2026-07-16
| C) HFO | M.Taka | 1023.2765 | 2026-07-26
| D) HSD | M.Taka | 34.252 | 2026-07-27 | -
| E) Hydro | M.Taka | 19.5101 | 2026-07-13 | -
| F) Solar | M.Taka | 85.6673 | 2026-07-04 | -
| G) Total Import | M.Taka | 385.6155 | 2026-07-27
| H) Wind | M.Taka | 18.8735 | 2026-07-04
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.685
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.8499
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.83 | 31/7/2026 | 06:00
b) | Actual | FT (MSL) | 102.2 | 31/7/2026 | 06:00
22 | Peak Genaration of July 2025 | MW | 16794 | 2025-07-23 | 21:00 Hr.
23 | Peak Demand of July 2025 | MW | 17099.14 | 2025-07-23 | 21:00 Hr.
24 | Maximum peak Generation recorded upto 31/07/2026 | MW | 17200.79 | 2026-05-20 | 21:00 Hr.
25 | Maximum peak Demand recorded upto 31/07/2026 | MW | 17610.79 | 2026-05-20 | 21:00 Hr.
26 | Maximum load shed recorded upto 31/07/2026 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [75 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Fuel | Installed capacity (MW) | Capability Status of Last Week | 30.07.2026 | 23.07.2026 | 16.07.2026 | 09.07.2026 | 02.07.2026 | 25.06.2026 | 18.06.2026 | 11.06.2026 | 04.06.2026 | 28.05.2026 | 21.05.2026 | 14.05.2026 | 07.05.2026 | 30.04.2026 | 23.04.2026 | 16.04.2026 | 09.04.2026 | 02.04.2026 | 26.03.2026 | 19.03.2026 | 12.03.2026 | 05.03.2026 | 26.02.2026 | 19.02.2026 | 12.02.2026 | 05.02.2026 | 29.01.2026 | 22.01.2026 | 15.01.2026 | 08.01.2026 | 01.01.2026 | 25.12.2025 | 18.12.2025 | 11.12.2025 | 04.12.2025 | 27.11.2025 | 20.11.2025 | 13.11.2025 | 06.11.2025 | 30.10.2025 | 23.10.2025 | 16.10.2025 | 09.10.2025 | 02.10.2025 | 25.09.2025 | 18.09.2025 | 11.09.2025 | 04.09.2025 | 28.08.2025 | 21.08.2025 | 14.08.2025 | 07.08.2025 | 31.07.2025 | 24.07.2025 | 17.07.2025 | 10.07.2025 | 03.07.2025 | 26.06.2025 | 19.06.2025 | 12.06.2025 | 05.06.2025 | 29.05.2025 | 22.05.2025 | 15.05.2025 | 08.05.2025 | 01.05.2025 | 24.04.2025 | 17.04.2025 | 10.04.2025 | 03.04.2025 | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | Capable | 15 | 15 | 15 |  | 5 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | Capable | [8 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220 | Capable | [50 empty] | 20 | 20 | [7 empty] | 20 | [41 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220 | Capable | [31 empty] | 20 | 20 | [18 empty] | 20 | [5 empty] | 20 | 20 | 20 | 20 | [40 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | Capable | 17 | 17 | 35 | 35 | [37 empty] | 7 | 7 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | Capable | [21 empty] | 30 | 30 | 30 | 30 | 30 | [56 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | Capable | [8 empty] | 20 | 20 | 20 | 20 | [5 empty] | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410 | Capable | [51 empty] | 45 | [47 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
9 | Haripur 412 MW CCPP | EGCB | Gas | 412 | Capable | [14 empty] | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [24 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163 | Capable
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210 | Capable
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225 | Capable
14 | Shikalbaha Peaking GT | BPDB | Gas | 150 | Capable
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330 | Capable | [75 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 | Capable | [17 empty] | 20 | 20 | 20 | [52 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104 | Capable | [14 empty] | 2 | 2 | 2 | [32 empty] | 2 |  |  | 2 | 2 | [18 empty] | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
18 | Bhola 225 MW CCPP | BPDB | Gas | 194 | Capable | [54 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365 | Capable
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210 | Capable | [23 empty] | 16 | 16 |  |  | 20 | 20 | 20 | 20 |  |  | 20 | 20 | 20 |  |  |  | 20 | [10 empty] | 20 | 16 | [7 empty] | 20 | 20 | [38 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | Capable | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | [47 empty] | 30 | 30 | 30 | 30 |  | 30 | 30
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | Capable | [15 empty] | 30 | 30 | 30 | 30 | 30 | 35 | 35 | 35 | 35 | [11 empty] | 30 | 30 | 30 | 30 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231 | Capable
24 | RPCL 210 MW CCPP | IPP | Gas | 210 | Capable but not tested recently
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100 | Not Capable but feasible
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50 | Not Capable but feasible
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410 | Not Capable but feasible
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400 | Capable | [80 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274 | Not Capable but feasible
16 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | Capable | 15 | 30 | 30 | 30 | 30 | 60 | 60 | 30 | 30 | 30 | 30 | 30 | [5 empty] | 20 | 20 | 20 | 30 | 30 | 30 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 60 |  |  |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | [7 empty] | 20 | 20
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | Capable | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [6 empty] | 16 | 16 | 30 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 10 | 10 | 10 | 10 | 10
32 | Bhola Nutan Bidyut | IPP | Gas | 220 | Capable
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360 | Not Capable but feasible
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450 | Not Capable but feasible
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150 | Capable | [49 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30
36 | Anwara 300 MW PP (United) | IPP | HFO | 300 | Capable
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | Capable
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104 | Capable
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105 | Capable
40 | Gazipur 100 MW PP | IPP | HFO | 105 | Capable
41 | United Payra Power Ltd. | IPP | HFO | 150 | Capable
42 | Madhumati 100 MW PP | IPP | HFO | 100 | Capable
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 | Capable
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 | Capable
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300 | Capable
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55 | Capable
47 | Kodda 149 MW PP Unit-1 (Summit) | IPP | HFO | 149 | Capable
48 | Feni Lanka Power | IPP | HFO | 114 | Capable
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110 | Capable
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162 | Capable
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55 | Capable
52 | Zodiac 54 MW | IPP | HFO | 54 | Capable
53 | Anlima Energy Ltd | IPP | HFO | 116 | Capable
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115 | Capable
55 | Confidence Unit-2 Bogura | IPP | HFO | 113 | Capable
56 | Confidence Unit-1 Bogura | IPP | HFO | 113 | Capable
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54 | Capable
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55 | Capable
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149 | Capable
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115 | Capable
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55 | Capable
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 | Capable | [6 empty] | 33 | 33 | 33 | 16.5 | 33 | 33 | 33 | 33 | 33 |  | 40 | 20 | 20 | 40 | 66 | 66 | 66 | 66 |  | 66 | 33 | 66 | 66 | 66 | 66 | 66 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | Capable | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 66 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  |  | 50 | 50 | 50 | 50 | 20 | 20 | 40 | 20 | 20 | 20 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 15 | 15 | 30 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 50 | 50 | 50 | 50 | 25 | 40 | 25 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 50 | 50 | 50 | 50
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | Capable | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  |  | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 25 | 30 | 30 | 30 | 30 | [11 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
66 | Unique Meghnaghat Power Ltd(UMPL) | IPP | Gas | 584 | Capable |  |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 |  | 30 | [12 empty] | 24 | 24 | 24 |  |  |  |  | 50 | 24 | 24 | 50
67 | Meghnaghat CCPP Unit 2 (Summit) | IPP | Gas | 583 | Capable | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | [10 empty] | 25 | 25 | 50 | 50 | 50 | 50 |  |  |  | 50 | 50 | 50 | 50 | 50 | 50
68 | Jera Meghnaghat Power Ltd. | IPP | Gas | 718 | Capable |  | 10 | 40 | [5 empty] | 20 | 20 | 20 | 20 | 20 | [11 empty] | 50 | 70
| Payra 1320 MW Unit-2 | BCPCL |  | 622 | Capable | [64 empty] | 20 | 20
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70 | Capable
| Shajibazar 100 MW PP | BPDB |  | 100 | Not Capable but feasible
| Khulna 225 MW CCPP | NWPGCL |  | 230 | Capable but not tested recently
Total Installed capacity | [5 empty] | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 21224 | 20506 | 20506 | 20506 | 20506 | 20506 | 20506 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19923 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19339 | 19739 | 19739 | 19739 | 19739 | 14388 | 14388 | 14388 | 14388 | 14388 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity | [5 empty] | 5430 | 5680 | 6495 | 5475 | 6060 | 6093 | 7377 | 6744 | 6794 | 4864 | 6567 | 6861 | 6051 | 4051 | 4051 | 4246 | 4752 | 5680 | 6978 | 8164 | 7834 | 8174 | 8174 | 7698 | 7298 | 6286 | 4146 | 5722 | 6660 | 6754 | 7086 | 6756 | 5564 | 5851 | 5937 | 5232 | 5185 | 3503 | 3503 | 6403 | 6525 | 5821 | 6221 | 6871 | 7523 | 8031 | 7313 | 7523 | 6939 | 8121 | 8527 | 9061 | 8099 | 8099 | 7580 | 8537 | 6163 | 6795 | 6632 | 2862 | 3135 | 2325 | 2165 | 2165 | 2525 | 2855 | 2325 | 1595 | 1635 | 1072 | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve | [5 empty] | 170 | 205 | 268 | 213 | 223 | 263 | 296 | 264 | 274 | 232.5 | 291 | 286 | 236 | 186 | 186 | 198 | 238 | 304 | 349 | 394 | 489 | 519 | 519 | 490 | 455 | 419 | 256 | 359 | 399 | 429 | 443 | 398 | 365 | 358 | 358 | 328 | 324 | 228 | 228 | 351 | 372 | 349 | 379 | 427 | 477 | 471 | 451 | 477 | 427 | 459 | 452 | 503 | 386 | 404 | 382 | 452 | 356 | 424 | 408 | 262 | 288 | 218 | 193 | 193 | 202 | 232 | 212 | 152 | 137 | 92 | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO | [5 empty] | 10 | 11 | 11 | 9 | 10 | 10 | 11 | 10 | 11 | 11 | 13 | 12 | 10 | 8 | 8 | 9 | 10 | 14 | 15 | 15 | 14 |  |  | 15 | 14 | 12 | 10 | 11 | 12 | 12 | 11 | 10 | 10 | 9 | 9 | 9 | 9 | 7 | 7 | 9 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 12 | 14 | 13 | 15 | 12 | 12 | 12 | 13 | 11 | 14 | 13 | 11 | 12 | 9 | 9 | 9 | 10 | 11 | 9 | 7 | 7 | 5 | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list | [5 empty] | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 68 | 68 | 68 | 68 | 64 | 64 | 64 | 64 | 64 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list | [5 empty] | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 74 | 74 | 74 | 74 | 70 | 70 | 70 | 70 | 70 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable | [5 empty] | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 63 | 63 | 61 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 58 | 58 | 58 | 58 | 58 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible | [5 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: July 2026
SL | Plant Name | Owner | Fuel | Installed capacity | FGMO Status
|  |  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | Gas | 341 | √ |  | √ | √ | √ |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ |  | √
2 | Sirajgonj 400 MW CCPP Unit-4 | IPP | Gas | 414 | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ |  | √ |  |  | √ | √ |  | √ |  |  | √
3 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | Gas | 220
4 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | Gas | 220
5 | Meghnaghat CCPP(Summit) | IPP | Gas | 305 | [6 empty] | √ | [5 empty] | √ | √
6 | Ashuganj 450 MW CCPP(North) | APSCL | Gas | 360 | [15 empty] | √
7 | Ashuganj 225 MW CCPP | APSCL | Gas | 221 | √ |  | √ | √ | √ | √ |  | √ | √ |  |  |  |  | √ | √ | √ |  |  |  |  | √ | √ | [7 empty] | √
8 | Bheramara 410 MW CCPP | NWPGCL | Gas | 410
9 | Haripur 412 MW CCPP | EGCB | Gas | 412
10 | Fenchugonj CCPP Phase-1 | BPDB | Gas | 97
11 | Chandpur 150 MW CCPP | BPDB | Gas | 163
12 | Siddhirganj 2x120 MW GTPP | EGCB | Gas | 210
13 | Shikalbaha 225 MW CCPP | BPDB | Gas | 225
14 | Shikalbaha Peaking GT | BPDB | Gas | 150
15 | Shahjibazar 330 MW CCPP | BPDB | Gas | 330
16 | Ashuganj 450 MW CCPP(South) | APSCL | Gas | 360 | [14 empty] | √ | √ | √ | √ | √
17 | Fenchugonj CCPP Phase-2 | BPDB | Gas | 104
18 | Bhola 225 MW CCPP | BPDB | Gas | 194
19 | Ghorasal 365 MW CCPP Unit-7 | BPDB | Gas | 365
20 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | Gas | 210
21 | Siddhirganj 335 MW CCPP | EGCB | Gas | 335 | [6 empty] | √ | [5 empty] | √ |  |  |  | √ | √ | √ |  |  | √
22 | Bibiyana-III 400 MW CCPP | BPDB | Gas | 400 | [23 empty] | √ | √ | √ | √ | √ | √ | √
23 | Sylhet 225 MW CCPP | BPDB | Gas | 231
24 | RPCL 210 MW CCPP | IPP | Gas | 210
25 | a) Baghabari 71 MW GTPP | BPDB | Gas | 71
| b) Baghabari 100 MW GTPP | BPDB | Gas | 100
26 | Karnaphuli Hydro PP Unit: 1 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | Hydro | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | Hydro | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | Hydro | 50
27 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | Gas | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | Gas | 410
28 | Bibiyana South 400 MW CCPP | BPDB | Gas | 400
29 | Barapukuria 275 MW TPP Unit-3 | BPDB | Coal | 274
30 | Payra 1320 MW Unit-1 & 2 | BCPCL | Coal | 1244 | √ |  | √ | √ | √ |  |  | √ | √ | √ | √ |  |  | √ | √ | √ | √ | √ | √ |  | √ | √ | [7 empty] | √
31 | Kushiara 163 MW CCPP (KP) | IPP | Gas | 163 | √ |  | √ | √ | √ |  | √ | √ | √ |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
32 | Bhola Nutan Bidyut | IPP | Gas | 220
33 | Haripur 360MW CCPP(HPL) | IPP | Gas | 360
34 | Meghnaghat 450 MW CCPP(MPL) | IPP | Gas | 450
35 | Matarbari 1200 MW U-1 & 2 | CPGCBL | Coal | 1150
36 | Anwara 300 MW PP (United) | IPP | HFO | 300
37 | Chandpur 200MW (Desh energy) | IPP | HFO | 200 | [26 empty] | √ | √ | √
38 | Meghnaghat 104 MW PP (OPCL) | IPP | HFO | 104
39 | Rupsha 105 MW PP (Orion rupsha) | IPP | HFO | 105
40 | Gazipur 100 MW PP | IPP | HFO | 105
41 | United Payra Power Ltd. | IPP | HFO | 150
42 | Madhumati 100 MW PP | IPP | HFO | 100
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | IPP | HFO | 105 |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
44 | Karnaphuli Power Ltd. | IPP | HFO | 110 |  | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
45 | Kodda 300 MW PP Unit-2 (Summit) | IPP | HFO | 300
46 | Madanganj-55 MW PP(Summit) | IPP | HFO | 55
47 | Kodda 150 MW PP BRPL | IPP | HFO | 149
48 | Feni Lanka Power | IPP | HFO | 114 | [5 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
49 | Barisal 110 MW PP (Summit) | IPP | HFO | 110 | [19 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
50 | Manikganj 162 MW (MPGL) | IPP | HFO | 162
51 | Nawabganj 55 MW (Dhaka southern Power) | IPP | HFO | 55
52 | Jodiac Power | IPP | HFO | 54
53 | Anlima Energy Ltd | IPP | HFO | 116 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
54 | Thakurgaon 115 MW (EPV) | IPP | HFO | 115
55 | Confidence Unit-2 Bogura | IPP | HFO | 113
56 | Confidence Unit-1 Bogura | IPP | HFO | 113
57 | Kamalaghat 54 MW Banco Energy | IPP | HFO | 54
58 | Manikganj 55 MW (Dhaka Northern Power) | IPP | HFO | 55
59 | Kodda 150 MW (BR Power) | IPP | HFO | 149
60 | Chandpur 115 MW (Doreen) | IPP | HFO | 115
61 | Kanchan Purbachal Power Ltd | IPP | HFO | 55
62 | Chattogram SS Power U- 1 & 2 | Private | Coal | 1224 |  | √ | [14 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
63 | Adani Power (Jharkhand) Limited U- 1 & 2 | Private | Coal | 1436 | [6 empty] | √ |  |  | √ |  | √ | √ | [7 empty] | √ | √ |  |  |  |  | √ | √
64 | Rampal 1320 MW U-1 & 2 | BIFPCL | Coal | 1234 | [6 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  | √ |  |  | √ | √ | √ | √ | √ | √ | √ | √
65 | Barishal 307 MW PP (BEPCL) | Private | Coal | 307 | √ | [5 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
66 | Unique Meghnaghat Power Limited (UMPL) | IPP | Gas | 584 | [6 empty] | √ |  | √ | √ | √
67 | Meghnaghat CCPP(Summit)-2 | IPP | Gas/HSD | 583 | √ |  |  | √ | √ |  | √ | √ | √ |  |  |  |  | √ |  | √ | √ | √ | √ |  | √ | √ |  | √ | √ | √ | √
| JERA Meghnaghat Power Limited | IPP | Gas | 718 | [16 empty] | √ | √ | √
| United Payra Power Ltd. | IPP |  | 150
| Mirsharai 150 MW | IPP | HFO/Gas | 150 | [15 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
Jangalia 52 MW PP (Lakdanavi)
| Ashuganj 420 MW CCPP(East) | APSCL |  | 400
| Ashuganj 55 MW PP (Precision) | QRPP |  | 55
| Bagura 113 MW PP (Confidence)-2 | IPP |  | 113
| Energypac Power Venture Thakurgaon Ltd. | IPP |  | 115 | [23 empty] | √ | √ | √
| Chandpur 150 MW CCPP | BPDB |  | 163
| Khulna 225 MW CCPP | NWPGCL |  | 230
| Shahjibazar GTPP Unit 8 & 9 | BPDB |  | 70
| Shajibazar 100 MW PP | BPDB |  | 100
| Payra 1320 MW Unit-1 | BCPCL |  | 622
| Patuakhali 1320 MW (RNPL) | [18 empty] | √