## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 04-09-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-09-2026 | during | 04-09-2026 | during | 04-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 374 | 334 | 412 | 412 | 382 | 382 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 0 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 312 | 302 | 335 | 335 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 35 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 96 | 80 | 149.36 | 149.36 | 45 | 142 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 4.5 | 4.5 | 33 | 33 | 5 | 5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 50 | 50 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 81 | 300 | 300 | 32 | 81 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 32 | 149 | 149 | 34 | 53 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 34 | 105
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 20 | 74 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 14 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 380 | 350 | 584 | 584 | 584 | 584 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 251 | 229 | 718 | 718 | 260 | 260 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 123 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 2018.5 | 2147.92 | 5396.16 | 5370.16 | 1759.42 | 2204.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 17 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 1 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 43 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 220 | 220 | 218 | 218 | 218 | 218 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 215 | 210 | 210 | 210 | 210 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 34 | 105 | 105 | 34 | 34 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 46 | 14 | 32 | 14 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 50 | 100 | 100 | 24 | 50 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 5 | 42 | 42 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 29 | 48 | 95.1 | 95.1 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1.29 | 0 | 3.54 | 0 | 3.54 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 17 | 35 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 64 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 50 | 100 | 100 | 25 | 50 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 90 | 109 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 53 | 53 | 163 | 163 | 35 | 55 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1165 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 3 | 27 | 22 | 8 | 22 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1130 | 1130 | 1150 | 1150 | 1150 | 1150 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3147.29 | 3436 | 4108.5 | 4153.96 | 3324.54 | 3510.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 207 | 218 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 300 | 300 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 320 | 280 | 342.01 | 342.01 | 306.01 | 306.01 | FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 250 | 280 | 393 | 393 | 250 | 250 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 43 | 43 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 50 | 150 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 30 | 30 | 30 | 30 | 30 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 86 | 90 | 163 | 163 | 91 | 91 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 156 | 189 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 162 | 162 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 105 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 64 | 74 | 113 | 113 | 9 | 70 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 114 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 3 | 0 | 9 | 0 | 9 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1829 | 2114.2 | 2701.44 | 2686.44 | 1895.47 | 2101.47
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 03-09-2026 | during | 04-09-2026 | during | 04-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 22.26 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 106 | 172 | 120 | 170 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 78 | 60 | 90 | 60 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 25.92 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 236.18 | 279 | 537.6 | 546.5 | 263.1 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 40 | 40 | 40 | 40 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 40 | 40 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | Under Maintenance
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 142 | 140 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 20 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 60 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 127 | 126 | 120 | 120 | 120 | 120 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 8 | 16 | 16 | 16 | 16 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 265 | 248 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 380 | 393 | 380 | 390 | 380 | 390 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 396 | 400 | 383 | 383 | 383 | 383 | Machine Problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1523 | 1466 | 1739 | 1749 | 1532 | 1542
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 867 | 889 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 50 | 50 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 0 | 34 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 85 | 105 | 105 | 67 | 67 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 50 | 0 | 55 | 0 | 55 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 150 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 370 | 370 | 370 | 370 | 370 | 370 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1287 | 1551 | 2720 | 2665 | 1847 | 1826
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 916 | 1000 | 800 | 800 | 700 | 700 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 0 | 32 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 117 | 118 | 120 | 120 | 119 | 119 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 570 | 570 | 580 | 580 | 580 | 580 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.25 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2147.25 | 2264 | 2288 | 2287 | 1944 | 1975
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 67.67 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 33 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 14 | 30 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 134 | 214 | 214 | 140 | 140 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 285 | 270 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 17 | 25 | 25 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 101 | 100 | 100 | 0 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 55 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.72 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 911.62 | 1398.88 | 900 | 1300 | 900 | 900 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 67.5 | 0 | 63 | 0 | 63 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1667.51 | 2083.88 | 2701.91 | 2881.99 | 1814.33 | 1744.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 48 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 157 | 155 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 99 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.8 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 9 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 184 | 0 | 156.3 | 0 | 156.3 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 518.8 | 582 | 663.3 | 472 | 550.3 | 394
System Total |  |  |  |  | 28843.2 | 29158.791 | 14374.53 | 15924 | 22855.91 | 22812.05 | 14930.16 | 15586.8
Forecast Scenario (04-09-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14741 |  | 1619 |  | 16436
|  |  |  | 1:00 | 13593 |  | 2222 |  | 15919.7016
|  |  |  | 2:00 | 13473 |  | 2209 |  | 15786.089
|  |  |  | 3:00 | 13384 |  | 2108 |  | 15591.3298
|  |  |  | 4:00 | 13355 |  | 1901 |  | 15345.5759
|  |  |  | 5:00 | 13117 |  | 1767 |  | 14967.2618
|  |  |  | 6:00 | 12754 |  | 914 |  | 13711.0681
|  |  |  | 7:00 | 13380 |  | 530 |  | 13934.9738
|  |  |  | 8:00 | 13310 |  | 344 |  | 13670.2094
|  |  |  | 9:00 | 13280 |  | 145 |  | 13431.8325
|  |  |  | 10:00 | 13600 |  | 0 |  | 13600
|  |  |  | 11:00 | 14060 |  | 0 |  | 14060
|  |  |  | 12:00 | 14370 |  | 500 |  | 14893.5602
|  |  |  | 13:00 | 13900 |  | 792.65 |  | 14730
|  |  |  | 14:00 | 14060 |  | 570 |  | 14656.8586
|  |  |  | 15:00 | 13890 |  | 238.75 |  | 14140
|  |  |  | 16:00 | 13480 |  | 248.3 |  | 13740
|  |  |  | 17:00 | 13820 |  | 0 |  | 13820
|  |  |  | 18:00 | 13850 |  | 0 |  | 13850
|  |  |  | 18:30 | 14330 |  | 0 |  | 14330
|  |  |  | 19:00 | 14810 |  | 650 |  | 15490.6283
|  |  |  | 19:30 | 15197 |  | 747.765 |  | 15980
|  |  |  | 20:00 | 15454 |  | 702.88 |  | 16190
|  |  |  | 21:00 | 15540 |  | 993 |  | 16579.7906
|  |  |  | 22:00 | 15550 |  | 878.6 |  | 16470
|  |  |  | 23:00 | 15430 |  | 1337 |  | 16830
Probable Maximum Temperature: |  |  | 33.3°C
Probable Maximum Demand at Day Peak: |  |  | 13930.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 993
Probable Maximum Demand at Evening Peak: |  |  | 16580.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15540.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 337.194 MKWHr. |  | 253 | 80 | 100 | 150 | 50 | 110 | 40 | 110 | 100 | 993
*** This report is generated digitally from Operation Information System (OIS) at 08:49 hrs on 04-09-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 03-09-2026 | [28 empty] | Date: | 03-09-2026 | [28 empty] | Date: | 03-09-2026 | [28 empty] | Date: | 03-09-2026 | [28 empty] | Date: | 03-09-2026 | [17 empty] | Date: | 03-09-2026
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [17 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 17 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 217 | 54 | 0 | 34 | 98 | 48 | 0 | 55 | 162 | 0 | 0 | 0 | 0 | 35 | 305 | 0 | 0 | 0 | 34 | 4.5 | 22 | 0 | 310 | 90 | 16 | 25 | 0 | 10 | 50 | 30 | 17 | 24 | 25 | 0 | 222 | 96 | 2 | 1130 | 53 | 0 | 43 | 25.5 | 34 | 219 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 260 | 300 | 285 | 43 | 0 | 201 | 0 | 115 | 90 | 188 | 0 | 19 | 105 | 170 | 52.2 | 0 | 24 | 260 | 400 | 392 | 40 | 30 | 0 | 0 | 16 | 0 | 86 | 25 | 143 | 0 | 126 | 17 | 87 | 0 | 165 | 0 | 0 | 0 | 12 | 8875.2 | 749 | 0 | 0 | 19 | 44 | 0 | 0 | 0 | 241 | 0 | 32 | 0 | 370 | 50 | 0 | 0 | 1301.32 | 0 | 33 | 0 | 55 | 70 | 0 | 102 | 28 | 8 | 0 | 0 | 18 | 0 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 158 | 50 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 200 | 117 | 220 | 0 | 700 | 570 | 17 | 5773.32 | 14648.52 | 105.58
01:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 245 | 35 | 0 | 34 | 98 | 48 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 305 | 0 | 0 | 0 | 34 | 4.5 | 22 | 0 | 380 | 90 | 16 | 24 | 0 | 12 | 50 | 30 | 0 | 24 | 25 | 0 | 222 | 83 | 2 | 1130 | 53 | 0 | 43 | 8 | 23 | 218 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 270 | 300 | 305 | 43 | 0 | 214 | 0 | 56 | 91 | 168 | 0 | 19 | 105 | 172 | 52.2 | 0 | 24 | 255 | 400 | 380 | 41 | 30 | 0 | 0 | 16 | 0 | 86 | 25 | 140 | 0 | 126 | 17 | 57 | 0 | 66 | 0 | 0 | 0 | 12 | 8572.7 | 868 | 0 | 0 | 19 | 40 | 0 | 0 | 0 | 150 | 0 | 32 | 0 | 370 | 0 | 0 | 0 | 1113.57 | 0 | 33 | 0 | 0 | 0 | 0 | 102 | 28 | 8 | 0 | 0 | 18 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 159 | 50 | 115 | 0 | 34 | 0 | 100 | 0 | 0 | 0 | 0 | 16 | 200 | 117 | 220 | 0 | 600 | 570 | 17 | 5410.57 | 13983.27 | 105.57
02:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 257 | 35 | 0 | 34 | 98 | 32 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 317 | 0 | 0 | 0 | 34 | 4.5 | 22 | 0 | 410 | 79 | 16 | 25 | 0 | 9 | 50 | 15 | 0 | 24 | 25 | 0 | 222 | 56 | 2 | 1130 | 53 | 0 | 50 | 8 | 34 | 219 | 0 | 0 | 0 | 1224 | 0 | 55 | 0 | 250 | 300 | 335 | 43 | 0 | 215 | 0 | 34 | 90 | 155 | 0 | 19 | 105 | 162 | 52.2 | 0 | 24 | 260 | 397 | 380 | 41 | 30 | 0 | 0 | 16 | 0 | 86 | 25 | 141 | 0 | 124 | 17 | 57 | 0 | 67 | 0 | 0 | 0 | 12 | 8536.7 | 773 | 0 | 0 | 19 | 40 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 370 | 0 | 0 | 0 | 964.2 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 0 | 0 | 18 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 160 | 51 | 115 | 0 | 34 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 307 | 117 | 220 | 0 | 600 | 570 | 17 | 4947.2 | 13483.9 | 105.56
03:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 249 | 35 | 0 | 34 | 98 | 32 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 312 | 0 | 0 | 0 | 143.42 | 4.5 | 22 | 0 | 390 | 90 | 16 | 24 | 0 | 2 | 0 | 15 | 0 | 24 | 25 | 0 | 222 | 55 | 7 | 1130 | 53 | 0 | 50 | 8 | 34 | 219 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 250 | 300 | 310 | 43 | 0 | 223 | 0 | 34 | 90 | 154 | 0 | 19 | 105 | 156 | 52.2 | 0 | 24 | 260 | 400 | 368 | 41 | 30 | 0 | 0 | 16 | 0 | 86 | 25 | 143 | 0 | 125 | 0 | 57 | 0 | 67 | 0 | 0 | 0 | 12 | 8502.12 | 773 | 0 | 0 | 19 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 370 | 0 | 0 | 0 | 951.53 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 0 | 0 | 18 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 156 | 51 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 117 | 220 | 0 | 600 | 570 | 17 | 4907.53 | 13409.65 | 105.55
04:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 215 | 35 | 0 | 34 | 98 | 32 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 4.8 | 22 | 0 | 330 | 90 | 16 | 25 | 0 | 1 | 0 | 16 | 0 | 24 | 25 | 0 | 222 | 55 | 12 | 1130 | 53 | 0 | 50 | 8 | 34 | 219 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 250 | 300 | 305 | 43 | 0 | 223 | 0 | 34 | 90 | 155 | 0 | 19 | 105 | 152 | 52.2 | 0 | 24 | 262 | 400 | 368 | 41 | 30 | 0 | 0 | 16 | 0 | 86 | 25 | 142 | 0 | 126 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8399.42 | 867 | 0 | 0 | 19 | 38 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 370 | 0 | 0 | 0 | 952.14 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 0 | 0 | 18 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 156 | 51 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 117 | 220 | 0 | 600 | 570 | 17 | 5002.14 | 13401.56 | 105.54
05:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 241 | 0 | 0 | 34 | 98 | 32 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 143.42 | 4.8 | 22 | 0 | 370 | 90 | 16 | 25 | 0 | 11 | 0 | 16 | 0 | 24 | 25 | 0 | 220 | 55 | 19 | 1130 | 53 | 0 | 50 | 8 | 34 | 219 | 0 | 0 | 0 | 1224 | 0 | 55 | 0 | 250 | 300 | 305 | 43 | 0 | 202 | 0 | 34 | 90 | 154 | 0 | 19 | 105 | 152 | 52.2 | 0 | 24 | 265 | 400 | 368 | 41 | 30 | 0 | 0 | 16 | 0 | 86 | 28 | 142 | 0 | 126 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8399.42 | 792 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 950.35 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 0 | 0 | 18 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 156 | 51 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 117 | 220 | 0 | 600 | 570 | 17 | 4865.35 | 13264.77 | 105.53
06:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 209 | 0 | 0 | 36 | 98 | 32 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 143.42 | 4.8 | 22 | 0 | 330 | 90 | 16 | 24 | 0 | 0 | 0 | 16 | 0 | 24 | 25 | 0 | 218 | 55 | 19 | 1130 | 53 | 0 | 50 | 8 | 34 | 223 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 250 | 300 | 290 | 43 | 0 | 192 | 0 | 24 | 90 | 155 | 0 | 19 | 105 | 144 | 52.2 | 1 | 23 | 264 | 400 | 367 | 41 | 30 | 0 | 0 | 16 | 0 | 86 | 30 | 142 | 0 | 126 | 0 | 58 | 0.24 | 67 | 0 | 0 | 0.05 | 12 | 8242.71 | 792 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 960.67 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 1.11 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 154 | 51 | 115 | 1 | 0 | 0 | 0 | 0 | 0.1 | 3 | 0 | 0 | 307 | 117 | 180 | 0 | 600 | 575 | 17 | 4830.88 | 13073.59 | 105.52
07:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 252 | 0 | 0 | 134 | 98 | 32 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 2 | 143.42 | 4.8 | 22 | 0 | 395 | 90 | 16 | 24 | 0 | 13 | 0 | 16 | 0 | 24 | 25 | 0.19 | 219 | 48 | 14 | 1130 | 53 | 0 | 50 | 8 | 34 | 222 | 0 | 0 | 0 | 1224 | 1 | 55 | 0 | 250 | 300 | 320 | 43 | 0 | 208 | 0 | 17 | 90 | 154 | 0 | 19 | 105 | 142 | 52.2 | 3 | 23 | 266 | 400 | 372 | 41 | 30 | 0 | 1 | 16 | 0 | 86 | 30 | 140 | 0 | 126 | 0 | 58 | 2 | 66 | 0 | 0.1 | 8.8 | 12 | 8496.51 | 792 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 930.55 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 3.78 | 9 | 0 | 0 | 4.69 | 139 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0.73 | 154 | 51 | 115 | 3 | 0 | 0 | 0 | 0 | 0.4 | 37 | 0.01 | 0 | 307 | 117 | 220 | 0 | 600 | 575 | 17 | 4886.16 | 13382.67 | 105.51
08:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 211 | 0 | 0 | 149 | 98 | 32 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 20 | 143.42 | 4.5 | 22 | 0 | 315 | 90 | 16 | 25 | 0 | 15 | 0 | 16 | 0 | 24 | 25 | 0.27 | 218 | 54 | 0 | 1130 | 53 | 0 | 50 | 8 | 34 | 222 | 0 | 0 | 0 | 1224 | 2 | 53 | 0 | 250 | 300 | 305 | 43 | 0 | 200 | 0 | 17 | 90 | 155 | 0 | 19 | 105 | 150 | 52.2 | 2 | 23 | 268 | 400 | 380 | 41 | 30 | 0 | 2 | 16 | 0 | 86 | 30 | 141 | 0 | 125 | 0 | 58 | 4.03 | 66 | 0 | 0.5 | 10.83 | 12 | 8381.75 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 370 | 0 | 0 | 0 | 908.71 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 8.75 | 23 | 0 | 0 | 11.62 | 140 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 1.07 | 157 | 52 | 115 | 3 | 0 | 0 | 0 | 0 | 0.7 | 43 | 0.03 | 0 | 307 | 115 | 220 | 0 | 600 | 565 | 17 | 4926.88 | 13308.63 | 105.5
09:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 188 | 0 | 0 | 149 | 98 | 32 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 3 | 143.42 | 4.5 | 22 | 0 | 313 | 90 | 16 | 24 | 0 | 4 | 0 | 16 | 17 | 24 | 25 | 1.66 | 219 | 54 | 0 | 1130 | 53 | 0 | 44 | 8 | 34 | 221 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 250 | 300 | 270 | 43 | 0 | 180 | 0 | 20 | 90 | 154 | 17 | 19 | 105 | 152 | 52.2 | 1 | 23 | 260 | 400 | 367 | 42 | 30 | 0 | 4 | 16 | 0 | 84 | 30 | 142 | 0 | 125 | 0 | 58 | 7.96 | 104 | 0 | 1.3 | 28.2 | 12 | 8369.24 | 866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 4 | 370 | 0 | 0 | 0 | 902.66 | 0 | 33 | 0 | 0 | 6 | 0 | 0 | 21 | 8 | 2.74 | 19 | 0 | 0 | 16.96 | 140 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 1.69 | 159 | 50 | 115 | 13 | 0 | 0 | 0 | 0 | 2 | 43 | 0.02 | 0 | 307 | 119 | 180 | 0 | 600 | 565 | 17 | 4914.07 | 13283.31 | 105.5
10:00 | 0 | 88 | 42 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 192 | 17 | 0 | 149 | 97 | 32 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 5 | 283 | 0 | 0 | 6 | 143.42 | 4.5 | 22 | 0 | 325 | 90 | 16 | 24 | 0 | 3 | 0 | 16 | 17 | 24 | 25 | 1.07 | 219 | 55 | 0 | 1130 | 55 | 0 | 44 | 8 | 34 | 224 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 250 | 300 | 270 | 43 | 0 | 180 | 0 | 17 | 90 | 154 | 36 | 13 | 105 | 156 | 34 | 7 | 23 | 265 | 400 | 380 | 41 | 30 | 0 | 3 | 16 | 0 | 84 | 30 | 140 | 0 | 125 | 0 | 68 | 13.82 | 105 | 0 | 1.6 | 30.11 | 12 | 8512.52 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 34 | 370 | 0 | 0 | 0 | 905.04 | 0 | 33 | 0 | 0 | 35 | 0 | 0 | 21 | 8 | 64.03 | 22 | 0 | 0 | 25.56 | 140 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 1.91 | 157 | 50 | 115 | 11 | 0 | 0 | 0 | 0 | 4 | 53 | 0.06 | 0 | 307 | 119 | 220 | 0 | 600 | 570 | 17 | 5089.6 | 13602.12 | 105.49
11:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 223 | 17 | 0 | 149 | 97 | 32 | 0 | 17 | 35 | 14 | 0 | 0 | 0 | 17 | 303 | 0 | 0 | 6 | 143.42 | 4.5 | 22 | 0 | 360 | 90 | 16 | 25 | 0 | 8 | 0 | 16 | 17 | 24 | 25 | 0.45 | 220 | 55 | 0 | 1130 | 55 | 0 | 44 | 8 | 34 | 223 | 0 | 0 | 0 | 1160 | 3 | 55 | 0 | 250 | 300 | 305 | 43 | 0 | 203 | 0 | 29 | 90 | 154 | 36 | 13 | 101 | 154 | 8 | 14 | 23 | 262 | 397 | 380 | 41 | 30 | 0 | 5 | 16 | 0 | 86 | 30 | 141 | 0 | 125 | 0 | 68 | 18.8 | 106 | 0 | 2.9 | 29.24 | 12 | 8649.31 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 33 | 370 | 0 | 0 | 0 | 916.14 | 0 | 33 | 0 | 0 | 35 | 0 | 0 | 14 | 8 | 40.1 | 93 | 0 | 0 | 42.7 | 140 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 2.08 | 157 | 50 | 115 | 15 | 0 | 0 | 0 | 0 | 3.3 | 116 | 0.06 | 0 | 307 | 118 | 220 | 0 | 800 | 565 | 17 | 5410.38 | 14059.69 | 105.49
12:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 251 | 17 | 0 | 149 | 96 | 32 | 0 | 17 | 35 | 20 | 0 | 0 | 0 | 17 | 312 | 0 | 0 | 14 | 123 | 4.5 | 22 | 0 | 380 | 90 | 16 | 29 | 0 | 3 | 0 | 16 | 17 | 24 | 25 | 1.29 | 220 | 55 | 0 | 1130 | 53 | 0 | 38 | 8 | 34 | 222 | 0 | 0 | 0 | 1165 | 1 | 50 | 0 | 250 | 300 | 320 | 43 | 0 | 207 | 0 | 34 | 86 | 156 | 64 | 19 | 98 | 162 | 8 | 3 | 29 | 265 | 396 | 380 | 41 | 30 | 0 | 10 | 16 | 0 | 86 | 30 | 142 | 0 | 127 | 0 | 68 | 22.26 | 106 | 0 | 2 | 25.92 | 12 | 8753.97 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 370 | 0 | 0 | 0 | 911.62 | 0 | 33 | 0 | 0 | 35 | 0 | 0 | 14 | 8 | 67.67 | 100 | 0 | 0 | 67.5 | 140 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 5.72 | 157 | 50 | 115 | 9 | 0 | 0 | 0 | 0 | 3.8 | 184 | 0.25 | 0 | 307 | 117 | 220 | 0 | 916 | 570 | 17 | 5620.56 | 14374.53 | 105.49
13:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 244 | 17 | 0 | 149 | 95 | 32 | 0 | 17 | 35 | 30 | 0 | 0 | 0 | 17 | 298 | 0 | 0 | 35 | 143.42 | 4.5 | 22 | 0 | 390 | 90 | 16 | 40 | 0 | 3 | 0 | 16 | 17 | 24 | 25 | 1.67 | 221 | 55 | 0 | 1130 | 55 | 0 | 38 | 8 | 34 | 221 | 0 | 0 | 0 | 1160 | 9 | 55 | 0 | 250 | 300 | 300 | 43 | 0 | 200 | 0 | 34 | 86 | 154 | 47 | 19 | 105 | 150 | 8 | 9 | 29 | 267 | 390 | 380 | 41 | 30 | 0 | 9 | 16 | 0 | 86 | 28 | 142 | 0 | 128 | 0 | 58 | 22.09 | 114 | 0 | 2.4 | 37.76 | 12 | 8669.84 | 875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 370 | 0 | 0 | 0 | 919.23 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 14 | 8 | 39.46 | 110 | 0 | 0 | 57.9 | 140 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 5.86 | 154 | 50 | 115 | 32 | 0 | 0 | 0 | 0 | 5.3 | 213 | 0.24 | 0 | 307 | 118 | 220 | 0 | 900 | 570 | 17 | 5627.99 | 14297.83 | 105.48
14:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 251 | 17 | 0 | 149 | 95 | 32 | 0 | 17 | 35 | 30 | 0 | 0 | 0 | 17 | 317 | 0 | 0 | 10 | 143.42 | 4.5 | 22 | 0 | 400 | 90 | 16 | 44 | 0 | 8 | 0 | 16 | 17 | 24 | 25 | 1.37 | 222 | 55 | 0 | 1130 | 53 | 0 | 40 | 8 | 34 | 220 | 0 | 0 | 0 | 1224 | 3 | 85 | 0 | 250 | 300 | 325 | 51 | 0 | 211 | 0 | 34 | 86 | 167 | 27 | 19 | 102 | 158 | 8 | 10 | 29 | 265 | 390 | 381 | 41 | 30 | 0 | 3 | 16 | 0 | 86 | 30 | 142 | 0 | 128 | 1 | 58 | 20.42 | 114 | 0 | 2.5 | 56.21 | 12 | 8833.42 | 883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 370 | 0 | 0 | 0 | 945.05 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 14 | 8 | 59.76 | 35 | 0 | 0 | 59.85 | 140 | 0 | 0 | 0 | 0 | 0 | 262 | 0 | 5.27 | 155 | 51 | 115 | 30 | 0 | 0 | 0 | 0 | 2.6 | 119 | 0.33 | 0 | 307 | 118 | 180 | 0 | 900 | 570 | 17 | 5431.86 | 14265.28 | 105.48
15:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 230 | 17 | 0 | 110 | 95 | 32 | 0 | 17 | 35 | 30 | 0 | 0 | 0 | 25 | 280 | 0 | 0 | 15 | 143.42 | 4.5 | 22 | 0 | 340 | 90 | 16 | 38 | 0 | 26 | 0 | 17 | 17 | 24 | 25 | 1.61 | 222 | 55 | 0 | 1130 | 55 | 0 | 43 | 8 | 34 | 217 | 0 | 0 | 0 | 1224 | 13 | 102 | 0 | 250 | 300 | 300 | 51 | 0 | 198 | 0 | 33 | 86 | 171 | 27 | 19 | 106 | 152 | 8 | 3 | 29 | 257 | 400 | 380 | 41 | 30 | 0 | 4 | 16 | 0 | 52 | 25 | 141 | 0 | 126 | 17 | 58 | 19 | 114 | 0 | 1.6 | 18.87 | 12 | 8632 | 889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 370 | 0 | 0 | 0 | 927.53 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 14 | 8 | 53.09 | 31 | 0 | 0 | 14.54 | 138 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0.85 | 155 | 48 | 115 | 27 | 0 | 0 | 0 | 0 | 1.4 | 16 | 0.17 | 0 | 280 | 118 | 220 | 0 | 900 | 570 | 17 | 5246.58 | 13878.58 | 105.5
16:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 226 | 17 | 0 | 17 | 95 | 32 | 0 | 17 | 35 | 30 | 0 | 0 | 0 | 35 | 283 | 0 | 0 | 8 | 140 | 4.5 | 22 | 0 | 350 | 104 | 16 | 38 | 0 | 20 | 0 | 31 | 17 | 24 | 25 | 1.29 | 221 | 55 | 0 | 1130 | 53 | 0 | 43 | 8 | 34 | 217 | 0 | 0 | 0 | 1224 | 4 | 120 | 0 | 250 | 300 | 310 | 51 | 0 | 199 | 0 | 34 | 86 | 172 | 28 | 19 | 103 | 140 | 8 | 6 | 29 | 261 | 400 | 380 | 38 | 22 | 0 | 2 | 16 | 0 | 52 | 25 | 142 | 0 | 126 | 17 | 58 | 7 | 114 | 0 | 0.7 | 16.61 | 12 | 8526.1 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 370 | 17 | 0 | 0 | 924.06 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 14 | 8 | 10.18 | 25 | 0 | 0 | 23.28 | 136 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 2.77 | 156 | 49 | 115 | 20 | 0 | 0 | 0 | 0 | 0.2 | 70 | 0.13 | 16 | 200 | 117 | 180 | 0 | 900 | 570 | 23 | 5140.62 | 13666.72 | 105.48
17:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 194 | 17 | 0 | 17 | 94 | 32 | 0 | 35 | 162 | 34 | 0 | 0 | 0 | 35 | 271 | 0 | 0 | 2 | 143.42 | 4.5 | 22 | 0 | 300 | 109 | 16 | 38 | 0 | 10 | 0 | 31 | 17 | 24 | 25 | 0.18 | 220 | 55 | 0 | 1130 | 53 | 0 | 43 | 8 | 34 | 217 | 0 | 0 | 0 | 1224 | 1 | 135 | 0 | 280 | 300 | 240 | 51 | 0 | 186 | 0 | 34 | 86 | 171 | 38 | 19 | 105 | 148 | 8 | 9 | 29 | 257 | 400 | 380 | 38 | 22 | 0 | 1 | 16 | 0 | 52 | 25 | 141 | 0 | 126 | 17 | 58 | 6.5 | 116 | 0 | 0.5 | 8.77 | 12 | 8523.87 | 889 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 8 | 370 | 17 | 0 | 0 | 1091.36 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 14 | 8 | 7.21 | 38 | 0 | 0 | 5.34 | 135 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0.31 | 155 | 49 | 115 | 10 | 44 | 0 | 0 | 0 | 0.5 | 40 | 0.09 | 16 | 200 | 115 | 220 | 0 | 900 | 570 | 30 | 5409.81 | 13933.68 | 105.47
18:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 246 | 17 | 0 | 17 | 94 | 32 | 0 | 35 | 162 | 50 | 0 | 0 | 0 | 35 | 307 | 0 | 0 | 1 | 143.42 | 4.5 | 22 | 0 | 385 | 107 | 16 | 38 | 0 | 14 | 0 | 46 | 17 | 50 | 50 | 0 | 219 | 55 | 0 | 1130 | 53 | 0 | 43 | 8 | 34 | 215 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 260 | 280 | 280 | 51 | 0 | 202 | 0 | 34 | 86 | 174 | 65 | 19 | 105 | 138 | 8 | 0 | 29 | 256 | 399 | 360 | 38 | 20 | 0 | 0 | 16 | 0 | 53 | 22 | 141 | 0 | 126 | 17 | 58 | 0.5 | 116 | 0 | 0 | 0.04 | 12 | 8897.46 | 889 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 67 | 1 | 370 | 17 | 0 | 0 | 1306.2 | 0 | 0 | 0 | 35 | 37 | 0 | 0 | 14 | 8 | 1.12 | 6 | 16 | 0 | 1.34 | 134 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0.11 | 154 | 49 | 115 | 0 | 84 | 0 | 0 | 0 | 0.1 | 2 | 0 | 16 | 200 | 117 | 180 | 0 | 900 | 570 | 17 | 5542.87 | 14440.33 | 105.47
19:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 229 | 35 | 0 | 17 | 96 | 81 | 0 | 55 | 162 | 60 | 0 | 0 | 0 | 55 | 297 | 0 | 0 | 0 | 143.42 | 4.5 | 22 | 0 | 347 | 107 | 16 | 42 | 0 | 28 | 50 | 46 | 18 | 50 | 50 | 0 | 219 | 55 | 2 | 1130 | 53 | 0 | 43 | 11 | 34 | 215 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 260 | 300 | 290 | 51 | 0 | 197 | 0 | 46 | 90 | 189 | 73 | 19 | 105 | 164 | 9 | 0 | 30 | 252 | 400 | 392 | 39 | 30 | 0 | 0 | 0 | 0 | 53 | 25 | 141 | 0 | 126 | 17 | 86 | 0 | 162 | 0 | 0 | 0 | 12 | 9238.92 | 890 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 150 | 0 | 67 | 0 | 370 | 17 | 0 | 0 | 1310.59 | 0 | 0 | 0 | 35 | 66 | 0 | 101 | 22 | 8 | 0 | 0 | 17 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 156 | 49 | 115 | 0 | 99 | 0 | 100 | 0 | 0 | 0 | 0 | 32 | 201 | 117 | 220 | 0 | 1000 | 570 | 17 | 6175.59 | 15414.51 | 105.47
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 213 | 35 | 0 | 35 | 96 | 81 | 0 | 55 | 162 | 70 | 0 | 0 | 0 | 55 | 307 | 0 | 0 | 0 | 143.42 | 4.5 | 22 | 0 | 325 | 109 | 16 | 51 | 0 | 28 | 50 | 46 | 35 | 50 | 50 | 0 | 219 | 55 | 2 | 1130 | 53 | 0 | 43 | 17 | 34 | 215 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 280 | 300 | 310 | 51 | 0 | 197 | 0 | 115 | 91 | 189 | 73 | 19 | 105 | 166 | 34 | 0 | 30 | 248 | 400 | 392 | 41 | 30 | 0 | 0 | 8 | 0 | 60 | 25 | 141 | 0 | 126 | 17 | 87 | 0 | 161 | 0 | 0 | 0 | 12 | 9360.92 | 888 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 150 | 0 | 72 | 0 | 370 | 17 | 0 | 0 | 1317.81 | 0 | 0 | 0 | 55 | 70 | 0 | 101 | 21 | 8 | 0 | 0 | 17 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 155 | 49 | 115 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 278 | 118 | 220 | 0 | 1000 | 570 | 17 | 6358.81 | 15719.73
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 229 | 54 | 0 | 32 | 80 | 81 | 15 | 55 | 162 | 74 | 0 | 0 | 0 | 55 | 302 | 0 | 0 | 0 | 143.42 | 4.5 | 22 | 0 | 350 | 109 | 16 | 48 | 0 | 27 | 50 | 46 | 35 | 50 | 50 | 0 | 220 | 64 | 5 | 1130 | 53 | 0 | 43 | 17 | 34 | 215 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 280 | 300 | 280 | 51 | 0 | 218 | 0 | 114 | 90 | 189 | 74 | 19 | 105 | 162 | 52.2 | 0 | 30 | 248 | 400 | 393 | 41 | 30 | 0 | 0 | 8 | 0 | 60 | 20 | 140 | 0 | 126 | 17 | 78 | 0 | 172 | 0 | 0 | 0 | 12 | 9443.12 | 889 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 150 | 0 | 85 | 0 | 370 | 17 | 0 | 0 | 1398.88 | 0 | 0 | 0 | 55 | 70 | 0 | 101 | 30 | 8 | 0 | 0 | 17 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 155 | 48 | 115 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 307 | 118 | 220 | 0 | 1000 | 570 | 17 | 6480.88 | 15924 | 105.46
21:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 241 | 54 | 0 | 35 | 96 | 81 | 15 | 55 | 162 | 70 | 0 | 0 | 0 | 55 | 310 | 0 | 0 | 0 | 143.42 | 4.5 | 22 | 0 | 375 | 107 | 16 | 50 | 0 | 14 | 50 | 46 | 35 | 50 | 50 | 0 | 220 | 55 | 2 | 1130 | 53 | 0 | 43 | 17 | 34 | 215 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 280 | 300 | 270 | 51 | 0 | 220 | 0 | 115 | 90 | 187 | 74 | 19 | 105 | 150 | 52.2 | 0 | 30 | 251 | 400 | 393 | 41 | 30 | 0 | 0 | 16 | 0 | 60 | 20 | 142 | 0 | 126 | 17 | 78 | 0 | 173 | 0 | 0 | 0 | 12 | 9476.12 | 889 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 370 | 17 | 0 | 0 | 1404.38 | 0 | 0 | 0 | 55 | 70 | 0 | 101 | 30 | 8 | 0 | 0 | 17 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 156 | 48 | 115 | 0 | 99 | 0 | 70 | 0 | 0 | 0 | 0 | 32 | 307 | 117 | 220 | 0 | 1000 | 570 | 17 | 6265.38 | 15741.5 | 105.46
22:00 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 233 | 54 | 0 | 35 | 96 | 81 | 15 | 55 | 144 | 16 | 0 | 0 | 0 | 35 | 300 | 0 | 0 | 0 | 143.42 | 4.5 | 22 | 0 | 340 | 109 | 16 | 50 | 0 | 24 | 45 | 46 | 35 | 50 | 50 | 0 | 221 | 55 | 2 | 1130 | 53 | 0 | 0 | 25.5 | 34 | 215 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 280 | 300 | 265 | 51 | 0 | 223 | 0 | 115 | 90 | 189 | 74 | 19 | 105 | 158 | 52.2 | 0 | 30 | 250 | 400 | 393 | 41 | 30 | 0 | 0 | 16 | 0 | 41 | 20 | 141 | 0 | 126 | 17 | 87 | 0 | 174 | 0 | 0 | 0 | 12 | 9334.62 | 787 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 370 | 17 | 0 | 0 | 1421.66 | 0 | 0 | 0 | 55 | 70 | 0 | 101 | 28 | 8 | 0 | 0 | 17 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 156 | 48 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 118 | 220 | 0 | 1000 | 570 | 17 | 6104.66 | 15439.28 | 105.44
23:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 226 | 54 | 0 | 17 | 96 | 81 | 15 | 55 | 144 | 16 | 0 | 0 | 0 | 35 | 310 | 0 | 0 | 0 | 143.42 | 4.5 | 22 | 0 | 350 | 107 | 16 | 50 | 0 | 8 | 50 | 45 | 17 | 50 | 50 | 0 | 222 | 55 | 2 | 1130 | 53 | 0 | 0 | 25.5 | 34 | 223 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 250 | 300 | 265 | 51 | 0 | 222 | 0 | 103 | 91 | 188 | 74 | 19 | 105 | 160 | 52.2 | 0 | 30 | 250 | 400 | 392 | 41 | 30 | 0 | 0 | 16 | 0 | 42 | 20 | 141 | 0 | 126 | 17 | 87 | 0 | 164 | 0 | 0 | 0 | 12 | 9195.62 | 787 | 0 | 0 | 20 | 35 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 370 | 0 | 0 | 0 | 1404.19 | 0 | 0 | 0 | 55 | 70 | 0 | 101 | 28 | 8 | 0 | 0 | 17 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 158 | 49 | 115 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 118 | 220 | 0 | 1000 | 570 | 17 | 6100.19 | 15295.81 | 105.4
Total KWH | 0 | 1429440 | 660480 | 0 | 0 | 0 | 0 | 0 | 8823600 | 0 | 5941600 | 563400 | 0 | 1753632 | 2294880 | 1066113 | 71298 | 668790 | 1971360 | 458880 | 0 | 0 | 0 | 617007 | 7320276 | 0 | 0 | 147812 | 3189600 | 102600 | 522360 | 0 | 8704090.91 | 2314636 | 373855 | 834240 | 0 | 272160 | 386704 | 601152 | 341822 | 726720 | 735360 | 9961 | 5332002 | 1373309 | 89760 | 27010909.09 | 1298036 | 0 | 981600 | 277473.6 | 838872 | 5391959 | 0 | 0 | 0 | 29241815 | 35235 | 2196291 | 0 | 6353000 | 7525500 | 7330000 | 1136796 | 0 | 5090000 | 0 | 1124160 | 2121691 | 4016160 | 829080 | 459500 | 2518260 | 3694080 | 814963 | 66282 | 639968 | 6230000 | 9536100 | 9287000 | 960000 | 685200 | 0 | 44089 | 374208 | 0 | 1715520 | 614112 | 3227000 | 0 | 2732110 | 219600 | 1566000 | 120236 | 2601600 | 0 | 11800 | 248250 | 290640 | 211153995.6 | 20471273 | 0 | 0 | 111360 | 499456 | 0 | 0 | 0 | 672520 | 0 | 715536 | 311760 | 9010909 | 128640 | 0 | 0 | 25545421 | 0 | 388703 | 0 | 386976 | 820416 | 0 | 687056 | 482068 | 205579 | 327120 | 519980 | 181300 | 0 | 313488 | 3314091 | 0 | 0 | 0 | 0 | 0 | 7152582 | 0 | 26640 | 3899000 | 1204363 | 2733743 | 188601 | 814867 | 0 | 566370 | 0 | 33437.4 | 900000 | 1269 | 262752 | 6785000 | 2820000 | 5350500 | 0 | 19098181 | 13890909.09 | 441600 | 131263466.49 | 342417462.09

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 03-09-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14374.53 | MW | 12:00 Hr. | Energy Generated |  |  | 342.4175 |  | MKWHr.
| Day Peak Demand |  |  | 15631.53 | MW | 12:00 Hr. | Energy Unserverd |  |  | 36.035 |  | MKWHr.
| Evening Peak Generation |  |  | 15924 | MW | 20:00 Hr. | Energy Demand |  |  | 378.4525 |  | MKWHr.
| Evening Peak Demand |  |  | 16843.51 | MW | 19:00 Hr. | Maximum Temperature |  |  | 33.3 |  | °C
| Minimum Generation of the Day |  |  | 13073.59 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 849.43 |  | MMCFD
| Maximum Generation of the Day |  |  | 15924 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 7.6939 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.4145 | 0 | 14.7449 | 0 | 0 | 0.14781 | 0 | 0 | 46.3072 | Gas | 120.9112 | Gas | 416355009.7947
| Chattogram Zone |  |  | 5.4817 | 56.2527 | 11.0838 | 0 | 5.332 | 0.045196 | 0 | 0.27216 | 78.4676 | Coal | 110.1411 | Coal | 765617145.0487
| Cumilla Zone |  |  | 30.0165 | 0 | 12.1389 | 0 | 0 | 0.066282 | 3.6941 | 0 | 45.9157 | HFO | 51.5054 | HFO | 1049499458.928
| Mymensingh Zone |  |  | 0 | 0 | 4.6778 | 0 | 0 | 0.38029 | 0 | 0 | 5.0581 | HSD | 1.2389 | HSD | 31074409.6
| Sylhet Zone |  |  | 35.3612 | 0 | 0 | 0 | 0 | 0.044089 | 0 | 0 | 35.4053 | Hydro | 5.332 | Hydro | 533200.2
| Khulna Zone |  |  | 0 | 9.0109 | 1.455 | 0.67252 | 0 | 0.31176 | 20.4713 | 0 | 31.9215 | Solar | 3.306 | Solar | 54295149.604
| Barishal Zone |  |  | 8.1705 | 39.7741 | 0.70435 | 0 | 0 | 0.001269 | 0 | 0 | 48.6502 | Import | 49.7108 | Import | 313144931.63
| Rajshahi Zone |  |  | 10.4667 | 0 | 3.1521 | 0 | 0 | 1.1872 | 25.5454 | 0 | 40.3514 | Wind | 0.27216 | Wind | 4003473.6
| Rangpur Zone |  |  | 0 | 5.1034 | 3.5486 | 0.56637 | 0 | 1.122 | 0 | 0 | 10.3404
| Total |  |  | 120.9112 | 110.1411 | 51.5054 | 1.2389 | 5.332 | 3.306 | 49.7108 | 0.27216 | 342.4175
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 416355009.7947 |  | Hydro | 533200.2
|  |  |  | Coal | 765617145.0487 |  | Solar | 54295149.604
|  |  |  | HFO | 1049499458.928 |  | Import | 313144931.63
|  |  |  | HSD | 31074409.6 |  | Wind | 4003473.6
[5 empty] | Total: | 263,45,22,778 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.4713 | Peak Hr Flow | 889.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 22924836.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.5454 | Peak Hr Flow | 1398.88 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1350 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.6941 | Peak Hr Flow | 162.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1586 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.7108 | Peak Hr Flow | 2449.88 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 142 |  | 5967
|  |  |  | Chattogram |  | 7 |  | 1460
|  |  |  | Cumilla |  | 71 |  | 1452
|  |  |  | Mymensingh |  | 265 |  | 1466
|  |  |  | Sylhet |  | 28 |  | 666
|  |  |  | Khulna |  | 114 |  | 1929
|  |  |  | Barishal |  | 10 |  | 441
|  |  |  | Rajshahi |  | 22 |  | 1636
|  |  |  | Rangpur |  | 40 |  | 1106
|  |  |  | Total |  | 699 |  | 16123
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 54
|  |  |  | Total Unavailable Capacity |  |  |  | 354
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:41 | Faridpur 132/33kV S/S Transformer-1 LT is restored.
|  | 08:41 | Faridpur 132/33kV S/S Transformer-1 HT is restored.
| 09:16 | 19:56 | Chandina-Cumilla(N) 132 kV Ckt-2 Scheduled S/D from Chandina 132/33kV end Due to due to
the maintenance work.
|  | 09:25 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 is restored.
| 11:36 | 22:26 | Baghabari-Bangura 132 kV Ckt-2 Scheduled S/D from Bhangura 132/33kV end Due to SAS
Integration
| 12:00 |  | Day Peak Generation: 14375 MW.
| 12:43 | 14:58 | Keranigonj 230/132/33kV S/S ATR-2 LT Scheduled S/D Due to SF6 Gas Compartment loss.
| 12:44 | 14:58 | Keranigonj 230/132/33kV S/S ATR-2 HT Scheduled S/D Due to SF6 Gas Compartment loss.
| 13:14 | 14:25 | Patiya 132/33kV S/S TRAFO-02 LT Forced S/D Due to 33kv DS2 work
| 13:14 | 14:25 | Patiya 132/33kV S/S TRAFO-02 HT Forced S/D Due to 33 KV DS2 work
| 15:53 | 15:58 | Kasba 132/33kV S/S TR-2 HT Tripped showing Main 2 relays Due to 33 kv braker R phase pole | [7 empty] | 12.0MW load
|  |  | blast | [7 empty] | interrup.
| 15:59 |  | Kasba 132/33kV S/S TR-2 HT Scheduled S/D Due to 33 kv braker R phase pole Blast
| 16:13 | 17:08 | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to Red
Hot Maintenance
|  | 18:56 | Fenchuganj-Sreemangal 132kV Ckt-1 is restored.
|  | 18:56 | Fenchuganj-Sreemangal 132kV Ckt-1 is restored.
| 21:11 | 21:43 | Bhangura 132/33kV S/S Tr-1(403T) LT Forced S/D Due to Red Hot
| 21:13 | 21:41 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D Due to Red hot
| 21:41 | 23:34 | Bhulta 400/230/132kV S/S 132kV Araihazar-01 Scheduled S/D Due to Due to red Hot
maintenance work
| 21:45 | 23:47 | Araihazar 132/33kV S/S Bhulta-Araihazar CKT-01 Forced S/D Due to Bhulta End Red hot | [7 empty] | 30.0MW load
interrup.
|  | 22:55 | Muradnagar 132/33kV S/S 132KV Transformar-02 HT is restored.
|  | 22:56 | Muradnagar 132/33kV S/S 132KV Transformar-02 LT is restored.
|  | 00:30 | Kulaura 132/33kV S/S TR-2 HT is restored.
| 05:27 | 07:49 | Mymensingh RPCL-Tangail 132kV Ckt-1 Project Work S/D from Ghatail 132/33kV end Due to | [7 empty] | 20.0MW load
|  |  | Installation of Dummy OPGW by EEGBPS Project | [7 empty] | interrup. Ghatail
132/33kV end
| 05:27 | 07:49 | Mymensingh RPCL-Tangail 132kV Ckt-2 Project Work S/D from Ghatail 132/33kV end Due to | [7 empty] | 20.0MW load
|  |  | Installation of Dummy OPGW by EEGBPS Project | [7 empty] | interrup. Ghatail
132/33kV end
| 06:05 |  | Mymensingh RPCL-Tangail 132kV Ckt-2 Project Work S/D from Ghatail 132/33kV end Due to
Installation of Dummy OPGW by EEGBPS Project
| 06:08 |  | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by NLDC
| 06:08 |  | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by NLDC
| 06:08 |  | Tangail 132/33kV S/S RPCL-2 Project Work S/D Due to OPGW Maintenance work.
| 06:38 |  | Ashuganj-Sreepur 230 kV Ckt-2 Project Work S/D from Sirajgonj 230 end Due to For project
work.
| 06:38 |  | Sirajganj-Sreepur 230 kV Ckt-1 Project Work S/D from Sirajgonj 230 end Due to For project
work.
| 06:54 |  | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-2 Scheduled S/D Due to G to G Project
Works
| 06:54 |  | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 Scheduled S/D Due to G to G Project
works
| 07:14 |  | Fenchuganj-Sreemangal 132kV Ckt-1 Project Work S/D from Sreemongol 132/33kV end Due to
G2G Project work and from Fenchuganj 230/132/33kV end Due to Project work
| 07:41 |  | Barapukuria(N)-Bogura West Old P/S 230kV Ckt-2 Project Work S/D from Bogura 400/230kV end
Due to Works Of LILO at Polasbari and from Barapukuria(N) 230kV end Due to LILO work at
Polashbari Substation
| 07:45 |  | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT Scheduled S/D Due to Change of
Main Protection Relay (RED 670)
| 07:45 |  | Maniknagar-Siddhirganj 230kV Ckt-2 Scheduled S/D from Maniknagar 230/132kV end Due to
Change of Main Protection Relay (RED 670)
| 07:50 |  | Ghatail 132/33kV S/S T-2 LT Tripped showing SPS relays Due to SPS Trip | [7 empty] | 40.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 03-09-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 334 | 8823600 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 71298 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 302 | 7320276 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 563400 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 80 | 2294880 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 668790 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 617007 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 4.5 | 102600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 522360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 660480 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 81 | 1066113 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 32 | 1753632 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1429440 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 74 | 458880 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1971360 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 147812 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 8704090.91 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 229 | 5941600 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3189600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2147.92 | 46307218.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 277473.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 35235 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 43 | 981600 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 220 | 5332002 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 215 | 5391959 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 838872 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 46 | 601152 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 386704 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 726720 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 89760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 48 | 834240 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 9961 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 373855 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 35 | 341822 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 64 | 1373309 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 735360 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 109 | 2314636 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 53 | 1298036 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 29241815 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 27 | 272160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1130 | 27010909.09 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3436 | 78467580.69
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 218 | 5090000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 300 | 7525500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 280 | 7330000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 280 | 6353000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1136796 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 2196291 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 639968 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2121691 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 189 | 4016160 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 162 | 3694080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 814963 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 459500 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 105 | 2518260 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 74 | 829080 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 114 | 1124160 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 66282 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 2114.2 | 45915731
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 120236 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 172 | 2601600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1566000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 248250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 290640 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 219600 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 279 | 5058126
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 44089 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 960000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 685200 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 140 | 3227000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 614112 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 60 | 1715520 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 126 | 2732110 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 374208 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 248 | 6230000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 393 | 9287000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9536100 | -
Sylhet Area Total |  |  |  |  | 2325 | 1466 | 35405339
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 889 | 20471273 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 111360 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 40 | 499456 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 128640 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 715536 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 311760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 150 | 672520 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 370 | 9010909 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1551 | 31921454
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1000 | 19098181 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 262752 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 118 | 2820000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 570 | 13890909.09 | machine problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5350500 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 441600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6785000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1269 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2264 | 48650211.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 327120 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 388703 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 482068 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 134 | 3314091 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 270 | 7152582 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 17 | 181300 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 205579 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 101 | 687056 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 820416 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 55 | 386976 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 26640 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1398.88 | 25545421 | Coal shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 313488 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 519980 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2083.88 | 40351420
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 566370 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1204363 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 155 | 3899000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 814867 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 33437.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2733743 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 188601 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 900000 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 582 | 10340381.4
Eastern Grid Total |  |  |  |  | 17427.666 | 9443.12 | 211153995.6
Western Grid Total |  |  |  |  | 11731.125 | 6480.88 | 131263466.49
National Grid Total |  |  |  |  | 29158.791 | 15924 | 342417462.09
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 03-09-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10498.31 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4925.8 | MW
i) Dhaka area |  |  | 5825.31 |  | MW | i) Khulna area |  |  |  | 1815 | MW
ii) Chattogram area |  |  | 1453 |  | MW | ii) Barishal area |  |  |  | 431.2 | MW
iii) Cumilla area |  |  | 1381 |  | MW | iii) Rajshahi area |  |  |  | 1613.6 | MW
iv) Mymensingh area |  |  | 1201 |  | MW | iv) Rangpur area |  |  |  | 1066 | MW
v) Sylhet area |  |  | 638 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15424.11 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Halishahar | 141 | 15:00 | 133 | Narinda | 75 | 13:00 | 199 | Ullon | 42 | 00:00
2 | AKSML | 167 | 04:00 | 68 | HaripurSBU | 134 | 19:00 | 134 | Narshingdi | 193 | 23:00 | 200 | Uttara | 100 | 13:00
3 | Aftabnagar | 44 | 13:00 | 69 | Hasnabad | 93 | 23:00 | 135 | Natore | 156 | 20:00 | 201 | UttaraNew | 53 | 00:00
4 | Agargaon | 125 | 14:00 | 70 | Hathazari | 83 | 18:00 | 136 | Nawabganj | 58.8 | 21:00 | 202 | Zigatola | 100 | 14:00
5 | Agrabad | 78 | 11:00 | 71 | Hatirjheel | 86 | 13:00 | 137 | Netrakona | 144 | 07:00
6 | Amnura | 29 | 22:00 | 72 | Ishurdi | 86 | 20:00 | 138 | New | 90 | 13:00
7 | Araihazar | 43 | 18:00 | 73 | Jaldhaka | 90 | 19:30 | 139 | Niamatpur | 68 | 22:00
8 | Ashuganj | 85 | 00:00 | 74 | Jamalpur | 139 | 19:30 | 140 | Noapara | 44 | 21:00
9 | BSRM | 199 | 22:00 | 75 | Jashore | 148 | 19:00 | 141 | PHP | 12 | 21:00
10 | Bagerhat | 84 | 20:00 | 76 | Jhenaidah | 91 | 21:00 | 142 | Pabna | 101 | 20:00
11 | Bajitpur | 93 | 19:00 | 77 | Joydebpur | 174 | 11:00 | 143 | Palashbari | 126 | 21:00
12 | Bakerganj | 12.6 | 02:00 | 78 | Joypurhat | 59 | 21:00 | 144 | Panchagarh | 68 | 19:00
13 | Bakulia | 91 | 12:00 | 79 | Juldah | 15 | 00:00 | 145 | Patiya | 22.6 | 02:00
14 | Banani | 52 | 14:00 | 80 | KSRM | 16 | 16:00 | 146 | Patnitala | 35 | 22:00
15 | Bangabhaban | 16 | 10:00 | 81 | Kabirpur | 274 | 11:00 | 147 | Patuakhali | 60 | 22:00
16 | Barapukuria | 73 | 20:00 | 82 | Kachua | 94 | 20:00 | 148 | Payra | 30 | 21:00
17 | Barguna | 20 | 20:00 | 83 | Kaliganj | 38 | 19:30 | 149 | Postogola | 64 | 14:00
18 | Barishal | 96 | 11:00 | 84 | Kallyanpur | 123 | 00:00 | 150 | Pubail | 47 | 18:30
19 | Barishal-230 | 98 | 19:30 | 85 | Kalurghat | 42 | 12:00 | 151 | Purbachal | 22 | 12:00
20 | Baroaulia | 59 | 05:00 | 86 | Kamrangirchar | 83 | 13:00 | 152 | Purbasadipur | 130 | 23:00
21 | Baroirhat | 53 | 04:00 | 87 | Kaptai | N/A | N/A | 153 | Rahanpur | 39 | 20:00
22 | Bashundhara | 239 | 13:00 | 88 | Kasba | 33 | 00:00 | 154 | Rahim | 58 | 13:00
23 | BashundharaCement | 6 | 16:00 | 89 | Kazla | 125 | 14:00 | 155 | Rajbari | 91 | 19:00
24 | Beanibazar | 80 | 20:00 | 90 | Keranigonj | 88 | 18:30 | 156 | Rajendrapur | 122 | 18:00
25 | Benapole | 66 | 22:00 | 91 | Khagrachori | 32 | 00:00 | 157 | Rajshahi | 110 | 22:00
26 | Bhaluka | 181 | 18:30 | 92 | Khulna | 52 | 08:00 | 158 | Rajshahi-230 | 98 | 13:00
27 | Bhandaria | 57 | 00:00 | 93 | Khulshi | 171 | 21:00 | 159 | Ramganj | 110 | 21:00
28 | Bhangura | 42 | 20:00 | 94 | Kishoreganj | 124 | 01:00 | 160 | Rampur | 36 | 00:00
29 | Bheramara(GK) | 69 | 21:00 | 95 | Kodda | 311 | 19:00 | 161 | Rangamati | 14 | 07:00
30 | Bhulta | 220 | 03:00 | 96 | Kulaura | 55 | 20:00 | 162 | Rangpur | 132 | 20:00
31 | Bog-Sherpur | 76 | 20:00 | 97 | Kurigram | 74 | 18:30 | 163 | Ruppur | 4.6 | 16:00
32 | Bogura | 203 | 19:00 | 98 | Kushtia | 154 | 21:00 | 164 | SSM | 10 | 23:00
33 | Borhanuddin | 62 | 00:00 | 99 | Laksam | 30 | 00:00 | 165 | Saidpur | 103 | 19:30
34 | Brahmanbaria | 142 | 21:00 | 100 | Lakshmipur | 49 | 00:00 | 166 | Santhia | 36 | 18:30
35 | Cantonment | 138 | 13:00 | 101 | Lalbag | 82 | 13:00 | 167 | Satkhira | 129 | 20:00
36 | Chandina | 16 | 00:00 | 102 | Lalmonirhat | 72 | 19:30 | 168 | Satmasjid | 109 | 13:00
37 | Chandpur | 80 | 21:00 | 103 | MI_Cement | 6.4 | 16:00 | 169 | Savar | 218 | 11:00
38 | Chandraghona | 31 | 19:30 | 104 | Madanganj | 54 | 12:00 | 170 | SevenRings | 21.11 | 17:00
39 | Chapai | 69 | 22:00 | 105 | Madaripur | 105 | 21:00 | 171 | ShahCement | 21 | 00:00
40 | Charfasson | 30 | 19:30 | 106 | Madartek | 87.3 | 00:00 | 172 | Shahjadpur | 82 | 21:00
41 | Charsaidpur | 43 | 11:00 | 107 | Madunaghat | 47 | 17:00 | 173 | Shahjibazar | 137 | 21:00
42 | Chauddagram | 68 | 21:00 | 108 | Magura | 66 | 21:00 | 174 | Shahmirpur | 57 | 18:00
43 | Chhatak | 39 | 20:00 | 109 | Mahasthangarh | 74 | 21:00 | 175 | Shariatpur | 101 | 22:00
44 | Chowmuhani | 140 | 00:00 | 110 | Maijdee | 34 | 21:00 | 176 | Sherpur | 164 | 21:00
45 | Chuadanga | 116 | 21:00 | 111 | Manikganj | 143 | 19:00 | 177 | Shikalbaha | 27.5 | 23:00
46 | Coxsbazar | 141 | 20:00 | 112 | Maniknagar | 78 | 13:00 | 178 | Shitalakhya | 84.5 | 13:00
47 | Cumilla(N) | 125 | 21:00 | 113 | Matarbari | 50 | 00:00 | 179 | Sholosohor | 49 | 12:00
48 | Cumilla(S) | 172 | 01:00 | 114 | Matuail | 80 | 15:00 | 180 | Shomvuganj | 50 | 17:00
49 | Daganbhuiyan | 35 | 00:00 | 115 | Metrorail_Motijheel | 32 | 20:00 | 181 | Shyampur | 174 | 12:00
50 | Daudkandi | 127 | 20:00 | 116 | Metrorail_Uttara | 0 | 00:00 | 182 | Siddhirganj | 129 | 14:00
51 | DhakaUniversity | 92 | 13:00 | 117 | Millgate | 100 | 15:00 | 183 | Sirajganj | 120 | 19:00
52 | Dhamrai | 94 | 23:00 | 118 | Mirpur | 155 | 13:00 | 184 | Sitakunda | 12 | 10:00
53 | Dhanmondi | 122 | 13:00 | 119 | Mirsorai | 46 | 10:00 | 185 | Sonargaon | 157 | 21:00
54 | Dohazari | 103 | 19:30 | 120 | Mirzapur | 45 | 18:30 | 186 | Sreemongol | 90 | 19:00
55 | Faridpur | 192 | 21:00 | 121 | Mithapukur | 84 | 19:30 | 187 | Sreepur | 142 | 20:00
56 | Fatullah | 113 | 10:00 | 122 | Modern | N/A | N/A | 188 | Srinagar | 47.7 | 22:00
57 | Fenchuganj | 42 | 00:00 | 123 | Mogbazar | 66 | 14:00 | 189 | Sunamganj | 54 | 19:00
58 | Feni | 97 | 00:00 | 124 | Mongla | 37 | 15:00 | 190 | Sylhet | 119 | 18:30
59 | GPH | 1 | 00:00 | 125 | Motijheel | 51 | 14:00 | 191 | Sylhet_(South) | 76 | 22:00
60 | Ghatail | 89 | 21:00 | 126 | Muktagacha | 40 | 22:00 | 192 | TK | 0 | 00:00
61 | Ghorashal | 0 | 00:00 | 127 | Munshiganj | 108 | 23:00 | 193 | Tangail | 178 | 20:00
62 | Ghorashal-230 | 112 | 18:00 | 128 | Muradnagar | 56 | 21:00 | 194 | Taraganj | 35 | 18:30
63 | Goalpara | 39 | 20:00 | 129 | Mymensingh | 152 | 19:30 | 195 | Tasnim | 43 | 17:00
64 | Gollamari | 96 | 19:30 | 130 | Nabinagar | 110 | 18:30 | 196 | Thakurgaon | 107 | 19:30
65 | Gopalganj | 116 | 20:00 | 131 | Naogaon | 122 | 22:00 | 197 | Tongi | 148 | 11:00
66 | Gulshan | 126 | 13:00 | 132 | Narail | 60 | 19:30 | 198 | Ullahpara | 41 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 03-09-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14648.52 | 1844 |  | 16575.5
1:00 | 13983.27 | 2273 |  | 16358.27
2:00 | 13483.9 | 2415 |  | 16007.9
3:00 | 13409.65 | 2344 |  | 15858.65
4:00 | 13401.56 | 2240 |  | 15742.56
5:00 | 13264.77 | 2157 |  | 15518.77
6:00 | 13073.59 | 1765 |  | 14917.59
7:00 | 13382.67 | 1459 |  | 14907.67
8:00 | 13308.63 | 1476 |  | 14850.63
9:00 | 13283.31 | 1309 |  | 14651.31
10:00 | 13602.12 | 1536 |  | 15207.12
11:00 | 14059.69 | 1172 |  | 15284.69
12:00 | 14374.53 | 1203 |  | 15631.53
13:00 | 14297.83 | 1457 |  | 15820.83
14:00 | 14265.28 | 1393 |  | 15721.28
15:00 | 13878.58 | 2098 |  | 16070.58
16:00 | 13666.72 | 1963 |  | 15717.72
17:00 | 13933.68 | 1450 |  | 15448.68
18:00 | 14440.33 | 355 |  | 14811.33
19:00 | 15414.51 | 1367 |  | 16843.51
19:30 | 15719.73 | 687 |  | 16437.73
20:00 | 15924 | 699 |  | 16654
21:00 | 15741.5 | 257 |  | 16010.5
22:00 | 15439.28 | 812 |  | 16288.28
23:00 | 15295.81 | 991 |  | 16331.81
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 03-09-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 115 | 41 | 356 | 190 | 866 | 668 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 116 | 39 | 302 | 180 | 738 | 680
2:00 | 80 | 46 | 204 | 178 | 596 | 656 |  | Import | 0
3:00 | 80 | 47 | 160 | 162 | 586 | 640
4:00 | 94 | 40 | 202 | 158 | 648 | 616 | Ishurdi-Ghorashal Ckt-2 | Export | 2714836.36
5:00 | 78 | 44 | 170 | 158 | 576 | 616
6:00 | 87 | 48 | 188 | 168 | 612 | 624 |  | Import | 0
7:00 | 75 | 45 | 172 | 186 | 536 | 636
8:00 | 101 | 44 | 230 | 178 | 658 | 616 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 115 | 51 | 260 | 176 | 752 | 676
10:00 | 127 | 49 | 300 | 172 | 828 | 660 |  | Import | 0
11:00 | 139 | 56 | 326 | 184 | 994 | 702
12:00 | 140 | 51 | 304 | 184 | 1018 | 690 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 141 | 48 | 332 | 168 | 1082 | 742
14:00 | 136 | 60 | 276 | 166 | 984 | 726 |  | Import | 0
15:00 | 123 | 51 | 272 | 174 | 1008 | 710
16:00 | 135 | 63 | 270 | 170 | 960 | 754 | Gopalganj-Aminbazar Ckt-1 | Export | 10090000
17:00 | 148 | 59 | 340 | 166 | 1098 | 748
18:00 | 142 | 53 | 356 | 202 | 1034 | 744 |  | Import | 0
18:30 | 139 | 50 | 346 | 204 | 1040 | 738
19:00 | 138 | 55 | 334 | 196 | 1022 | 738 | Gopalganj-Aminbazar Ckt-2 | Export | 10120000
19:30 | 132 | 52 | 314 | 190 | 988 | 702
20:00 | 114 | 48 | 292 | 186 | 944 | 670 |  | Import | 0
21:00 | 100 | 39 | 236 | 176 | 816 | 630
22:00 | 98 | 52 | 270 | 206 | 872 | 634 |  | Total Export | 22924836.36
23:00 | 101 | 52 | 286 | 200 | 872 | 642 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 03-09-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8875.2 | 5773.32 | 14648.52 | DAILY GENERATION CURVE
00:30 | 8723.95 | 5591.945 | 14315.895
01:00 | 8572.7 | 5410.57 | 13983.27 | 03-09-2026
01:30 | 8554.7 | 5178.885 | 13733.585
02:00 | 8536.7 | 4947.2 | 13483.9
02:30 | 8519.41 | 4927.365 | 13446.775
03:00 | 8502.12 | 4907.53 | 13409.65
03:30 | 8450.77 | 4954.835 | 13405.605
04:00 | 8399.42 | 5002.14 | 13401.56
04:30 | 8399.42 | 4933.745 | 13333.165
05:00 | 8399.42 | 4865.35 | 13264.77
05:30 | 8321.065 | 4848.115 | 13169.18
06:00 | 8242.71 | 4830.88 | 13073.59
06:30 | 8369.61 | 4858.52 | 13228.13
07:00 | 8496.51 | 4886.16 | 13382.67
07:30 | 8439.13 | 4906.52 | 13345.65
08:00 | 8381.75 | 4926.88 | 13308.63
08:30 | 8375.495 | 4920.475 | 13295.97
09:00 | 8369.24 | 4914.07 | 13283.31
09:30 | 8440.88 | 5001.835 | 13442.715
10:00 | 8512.52 | 5089.6 | 13602.12
10:30 | 8580.915 | 5249.99 | 13830.905
11:00 | 8649.31 | 5410.38 | 14059.69
11:30 | 8701.64 | 5515.47 | 14217.11
12:00 | 8753.97 | 5620.56 | 14374.53
12:30 | 8711.905 | 5624.275 | 14336.18
13:00 | 8669.84 | 5627.99 | 14297.83
13:30 | 8751.63 | 5529.925 | 14281.555
14:00 | 8833.42 | 5431.86 | 14265.28
14:30 | 8732.71 | 5339.22 | 14071.93
15:00 | 8632 | 5246.58 | 13878.58
15:30 | 8579.05 | 5193.6 | 13772.65
16:00 | 8526.1 | 5140.62 | 13666.72
16:30 | 8524.985 | 5275.215 | 13800.2
17:00 | 8523.87 | 5409.81 | 13933.68
17:30 | 8710.665 | 5476.34 | 14187.005
18:00 | 8897.46 | 5542.87 | 14440.33
18:30 | 9068.19 | 5859.23 | 14927.42
19:00 | 9238.92 | 6175.59 | 15414.51
19:30 | 9360.92 | 6358.81 | 15719.73
20:00 | 9443.12 | 6480.88 | 15924
20:30 | 9459.62 | 6373.13 | 15832.75 |  | Executive Engineer
21:00 | 9476.12 | 6265.38 | 15741.5 |  | Network Operation Division
21:30 | 9405.37 | 6185.02 | 15590.39
22:00 | 9334.62 | 6104.66 | 15439.28
22:30 | 9265.12 | 6102.425 | 15367.545
23:00 | 9195.62 | 6100.19 | 15295.81

## En-Curve
QF-LDC-12
Date | 03-09-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3693 | 1199.5 | 749 | 0 | 170 | 1301.32 | 222 | 4402 | 0 | 634 | 2026.7 | 241 | 0 | 10 | 1844 | DAILY ENERGY CURVE
00:30 | 3730 | 1246 | 808.5 | 0 | 171 | 1207.445 | 222 | 4352.5 | 0 | 596.5 | 1725.45 | 245.5 | 0 | 11 | 2058.5 | 03-09-2026
01:00 | 3767 | 1292.5 | 868 | 0 | 172 | 1113.57 | 222 | 4303 | 0 | 559 | 1424.2 | 250 | 0 | 12 | 2273
01:30 | 3776.5 | 1316 | 820.5 | 0 | 167 | 1038.885 | 222 | 4357.5 | 0 | 492 | 1382.7 | 150 | 0 | 10.5 | 2344 | Energy Generated | 342.4175 |  | MKWHr
02:00 | 3786 | 1339.5 | 773 | 0 | 162 | 964.2 | 222 | 4412 | 0 | 425 | 1341.2 | 50 | 0 | 9 | 2415 | Energy not Served | 36.035 |  | MKWHr
02:30 | 3777 | 1328 | 773 | 0 | 159 | 957.865 | 222 | 4410 | 0 | 453.71 | 1335.7 | 25 | 0 | 5.5 | 2379.5 | Total Energy Requirement | 378.4525 |  | MKWHr
03:00 | 3768 | 1316.5 | 773 | 0 | 156 | 951.53 | 222 | 4408 | 0 | 482.42 | 1330.2 | 0 | 0 | 2 | 2344
03:30 | 3760.5 | 1273.15 | 820 | 0 | 154 | 951.835 | 222 | 4408 | 0 | 482.92 | 1331.7 | 0 | 0 | 1.5 | 2292
04:00 | 3753 | 1229.8 | 867 | 0 | 152 | 952.14 | 222 | 4408 | 0 | 483.42 | 1333.2 | 0 | 0 | 1 | 2240
04:30 | 3751.5 | 1267.8 | 829.5 | 0 | 152 | 951.245 | 221 | 4408 | 0 | 464.42 | 1281.7 | 0 | 0 | 6 | 2198.5
05:00 | 3750 | 1305.8 | 792 | 0 | 152 | 950.35 | 220 | 4408 | 0 | 445.42 | 1230.2 | 0 | 0 | 11 | 2157
05:30 | 3743.5 | 1249.3 | 792 | 0 | 148 | 955.51 | 219 | 4409.5 | 3.25 | 435.92 | 1207.7 | 0 | 0 | 5.5 | 1961
06:00 | 3737 | 1192.8 | 792 | 0 | 144 | 960.67 | 218 | 4411 | 6.5 | 426.42 | 1185.2 | 0 | 0 | 0 | 1765
06:30 | 3771.5 | 1265.3 | 792 | 0 | 143 | 945.61 | 218.5 | 4411 | 41.6 | 424.42 | 1208.7 | 0 | 0 | 6.5 | 1612
07:00 | 3806 | 1337.8 | 792 | 0 | 142 | 930.55 | 219 | 4411 | 76.7 | 422.42 | 1232.2 | 0 | 0 | 13 | 1459
07:30 | 3786 | 1271.15 | 829.5 | 0 | 146 | 919.63 | 218.5 | 4408 | 106.25 | 403.92 | 1242.7 | 0 | 0 | 14 | 1467.5
08:00 | 3766 | 1204.5 | 867 | 0 | 150 | 908.71 | 218 | 4405 | 135.8 | 385.42 | 1253.2 | 0 | 0 | 15 | 1476
08:30 | 3739 | 1167 | 866.5 | 0 | 151 | 905.685 | 218.5 | 4405 | 142.665 | 401.42 | 1289.7 | 0 | 0 | 9.5 | 1392.5
09:00 | 3712 | 1129.5 | 866 | 0 | 152 | 902.66 | 219 | 4405 | 149.53 | 417.42 | 1326.2 | 0 | 0 | 4 | 1309
09:30 | 3696 | 1157 | 866.5 | 0 | 154 | 903.85 | 219 | 4406.5 | 213.845 | 456.42 | 1366.1 | 0 | 0 | 3.5 | 1422.5
10:00 | 3680 | 1184.5 | 867 | 0 | 156 | 905.04 | 219 | 4408 | 278.16 | 495.42 | 1406 | 0 | 0 | 3 | 1536
10:30 | 3715 | 1217 | 867 | 0 | 155 | 910.59 | 219.5 | 4473.5 | 351.395 | 504.42 | 1412 | 0 | 0 | 5.5 | 1354
11:00 | 3750 | 1249.5 | 867 | 0 | 154 | 916.14 | 220 | 4539 | 424.63 | 513.42 | 1418 | 0 | 0 | 8 | 1172
11:30 | 3754.5 | 1278 | 867 | 0 | 158 | 913.88 | 220 | 4602 | 496.02 | 489.71 | 1432.5 | 0 | 0 | 5.5 | 1187.5
12:00 | 3759 | 1306.5 | 867 | 0 | 162 | 911.62 | 220 | 4665 | 567.41 | 466 | 1447 | 0 | 0 | 3 | 1203
12:30 | 3729.5 | 1309 | 871 | 0 | 156 | 915.425 | 220.5 | 4653 | 617.545 | 407.21 | 1454 | 0 | 0 | 3 | 1330
13:00 | 3700 | 1311.5 | 875 | 0 | 150 | 919.23 | 221 | 4641 | 667.68 | 348.42 | 1461 | 0 | 0 | 3 | 1457
13:30 | 3722.5 | 1303 | 879 | 0 | 154 | 932.14 | 221.5 | 4674 | 567.995 | 348.42 | 1473.5 | 0 | 0 | 5.5 | 1425
14:00 | 3745 | 1294.5 | 883 | 0 | 158 | 945.05 | 222 | 4707 | 468.31 | 348.42 | 1486 | 0 | 0 | 8 | 1393
14:30 | 3708.5 | 1253 | 886 | 0 | 155 | 936.29 | 222 | 4692 | 363.22 | 348.92 | 1490 | 0 | 0 | 17 | 1745.5
15:00 | 3672 | 1211.5 | 889 | 0 | 152 | 927.53 | 222 | 4677 | 258.13 | 349.42 | 1494 | 0 | 0 | 26 | 2098
15:30 | 3658.5 | 1196.5 | 889.5 | 0 | 146 | 925.795 | 221.5 | 4638 | 232.145 | 354.71 | 1487 | 0 | 0 | 23 | 2030.5
16:00 | 3645 | 1181.5 | 890 | 0 | 140 | 924.06 | 221 | 4599 | 206.16 | 360 | 1480 | 0 | 0 | 20 | 1963
16:30 | 3603 | 1158.5 | 889.5 | 0 | 144 | 1007.71 | 220.5 | 4598.5 | 172.28 | 377.21 | 1614 | 0 | 0 | 15 | 1706.5
17:00 | 3561 | 1135.5 | 889 | 0 | 148 | 1091.36 | 220 | 4598 | 138.4 | 394.42 | 1748 | 0 | 0 | 10 | 1450
17:30 | 3562.5 | 1184 | 889 | 0 | 143 | 1198.78 | 219.5 | 4597.5 | 75.805 | 487.42 | 1817.5 | 0 | 0 | 12 | 902.5
18:00 | 3564 | 1232.5 | 889 | 0 | 138 | 1306.2 | 219 | 4597 | 13.21 | 580.42 | 1887 | 0 | 0 | 14 | 355
18:30 | 3631 | 1216 | 889.5 | 0 | 151 | 1308.395 | 219 | 4648.5 | 6.605 | 676.92 | 2034.5 | 125 | 0 | 21 | 861
19:00 | 3698 | 1199.5 | 890 | 0 | 164 | 1310.59 | 219 | 4700 | 0 | 773.42 | 2182 | 250 | 0 | 28 | 1367
19:30 | 3694 | 1172.5 | 888 | 0 | 166 | 1317.81 | 219 | 4776 | 0 | 781.42 | 2362 | 315 | 0 | 28 | 687
20:00 | 3691 | 1216.5 | 889 | 0 | 162 | 1398.88 | 220 | 4804 | 0 | 777.42 | 2423.2 | 315 | 0 | 27 | 699
20:30 | 3708 | 1239 | 889 | 0 | 156 | 1401.63 | 220 | 4804.5 | 0 | 783.42 | 2418.2 | 192.5 | 0 | 20.5 | 478
21:00 | 3725 | 1261.5 | 889 | 0 | 150 | 1404.38 | 220 | 4805 | 0 | 789.42 | 2413.2 | 70 | 0 | 14 | 257
21:30 | 3736.5 | 1230 | 838 | 0 | 154 | 1413.02 | 220.5 | 4805 | 0 | 782.42 | 2356.95 | 35 | 0 | 19 | 534.5
22:00 | 3748 | 1198.5 | 787 | 0 | 158 | 1421.66 | 221 | 4805 | 0 | 775.42 | 2300.7 | 0 | 0 | 24 | 812
22:30 | 3716 | 1200.5 | 787 | 0 | 159 | 1412.925 | 221.5 | 4806.5 | 0 | 786.42 | 2261.7 | 0 | 0 | 16 | 901.5
23:00 | 3684 | 1202.5 | 787 | 0 | 160 | 1404.19 | 222 | 4808 | 0 | 797.42 | 2222.7 | 0 | 0 | 8 | 991
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 03-09-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 374 | 04:00 | 360 | 14:00 | Madunaghat | 398 | 06:00 | 393 | 13:00
Amtali | 414 | 10:00 | 407 | 19:30 | Meghnaghat | 378 | 04:00 | 367 | 14:00
Ashuganj | 365 | 04:00 | 348 | 19:30 | Mirsorai | 395 | 06:00 | 388 | 14:00
Bhulta | 392 | 04:00 | 374 | 14:00 | Payra | 414 | 01:00 | 410 | 14:00
Bibiana | 381 | 08:00 | 372 | 19:00 | Rahanpur | 411 | 10:00 | 397 | 21:00
BIPTC | 405 | 02:00 | 396 | 19:00 | Rampal | 395 | 06:00 | 381 | 21:00
Bogura | 396 | 02:00 | 381 | 21:00
Gopalganj | 392 | 10:00 | 380 | 20:00
Kaliakoir | 365 | 04:00 | 348 | 19:30
Korerhat | 393 | 04:00 | 387 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 04:00 | 216 | 14:00 | Hasnabad | 225 | 07:00 | 213 | 13:00
AKSML | 233 | 01:00 | 221 | 13:00 | Hathazari | 234 | 03:00 | 231 | 11:00
Aminbazar | 228 | 04:00 | 216 | 14:00 | Ishurdi | 236 | 03:00 | 221 | 21:00
Ashuganj | 226 | 02:00 | 219 | 18:30 | Jhenaidah | 226 | 03:00 | 209 | 21:00
Ashuganj-400 | 226 | 02:00 | 219 | 18:30 | Kachua | 227 | 04:00 | 223 | 14:00
Baghabari | 233 | 04:00 | 223 | 20:00 | Kaliakoir | 226 | 03:00 | 215 | 14:00
Barapukuria | 227 | 02:00 | 222 | 21:00 | Keranigonj | 226 | 04:00 | 214 | 14:00
Barapukuria-230 | 227 | 02:00 | 222 | 21:00 | Khulna(S) | 226 | 05:00 | 216 | 21:00
Barapukuria(N) | 228 | 17:00 | 223 | 21:00 | Korerhat | 225 | 09:00 | 221 | 12:00
Barishal | 227 | 10:00 | 221 | 20:00 | Madunaghat | 237 | 06:00 | 234 | 12:00
Bheramara | 235 | 06:00 | 220 | 21:00 | Madunaghat-400 | 238 | 03:00 | 235 | 13:00
Bhulta | 224 | 03:00 | 211 | 14:00 | Maniknagar | 222 | 03:00 | 209 | 13:00
Bibiana | 218 | 08:00 | 211 | 21:00 | Meghnaghat | 230 | 05:00 | 219 | 14:00
BIPTC | 236 | 05:00 | 219 | 21:00 | Meghnaghat-400 | 226 | 04:00 | 215 | 14:00
Birulia | 228 | 04:00 | 217 | 18:30 | Mirsorai | 229 | 04:00 | 226 | 12:00
Bogura | 239 | 10:00 | 231 | 21:00 | Naogaon | 225 | 02:00 | 208 | 21:00
Bogura-400 | 238 | 02:00 | 231 | 21:00 | Purbasadipur | 226 | 02:00 | 220 | 20:00
Borhanuddin | 229 | 08:00 | 225 | 21:00 | Rajshahi | 234 | 03:00 | 219 | 21:00
BSRM | 227 | 06:00 | 222 | 14:00 | Rampal | 225 | 04:00 | 215 | 21:00
Charfasson | 230 | 08:00 | 226 | 19:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 227 | 06:00 | 222 | 18:30 | Rampura | 224 | 04:00 | 211 | 14:00
Cumilla(N) | 223 | 04:00 | 215 | 14:00 | Shikalbaha | 237 | 05:00 | 234 | 12:00
Faridpur | 222 | 03:00 | 214 | 20:00 | Shyampur | 225 | 04:00 | 215 | 13:00
Fenchuganj | 217 | 06:00 | 212 | 18:30 | Siddhirganj | 224 | 04:00 | 221 | 00:00
Feni | 225 | 06:00 | 219 | 18:30 | Sirajgonj | 237 | 10:00 | 231 | 18:30
Ghorashal | 230 | 01:00 | 220 | 00:00 | Sreepur | 223 | 03:00 | 215 | 18:30
Ghorashal-230 | 214 | 01:00 | 200 | 19:00 | Tongi | 215 | 04:00 | 201 | 13:00
Gopalganj | 223 | 08:00 | 215 | 21:00
GPH | 232 | 04:00 | 230 | 16:00
Haripur | 223 | 03:00 | 212 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 04:00 | 125 | 15:00 | Madanganj | 131 | 00:00 | 124 | 14:00
Agargaon | 135 | 06:00 | 124 | 14:00 | Madaripur | 132 | 07:00 | 126 | 21:00
Agrabad | 135 | 02:00 | 132 | 11:00 | Madartek | 136 | 04:00 | 125 | 14:00
AKS | 133 | 08:00 | 128 | 05:00 | Madunaghat | 137 | 06:00 | 135 | 00:00
Aminbazar | 131 | 03:00 | 122 | 14:00 | Magura | 136 | 10:00 | 124 | 21:00
Amnura | 136 | 02:00 | 129 | 19:30 | Mahasthangarh | 135 | 02:00 | 129 | 21:00
Araihazar | 125 | 17:00 | 122 | 18:00 | Maijdee | 127 | 04:00 | 125 | 14:00
Ashuganj | 129 | 03:00 | 124 | 18:30 | Manikganj | 129 | 08:00 | 117 | 19:30
Ashuganj-230 | 135 | 10:00 | 130 | 18:30 | Maniknagar | 138 | 04:00 | 128 | 14:00
Bagerhat | 128 | 09:00 | 121 | 21:00 | Matarbari | 127 | 09:00 | 115 | 20:00
Bajitpur | 126 | 04:00 | 120 | 19:00 | Matuail | 132 | 03:00 | 125 | 14:00
Bakerganj | 133 | 16:00 | 129 | 19:30 | Metrorail_Motijheel | 138 | 04:00 | 128 | 14:00
Bakulia | 136 | 04:00 | 132 | 11:00 | Metrorail_Uttara | 132 | 12:00 | 119 | 18:30
Banani | 137 | 03:00 | 126 | 13:00 | Millgate | 132 | 03:00 | 119 | 18:30
Bangabhaban | 138 | 04:00 | 128 | 14:00 | Mirpur | 130 | 04:00 | 120 | 14:00
Barapukuria | 139 | 14:00 | 131 | 13:00 | Mirzapur | 130 | 09:00 | 120 | 20:00
Barguna | 133 | 10:00 | 129 | 19:30 | Mithapukur | 132 | 17:00 | 127 | 21:00
Barishal | 132 | 08:00 | 127 | 21:00 | MI_Cement | 133 | 05:00 | 124 | 14:00
Barishal-230 | 132 | 09:00 | 128 | 19:30 | Modern | 0 | 00:00 | 0 | 00:00
Baroaulia | 135 | 07:00 | 134 | 00:00 | Mogbazar | 140 | 05:00 | 128 | 14:00
Baroirhat | 131 | 07:00 | 129 | 15:00 | Mongla | 128 | 09:00 | 122 | 21:00
Bashundhara | 137 | 03:00 | 119 | 14:00 | Motijheel | 138 | 04:00 | 128 | 14:00
BashundharaCement | 131 | 01:00 | 126 | 12:00 | Muktagacha | 128 | 09:00 | 117 | 21:00
Beanibazar | 122 | 05:00 | 117 | 20:00 | Munshiganj | 132 | 05:00 | 123 | 14:00
Benapole | 131 | 05:00 | 118 | 21:00 | Muradnagar | 127 | 03:00 | 122 | 12:00
Bhaluka | 131 | 09:00 | 123 | 22:00 | Mymensingh | 128 | 09:00 | 111 | 22:00
Bhandaria | 130 | 10:00 | 124 | 21:00 | Nabinagar | 130 | 09:00 | 119 | 18:30
Bhangura | 134 | 02:00 | 126 | 21:00 | Naogaon | 136 | 10:00 | 125 | 21:00
Bheramara | 138 | 10:00 | 128 | 21:00 | Narail | 136 | 10:00 | 124 | 21:00
Bheramara(GK) | 137 | 04:00 | 128 | 21:00 | Narinda | 138 | 04:00 | 128 | 14:00
Bhulta | 128 | 07:00 | 121 | 12:00 | Narshingdi | 128 | 01:00 | 117 | 14:00
Bhulta-400 | 128 | 03:00 | 121 | 12:00 | Natore | 135 | 10:00 | 126 | 21:00
Birulia | 133 | 04:00 | 127 | 18:30 | Nawabganj | 136 | 05:00 | 126 | 14:00
Bog-Sherpur | 136 | 02:00 | 130 | 20:00 | Netrakona | 121 | 16:00 | 109 | 22:00
Bogura | 137 | 00:00 | 132 | 21:00 | New | 132 | 03:00 | 121 | 19:00
Bogura-230 | 138 | 10:00 | 133 | 20:00 | Niamatpur | 135 | 06:00 | 128 | 21:00
Brahmanbaria | 128 | 05:00 | 121 | 18:30 | Noapara | 133 | 10:00 | 126 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 134 | 04:00 | 124 | 14:00 | Pabna | 135 | 03:00 | 126 | 21:00
Chandina | 130 | 04:00 | 125 | 14:00 | Palashbari | 131 | 17:00 | 125 | 21:00
Chandpur | 134 | 00:00 | 131 | 11:00 | Panchagarh | 138 | 09:00 | 132 | 20:00
Chandraghona | 137 | 03:00 | 136 | 00:00 | Patiya | 136 | 06:00 | 132 | 18:00
Chapai | 134 | 10:00 | 129 | 21:00 | Patnitala | 133 | 06:00 | 126 | 21:00
Charsaidpur | 131 | 04:00 | 124 | 14:00 | Patuakhali | 133 | 10:00 | 129 | 18:30
Chauddagram | 130 | 05:00 | 126 | 14:00 | Payra | 135 | 01:00 | 133 | 19:30
Chhatak | 120 | 04:00 | 115 | 19:30 | PHP | 131 | 04:00 | 129 | 12:00
Chowmuhani | 128 | 07:00 | 125 | 02:00 | Postogola | 134 | 04:00 | 126 | 14:00
Chuadanga | 135 | 04:00 | 120 | 21:00 | Pubail | 127 | 01:00 | 119 | 14:00
Coxsbazar | 127 | 08:00 | 120 | 00:00 | Purbachal | 137 | 03:00 | 126 | 13:00
Cumilla(N) | 130 | 04:00 | 125 | 12:00 | Purbasadipur | 137 | 02:00 | 132 | 23:00
Cumilla(S) | 131 | 04:00 | 124 | 11:00 | Rahanpur | 139 | 03:00 | 132 | 20:00
Daganbhuiyan | 130 | 04:00 | 127 | 13:00 | Rahanpur-400 | 138 | 10:00 | 132 | 21:00
Daudkandi | 126 | 03:00 | 120 | 18:30 | Rahim | 132 | 04:00 | 125 | 14:00
DhakaUniversity | 137 | 05:00 | 126 | 14:00 | Rajbari | 127 | 04:00 | 120 | 22:00
Dhamrai | 133 | 09:00 | 121 | 14:00 | Rajendrapur | 134 | 02:00 | 128 | 18:30
Dhanmondi | 137 | 06:00 | 125.7 | 14:00 | Rajshahi | 134 | 05:00 | 125 | 21:00
Dohazari | 133 | 04:00 | 129 | 12:00 | Rajshahi-230 | 134 | 02:00 | 126 | 21:00
Faridpur | 128 | 04:00 | 123 | 21:00 | Ramganj | 129 | 00:00 | 126 | 18:30
Fatullah | 134 | 04:00 | 125 | 14:00 | Rampur | 136 | 06:00 | 133 | 12:00
Fenchuganj | 129 | 06:00 | 125 | 19:30 | Rampura | 137 | 03:00 | 127 | 14:00
Feni | 130 | 00:00 | 127 | 14:00 | Rangamati | 138 | 01:00 | 134 | 11:00
Feni-230 | 131 | 04:00 | 128 | 12:00 | Rangpur | 132 | 17:00 | 126 | 21:00
Ghatail | 128 | 09:00 | 114 | 20:00 | Ruppur | 138 | 10:00 | 129 | 21:00
Ghorashal | 130 | 01:00 | 122 | 14:00 | Saidpur | 136 | 02:00 | 131 | 13:00
Goalpara | 136 | 00:00 | 130 | 14:00 | Santhia | 135 | 05:00 | 127 | 20:00
Gollamari | 135 | 00:00 | 129 | 21:00 | Satkhira | 131 | 01:00 | 122 | 21:00
Gopalganj | 138 | 17:00 | 127 | 12:00 | Satmasjid | 134 | 04:00 | 124 | 14:00
Gopalganj-400 | 132 | 02:00 | 128 | 13:00 | Savar | 131 | 01:00 | 120 | 14:00
Gulshan | 137 | 05:00 | 126 | 14:00 | SevenRings | 130 | 10:00 | 121 | 19:00
Halishahar | 137 | 06:00 | 133 | 12:00 | ShahCement | 131 | 04:00 | 124 | 14:00
Haripur | 132 | 03:00 | 125 | 14:00 | Shahjadpur | 136 | 01:00 | 132 | 19:30
HaripurSBU | 132 | 03:00 | 125 | 14:00 | Shahjibazar | 127 | 05:00 | 119 | 18:30
Hasnabad | 134 | 05:00 | 127 | 13:00 | Shahmirpur | 137 | 07:00 | 134 | 12:00
Hathazari | 137 | 03:00 | 135 | 12:00 | Shariatpur | 131 | 03:00 | 124 | 21:00
Hatirjheel | 137 | 03:00 | 127 | 14:00 | Sherpur | 129 | 19:00 | 115 | 19:30
Ishurdi | 138 | 02:00 | 129 | 21:00 | Shikalbaha | 127 | 02:00 | 123 | 12:00
Jaldhaka | 133 | 01:00 | 128 | 14:00 | Shikalbaha-230 | 137 | 02:00 | 135 | 11:00
Jamalpur | 131 | 09:00 | 116 | 03:00 | Shitalakhya | 133 | 05:00 | 124 | 14:00
Jashore | 133 | 10:00 | 119 | 21:00 | Sholosohor | 137 | 06:00 | 134 | 12:00
Jhenaidah | 138 | 10:00 | 125 | 21:00 | Shomvuganj | 121 | 04:00 | 114 | 23:00
Jhenaidah-230 | 138 | 10:00 | 126 | 21:00 | Shyampur | 133 | 05:00 | 125 | 13:00
Joydebpur | 128 | 00:00 | 117 | 16:00 | Shyampur-230 | 135 | 04:00 | 127 | 13:00
Joypurhat | 134 | 10:00 | 126 | 21:00 | Siddhirganj | 133 | 05:00 | 125 | 14:00
Juldah | 136 | 04:00 | 134 | 12:00 | Sirajganj | 132 | 03:00 | 124 | 21:00
Kabirpur | 133 | 10:00 | 115 | 14:00 | Sitakunda | 136 | 06:00 | 134 | 02:00
Kachua | 130 | 00:00 | 128 | 14:00 | Sonargaon | 126 | 00:00 | 123 | 12:00
Kaliakoir | 135 | 09:00 | 125 | 20:00 | Sreemongol | 125 | 01:00 | 120 | 18:00
Kaliganj | 137 | 10:00 | 124 | 21:00 | Sreepur | 135 | 03:00 | 128 | 22:00
Kallyanpur | 130 | 05:00 | 122 | 13:00 | Srinagar | 136 | 05:00 | 127 | 14:00
Kalurghat | 139 | 01:00 | 135 | 12:00 | SSM | 140 | 00:00 | 140 | 00:00
Kamrangirchar | 136 | 04:00 | 118 | 13:00 | Sunamganj | 119 | 06:00 | 11 | 06:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 123 | 03:00 | 120 | 19:30
Kasba | 127 | 03:00 | 122 | 12:00 | Sylhet_(South) | 123 | 02:00 | 120 | 19:00
Kazla | 137 | 07:00 | 128 | 14:00 | Tangail | 127 | 09:00 | 116 | 20:00
Keranigonj | 137 | 04:00 | 127 | 14:00 | Taraganj | 133 | 00:00 | 128 | 21:00
Khagrachori | 136 | 06:00 | 133 | 13:00 | Tasnim | 130 | 04:00 | 123 | 12:00
Khulna | 134 | 00:00 | 127 | 21:00 | Thakurgaon | 139 | 09:00 | 133 | 22:00
Khulna(S) | 136 | 05:00 | 129 | 21:00 | TK | 136 | 07:00 | 134 | 03:00
Khulshi | 135 | 02:00 | 131 | 12:00 | Tongi | 132 | 04:00 | 123 | 18:30
Kishoreganj | 125 | 04:00 | 117 | 22:00 | Ullahpara | 134 | 04:00 | 126 | 21:00
Kodda | 133 | 09:00 | 118 | 14:00 | Ullon | 137 | 04:00 | 126 | 14:00
Korerhat | 133 | 09:00 | 130 | 12:00 | Uttara | 130 | 03:00 | 118 | 14:00
KSRM | 137 | 19:00 | 133 | 12:00 | UttaraNew | 132 | 04:00 | 11 | 19:00
Kulaura | 127 | 04:00 | 123 | 19:30 | Zigatola | 137 | 04:00 | 126 | 14:00
Kurigram | 128 | 03:00 | 120 | 21:00
Kushtia | 137 | 05:00 | 126 | 21:00
Laksam | 130 | 04:00 | 124 | 19:00
Lakshmipur | 127 | 06:00 | 124 | 18:30
Lalbag | 136 | 03:00 | 126 | 13:00
Lalmonirhat | 128 | 17:00 | 122 | 19:30
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division