## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-09-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-09-2026 | during | 05-09-2026 | during | 05-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 383 | 393 | 412 | 412 | 382 | 382 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 7 | 15 | 55 | 55 | 0 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 96 | 98 | 210 | 210 | 100 | 100 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 35 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 70 | 141 | 149.36 | 149.36 | 45 | 142 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 5 | 5.5 | 33 | 33 | 5 | 5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 50 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 81 | 300 | 300 | 32 | 81 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 35 | 149 | 149 | 34 | 53 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 34 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 35 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 500 | 584 | 584 | 450 | 450 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 339 | 333 | 718 | 718 | 270 | 270 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 86 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1740 | 2227.92 | 5063.16 | 5035.16 | 1737.42 | 2180.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 11 | 0 | 3 | 0 | 3 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 34 | 44 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 222 | 219 | 218 | 218 | 218 | 218 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 82 | 215 | 215 | 210 | 210 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 34 | 105 | 105 | 34 | 34 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 15 | 46 | 14 | 32 | 14 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 50 | 100 | 100 | 24 | 50 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 19 | 34 | 25 | 30 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 12 | 44 | 95.1 | 95.1 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2.37 | 0 | 5.02 | 0 | 5.02 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 18 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 51 | 72 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 36 | 100 | 100 | 25 | 50 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 105 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 35 | 55 | 163 | 163 | 35 | 55 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1212 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 9 | 3 | 0 | 3 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 770 | 900 | 1150 | 1150 | 1130 | 1130 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 2816.37 | 3063.5 | 4075.98 | 4138.96 | 3284.02 | 3482.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 214 | 205 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 320 | 300 | 350.01 | 350.01 | 350.01 | 350.01
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 260 | 285 | 342.01 | 342.01 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 240 | 280 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 20 | 20 | 41.65 | 41.65 | 34 | 34 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 25 | 25 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 45 | 8 | 195 | 195 | 55 | 55 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 55 | 150 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 30 | 30 | 30 | 30 | 30 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 91 | 163 | 163 | 91 | 91 | Machine Problem
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 189 | 188 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 138 | 150 | 84 | 76 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 105 | 104 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 63 | 113 | 113 | 9 | 70 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 115 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 57 | 0 | 62 | 0 | 62 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1905.2 | 2111.2 | 2754.44 | 2684.44 | 1899.46 | 2052.46
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-09-2026 | during | 05-09-2026 | during | 05-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 2.5 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2.5 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 163 | 120 | 170 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 94 | 60 | 90 | 60 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.44 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 232.44 | 286 | 538.6 | 546.5 | 264.1 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 41 | 40 | 40 | 40 | 40 | machine problem
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 39 | 39 | 30 | 30 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 141 | 141 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 28 | 25 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 42 | 86 | 86 | 86 | 42 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 126 | 126 | 120 | 120 | 120 | 120 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 246 | 255 | 341 | 341 | 250 | 250
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 393 | 380 | 360 | 390 | 380 | 380
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 398 | 400 | 383 | 383 | 383 | 383
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1471 | 1500 | 1575 | 1605 | 1431 | 1475
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 896 | 766 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 25 | 41 | 50 | 50 | 0 | 0 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 0 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 67 | 105 | 105 | 67 | 67 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 89 | 0 | 74 | 0 | 74 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 370 | 500 | 500 | 500 | 500 | 500 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1380 | 1391 | 2869 | 2795 | 2226 | 2169
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 800 | 850 | 800 | 800 | 800 | 800 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 48 | 110 | 110 | 0 | 32 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 115 | 115 | 120 | 120 | 119 | 119 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 570 | 570 | 580 | 580 | 580 | 580 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 289 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.61 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2027.61 | 2127 | 2288 | 2287 | 2044 | 2075
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 6.54 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 47 | 47 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 149 | 155 | 214 | 214 | 150 | 150 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 370 | 365 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 17 | 26 | 26 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 1 | 8 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 100 | 100 | 0 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 57 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 0.95 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 926.54 | 1321.29 | 900 | 1300 | 900 | 900 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 9.99 | 0 | 63 | 0 | 63 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 88 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1587.02 | 2015.29 | 2655.91 | 2835.99 | 1824.33 | 1754.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 0 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 50 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 153 | 157 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 92 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.6 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 72 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 21 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 123 | 0 | 161.06 | 0 | 161.06 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 423.6 | 414 | 669.06 | 472 | 556.06 | 394
System Total |  |  |  |  | 28843.2 | 29158.791 | 13583.24 | 15135.91 | 22489.15 | 22400.05 | 15266.39 | 15871.79
Forecast Scenario (05-09-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14750 |  | 563.45 |  | 15340
|  |  |  | 1:00 | 13980 |  | 458.4 |  | 14460
|  |  |  | 2:00 | 13480 |  | 697.15 |  | 14210
|  |  |  | 3:00 | 13410 |  | 630.3 |  | 14070
|  |  |  | 4:00 | 13400 |  | 305.6 |  | 13720
|  |  |  | 5:00 | 13260 |  | 305.6 |  | 13580
|  |  |  | 6:00 | 13658.55 |  | 0 |  | 13170
|  |  |  | 7:00 | 13808.11 |  | 0 |  | 12980
|  |  |  | 8:00 | 13310 |  | 0 |  | 13030
|  |  |  | 9:00 | 13290 |  | 0 |  | 12890
|  |  |  | 10:00 | 13600 |  | 0 |  | 12910
|  |  |  | 11:00 | 14060 |  | 0 |  | 13260
|  |  |  | 12:00 | 14380 |  | 0 |  | 14060
|  |  |  | 13:00 | 14300 |  | 0 |  | 14030
|  |  |  | 14:00 | 14270 |  | 0 |  | 14130
|  |  |  | 15:00 | 13880 |  | 926.35 |  | 14850
|  |  |  | 16:00 | 13670 |  | 935.9 |  | 14650
|  |  |  | 17:00 | 13940 |  | 706.7 |  | 14680
|  |  |  | 18:00 | 14440 |  | 38.2 |  | 14480
|  |  |  | 18:30 | 14822.25 |  | 122.0012 |  | 14950
|  |  |  | 19:00 | 15297.48 |  | 202.9566 |  | 15510
|  |  |  | 19:30 | 15850 |  | 347 |  | 16077
|  |  |  | 20:00 | 16000 |  | 888 |  | 17218
|  |  |  | 21:00 | 16050 |  | 850 |  | 16900
|  |  |  | 22:00 | 15900 |  | 900 |  | 16800
|  |  |  | 23:00 | 15500 |  | 1000 |  | 16500
Probable Maximum Temperature: |  |  | 26.00°C
Probable Maximum Demand at Day Peak: |  |  | 14060.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 17218.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16050.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 339.72583 MKWHr. |  | 140 | 80 | 100 | 200 | 50 | 140 | 42 | 80 | 56 | 888
*** This report is generated digitally from Operation Information System (OIS) at 09:11 hrs on 05-09-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-09-2026 | [28 empty] | Date: | 04-09-2026 | [28 empty] | Date: | 04-09-2026 | [28 empty] | Date: | 04-09-2026 | [28 empty] | Date: | 04-09-2026 | [17 empty] | Date: | 04-09-2026
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [17 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 216 | 54 | 0 | 17 | 80 | 48 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 35 | 310 | 0 | 0 | 0 | 143.42 | 4.5 | 22 | 0 | 330 | 107 | 16 | 46 | 0 | 15 | 50 | 45 | 17 | 24 | 25 | 0 | 222 | 55 | 2 | 925 | 53 | 0 | 8 | 25.5 | 34 | 223 | 0 | 0 | 0 | 1224 | 0 | 132 | 0 | 300 | 300 | 265 | 51 | 0 | 224 | 0 | 68 | 90 | 189 | 64 | 19 | 105 | 152 | 52.2 | 0 | 30 | 245 | 400 | 392 | 41 | 30 | 0 | 0 | 16 | 0 | 42 | 26 | 142 | 0 | 126 | 17 | 87 | 0 | 165 | 0 | 0 | 0 | 12 | 8892.62 | 788 | 0 | 0 | 20 | 35 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 370 | 0 | 0 | 0 | 1402.99 | 0 | 0 | 0 | 55 | 70 | 0 | 101 | 28 | 8 | 0 | 0 | 17 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 158 | 49 | 115 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 118 | 220 | 0 | 800 | 570 | 17 | 5848.99 | 14741.61 | 105.42
01:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 258 | 17 | 0 | 17 | 80 | 48 | 15 | 17 | 35 | 0 | 0 | 0 | 0 | 17 | 29 | 0 | 0 | 0 | 86 | 4.5 | 22 | 0 | 400 | 109 | 16 | 26 | 0 | 35 | 50 | 15 | 0 | 24 | 25 | 0 | 222 | 55 | 4 | 770 | 53 | 0 | 28 | 8 | 34 | 221 | 0 | 0 | 0 | 1224 | 0 | 102 | 0 | 300 | 300 | 335 | 51 | 0 | 222 | 0 | 38 | 90 | 189 | 18 | 19 | 105 | 146 | 52.2 | 0 | 30 | 245 | 400 | 393 | 41 | 30 | 0 | 0 | 16 | 0 | 42 | 26 | 141 | 0 | 124 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8011.7 | 787 | 0 | 0 | 19 | 30 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 370 | 0 | 0 | 0 | 1316.98 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 28 | 8 | 0 | 0 | 17 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 156 | 50 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 118 | 220 | 0 | 800 | 570 | 17 | 5581.98 | 13593.68 | 105.41
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 327 | 17 | 0 | 17 | 80 | 32 | 15 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 86 | 4.5 | 22 | 0 | 470 | 107 | 16 | 24 | 0 | 13 | 50 | 15 | 0 | 24 | 25 | 0 | 222 | 55 | 4 | 770 | 53 | 0 | 45 | 8 | 34 | 221 | 0 | 0 | 0 | 1224 | 0 | 102 | 0 | 270 | 300 | 305 | 51 | 0 | 222 | 0 | 33 | 90 | 188 | 17 | 19 | 105 | 146 | 52.2 | 0 | 30 | 248 | 400 | 392 | 41 | 30 | 0 | 0 | 16 | 0 | 42 | 30 | 141 | 0 | 126 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 8007.7 | 788 | 0 | 0 | 19 | 30 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 370 | 0 | 0 | 0 | 1312.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 0 | 0 | 17 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 158 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 118 | 220 | 0 | 800 | 570 | 17 | 5464.88 | 13472.58 | 105.4
03:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 270 | 17 | 0 | 13 | 80 | 32 | 15 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 100 | 0 | 0 | 86 | 4.5 | 22 | 0 | 420 | 99 | 16 | 25 | 0 | 13 | 10 | 15 | 0 | 24 | 25 | 0 | 222 | 55 | 10 | 770 | 53 | 0 | 50 | 8 | 34 | 220 | 0 | 0 | 0 | 1224 | 0 | 102 | 0 | 270 | 300 | 265 | 51 | 0 | 223 | 0 | 34 | 90 | 189 | 0 | 19 | 105 | 146 | 52.2 | 0 | 31 | 243 | 400 | 392 | 41 | 30 | 0 | 0 | 16 | 0 | 42 | 30 | 141 | 0 | 126 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 7884.7 | 837 | 0 | 0 | 19 | 30 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 370 | 0 | 0 | 0 | 1306.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 0 | 0 | 17 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 155 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 118 | 220 | 0 | 800 | 560 | 17 | 5499.89 | 13384.59 | 105.39
04:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 239 | 17 | 0 | 17 | 80 | 32 | 15 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 100 | 0 | 0 | 86 | 4.5 | 22 | 0 | 460 | 96 | 16 | 25 | 0 | 13 | 0 | 15 | 0 | 24 | 25 | 0 | 222 | 64 | 17 | 770 | 53 | 0 | 50 | 8 | 34 | 223 | 0 | 0 | 0 | 1224 | 0 | 58 | 0 | 270 | 300 | 280 | 51 | 0 | 223 | 0 | 21 | 90 | 188 | 0 | 19 | 105 | 148 | 52.2 | 0 | 31 | 255 | 400 | 392 | 41 | 30 | 0 | 0 | 16 | 0 | 42 | 30 | 141 | 0 | 126 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 7855.7 | 838 | 0 | 0 | 19 | 30 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 370 | 0 | 0 | 0 | 1314.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 156 | 51 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 117 | 220 | 0 | 800 | 565 | 17 | 5498.64 | 13354.34 | 105.38
05:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 233 | 0 | 0 | 17 | 80 | 32 | 15 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 86 | 4.5 | 22 | 0 | 400 | 90 | 16 | 24 | 0 | 9 | 0 | 15 | 0 | 24 | 25 | 0 | 220 | 54 | 26 | 770 | 53 | 0 | 50 | 8 | 25 | 222 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 270 | 300 | 265 | 51 | 0 | 223 | 0 | 17 | 90 | 189 | 0 | 19 | 105 | 142 | 43 | 0 | 31 | 248 | 400 | 392 | 41 | 30 | 0 | 0 | 16 | 0 | 42 | 30 | 142 | 0 | 125 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 12 | 7633.5 | 886 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 1315.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 155 | 51 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 117 | 220 | 0 | 800 | 575 | 17 | 5484.12 | 13117.62 | 105.37
06:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 204 | 0 | 0 | 17 | 79 | 32 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 86 | 4.5 | 22 | 0 | 310 | 90 | 16 | 25 | 0 | 3 | 0 | 15 | 0 | 24 | 25 | 0.01 | 219 | 55 | 28 | 770 | 36 | 0 | 50 | 8 | 34 | 222 | 0 | 0 | 0 | 1160 | 1 | 55 | 0 | 230 | 300 | 255 | 51 | 0 | 191 | 0 | 17 | 92 | 189 | 0 | 19 | 105 | 138 | 43 | 1 | 31 | 248 | 400 | 392 | 41 | 30 | 0 | 0 | 16 | 0 | 42 | 30 | 141 | 0 | 126 | 0 | 58 | 0.55 | 67 | 0 | 0 | 0.15 | 12 | 7305.21 | 891 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 370 | 0 | 0 | 0 | 1312.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0.7 | 0 | 0 | 0 | 0.23 | 142 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0.06 | 155 | 51 | 115 | 0 | 0 | 0 | 0 | 0 | 0.1 | 1 | 0.01 | 0 | 307 | 118 | 180 | 0 | 800 | 575 | 17 | 5449.54 | 12754.75 | 105.36
07:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 227 | 0 | 0 | 17 | 79 | 32 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 2 | 86 | 4.5 | 22 | 0 | 340 | 90 | 16 | 25 | 0 | 10 | 0 | 15 | 0 | 24 | 25 | 0.18 | 219 | 55 | 32 | 770 | 36 | 0 | 50 | 8 | 34 | 221 | 0 | 0 | 0 | 1170 | 1 | 53 | 8 | 230 | 280 | 230 | 51 | 0 | 221 | 0 | 17 | 92 | 188 | 0 | 19 | 105 | 126 | 43 | 10 | 31 | 246 | 400 | 392 | 41 | 30 | 0 | 1 | 16 | 0 | 42 | 30 | 141 | 0 | 126 | 0 | 58 | 2.26 | 113 | 0 | 0.2 | 2.42 | 12 | 7451.56 | 890 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 370 | 0 | 0 | 0 | 1306.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 8.95 | 4 | 0 | 0 | 1.41 | 143 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0.4 | 154 | 51 | 115 | 4 | 0 | 0 | 0 | 0 | 1.2 | 3 | 0.09 | 0 | 297 | 105 | 180 | 0 | 800 | 575 | 17 | 5335.35 | 12786.91 | 105.35
08:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 289 | 0 | 0 | 17 | 79 | 32 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 12 | 86 | 5 | 22 | 0 | 425 | 90 | 16 | 24 | 0 | 0 | 0 | 15 | 0 | 24 | 25 | 0.3 | 219 | 55 | 33 | 770 | 35 | 0 | 50 | 8 | 34 | 222 | 0 | 0 | 0 | 1053 | 2 | 55 | 43 | 230 | 280 | 230 | 51 | 0 | 221 | 20 | 17 | 92 | 188 | 1 | 19 | 105 | 116 | 43 | 33 | 30 | 245 | 400 | 392 | 41 | 30 | 0 | 3 | 16 | 0 | 42 | 28 | 143 | 0 | 125 | 0 | 58 | 3.85 | 114 | 0 | 0.5 | 5.23 | 12 | 7592.88 | 896 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 370 | 0 | 0 | 0 | 1154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8.81 | 32 | 0 | 0 | 9.35 | 146 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0.78 | 156 | 51 | 0 | 16 | 0 | 0 | 0 | 0 | 2 | 4 | 0.12 | 0 | 199 | 105 | 180 | 0 | 800 | 570 | 17 | 5021.06 | 12613.94 | 105.34
09:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 279 | 0 | 0 | 17 | 79 | 32 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 19 | 86 | 5 | 22 | 0 | 430 | 90 | 16 | 23 | 0 | 2 | 0 | 15 | 0 | 24 | 25 | 1.51 | 219 | 54 | 35 | 770 | 36 | 0 | 50 | 8 | 34 | 223 | 0 | 0 | 0 | 1030 | 6 | 53 | 51 | 220 | 270 | 220 | 51 | 0 | 221 | 20 | 16 | 92 | 189 | 8.4 | 19 | 105 | 124 | 43 | 50 | 30 | 248 | 400 | 393 | 41 | 30 | 0 | 7 | 16 | 0 | 42 | 25 | 141 | 0 | 126 | 0 | 58 | 13.52 | 114 | 0 | 1.3 | 27.99 | 12 | 7646.72 | 897 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 50.03 | 370 | 0 | 0 | 0 | 919.65 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 8 | 15.93 | 38 | 0 | 0 | 21.12 | 147 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.67 | 156 | 51 | 0 | 31 | 0 | 0 | 0 | 0 | 1.5 | 44 | 0.45 | 0 | 189 | 105 | 220 | 0 | 800 | 570 | 17 | 4987.35 | 12634.07 | 105.34
10:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 252 | 0 | 0 | 17 | 79 | 32 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 18 | 86 | 5 | 22 | 0 | 405 | 90 | 16 | 12 | 0 | 3 | 0 | 15 | 0 | 0 | 25 | 2.01 | 220 | 55 | 27 | 770 | 35 | 0 | 50 | 8 | 34 | 223 | 0 | 0 | 0 | 1030 | 6 | 53 | 80 | 220 | 270 | 220 | 51 | 0 | 222 | 20 | 17 | 91 | 189 | 8 | 19 | 105 | 130 | 8 | 66 | 23 | 246 | 400 | 393 | 41 | 30 | 0 | 3 | 16 | 0 | 42 | 25 | 141 | 0 | 126 | 0 | 58 | 17.51 | 114 | 0 | 1.7 | 30.05 | 12 | 7554.27 | 896 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 370 | 0 | 0 | 0 | 910.07 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 50.36 | 60 | 0 | 0 | 29.98 | 147 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.01 | 157 | 50 | 0 | 12 | 0 | 0 | 0 | 0 | 5.4 | 92 | 0.43 | 0 | 200 | 116 | 220 | 0 | 800 | 570 | 17 | 5109.25 | 12663.52 | 105.34
11:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 304 | 0 | 0 | 17 | 78 | 32 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 23 | 86 | 5 | 22 | 0 | 460 | 96 | 16 | 13 | 0 | 2 | 0 | 15 | 0 | 0 | 25 | 2.29 | 221 | 55 | 24 | 770 | 36 | 0 | 25 | 8 | 34 | 222 | 0 | 0 | 0 | 1020 | 18 | 53 | 80 | 220 | 270 | 220 | 51 | 0 | 218 | 20 | 17 | 91 | 187 | 8 | 19 | 105 | 132 | 8 | 75 | 23 | 245 | 398 | 393 | 41 | 30 | 0 | 5 | 16 | 0 | 42 | 25 | 143 | 0 | 125 | 0 | 58 | 22.23 | 114 | 0 | 0.7 | 42.45 | 12 | 7737.67 | 896 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 370 | 0 | 0 | 0 | 914.63 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 43.31 | 74 | 0 | 0 | 28.39 | 147 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 2.89 | 156 | 50 | 0 | 4 | 0 | 0 | 0 | 0 | 6.8 | 84 | 0.69 | 0 | 198 | 116 | 220 | 0 | 800 | 577 | 17 | 5106.71 | 12844.38 | 105.34
12:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 339 | 0 | 0 | 17 | 70 | 32 | 7 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 35 | 86 | 5 | 14 | 0 | 500 | 107 | 16 | 12 | 0 | 0 | 0 | 15 | 0 | 24 | 25 | 2.37 | 222 | 51 | 19 | 770 | 35 | 0 | 34 | 8 | 34 | 219 | 0 | 0 | 0 | 1212 | 11 | 55 | 45 | 240 | 320 | 260 | 51 | 0 | 214 | 20 | 17 | 85 | 189 | 8 | 19 | 105 | 138 | 52.2 | 57 | 30 | 246 | 398 | 393 | 41 | 30 | 0 | 10 | 16 | 0 | 42 | 28 | 141 | 0 | 126 | 0 | 58 | 2.5 | 114 | 0 | 2.5 | 43.44 | 12 | 8165.01 | 896 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 370 | 0 | 0 | 0 | 926.54 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 6.54 | 88 | 0 | 0 | 9.99 | 149 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0.95 | 153 | 51 | 72 | 21 | 0 | 0 | 0 | 0 | 3.6 | 123 | 0.61 | 16 | 289 | 115 | 220 | 0 | 800 | 570 | 17 | 5418.23 | 13583.24 | 105.33
13:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 277 | 0 | 0 | 17 | 78 | 32 | 15 | 17 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 97 | 0 | 12 | 86 | 5 | 14 | 0 | 460 | 109 | 16 | 13 | 0 | 2 | 0 | 15 | 0 | 24 | 25 | 1.9 | 222 | 46 | 17 | 770 | 35 | 0 | 50 | 8 | 34 | 216 | 0 | 0 | 0 | 1224 | 13 | 55 | 8 | 240 | 355 | 280 | 51 | 0 | 213 | 20 | 17 | 85 | 187 | 8 | 19 | 105 | 146 | 52.2 | 50 | 29 | 245 | 394 | 393 | 41 | 30 | 0 | 6 | 16 | 0 | 42 | 25 | 141 | 0 | 127 | 0 | 58 | 11.2 | 113 | 0 | 0.6 | 33.37 | 12 | 8129.27 | 896 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 378 | 0 | 0 | 0 | 1193.88 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 8.19 | 80 | 0 | 0 | 32.28 | 149 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 6.97 | 156 | 50 | 74 | 13 | 0 | 0 | 0 | 0 | 6.9 | 212 | 0.72 | 16 | 307 | 116 | 220 | 0 | 800 | 570 | 17 | 5734.94 | 13864.21 | 105.33
14:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 225 | 0 | 0 | 17 | 78 | 32 | 15 | 17 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 97 | 0 | 27 | 86 | 5 | 14 | 0 | 360 | 109 | 16 | 20 | 0 | 0 | 0 | 15 | 17 | 24 | 25 | 3.45 | 222 | 54 | 16 | 770 | 36 | 0 | 50 | 8 | 34 | 144 | 0 | 0 | 0 | 1160 | 11 | 53 | 8 | 220 | 300 | 265 | 51 | 0 | 219 | 20 | 17 | 85 | 188 | 8 | 19 | 105 | 148 | 52.2 | 58 | 29 | 260 | 400 | 340 | 41 | 30 | 0 | 9 | 16 | 0 | 41 | 28 | 141 | 0 | 127 | 9 | 58 | 3 | 113 | 0 | 0.6 | 1.06 | 12 | 7720.31 | 865 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 420 | 0 | 0 | 0 | 1291.35 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 55.26 | 29 | 0 | 0 | 11.24 | 148 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 1.04 | 157 | 51 | 95 | 10 | 0 | 0 | 0 | 0 | 2 | 107 | 0.41 | 16 | 277 | 115 | 220 | 0 | 800 | 570 | 17 | 5629.3 | 13349.61 | 105.33
15:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 253 | 17 | 0 | 17 | 77 | 32 | 15 | 17 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 97 | 0 | 18 | 86 | 5.6 | 14 | 0 | 400 | 107 | 16 | 24 | 0 | 27 | 0 | 15 | 17 | 24 | 25 | 2.96 | 222 | 55 | 16 | 770 | 35 | 0 | 50 | 8 | 34 | 147 | 0 | 0 | 0 | 1160 | 13 | 53 | 8 | 220 | 300 | 260 | 51 | 0 | 201 | 20 | 17 | 85 | 188 | 8 | 19 | 104 | 142 | 52.2 | 33 | 29 | 262 | 394 | 340 | 41 | 30 | 0 | 9 | 16 | 0 | 41 | 25 | 143 | 0 | 126 | 17 | 58 | 3.5 | 112 | 0 | 0.6 | 11.58 | 12 | 7690.44 | 865 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 423 | 0 | 0 | 0 | 1192.23 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 47.97 | 20 | 0 | 0 | 11.12 | 147 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0.44 | 159 | 51 | 95 | 26 | 0 | 0 | 0 | 0 | 4.4 | 38 | 0.1 | 16 | 276 | 115 | 220 | 0 | 850 | 570 | 17 | 5628.26 | 13318.7 | 105.32
16:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 275 | 17 | 0 | 17 | 46 | 32 | 15 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 4 | 86 | 5.6 | 0 | 0 | 450 | 50 | 16 | 28 | 0 | 22 | 0 | 15 | 17 | 24 | 25 | 2.12 | 222 | 55 | 18 | 770 | 35 | 0 | 50 | 8 | 34 | 146 | 0 | 0 | 0 | 1160 | 8 | 76 | 8 | 250 | 300 | 275 | 51 | 0 | 205 | 20 | 17 | 85 | 187 | 8 | 16 | 52 | 142 | 25 | 31 | 29 | 260 | 391 | 340 | 41 | 30 | 0 | 1 | 16 | 0 | 41 | 25 | 141 | 0 | 126 | 17 | 58 | 4.9 | 83 | 0 | 0.6 | 10.28 | 12 | 7573.5 | 865 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 420 | 0 | 0 | 0 | 967.11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 3 | 8 | 34.13 | 17 | 0 | 0 | 1.76 | 147 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0.48 | 159 | 51 | 70 | 17 | 0 | 0 | 0 | 0 | 1.5 | 46 | 0.15 | 16 | 276 | 115 | 220 | 0 | 800 | 570 | 17 | 5272.13 | 12845.63 | 105.32
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 216 | 17 | 0 | 30 | 30 | 15 | 15 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 86 | 5.6 | 15 | 0 | 345 | 34 | 16 | 31 | 0 | 11 | 0 | 15 | 17 | 12 | 25 | 0.18 | 222 | 55 | 24 | 770 | 36 | 0 | 44 | 8 | 34 | 147 | 0 | 0 | 0 | 1140 | 0 | 120 | 8 | 250 | 300 | 275 | 51 | 0 | 205 | 20 | 17 | 85 | 120 | 13 | 16 | 34 | 124 | 16 | 11 | 29 | 267 | 391 | 340 | 41 | 30 | 0 | 2 | 16 | 0 | 41 | 28 | 141 | 0 | 126 | 17 | 62 | 3 | 84 | 0 | 0.2 | 7.49 | 12 | 7217.47 | 837 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 440 | 0 | 0 | 0 | 1083.25 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 8 | 9 | 3.52 | 9 | 0 | 0 | 2.78 | 147 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0.37 | 158 | 51 | 50 | 5 | 24 | 0 | 0 | 0 | 0.1 | 24 | 0.05 | 16 | 272 | 115 | 220 | 0 | 800 | 570 | 17 | 5356.07 | 12573.54 | 105.31
18:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 222 | 17 | 0 | 35 | 30 | 15 | 15 | 17 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 36 | 0 | 0 | 86 | 5 | 18 | 0 | 335 | 28 | 16 | 31 | 0 | 11 | 3 | 46 | 17 | 12 | 36 | 0 | 221 | 55 | 23 | 770 | 35 | 0 | 44 | 8 | 34 | 147 | 0 | 0 | 0 | 1050 | 0 | 120 | 8 | 250 | 300 | 265 | 51 | 0 | 202 | 20 | 29 | 85 | 82 | 27 | 19 | 31 | 118 | 16 | 1 | 29 | 259 | 399 | 340 | 41 | 30 | 0 | 0 | 16 | 0 | 41 | 30 | 141 | 0 | 126 | 17 | 63 | 0.2 | 84 | 0 | 0 | 0.46 | 12 | 7057.66 | 837 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 473 | 2 | 0 | 0 | 1299.42 | 0 | 0 | 0 | 35 | 40 | 0 | 25 | 20 | 8 | 0 | 0 | 10 | 0 | 0.12 | 147 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.04 | 158 | 51 | 50 | 0 | 62 | 0 | 0 | 0 | 0.1 | 3 | 0.01 | 16 | 238 | 115 | 220 | 0 | 800 | 570 | 17 | 5540.69 | 12598.35 | 105.31
19:00 | 0 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 336 | 54 | 0 | 35 | 104 | 81 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 35 | 0 | 86 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 500 | 65 | 16 | 39 | 0 | 10 | 50 | 46 | 17 | 50 | 36 | 0 | 220 | 67 | 29 | 770 | 45 | 0 | 50 | 13 | 34 | 147 | 0 | 0 | 0 | 1224 | 0 | 138 | 8 | 300 | 300 | 290 | 51 | 0 | 214 | 20 | 51 | 85 | 141 | 49 | 19 | 104 | 148 | 34 | 0 | 30 | 260 | 396 | 382 | 41 | 30 | 0 | 0 | 16 | 0 | 42 | 25 | 141 | 0 | 126 | 17 | 88 | 0 | 158 | 0 | 0 | 0 | 12 | 8738.92 | 767 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 500 | 17 | 0 | 0 | 1314.69 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 22 | 8 | 0 | 0 | 17 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 157 | 50 | 95 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 291 | 115 | 220 | 0 | 850 | 570 | 17 | 5910.69 | 14649.61 | 105.3
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 329 | 54 | 0 | 35 | 140 | 81 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 35 | 0 | 98 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 500 | 92 | 16 | 43 | 0 | 12 | 50 | 46 | 17 | 50 | 36 | 0 | 216 | 68 | 30 | 800 | 52 | 0 | 44 | 25.5 | 34 | 147 | 0 | 0 | 0 | 1224 | 0 | 150 | 8 | 300 | 300 | 275 | 51 | 0 | 208 | 20 | 115 | 85 | 190 | 63 | 8 | 105 | 148 | 52.2 | 0 | 30 | 254 | 396 | 380 | 41 | 30 | 0 | 0 | 16 | 0 | 75 | 25 | 141 | 0 | 126 | 17 | 91 | 0 | 161 | 0 | 0 | 0 | 12 | 9100.62 | 719 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 500 | 17 | 0 | 0 | 1313.98 | 0 | 0 | 0 | 55 | 70 | 0 | 0 | 22 | 8 | 0 | 0 | 17 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 158 | 50 | 95 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 115 | 220 | 0 | 850 | 570 | 17 | 5870.98 | 14971.6
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 333 | 54 | 0 | 35 | 141 | 81 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 35 | 0 | 98 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 500 | 105 | 16 | 44 | 0 | 9 | 50 | 46 | 18 | 50 | 36 | 0 | 219 | 72 | 34 | 900 | 55 | 0 | 44 | 25.5 | 34 | 82 | 0 | 0 | 0 | 1224 | 0 | 150 | 8 | 280 | 300 | 285 | 51 | 0 | 205 | 20 | 115 | 91 | 188 | 63 | 19 | 104 | 150 | 52.2 | 0 | 30 | 255 | 400 | 380 | 41 | 30 | 0 | 0 | 16 | 0 | 86 | 25 | 141 | 0 | 126 | 17 | 94 | 0 | 163 | 0 | 0 | 0 | 12 | 9188.62 | 766 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 500 | 17 | 0 | 0 | 1321.29 | 0 | 0 | 0 | 57 | 70 | 0 | 0 | 22 | 8 | 0 | 0 | 17 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 157 | 50 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 115 | 220 | 0 | 850 | 570 | 17 | 5947.29 | 15135.91 | 105.3
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 300 | 54 | 0 | 35 | 142 | 81 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 440 | 109 | 16 | 41 | 0 | 5 | 50 | 46 | 35 | 50 | 36 | 0 | 219 | 68 | 33 | 1050 | 53 | 0 | 50 | 25.5 | 34 | 92 | 0 | 0 | 0 | 1224 | 0 | 150 | 8 | 260 | 300 | 270 | 51 | 0 | 218 | 5 | 115 | 90 | 189 | 64 | 19 | 104 | 152 | 52.2 | 0 | 30 | 250 | 400 | 380 | 41 | 30 | 0 | 0 | 16 | 0 | 86 | 25 | 141 | 0 | 126 | 17 | 89 | 0 | 163 | 0 | 0 | 0 | 12 | 9225.62 | 718 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 505 | 17 | 0 | 0 | 1308.09 | 0 | 0 | 0 | 57 | 70 | 0 | 0 | 21 | 8 | 0 | 0 | 17 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 156 | 51 | 115 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 220 | 0 | 850 | 570 | 27 | 5884.09 | 15109.71 | 105.29
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 338 | 54 | 0 | 35 | 141 | 81 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 35 | 0 | 98 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 515 | 107 | 16 | 37 | 0 | 13 | 50 | 46 | 37 | 50 | 36 | 0 | 220 | 55 | 33 | 1130 | 53 | 0 | 50 | 25.5 | 34 | 107 | 0 | 0 | 0 | 1224 | 0 | 150 | 8 | 260 | 300 | 305 | 51 | 0 | 220 | 5 | 79 | 90 | 188 | 66 | 19 | 104 | 168 | 52.2 | 0 | 21 | 250 | 400 | 393 | 41 | 30 | 0 | 0 | 16 | 0 | 41 | 20 | 141 | 0 | 126 | 17 | 95 | 0 | 163 | 0 | 0 | 0 | 12 | 9399.62 | 719 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 500 | 17 | 0 | 0 | 1316.91 | 0 | 0 | 0 | 57 | 70 | 0 | 0 | 21 | 8 | 0 | 0 | 17 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 156 | 50 | 115 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 115 | 220 | 0 | 850 | 570 | 17 | 5870.91 | 15270.53 | 105.3
23:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 325 | 35 | 0 | 35 | 141 | 81 | 15 | 55 | 90 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 490 | 109 | 16 | 37 | 0 | 14 | 50 | 46 | 18 | 50 | 36 | 0 | 222 | 45 | 31 | 1130 | 53 | 0 | 50 | 25.5 | 34 | 150 | 0 | 0 | 0 | 1224 | 0 | 140 | 0 | 260 | 300 | 280 | 51 | 0 | 220 | 0 | 60 | 91 | 189 | 66 | 19 | 104 | 166 | 52.2 | 0 | 21 | 245 | 400 | 394 | 41 | 30 | 0 | 0 | 16 | 0 | 42 | 27 | 141 | 0 | 126 | 17 | 87 | 0 | 162 | 0 | 0 | 0 | 12 | 9219.62 | 671 | 0 | 0 | 19 | 25 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 500 | 0 | 0 | 0 | 1305.89 | 0 | 0 | 0 | 57 | 70 | 0 | 50 | 21 | 8 | 0 | 0 | 17 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 156 | 51 | 115 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 117 | 220 | 0 | 850 | 570 | 17 | 5883.89 | 15103.51 | 105.28
Total KWH | 0 | 1420800 | 604320 | 0 | 0 | 0 | 0 | 0 | 8874000 | 0 | 6947581 | 395280 | 0 | 554256 | 2031360 | 989084 | 281378 | 406162 | 1183680 | 0 | 0 | 0 | 0 | 350539 | 236482 | 1991000 | 0 | 182664 | 2486400 | 107200 | 458280 | 0 | 10272727.27 | 2246891 | 383891 | 655680 | 0 | 240480 | 433653 | 695184 | 253974 | 631680 | 659520 | 17520 | 5353982 | 1368291 | 549600 | 19956363.64 | 1057164 | 0 | 1126080 | 301941 | 835527 | 4309833 | 0 | 0 | 0 | 28063634 | 87075 | 2191273 | 401455 | 6167500 | 7541600 | 6456000 | 1225160 | 0 | 5247000 | 289152 | 854400 | 2138913 | 4332480 | 515760 | 454140 | 2338140 | 3365760 | 991810 | 469200 | 680256 | 6037000 | 9565800 | 9257000 | 990000 | 718560 | 0 | 56223 | 401664 | 0 | 1097280 | 635424 | 3229000 | 0 | 2734820 | 215640 | 1593600 | 79434 | 2599200 | 0 | 8400 | 227560 | 290880 | 194398640.91 | 20072000 | 0 | 0 | 117120 | 661504 | 0 | 0 | 0 | 0 | 0 | 469728 | 433440 | 10072732 | 72000 | 0 | 0 | 29262909 | 0 | 0 | 0 | 388704 | 826368 | 0 | 298736 | 271123 | 174029 | 301256 | 473632 | 152630 | 0 | 178512 | 3573364 | 0 | 0 | 0 | 0 | 0 | 8189672 | 0 | 15600 | 3883000 | 1224436 | 1997337 | 142803 | 816825 | 0 | 0 | 0 | 34228.68 | 670320 | 3903 | 391872 | 6742000 | 2759000 | 5369920 | 0 | 19658182 | 14050909.09 | 441600 | 134191394.77 | 328590035.68

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-09-2026
Power Supply Scenario
| Day Peak Generation |  |  | 13583.24 | MW | 12:00 Hr. | Energy Generated |  |  | 328.59 |  | MKWHr.
| Day Peak Demand |  |  | 13653.24 | MW | 12:00 Hr. | Energy Unserverd |  |  | 16.748 |  | MKWHr.
| Evening Peak Generation |  |  | 15135.91 | MW | 20:00 Hr. | Energy Demand |  |  | 345.338 |  | MKWHr.
| Evening Peak Demand |  |  | 15510.71 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34 |  | °C
| Minimum Generation of the Day |  |  | 12573.54 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 865.61 |  | MMCFD
| Maximum Generation of the Day |  |  | 15270.53 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 7.4422 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 28.8873 | 0 | 10.7033 | 0 | 0 | 0.18266 | 0 | 0 | 39.7732 | Gas | 118.2261 | Gas | 412272622.5559
| Chattogram Zone |  |  | 4.8594 | 48.02 | 10.6495 | 0 | 5.354 | 0.10459 | 0 | 0.24048 | 69.228 | Coal | 103.6513 | Coal | 723163317.0202
| Cumilla Zone |  |  | 29.9209 | 0 | 11.9041 | 0 | 0 | 0.4692 | 3.3658 | 0 | 45.66 | HFO | 45.0358 | HFO | 914361582.4
| Mymensingh Zone |  |  | 0 | 0 | 4.6993 | 0 | 0 | 0.31539 | 0 | 0 | 5.0147 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.6665 | 0 | 0 | 0 | 0 | 0.056223 | 0 | 0 | 34.7228 | Hydro | 5.354 | Hydro | 535398.2
| Khulna Zone |  |  | 0 | 10.0727 | 1.3204 | 0 | 0 | 0.43344 | 20.072 | 0 | 31.8985 | Solar | 3.3818 | Solar | 53422620.6348
| Barishal Zone |  |  | 8.1289 | 40.4511 | 0.83347 | 0 | 0 | 0.003903 | 0 | 0 | 49.4174 | Import | 52.7007 | Import | 338131120.59
| Rajshahi Zone |  |  | 11.763 | 0 | 2.1116 | 0 | 0 | 0.969 | 29.2629 | 0 | 44.1065 | Wind | 0.24048 | Wind | 3537460.8
| Rangpur Zone |  |  | 0 | 5.1074 | 2.8142 | 0 | 0 | 0.84735 | 0 | 0 | 8.7689
| Total |  |  | 118.2261 | 103.6513 | 45.0358 | 0 | 5.354 | 3.3818 | 52.7007 | 0.24048 | 328.59
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 412272622.5559 |  | Hydro | 535398.2
|  |  |  | Coal | 723163317.0202 |  | Solar | 53422620.6348
|  |  |  | HFO | 914361582.4 |  | Import | 338131120.59
|  |  |  | HSD | 0 |  | Wind | 3537460.8
[5 empty] | Total: | 244,54,24,122 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.072 | Peak Hr Flow | 766.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 30712581.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.2629 | Peak Hr Flow | 1321.29 MW at 20:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1226 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.3658 | Peak Hr Flow | 150.00 MW at 20:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2000 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.7007 | Peak Hr Flow | 2237.29 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5399
|  |  |  | Chattogram |  | 0 |  | 1353
|  |  |  | Cumilla |  | 0 |  | 1460
|  |  |  | Mymensingh |  | 31 |  | 1287
|  |  |  | Sylhet |  | 0 |  | 661
|  |  |  | Khulna |  | 144 |  | 1793
|  |  |  | Barishal |  | 0 |  | 472
|  |  |  | Rajshahi |  | 27 |  | 1469
|  |  |  | Rangpur |  | 12 |  | 970
|  |  |  | Total |  | 214 |  | 14864
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 54
|  |  |  | Total Unavailable Capacity |  |  |  | 354
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:04 | Ghatail 132/33kV S/S T-2 LT is restored.
|  | 08:22 | Tangail 132/33kV S/S RPCL-2 is restored.
|  | 08:23 | Mymensingh RPCL-Tangail 132kV Ckt-2 is restored.
| 09:08 | 12:42 | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by New Tongi grid substations (Tower erection work)
| 09:29 |  | Kushtia 132/33kV S/S 132 KV Bus-B Project Work S/D Due to PT shifting of Bus-B at
meherpur project
| 09:35 | 16:25 | Bheramara P/S-Kushtia 132 kV Ckt-1 Project Work S/D from Kushtia 132/33kV end Due to Pt
shifting of Bus B at meherpur project and from Bheramara 230/132kV end Due to Project
Work
| 09:40 | 11:54 | Savar 132/33kV S/S Bus-A Scheduled S/D Due to Red hot maintenance | [7 empty] | 35.0MW load
interrup.
| 09:57 | 10:40 | Hathazari-Raozan 230kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end Due to Relay
panel replaced work
| 10:50 | 11:34 | Hathazari 230/132/33kV S/S MT-01 HT Scheduled S/D Due to Relay panel replaced work
|  | 10:56 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 is restored.
|  | 10:56 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-2 is restored.
|  | 10:57 | Sirajganj-Sreepur 230 kV Ckt-1 is restored.
|  | 10:58 | Ashuganj-Sreepur 230 kV Ckt-2 is restored.
|  | 11:05 | Ghorasal-Tongi 230kV Ckt-2 is restored.
|  | 11:05 | Ghorasal-Tongi 230kV Ckt-1 is restored.
| 11:21 | 12:32 | Jhenaidah 132/33kV S/S Transformer T-3 LT Forced S/D Due to Redhot maintenance | [7 empty] | 20.0MW load
interrup.
| 11:22 | 12:31 | Jhenaidah 132/33kV S/S Transformer T-3 HT Forced S/D
| 13:07 | 14:15 | Bheramara(GK) 132/33kV S/S TR-2 LT Tripped showing OC/EF relays Due to Bheramara 33kV pbs
Feeder Source side Isolator Crack
| 13:07 | 14:15 | Bheramara(GK) 132/33kV S/S TR-1 LT Tripped showing OC/EF relays Due to Bheramara 33kV pbs
Feeder Source side Isolator Crack
| 15:19 | 19:47 | Barishal 230/132kV S/S ATR-2 HT Tripped showing BFP relays Due to OLTC PRD Trip
| 15:19 | 19:45 | Barishal 230/132kV S/S ATR-2 LT Tripped showing BFP relays Due to OLTC PRD TRIP
|  | 16:25 | Kasba 132/33kV S/S TR-2 HT is restored.
| 16:38 | 17:37 | Bheramara(GK) 132/33kV S/S TR-2 LT Scheduled S/D Due to Bheramara 33 kV PBS (B phase)
Isolator Crack Down
| 16:39 | 17:35 | Bheramara(GK) 132/33kV S/S TR-2 HT Scheduled S/D Due to Bheramara 33 kV PBS (B phase)
Isolator Crack Down
|  | 17:54 | Fenchuganj-Sreemangal 132kV Ckt-1 is restored.
| 20:00 |  | Evening Peak Generation: 15136 MW.
|  | 21:14 | Maniknagar-Siddhirganj 230kV Ckt-2 is restored.
|  | 21:15 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT is restored.
| 01:16 |  | Ashuganj South 360 MW CCPP was shutdown due to offline wash purposes
| 05:42 |  | Lalmonirhat-Rangpur 132 kV Ckt-2 Project Work S/D from Lalmonirhat 132/33kV end. and from
Rangpur 132/33kV end Due to Gantry Structure Erection Work.
| 06:13 |  | Rangpur-Saidpur 132kV Ckt-1 Project Work S/D from Rangpur 132/33kV end Due to Gantry
structure erection work
| 06:15 |  | Rangpur - Taraganj 132kV Ckt-1 Project Work S/D from Taraganj 132/33kV end Due to PGNS
Project under PGCB (G2G) work
| 07:09 |  | Fenchuganj-Sreemangal 132kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
G2G project work
| 07:19 |  | Siddhirganj 230/132kV S/S 335MW EGCB 1 Scheduled S/D Due to Maintenance Work for EGCB
end.
| 07:19 |  | Sylhet_(South) 132/33kV S/S Trafo-2 HT Scheduled S/D Due to 33kv busbar maintenance | [7 empty] | 16.0MW load
interrup.
| 07:20 |  | Sylhet_(South) 132/33kV S/S Trafo-2 LT Scheduled S/D Due to 33kv busbar maintenance | [7 empty] | 16.0MW load
interrup.
| 07:24 |  | Fenchuganj-Sreemangal 132kV Ckt-2 Project Work S/D from Sreemongol 132/33kV end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-09-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 393 | 8874000 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 281378 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 98 | 1991000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 236482 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 395280 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 141 | 2031360 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 406162 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 350539 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 5.5 | 107200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 458280 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 604320 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 81 | 989084 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 35 | 554256 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1420800 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1183680 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 182664 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 10272727.27 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 333 | 6947581 | -
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 2486400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2227.92 | 39773193.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 301941 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 87075 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 1126080 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 219 | 5353982 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 82 | 4309833 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 835527 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 46 | 695184 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 433653 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 631680 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 34 | 549600 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 44 | 655680 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 17520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 383891 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 18 | 253974 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 72 | 1368291 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 659520 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 105 | 2246891 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 55 | 1057164 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28063634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 9 | 240480 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 900 | 19956363.64 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3063.5 | 69227963.64
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 205 | 5247000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 300 | 7541600 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 285 | 6456000 | FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 280 | 6167500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 20 | 289152 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 401455 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1225160 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 2191273 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 680256 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 2138913 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 188 | 4332480 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 150 | 3365760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 991810 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 454140 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 104 | 2338140 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 63 | 515760 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 854400 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 469200 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 2111.2 | 45659999
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 79434 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 2599200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 94 | 1593600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 227560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 290880 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 215640 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 286 | 5014714
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 56223 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 41 | 990000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 718560 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under Maintenance
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 141 | 3229000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 25 | 635424 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1097280 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 126 | 2734820 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 401664 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 255 | 6037000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 380 | 9257000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9565800 | Machine Problem
Sylhet Area Total |  |  |  |  | 2325 | 1500 | 34722771
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 766 | 20072000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 117120 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 41 | 661504 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 72000 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 469728 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 433440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 500 | 10072732 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1391 | 31898524
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 850 | 19658182 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 391872 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2759000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 570 | 14050909.09 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5369920 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 441600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6742000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3903 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2127 | 49417386.09
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 301256 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 271123 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 155 | 3573364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 365 | 8189672 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 17 | 152630 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 174029 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 298736 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 826368 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 57 | 388704 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 15600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1321.29 | 29262909 | Coal shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 178512 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 473632 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2015.29 | 44106535
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1224436 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 157 | 3883000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 816825 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34228.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1997337 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 142803 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 670320 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 414 | 8768949.68
Eastern Grid Total |  |  |  |  | 17427.666 | 9188.62 | 194398640.91
Western Grid Total |  |  |  |  | 11731.125 | 5947.29 | 134191394.77
National Grid Total |  |  |  |  | 29158.791 | 15135.91 | 328590035.68
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-09-2026
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10128.52 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4520.8 | MW
i) Dhaka area |  |  | 5398.92 |  | MW | i) Khulna area |  |  |  | 1649 | MW
ii) Chattogram area |  |  | 1352.6 |  | MW | ii) Barishal area |  |  |  | 471.6 | MW
iii) Cumilla area |  |  | 1460 |  | MW | iii) Rajshahi area |  |  |  | 1442.2 | MW
iv) Mymensingh area |  |  | 1256 |  | MW | iv) Rangpur area |  |  |  | 958 | MW
v) Sylhet area |  |  | 661 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14649.32 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Halishahar | 72 | 01:00 | 133 | Narinda | 48 | 00:00 | 199 | Ullon | 59 | 13:00
2 | AKSML | 156 | 01:00 | 68 | HaripurSBU | 112 | 07:00 | 134 | Narshingdi | 197 | 22:00 | 200 | Uttara | 88 | 18:30
3 | Aftabnagar | 42 | 13:00 | 69 | Hasnabad | 85 | 23:00 | 135 | Natore | 133 | 19:30 | 201 | UttaraNew | 52 | 13:00
4 | Agargaon | 108 | 13:00 | 70 | Hathazari | 87 | 22:00 | 136 | Nawabganj | 62.1 | 22:00 | 202 | Zigatola | 92 | 13:00
5 | Agrabad | 58 | 02:00 | 71 | Hatirjheel | 58 | 16:00 | 137 | Netrakona | 146 | 20:00
6 | Amnura | 29 | 00:00 | 72 | Ishurdi | 76 | 19:00 | 138 | New | 80 | 00:00
7 | Araihazar | 64 | 21:00 | 73 | Jaldhaka | 80 | 20:00 | 139 | Niamatpur | 60 | 22:00
8 | Ashuganj | 81 | 00:00 | 74 | Jamalpur | 135 | 19:30 | 140 | Noapara | 43 | 00:00
9 | BSRM | 196 | 22:00 | 75 | Jashore | 140 | 21:00 | 141 | PHP | 10 | 00:00
10 | Bagerhat | 89 | 19:00 | 76 | Jhenaidah | 92 | 19:00 | 142 | Pabna | 90 | 21:00
11 | Bajitpur | 101 | 19:00 | 77 | Joydebpur | 145 | 22:00 | 143 | Palashbari | 124 | 20:00
12 | Bakerganj | 14 | 18:30 | 78 | Joypurhat | 54 | 19:00 | 144 | Panchagarh | 67 | 19:00
13 | Bakulia | 83 | 19:30 | 79 | Juldah | 16 | 11:00 | 145 | Patiya | 20 | 18:30
14 | Banani | 38 | 18:30 | 80 | KSRM | 15 | 04:00 | 146 | Patnitala | 30 | 19:30
15 | Bangabhaban | 4 | 11:00 | 81 | Kabirpur | 252 | 12:00 | 147 | Patuakhali | 68 | 22:00
16 | Barapukuria | 61 | 04:00 | 82 | Kachua | 100 | 19:00 | 148 | Payra | 34 | 21:00
17 | Barguna | 22 | 21:00 | 83 | Kaliganj | 40 | 19:00 | 149 | Postogola | 56 | 01:00
18 | Barishal | 94 | 12:00 | 84 | Kallyanpur | 123 | 14:00 | 150 | Pubail | 45 | 23:00
19 | Barishal-230 | 130 | 06:00 | 85 | Kalurghat | 31 | 00:00 | 151 | Purbachal | 22 | 18:30
20 | Baroaulia | 52 | 22:00 | 86 | Kamrangirchar | 71 | 01:00 | 152 | Purbasadipur | 120 | 23:00
21 | Baroirhat | 61 | 18:30 | 87 | Kaptai | N/A | N/A | 153 | Rahanpur | 37 | 19:30
22 | Bashundhara | 206 | 18:30 | 88 | Kasba | 40 | 19:00 | 154 | Rahim | 53 | 01:00
23 | BashundharaCement | 5 | 00:00 | 89 | Kazla | 109 | 00:00 | 155 | Rajbari | 85 | 19:00
24 | Beanibazar | 82 | 18:30 | 90 | Keranigonj | 76 | 13:00 | 156 | Rajendrapur | 123 | 19:00
25 | Benapole | 72 | 21:00 | 91 | Khagrachori | 30 | 19:30 | 157 | Rajshahi | 110 | 00:00
26 | Bhaluka | 164 | 00:00 | 92 | Khulna | 60 | 19:00 | 158 | Rajshahi-230 | 110 | 13:00
27 | Bhandaria | 57 | 21:00 | 93 | Khulshi | 168 | 19:00 | 159 | Ramganj | 116 | 18:30
28 | Bhangura | 38 | 18:30 | 94 | Kishoreganj | 139 | 19:00 | 160 | Rampur | 40 | 18:30
29 | Bheramara(GK) | 69 | 18:30 | 95 | Kodda | 307 | 12:00 | 161 | Rangamati | 15 | 19:00
30 | Bhulta | 214 | 22:00 | 96 | Kulaura | 55 | 19:00 | 162 | Rangpur | 128 | 13:00
31 | Bog-Sherpur | 70 | 19:30 | 97 | Kurigram | 64 | 18:30 | 163 | Ruppur | 4 | 09:00
32 | Bogura | 204 | 01:00 | 98 | Kushtia | 140 | 00:00 | 164 | SSM | 13 | 06:00
33 | Borhanuddin | 77 | 22:00 | 99 | Laksam | 28 | 23:00 | 165 | Saidpur | 86 | 00:00
34 | Brahmanbaria | 148 | 21:00 | 100 | Lakshmipur | 52 | 21:00 | 166 | Santhia | 34 | 18:30
35 | Cantonment | 122 | 12:00 | 101 | Lalbag | 72 | 12:00 | 167 | Satkhira | 129 | 00:00
36 | Chandina | 19 | 21:00 | 102 | Lalmonirhat | 66 | 18:30 | 168 | Satmasjid | 101 | 13:00
37 | Chandpur | 90 | 21:00 | 103 | MI_Cement | 9.5 | 23:00 | 169 | Savar | 178 | 13:00
38 | Chandraghona | 32 | 18:30 | 104 | Madanganj | 57 | 23:00 | 170 | SevenRings | 20.38 | 04:00
39 | Chapai | 64 | 20:00 | 105 | Madaripur | 98 | 00:00 | 171 | ShahCement | 21 | 00:00
40 | Charfasson | 31 | 21:00 | 106 | Madartek | 93 | 13:00 | 172 | Shahjadpur | 73 | 20:00
41 | Charsaidpur | 42 | 04:00 | 107 | Madunaghat | 49 | 00:00 | 173 | Shahjibazar | 133 | 21:00
42 | Chauddagram | 72 | 18:30 | 108 | Magura | 69 | 19:00 | 174 | Shahmirpur | 53 | 19:00
43 | Chhatak | 41 | 18:00 | 109 | Mahasthangarh | 68 | 23:00 | 175 | Shariatpur | 85 | 19:30
44 | Chowmuhani | 141 | 21:00 | 110 | Maijdee | 35 | 19:30 | 176 | Sherpur | 162 | 00:00
45 | Chuadanga | 116 | 13:00 | 111 | Manikganj | 144 | 20:00 | 177 | Shikalbaha | 28.5 | 23:00
46 | Coxsbazar | 138 | 19:00 | 112 | Maniknagar | 71 | 00:00 | 178 | Shitalakhya | 59.7 | 13:00
47 | Cumilla(N) | 129 | 22:00 | 113 | Matarbari | 55 | 19:00 | 179 | Sholosohor | 41 | 22:00
48 | Cumilla(S) | 166 | 23:00 | 114 | Matuail | 70 | 00:00 | 180 | Shomvuganj | 54 | 18:00
49 | Daganbhuiyan | 38 | 21:00 | 115 | Metrorail_Motijheel | 45 | 18:00 | 181 | Shyampur | 158 | 00:00
50 | Daudkandi | 138 | 21:00 | 116 | Metrorail_Uttara | 0 | 00:00 | 182 | Siddhirganj | 113 | 00:00
51 | DhakaUniversity | 46 | 12:00 | 117 | Millgate | 68 | 01:00 | 183 | Sirajganj | 112 | 00:00
52 | Dhamrai | 104 | 19:30 | 118 | Mirpur | 141 | 14:00 | 184 | Sitakunda | 12 | 18:30
53 | Dhanmondi | 90 | 18:30 | 119 | Mirsorai | 45 | 05:00 | 185 | Sonargaon | 137 | 23:00
54 | Dohazari | 105 | 22:00 | 120 | Mirzapur | 52 | 19:00 | 186 | Sreemongol | 86 | 19:30
55 | Faridpur | 175 | 00:00 | 121 | Mithapukur | 76 | 19:00 | 187 | Sreepur | 123 | 19:00
56 | Fatullah | 106 | 00:00 | 122 | Modern | N/A | N/A | 188 | Srinagar | 50.3 | 22:00
57 | Fenchuganj | 42 | 21:00 | 123 | Mogbazar | 61.1 | 13:00 | 189 | Sunamganj | 63 | 21:00
58 | Feni | 99 | 20:00 | 124 | Mongla | 29 | 00:00 | 190 | Sylhet | 107 | 18:30
59 | GPH | 1 | 00:00 | 125 | Motijheel | 39 | 18:30 | 191 | Sylhet_(South) | 75 | 00:00
60 | Ghatail | 93 | 19:30 | 126 | Muktagacha | 41 | 00:00 | 192 | TK | 0 | 00:00
61 | Ghorashal | 0 | 00:00 | 127 | Munshiganj | 111 | 23:00 | 193 | Tangail | 180 | 21:00
62 | Ghorashal-230 | 107 | 19:30 | 128 | Muradnagar | 60 | 20:00 | 194 | Taraganj | 31 | 19:00
63 | Goalpara | 39 | 21:00 | 129 | Mymensingh | 144 | 00:00 | 195 | Tasnim | 44 | 02:00
64 | Gollamari | 98 | 00:00 | 130 | Nabinagar | 96 | 12:00 | 196 | Thakurgaon | 106 | 19:30
65 | Gopalganj | 112 | 19:00 | 131 | Naogaon | 107 | 20:00 | 197 | Tongi | 127 | 00:00
66 | Gulshan | 86 | 15:00 | 132 | Narail | 62 | 18:30 | 198 | Ullahpara | 38 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-09-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14741.61 | 1768 |  | 16589.61
1:00 | 13593.68 | 2222 |  | 15915.68
2:00 | 13472.58 | 2209 |  | 15780.58
3:00 | 13384.59 | 2108 |  | 15587.59
4:00 | 13354.34 | 1901 |  | 15341.34
5:00 | 13117.62 | 1767 |  | 14964.62
6:00 | 12754.75 | 914 |  | 13709.75
7:00 | 12786.91 | 536 |  | 13346.91
8:00 | 12613.94 | 344 |  | 12972.94
9:00 | 12634.07 | 130 |  | 12770.07
10:00 | 12663.52 | 80 |  | 12747.52
11:00 | 12844.38 | 85 |  | 12933.38
12:00 | 13583.24 | 67 |  | 13653.24
13:00 | 13864.21 | 387 |  | 14268.21
14:00 | 13349.61 | 80 |  | 13433.61
15:00 | 13318.7 | 20 |  | 13339.7
16:00 | 12845.63 | 0 |  | 12845.63
17:00 | 12573.54 | 0 |  | 12573.54
18:00 | 12598.35 | 0 |  | 12598.35
19:00 | 14649.61 | 90 |  | 14743.61
19:30 | 14971.6 | 85 |  | 15060.43
20:00 | 15135.91 | 214 |  | 15359.91
21:00 | 15109.71 | 384 |  | 15510.71
22:00 | 15270.53 | 679 |  | 15980.53
23:00 | 15103.51 | 763 |  | 15900.51
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-09-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8892.62 | 5848.99 | 14741.61 | DAILY GENERATION CURVE
00:30 | 8452.16 | 5715.485 | 14167.645
01:00 | 8011.7 | 5581.98 | 13593.68 | 04-09-2026
01:30 | 8009.7 | 5523.43 | 13533.13
02:00 | 8007.7 | 5464.88 | 13472.58
02:30 | 7946.2 | 5482.385 | 13428.585
03:00 | 7884.7 | 5499.89 | 13384.59
03:30 | 7870.2 | 5499.265 | 13369.465
04:00 | 7855.7 | 5498.64 | 13354.34
04:30 | 7744.6 | 5491.38 | 13235.98
05:00 | 7633.5 | 5484.12 | 13117.62
05:30 | 7469.355 | 5466.83 | 12936.185
06:00 | 7305.21 | 5449.54 | 12754.75
06:30 | 7378.385 | 5392.445 | 12770.83
07:00 | 7451.56 | 5335.35 | 12786.91
07:30 | 7522.22 | 5178.205 | 12700.425
08:00 | 7592.88 | 5021.06 | 12613.94
08:30 | 7619.8 | 5004.205 | 12624.005
09:00 | 7646.72 | 4987.35 | 12634.07
09:30 | 7600.495 | 5048.3 | 12648.795
10:00 | 7554.27 | 5109.25 | 12663.52
10:30 | 7645.97 | 5107.98 | 12753.95
11:00 | 7737.67 | 5106.71 | 12844.38
11:30 | 7951.34 | 5262.47 | 13213.81
12:00 | 8165.01 | 5418.23 | 13583.24
12:30 | 8147.14 | 5576.585 | 13723.725
13:00 | 8129.27 | 5734.94 | 13864.21
13:30 | 7924.79 | 5682.12 | 13606.91
14:00 | 7720.31 | 5629.3 | 13349.61
14:30 | 7705.375 | 5628.78 | 13334.155
15:00 | 7690.44 | 5628.26 | 13318.7
15:30 | 7631.97 | 5450.195 | 13082.165
16:00 | 7573.5 | 5272.13 | 12845.63
16:30 | 7395.485 | 5314.1 | 12709.585
17:00 | 7217.47 | 5356.07 | 12573.54
17:30 | 7137.565 | 5448.38 | 12585.945
18:00 | 7057.66 | 5540.69 | 12598.35
18:30 | 7898.29 | 5725.69 | 13623.98
19:00 | 8738.92 | 5910.69 | 14649.61
19:30 | 9100.62 | 5870.98 | 14971.6
20:00 | 9188.62 | 5947.29 | 15135.91
20:30 | 9207.12 | 5915.69 | 15122.81 |  | Executive Engineer
21:00 | 9225.62 | 5884.09 | 15109.71 |  | Network Operation Division
21:30 | 9312.62 | 5877.5 | 15190.12
22:00 | 9399.62 | 5870.91 | 15270.53
22:30 | 9309.62 | 5877.4 | 15187.02
23:00 | 9219.62 | 5883.89 | 15103.51

## En-Curve
QF-LDC-12
Date | 04-09-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3819 | 1167.5 | 788 | 0 | 152 | 1402.99 | 222 | 4403 | 0 | 702.42 | 2069.7 | 0 | 0 | 15 | 1768 | DAILY ENERGY CURVE
00:30 | 3716 | 1224.5 | 787.5 | 0 | 149 | 1359.985 | 222 | 4325 | 0 | 620.21 | 1738.45 | 0 | 0 | 25 | 1995 | 04-09-2026
01:00 | 3613 | 1281.5 | 787 | 0 | 146 | 1316.98 | 222 | 4247 | 0 | 538 | 1407.2 | 0 | 0 | 35 | 2222
01:30 | 3581.5 | 1352.5 | 787.5 | 0 | 146 | 1314.93 | 222 | 4248 | 0 | 479 | 1377.7 | 0 | 0 | 24 | 2215.5 | Energy Generated | 328.59 |  | MKWHr
02:00 | 3550 | 1423.5 | 788 | 0 | 146 | 1312.88 | 222 | 4249 | 0 | 420 | 1348.2 | 0 | 0 | 13 | 2209 | Energy not Served | 16.748 |  | MKWHr
02:30 | 3573.5 | 1370.5 | 812.5 | 0 | 146 | 1309.885 | 222 | 4242.5 | 0 | 401 | 1337.7 | 0 | 0 | 13 | 2158.5 | Total Energy Requirement | 345.338 |  | MKWHr
03:00 | 3597 | 1317.5 | 837 | 0 | 146 | 1306.89 | 222 | 4236 | 0 | 382 | 1327.2 | 0 | 0 | 13 | 2108
03:30 | 3604.5 | 1331.5 | 837.5 | 0 | 147 | 1310.765 | 222 | 4239.5 | 0 | 368.5 | 1295.2 | 0 | 0 | 13 | 2004.5
04:00 | 3612 | 1345.5 | 838 | 0 | 148 | 1314.64 | 222 | 4243 | 0 | 355 | 1263.2 | 0 | 0 | 13 | 1901
04:30 | 3582.5 | 1313.5 | 862 | 0 | 145 | 1314.88 | 221 | 4247.5 | 0 | 331 | 1207.6 | 0 | 0 | 11 | 1834
05:00 | 3553 | 1281.5 | 886 | 0 | 142 | 1315.12 | 220 | 4252 | 0 | 307 | 1152 | 0 | 0 | 9 | 1767
05:30 | 3495.5 | 1203 | 888.5 | 0 | 140 | 1313.78 | 219.5 | 4220 | 2.905 | 304.5 | 1142.5 | 0 | 0 | 6 | 1340.5
06:00 | 3438 | 1124.5 | 891 | 0 | 138 | 1312.44 | 219 | 4188 | 5.81 | 302 | 1133 | 0 | 0 | 3 | 914
06:30 | 3393 | 1156 | 890.5 | 0 | 132 | 1309.37 | 219 | 4187.5 | 29.46 | 302 | 1145.5 | 0 | 0 | 6.5 | 725
07:00 | 3348 | 1187.5 | 890 | 0 | 126 | 1306.3 | 219 | 4187 | 53.11 | 302 | 1158 | 0 | 0 | 10 | 536
07:30 | 3376.5 | 1278.75 | 893 | 0 | 121 | 1230.15 | 219 | 4078 | 102.525 | 295 | 1101.5 | 0 | 0 | 5 | 440
08:00 | 3405 | 1370 | 896 | 0 | 116 | 1154 | 219 | 3969 | 151.94 | 288 | 1045 | 0 | 0 | 0 | 344
08:30 | 3424.5 | 1394 | 896.5 | 0 | 120 | 1036.825 | 219 | 3952.5 | 241.48 | 288 | 1050.2 | 0 | 0 | 1 | 237
09:00 | 3444 | 1418 | 897 | 0 | 124 | 919.65 | 219 | 3936 | 331.02 | 288 | 1055.4 | 0 | 0 | 2 | 130
09:30 | 3445 | 1401.5 | 896.5 | 0 | 127 | 914.86 | 219.5 | 3941.5 | 384.735 | 284.5 | 1031.2 | 0 | 0 | 2.5 | 105
10:00 | 3446 | 1385 | 896 | 0 | 130 | 910.07 | 220 | 3947 | 438.45 | 281 | 1007 | 0 | 0 | 3 | 80
10:30 | 3443 | 1436.5 | 896 | 0 | 131 | 912.35 | 220.5 | 3944 | 455.6 | 315 | 997.5 | 0 | 0 | 2.5 | 82.5
11:00 | 3440 | 1488 | 896 | 0 | 132 | 914.63 | 221 | 3941 | 472.75 | 349 | 988 | 0 | 0 | 2 | 85
11:30 | 3534 | 1502 | 896 | 0 | 135 | 920.585 | 221.5 | 4078 | 489.625 | 357 | 1079.1 | 0 | 0 | 1 | 76
12:00 | 3628 | 1516 | 896 | 0 | 138 | 926.54 | 222 | 4215 | 506.5 | 365 | 1170.2 | 0 | 0 | 0 | 67
12:30 | 3615.5 | 1445 | 896 | 0 | 142 | 1060.21 | 222 | 4235 | 529.815 | 376 | 1201.2 | 0 | 0 | 1 | 227
13:00 | 3603 | 1374 | 896 | 0 | 146 | 1193.88 | 222 | 4255 | 553.13 | 387 | 1232.2 | 0 | 0 | 2 | 387
13:30 | 3486 | 1304.5 | 880.5 | 0 | 147 | 1242.615 | 222 | 4230 | 443.095 | 387 | 1263.2 | 0 | 0 | 1 | 233.5
14:00 | 3369 | 1235 | 865 | 0 | 148 | 1291.35 | 222 | 4205 | 333.06 | 387 | 1294.2 | 0 | 0 | 0 | 80
14:30 | 3391.5 | 1270.3 | 865 | 0 | 145 | 1241.79 | 222 | 4232 | 310.865 | 335.5 | 1306.7 | 0 | 0 | 13.5 | 50
15:00 | 3414 | 1305.6 | 865 | 0 | 142 | 1192.23 | 222 | 4259 | 288.67 | 284 | 1319.2 | 0 | 0 | 27 | 20
15:30 | 3439 | 1333.1 | 865 | 0 | 142 | 1079.67 | 222 | 4232.5 | 245.795 | 270 | 1228.6 | 0 | 0 | 24.5 | 10
16:00 | 3464 | 1360.6 | 865 | 0 | 142 | 967.11 | 222 | 4206 | 202.92 | 256 | 1138 | 0 | 0 | 22 | 0
16:30 | 3450 | 1292.6 | 851 | 0 | 133 | 1025.18 | 222 | 4203.5 | 145.805 | 249 | 1121 | 0 | 0 | 16.5 | 0
17:00 | 3436 | 1224.6 | 837 | 0 | 124 | 1083.25 | 222 | 4201 | 88.69 | 242 | 1104 | 0 | 0 | 11 | 0
17:30 | 3365 | 1220.8 | 837 | 0 | 121 | 1191.335 | 221.5 | 4155.5 | 47.31 | 283.5 | 1132 | 0 | 0 | 11 | 0
18:00 | 3294 | 1217 | 837 | 0 | 118 | 1299.42 | 221 | 4110 | 5.93 | 325 | 1160 | 0 | 0 | 11 | 0
18:30 | 3444 | 1362.75 | 802 | 0 | 133 | 1307.055 | 220.5 | 4261 | 2.965 | 477.21 | 1603 | 0 | 0 | 10.5 | 45
19:00 | 3594 | 1508.5 | 767 | 0 | 148 | 1314.69 | 220 | 4412 | 0 | 629.42 | 2046 | 0 | 0 | 10 | 90
19:30 | 3602 | 1518.5 | 719 | 0 | 148 | 1313.98 | 216 | 4459 | 0 | 710.42 | 2272.7 | 0 | 0 | 12 | 85
20:00 | 3532 | 1549.5 | 766 | 0 | 150 | 1321.29 | 219 | 4558 | 0 | 712.42 | 2318.7 | 0 | 0 | 9 | 214
20:30 | 3523.5 | 1500 | 742 | 0 | 151 | 1314.69 | 219 | 4635.5 | 0 | 708.42 | 2321.7 | 0 | 0 | 7 | 299
21:00 | 3515 | 1450.5 | 718 | 0 | 152 | 1308.09 | 219 | 4713 | 0 | 704.42 | 2324.7 | 0 | 0 | 5 | 384
21:30 | 3542.5 | 1484.5 | 718.5 | 0 | 160 | 1312.5 | 219.5 | 4750 | 0 | 695.92 | 2297.7 | 0 | 0 | 9 | 531.5
22:00 | 3570 | 1518.5 | 719 | 0 | 168 | 1316.91 | 220 | 4787 | 0 | 687.42 | 2270.7 | 0 | 0 | 13 | 679
22:30 | 3584.5 | 1492.5 | 695 | 0 | 167 | 1311.4 | 221 | 4787.5 | 0 | 721.42 | 2193.2 | 0 | 0 | 13.5 | 721
23:00 | 3599 | 1466.5 | 671 | 0 | 166 | 1305.89 | 222 | 4788 | 0 | 755.42 | 2115.7 | 0 | 0 | 14 | 763
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 04-09-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 99 | 42 | 294 | 180 | 800 | 568 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 110 | 49 | 322 | 140 | 950 | 608
2:00 | 107 | 46 | 290 | 146 | 858 | 596 |  | Import | 0
3:00 | 106 | 35 | 290 | 128 | 906 | 558
4:00 | 113 | 38 | 310 | 144 | 932 | 556 | Ishurdi-Ghorashal Ckt-2 | Export | 3104581.82
5:00 | 117 | 34 | 326 | 132 | 952 | 540
6:00 | 129 | 39 | 364 | 130 | 998 | 556 |  | Import | 0
7:00 | 175 | 79 | 0 | 0 | 1140 | 592
8:00 | 138 | 65 | 0 | 0 | 928 | 534 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 156 | 82 | 0 | 0 | 1122 | 650
10:00 | 179 | 87 | 0 | 0 | 1216 | 660 |  | Import | 0
11:00 | 114 | 57 | 274 | 142 | 940 | 646
12:00 | 133 | 50 | 350 | 192 | 950 | 680 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 123 | 28 | 350 | 176 | 964 | 606
14:00 | 147 | 41 | 430 | 166 | 1110 | 588 |  | Import | 0
15:00 | 157 | 54 | 430 | 176 | 1164 | 618
16:00 | 148 | 57 | 370 | 170 | 1072 | 648 | Gopalganj-Aminbazar Ckt-1 | Export | 12090000
17:00 | 167 | 51 | 440 | 166 | 1294 | 630
18:00 | 172 | 49 | 480 | 164 | 1348 | 628 |  | Import | 0
18:30 | 152 | 44 | 420 | 170 | 1086 | 622
19:00 | 100 | 24 | 330 | 156 | 890 | 546 | Gopalganj-Aminbazar Ckt-2 | Export | 12120000
19:30 | 85 | 22 | 320 | 166 | 878 | 530
20:00 | 84 | 20 | 290 | 174 | 852 | 554 |  | Import | 0
21:00 | 94 | 33 | 320 | 180 | 812 | 562
22:00 | 91 | 30 | 320 | 190 | 828 | 586 |  | Total Export | 27314581.82
23:00 | 88 | 31 | 310 | 188 | 876 | 588 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-09-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 374 | 05:00 | 366 | 11:00 | Madunaghat | 401 | 06:00 | 396 | 23:00
Amtali | 412 | 03:00 | 410 | 12:00 | Meghnaghat | 380 | 05:00 | 373 | 12:00
Ashuganj | 403 | 3:00 | 391 | 10:00 | Mirsorai | 398 | 05:00 | 388 | 00:00
Bhulta | 393 | 03:00 | 384 | 10:00 | Payra | 415 | 10:00 | 411 | 13:00
Bibiana | 379 | 08:00 | 374 | 22:00 | Rahanpur | 411 | 17:00 | 401 | 20:00
BIPTC | 404 | 01:00 | 398 | 12:00 | Rampal | 395 | 08:00 | 384 | 23:00
Bogura | 397 | 10:00 | 387 | 19:30
Gopalganj | 390 | 06:00 | 384 | 13:00
Kaliakoir | 364 | 03:00 | 354 | 12:00
Korerhat | 398 | 05:00 | 390 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 228 | 04:00 | 221 | 12:00 | Hasnabad | 225 | 18:30 | 220 | 11:00
AKSML | 238 | 08:00 | 232 | 22:00 | Hathazari | 236 | 01:00 | 232 | 14:00
Aminbazar | 229 | 05:00 | 221 | 11:00 | Ishurdi | 236 | 09:00 | 225 | 20:00
Ashuganj | 226 | 05:00 | 219 | 07:00 | Jhenaidah | 227 | 16:00 | 213 | 13:00
Ashuganj-400 | 226 | 05:00 | 219 | 07:00 | Kachua | 230 | 05:00 | 225 | 22:00
Baghabari | 234 | 09:00 | 226 | 19:30 | Kaliakoir | 226 | 03:00 | 219 | 12:00
Barapukuria | 228 | 17:00 | 220 | 07:00 | Keranigonj | 226 | 05:00 | 219 | 12:00
Barapukuria-230 | 228 | 17:00 | 220 | 07:00 | Khulna(S) | 226 | 09:00 | 218 | 13:00
Barapukuria(N) | 230 | 17:00 | 222 | 08:00 | Korerhat | 228 | 05:00 | 223 | 23:00
Barishal | 226 | 18:00 | 221 | 18:30 | Madunaghat | 240 | 19:30 | 235 | 23:00
Bheramara | 235 | 01:00 | 224 | 13:00 | Madunaghat-400 | 241 | 09:00 | 238 | 00:00
Bhulta | 224 | 03:00 | 218 | 12:00 | Maniknagar | 222 | 03:00 | 215 | 12:00
Bibiana | 218 | 15:00 | 213 | 22:00 | Meghnaghat | 230 | 04:00 | 224 | 12:00
BIPTC | 237 | 09:00 | 223 | 19:00 | Meghnaghat-400 | 226 | 06:00 | 221 | 12:00
Birulia | 227 | 03:00 | 221 | 12:00 | Mirsorai | 232 | 18:00 | 228 | 22:00
Bogura | 240 | 17:00 | 234 | 20:00 | Naogaon | 228 | 18:00 | 214 | 20:00
Bogura-400 | 240 | 17:00 | 234 | 19:30 | Purbasadipur | 226 | 17:00 | 217 | 08:00
Borhanuddin | 229 | 16:00 | 226 | 13:00 | Rajshahi | 234 | 10:00 | 222 | 13:00
BSRM | 229 | 08:00 | 224 | 22:00 | Rampal | 225 | 09:00 | 216 | 23:00
Charfasson | 229 | 10:00 | 225 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 229 | 08:00 | 225 | 00:00 | Rampura | 224 | 06:00 | 217 | 12:00
Cumilla(N) | 223 | 03:00 | 218 | 23:00 | Shikalbaha | 239 | 08:00 | 235 | 23:00
Faridpur | 221 | 09:00 | 216 | 22:00 | Shyampur | 225 | 06:00 | 218 | 12:00
Fenchuganj | 216 | 01:00 | 213 | 20:00 | Siddhirganj | 224 | 17:00 | 218 | 12:00
Feni | 226 | 05:00 | 222 | 22:00 | Sirajgonj | 238 | 16:00 | 230 | 08:00
Ghorashal | 230 | 04:00 | 220 | 00:00 | Sreepur | 223 | 01:00 | 205 | 07:00
Ghorashal-230 | 215 | 03:00 | 203 | 07:00 | Tongi | 217 | 09:00 | 208 | 00:00
Gopalganj | 222 | 17:00 | 217 | 22:00
GPH | 234 | 01:00 | 230 | 00:00
Haripur | 223 | 18:00 | 218 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 03:00 | 132 | 12:00 | Madanganj | 131 | 20:00 | 129 | 00:00
Agargaon | 134 | 03:00 | 129 | 12:00 | Madaripur | 130 | 00:00 | 127 | 20:00
Agrabad | 138 | 19:30 | 134 | 12:00 | Madartek | 137 | 05:00 | 131 | 12:00
AKS | 135 | 06:00 | 131 | 19:30 | Madunaghat | 139 | 19:00 | 136 | 01:00
Aminbazar | 132 | 19:00 | 126 | 11:00 | Magura | 137 | 10:00 | 127 | 13:00
Amnura | 135 | 10:00 | 129 | 20:00 | Mahasthangarh | 137 | 17:00 | 131 | 04:00
Araihazar | 129 | 17:00 | 124 | 22:00 | Maijdee | 128 | 01:00 | 126 | 12:00
Ashuganj | 130 | 01:00 | 125 | 07:00 | Manikganj | 128 | 14:00 | 118 | 18:30
Ashuganj-230 | 135 | 03:00 | 130 | 07:00 | Maniknagar | 138 | 03:00 | 130 | 12:00
Bagerhat | 129 | 17:00 | 122 | 19:00 | Matarbari | 130 | 02:00 | 119 | 22:00
Bajitpur | 126 | 05:00 | 120 | 22:00 | Matuail | 134 | 18:00 | 129 | 12:00
Bakerganj | 132 | 06:00 | 129 | 13:00 | Metrorail_Motijheel | 138 | 03:00 | 130 | 11:00
Bakulia | 138 | 02:00 | 134 | 23:00 | Metrorail_Uttara | 131 | 05:00 | 121 | 16:00
Banani | 137 | 03:00 | 131 | 12:00 | Millgate | 132 | 03:00 | 125 | 12:00
Bangabhaban | 138 | 03:00 | 129 | 12:00 | Mirpur | 130 | 05:00 | 125 | 12:00
Barapukuria | 138 | 16:00 | 129 | 07:00 | Mirzapur | 128 | 14:00 | 121 | 18:30
Barguna | 132 | 06:00 | 128 | 22:00 | Mithapukur | 135 | 17:00 | 127 | 08:00
Barishal | 131 | 17:00 | 128 | 00:00 | MI_Cement | 133 | 03:00 | 128 | 12:00
Barishal-230 | 131 | 07:00 | 128 | 19:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 137 | 07:00 | 134 | 12:00 | Mogbazar | 140 | 06:00 | 134 | 12:00
Baroirhat | 133 | 04:00 | 129 | 00:00 | Mongla | 129 | 10:00 | 122 | 19:00
Bashundhara | 137 | 03:00 | 126 | 15:00 | Motijheel | 138 | 03:00 | 129 | 12:00
BashundharaCement | 131 | 21:00 | 129 | 00:00 | Muktagacha | 126 | 16:00 | 115 | 07:00
Beanibazar | 121 | 01:00 | 117 | 18:30 | Munshiganj | 132 | 18:00 | 127 | 00:00
Benapole | 133 | 10:00 | 121 | 13:00 | Muradnagar | 128 | 05:00 | 123 | 22:00
Bhaluka | 133 | 11:00 | 122 | 07:00 | Mymensingh | 126 | 15:00 | 112 | 07:00
Bhandaria | 129 | 08:00 | 124 | 18:30 | Nabinagar | 130 | 05:00 | 123 | 12:00
Bhangura | 134 | 09:00 | 130 | 13:00 | Naogaon | 137 | 17:00 | 129 | 20:00
Bheramara | 138 | 01:00 | 131 | 13:00 | Narail | 138 | 16:00 | 126 | 23:00
Bheramara(GK) | 137 | 09:00 | 130 | 13:00 | Narinda | 138 | 03:00 | 130 | 12:00
Bhulta | 127 | 17:00 | 123 | 22:00 | Narshingdi | 130 | 13:00 | 120 | 22:00
Bhulta-400 | 129 | 05:00 | 124 | 23:00 | Natore | 135 | 09:00 | 129 | 13:00
Birulia | 133 | 03:00 | 129 | 12:00 | Nawabganj | 136 | 03:00 | 131 | 13:00
Bog-Sherpur | 137 | 16:00 | 132 | 20:00 | Netrakona | 122 | 06:00 | 109 | 20:00
Bogura | 138 | 16:00 | 135 | 01:00 | New | 133 | 06:00 | 127 | 12:00
Bogura-230 | 139 | 17:00 | 135 | 04:00 | Niamatpur | 136 | 17:00 | 131 | 22:00
Brahmanbaria | 126 | 01:00 | 122 | 07:00 | Noapara | 133 | 18:00 | 126 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 134 | 03:00 | 129 | 12:00 | Pabna | 135 | 01:00 | 129 | 13:00
Chandina | 131 | 06:00 | 127 | 22:00 | Palashbari | 133 | 17:00 | 127 | 20:00
Chandpur | 135 | 18:30 | 131 | 17:00 | Panchagarh | 137 | 16:00 | 128 | 08:00
Chandraghona | 139 | 08:00 | 137 | 11:00 | Patiya | 138 | 18:30 | 133 | 23:00
Chapai | 135 | 01:00 | 130 | 23:00 | Patnitala | 135 | 17:00 | 130 | 19:30
Charsaidpur | 132 | 17:00 | 128 | 10:00 | Patuakhali | 132 | 07:00 | 128 | 18:30
Chauddagram | 131 | 06:00 | 127 | 22:00 | Payra | 134 | 00:00 | 133 | 15:00
Chhatak | 120 | 01:00 | 114 | 22:00 | PHP | 132 | 01:00 | 130 | 12:00
Chowmuhani | 128 | 00:00 | 127 | 04:00 | Postogola | 134 | 04:00 | 130 | 12:00
Chuadanga | 135 | 10:00 | 124 | 13:00 | Pubail | 130 | 14:00 | 123 | 09:00
Coxsbazar | 126 | 11:00 | 121 | 00:00 | Purbachal | 137 | 03:00 | 132 | 12:00
Cumilla(N) | 130 | 01:00 | 126 | 23:00 | Purbasadipur | 137 | 18:00 | 130 | 08:00
Cumilla(S) | 131 | 04:00 | 124 | 18:30 | Rahanpur | 138 | 17:00 | 134 | 19:30
Daganbhuiyan | 130 | 02:00 | 128 | 22:00 | Rahanpur-400 | 138 | 16:00 | 134 | 19:30
Daudkandi | 127 | 18:00 | 122 | 22:00 | Rahim | 133 | 18:00 | 129 | 11:00
DhakaUniversity | 138 | 05:00 | 132 | 12:00 | Rajbari | 126 | 09:00 | 122 | 00:00
Dhamrai | 131 | 03:00 | 125 | 12:00 | Rajendrapur | 134 | 01:00 | 123 | 07:00
Dhanmondi | 138 | 04:00 | 132 | 13:00 | Rajshahi | 133 | 09:00 | 127 | 13:00
Dohazari | 135 | 00:00 | 129 | 23:00 | Rajshahi-230 | 135 | 16:00 | 128 | 13:00
Faridpur | 128 | 01:00 | 125 | 13:00 | Ramganj | 129 | 00:00 | 126 | 12:00
Fatullah | 134 | 19:00 | 129 | 12:00 | Rampur | 138 | 06:00 | 133 | 23:00
Fenchuganj | 128 | 10:00 | 125 | 22:00 | Rampura | 137 | 03:00 | 132 | 12:00
Feni | 131 | 05:00 | 130 | 00:00 | Rangamati | 138 | 04:00 | 136 | 00:00
Feni-230 | 132 | 06:00 | 129 | 22:00 | Rangpur | 133 | 17:00 | 125 | 08:00
Ghatail | 124 | 15:00 | 116 | 07:00 | Ruppur | 137 | 01:00 | 132 | 19:00
Ghorashal | 130 | 04:00 | 125 | 00:00 | Saidpur | 136 | 18:00 | 129 | 08:00
Goalpara | 136 | 18:00 | 129 | 13:00 | Santhia | 137 | 10:00 | 130 | 19:30
Gollamari | 135 | 16:00 | 129 | 23:00 | Satkhira | 131 | 10:00 | 122 | 23:00
Gopalganj | 132 | 17:00 | 127 | 13:00 | Satmasjid | 134 | 04:00 | 129 | 12:00
Gopalganj-400 | 131 | 01:00 | 129 | 12:00 | Savar | 131 | 19:00 | 123 | 12:00
Gulshan | 137 | 05:00 | 132 | 12:00 | SevenRings | 131 | 14:00 | 123 | 07:00
Halishahar | 138 | 02:00 | 134 | 12:00 | ShahCement | 132 | 17:00 | 128 | 10:00
Haripur | 134 | 18:00 | 129 | 12:00 | Shahjadpur | 136 | 14:00 | 134 | 00:00
HaripurSBU | 133 | 17:00 | 129 | 00:00 | Shahjibazar | 125 | 01:00 | 120 | 13:00
Hasnabad | 134 | 05:00 | 131 | 11:00 | Shahmirpur | 140 | 18:30 | 136 | 12:00
Hathazari | 138 | 07:00 | 136 | 04:00 | Shariatpur | 129 | 09:00 | 126 | 12:00
Hatirjheel | 137 | 03:00 | 132 | 12:00 | Sherpur | 124 | 01:00 | 117 | 10:00
Ishurdi | 139 | 09:00 | 132 | 19:30 | Shikalbaha | 129 | 18:30 | 120 | 19:00
Jaldhaka | 133 | 17:00 | 126 | 07:00 | Shikalbaha-230 | 139 | 02:00 | 136 | 12:00
Jamalpur | 129 | 15:00 | 119 | 10:00 | Shitalakhya | 133 | 03:00 | 128 | 12:00
Jashore | 134 | 10:00 | 122 | 19:30 | Sholosohor | 138 | 06:00 | 135 | 12:00
Jhenaidah | 139 | 10:00 | 124 | 13:00 | Shomvuganj | 122 | 18:00 | 114 | 00:00
Jhenaidah-230 | 139 | 16:00 | 128 | 13:00 | Shyampur | 134 | 17:00 | 129 | 23:00
Joydebpur | 130 | 14:00 | 120 | 07:00 | Shyampur-230 | 135 | 00:00 | 130 | 12:00
Joypurhat | 135 | 16:00 | 130 | 01:00 | Siddhirganj | 134 | 17:00 | 129 | 00:00
Juldah | 139 | 18:30 | 136 | 00:00 | Sirajganj | 134 | 18:00 | 128 | 20:00
Kabirpur | 130 | 13:00 | 121 | 12:00 | Sitakunda | 138 | 08:00 | 135 | 12:00
Kachua | 132 | 19:30 | 129 | 12:00 | Sonargaon | 129 | 04:00 | 127 | 00:00
Kaliakoir | 133 | 00:00 | 128 | 12:00 | Sreemongol | 124 | 02:00 | 120 | 22:00
Kaliganj | 138 | 10:00 | 127 | 13:00 | Sreepur | 136 | 11:00 | 125 | 07:00
Kallyanpur | 130 | 01:00 | 125 | 12:00 | Srinagar | 137 | 06:00 | 131 | 13:00
Kalurghat | 139 | 06:00 | 137 | 00:00 | SSM | 140 | 00:00 | 140 | 00:00
Kamrangirchar | 137 | 03:00 | 123 | 12:00 | Sunamganj | 118 | 04:00 | 112 | 20:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 123 | 03:00 | 121 | 13:00
Kasba | 128 | 06:00 | 122 | 22:00 | Sylhet_(South) | 123 | 01:00 | 120 | 18:30
Kazla | 138 | 04:00 | 130 | 13:00 | Tangail | 126 | 05:00 | 118 | 18:30
Keranigonj | 137 | 05:00 | 132 | 12:00 | Taraganj | 134 | 17:00 | 126 | 08:00
Khagrachori | 136 | 00:00 | 135 | 01:00 | Tasnim | 129 | 04:00 | 126 | 09:00
Khulna | 134 | 17:00 | 127 | 23:00 | Thakurgaon | 138 | 15:00 | 128 | 08:00
Khulna(S) | 135 | 01:00 | 130 | 13:00 | TK | 137 | 08:00 | 135 | 04:00
Khulshi | 137 | 02:00 | 133 | 12:00 | Tongi | 133 | 04:00 | 128 | 00:00
Kishoreganj | 125 | 06:00 | 118 | 20:00 | Ullahpara | 134 | 09:00 | 130 | 19:30
Kodda | 130 | 00:00 | 119 | 18:30 | Ullon | 137 | 05:00 | 132 | 12:00
Korerhat | 134 | 05:00 | 131 | 23:00 | Uttara | 131 | 07:00 | 124 | 12:00
KSRM | 138 | 18:30 | 134 | 23:00 | UttaraNew | 131 | 05:00 | 121 | 16:00
Kulaura | 127 | 01:00 | 124 | 18:30 | Zigatola | 138 | 08:00 | 132 | 12:00
Kurigram | 130 | 17:00 | 122 | 08:00
Kushtia | 136 | 09:00 | 125 | 13:00
Laksam | 130 | 01:00 | 129 | 00:00
Lakshmipur | 127 | 01:00 | 125 | 00:00
Lalbag | 135 | 07:00 | 131 | 12:00
Lalmonirhat | 130 | 17:00 | 124 | 06:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division