## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-09-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-09-2026 | during | 06-09-2026 | during | 06-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 367 | 412 | 412 | 412 | 382 | 382 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 0 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 100 | 99 | 210 | 210 | 100 | 100 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 35 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 63 | 92 | 149.36 | 149.36 | 45 | 142 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 5 | 5 | 33 | 33 | 5 | 5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 0 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 42 | 49 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 81 | 300 | 300 | 32 | 81 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 35 | 149 | 149 | 34 | 53 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 34 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 18 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 400 | 584 | 584 | 450 | 450 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 1 | 1 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 326 | 254 | 718 | 718 | 270 | 270 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1857.42 | 2049.42 | 5065.16 | 5035.16 | 1740.42 | 2181.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 7 | 0 | 7 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 43 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 221 | 221 | 218 | 218 | 218 | 218 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 92 | 217 | 142 | 142 | 210 | 210 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 34 | 105 | 105 | 34 | 34 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 15 | 31 | 24 | 50 | 14 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 36 | 100 | 100 | 24 | 50 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 2 | 25 | 30 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 19 | 44 | 95.1 | 95.1 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.46 | 0 | 2.36 | 0 | 2.36 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 35 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 110 | 110 | 99 | 99 | FGMO
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 50 | 100 | 100 | 25 | 50 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 89 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 53 | 53 | 163 | 163 | 35 | 55 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1190 | 1224 | 1224 | 1224 | 1224 | 1224 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 12 | 11 | 4 | 1 | 4 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1130 | 1130 | 1150 | 1150 | 1130 | 1130 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3030.46 | 3392.5 | 4015.32 | 4084.96 | 3286.36 | 3483.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 211 | 221 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 354 | 353 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 62 | 342.01 | 342.01 | 400 | 400 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 360 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 36 | 5 | 41.65 | 41.65 | 34 | 34 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 25 | 0 | 52.82 | 52.82 | 25 | 25 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 53 | 0 | 195 | 195 | 55 | 55 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 45 | 51 | 51 | 51 | 43 | 43 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 53 | 150 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 28 | 29 | 30 | 30 | 30 | 30 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 85 | 163 | 163 | 91 | 91 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 156 | 191 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 148 | 172 | 84 | 82 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 103 | 103 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 74 | 113 | 113 | 9 | 70 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 29 | 115 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 7 | 0 | 62 | 0 | 62 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1786 | 2042.2 | 2754.44 | 2690.44 | 2299.46 | 2452.46
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-09-2026 | during | 06-09-2026 | during | 06-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 20.85 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 162 | 120 | 170 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 87 | 60 | 90 | 60 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 13.91 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 213.96 | 284 | 537.6 | 546.5 | 263.1 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 41 | 40 | 40 | 40 | 40 | 40 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 40 | 40 | 40 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 141 | 141 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 28 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 52 | 86 | 86 | 42 | 42 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 126 | 126 | 120 | 120 | 120 | 120 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 242 | 252 | 341 | 341 | 250 | 250 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 381 | 390 | 380 | 370 | 380 | 370 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 395 | 400 | 383 | 383 | 383 | 383 | Machine Problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1435 | 1487 | 1576 | 1566 | 1431 | 1421
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 891 | 734 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 42 | 50 | 50 | 0.13 | 0.13 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 50 | 105 | 105 | 0 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 67 | 105 | 105 | 67 | 67 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 88.94 | 0 | 82 | 0 | 82 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 238 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 500 | 455 | 500 | 500 | 500 | 500 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1496.94 | 1586 | 2877 | 2795 | 2234.13 | 2169.13
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 800 | 1000 | 1000 | 1000 | 800 | 800 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 16 | 48 | 110 | 110 | 0 | 16 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 114 | 117 | 120 | 120 | 119 | 119 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 580 | 570 | 580 | 580 | 580 | 580 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 35 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 287 | 200 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.23 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2034.23 | 2190 | 2488 | 2487 | 2044 | 2059
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 39.99 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 47 | 47 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 14 | 30 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 161 | 155 | 214 | 214 | 150 | 150 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 396 | 336 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 17 | 22 | 22 | 22 | 25 | 25 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 100 | 100 | 0 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 55 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 3.42 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 921.68 | 1046.62 | 1100 | 1300 | 900 | 900 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 41.08 | 0 | 64 | 0 | 64 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 70 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1699.17 | 1764.62 | 2852.91 | 2831.99 | 1825.33 | 1754.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 49 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 157 | 155 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 99 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.3 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 93 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 106 | 0 | 152.67 | 0 | 152.67 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 448.3 | 561 | 660.67 | 472 | 547.67 | 394
System Total |  |  |  |  | 28843.2 | 29158.791 | 14001.48 | 15356.74 | 22827.1 | 22509.05 | 15671.47 | 16203.92
Forecast Scenario (06-09-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14650 |  | 2120.1 |  | 16870
|  |  |  | 1:00 | 13990 |  | 2540.3 |  | 16650
|  |  |  | 2:00 | 13490 |  | 2683.55 |  | 16300
|  |  |  | 3:00 | 13400 |  | 2626.25 |  | 16150
|  |  |  | 4:00 | 13400 |  | 2521.2 |  | 16040
|  |  |  | 5:00 | 13270 |  | 2425.7 |  | 15810
|  |  |  | 6:00 | 13080 |  | 2034.15 |  | 15210
|  |  |  | 7:00 | 13390 |  | 1728.55 |  | 15200
|  |  |  | 8:00 | 13300 |  | 1766.75 |  | 15150
|  |  |  | 9:00 | 13290 |  | 1585.3 |  | 14950
|  |  |  | 10:00 | 13720 |  | 1699.9 |  | 15500
|  |  |  | 11:00 | 14000 |  | 1508.9 |  | 15580
|  |  |  | 12:00 | 13910 |  | 1929.1 |  | 15930
|  |  |  | 13:00 | 12930 |  | 3046.45 |  | 16120
|  |  |  | 14:00 | 13840 |  | 2081.9 |  | 16020
|  |  |  | 15:00 | 13820 |  | 2435.25 |  | 16370
|  |  |  | 16:00 | 13710 |  | 2196.5 |  | 16010
|  |  |  | 17:00 | 13910 |  | 1747.65 |  | 15740
|  |  |  | 18:00 | 14200 |  | 869.05 |  | 15110
|  |  |  | 18:30 | 14600 |  | 955 |  | 15600
|  |  |  | 19:00 | 15090 |  | 1957.75 |  | 17140
|  |  |  | 19:30 | 15170 |  | 1489.8 |  | 16730
|  |  |  | 20:00 | 15290 |  | 1585.3 |  | 16950
|  |  |  | 21:00 | 15360 |  | 1709 |  | 17150
|  |  |  | 22:00 | 15440 |  | 1088.7 |  | 16580
|  |  |  | 23:00 | 15240 |  | 1327.45 |  | 16630
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 15930.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 1709
Probable Maximum Demand at Evening Peak: |  |  | 17150.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15360.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 335.72 MKWHr. |  | 400 | 120 | 150 | 250 | 120 | 190 | 99 | 200 | 180 | 1709
*** This report is generated digitally from Operation Information System (OIS) at 10:14 hrs on 06-09-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-09-2026 | [28 empty] | Date: | 05-09-2026 | [28 empty] | Date: | 05-09-2026 | [28 empty] | Date: | 05-09-2026 | [28 empty] | Date: | 05-09-2026 | [17 empty] | Date: | 05-09-2026
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 16 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 216 | 35 | 0 | 27 | 109 | 48 | 15 | 55 | 90 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 430 | 107 | 16 | 38 | 0 | 11 | 50 | 46 | 18 | 24 | 25 | 0 | 222 | 54 | 31 | 1130 | 53 | 0 | 50 | 25.5 | 34 | 151 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 300 | 354 | 155 | 51 | 0 | 184 | 0 | 51 | 91 | 189 | 57 | 19 | 104 | 166 | 52.2 | 0 | 21 | 245 | 400 | 330 | 41 | 30 | 0 | 0 | 16 | 0 | 42 | 30 | 141 | 0 | 126 | 17 | 87 | 0 | 162 | 0 | 0 | 0 | 12 | 8751.62 | 671 | 0 | 0 | 19 | 24 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 500 | 0 | 0 | 0 | 1299.04 | 0 | 0 | 0 | 57 | 70 | 0 | 50 | 21 | 0 | 0 | 0 | 14 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 155 | 52 | 115 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 113 | 220 | 0 | 800 | 570 | 17 | 5698.04 | 14449.66 | 105.28
01:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 247 | 35 | 0 | 17 | 78 | 48 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 430 | 107 | 16 | 27 | 0 | 7 | 50 | 16 | 0 | 24 | 25 | 0 | 222 | 55 | 35 | 1130 | 53 | 0 | 47 | 8 | 34 | 151 | 0 | 0 | 0 | 1224 | 0 | 107 | 0 | 340 | 354 | 40 | 51 | 0 | 202 | 0 | 59 | 91 | 110 | 20 | 19 | 104 | 156 | 52.2 | 0 | 21 | 245 | 400 | 364 | 40 | 30 | 0 | 0 | 16 | 0 | 42 | 30 | 141 | 0 | 126 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 6 | 8243.12 | 817 | 0 | 0 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 500 | 0 | 0 | 0 | 1310.8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 21 | 0 | 0 | 0 | 17 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 156 | 51 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 117 | 220 | 0 | 800 | 570 | 17 | 5740.8 | 13983.92 | 105.27
02:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 293 | 35 | 0 | 17 | 78 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 455 | 109 | 16 | 25 | 0 | 3 | 50 | 16 | 0 | 24 | 25 | 0 | 222 | 55 | 37 | 1130 | 53 | 0 | 50 | 8 | 34 | 151 | 0 | 0 | 0 | 1224 | 0 | 100 | 0 | 393 | 354 | 0 | 51 | 0 | 202 | 25 | 68 | 91 | 101 | 0 | 19 | 104 | 144 | 52.2 | 0 | 21 | 246 | 400 | 362 | 40 | 30 | 0 | 0 | 16 | 0 | 42 | 30 | 141 | 0 | 126 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 6 | 8276.12 | 766 | 0 | 0 | 19 | 30 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 500 | 0 | 0 | 0 | 1067.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 17 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 158 | 52 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 117 | 220 | 0 | 800 | 570 | 17 | 5398.92 | 13675.04 | 105.26
03:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 316 | 35 | 0 | 17 | 78 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 480 | 107 | 16 | 25 | 0 | 3 | 34 | 16 | 0 | 24 | 25 | 0 | 222 | 55 | 42 | 1130 | 53 | 0 | 50 | 8 | 34 | 151 | 0 | 0 | 0 | 1224 | 0 | 102 | 8 | 393 | 355 | 0 | 51 | 0 | 204 | 35 | 69 | 90 | 100 | 0 | 19 | 104 | 142 | 52.2 | 0 | 23 | 246 | 400 | 365 | 40 | 30 | 0 | 0 | 16 | 0 | 42 | 30 | 141 | 0 | 126 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 6 | 8345.12 | 701 | 0 | 0 | 19 | 29 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 500 | 0 | 0 | 0 | 941.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 17 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 157 | 50 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 117 | 220 | 0 | 800 | 570 | 17 | 5206.02 | 13551.14 | 105.25
04:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 231 | 35 | 0 | 17 | 78 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 410 | 107 | 16 | 24 | 0 | 19 | 0 | 16 | 0 | 24 | 25 | 0 | 222 | 55 | 42 | 1130 | 53 | 0 | 50 | 8 | 34 | 151 | 0 | 0 | 0 | 1224 | 0 | 60 | 16 | 393 | 355 | 0 | 51 | 10 | 193 | 30 | 69 | 91 | 101 | 0 | 19 | 104 | 144 | 52.2 | 0 | 23 | 244 | 400 | 378 | 40 | 30 | 0 | 0 | 16 | 0 | 42 | 30 | 142 | 0 | 126 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 6 | 8139.12 | 701 | 0 | 0 | 19 | 30 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 500 | 0 | 0 | 0 | 925.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 17 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 157 | 50 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 117 | 220 | 0 | 800 | 570 | 17 | 5190.91 | 13330.03 | 105.24
05:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 229 | 35 | 0 | 17 | 78 | 32 | 15 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 445 | 109 | 16 | 17 | 0 | 13 | 0 | 16 | 0 | 24 | 25 | 0 | 222 | 55 | 42 | 1130 | 53 | 0 | 50 | 8 | 34 | 151 | 0 | 0 | 0 | 1224 | 0 | 53 | 16 | 393 | 355 | 0 | 51 | 10 | 198 | 32 | 69 | 91 | 101 | 0 | 19 | 103 | 140 | 52.2 | 0 | 23 | 245 | 400 | 392 | 40 | 30 | 0 | 0 | 16 | 0 | 42 | 30 | 142 | 0 | 124 | 0 | 58 | 0 | 67 | 0 | 0 | 0 | 6 | 8087.12 | 701 | 0 | 0 | 19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 991.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 17 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 158 | 50 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 117 | 220 | 0 | 800 | 570 | 17 | 5212.21 | 13299.33 | 105.23
06:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 246 | 35 | 0 | 17 | 79 | 32 | 15 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 143.42 | 5.5 | 22 | 0 | 440 | 107 | 16 | 12 | 0 | 13 | 0 | 16 | 0 | 24 | 25 | 0.04 | 222 | 55 | 42 | 1130 | 53 | 0 | 50 | 8 | 34 | 151 | 0 | 0 | 0 | 1224 | 0 | 53 | 16 | 393 | 354 | 0 | 51 | 10 | 199 | 34 | 28 | 91 | 101 | 0 | 19 | 103 | 134 | 52.2 | 0 | 23 | 247 | 400 | 377 | 40 | 30 | 0 | 0 | 16 | 0 | 42 | 30 | 142 | 0 | 125 | 0 | 58 | 0.08 | 67 | 0 | 0 | 0.37 | 6 | 8039.61 | 701 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 500 | 0 | 0 | 0 | 982.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0.6 | 0 | 17 | 0 | 0.3 | 159 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.06 | 157 | 52 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.02 | 16 | 307 | 117 | 220 | 0 | 800 | 570 | 17 | 5189.54 | 13229.15 | 105.22
07:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 269 | 0 | 0 | 17 | 79 | 32 | 15 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 2 | 143.42 | 5.5 | 22 | 0 | 465 | 107 | 16 | 12 | 0 | 9 | 0 | 16 | 0 | 24 | 25 | 0.22 | 181 | 55 | 40 | 1130 | 55 | 0 | 50 | 8 | 34 | 151 | 0 | 0 | 0 | 1224 | 1 | 55 | 16 | 393 | 354 | 0 | 51 | 17 | 205 | 34 | 17 | 91 | 153 | 0 | 19 | 103 | 128 | 52.2 | 1 | 23 | 244 | 400 | 377 | 40 | 30 | 0 | 4 | 16 | 0 | 42 | 30 | 142 | 0 | 125 | 0 | 58 | 1.4 | 67 | 0 | 0.3 | 4.54 | 2 | 8033.58 | 890 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 500 | 0 | 0 | 0 | 951.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 6.03 | 19 | 17 | 0 | 3.72 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.52 | 160 | 52 | 115 | 3 | 0 | 0 | 0 | 0 | 1 | 26 | 0.12 | 16 | 307 | 117 | 220 | 0 | 800 | 570 | 17 | 5412.27 | 13445.85 | 105.21
08:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 268 | 0 | 0 | 17 | 79 | 32 | 15 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 15 | 143.42 | 5 | 22 | 0 | 450 | 109 | 16 | 12 | 0 | 17 | 0 | 16 | 0 | 24 | 25 | 0.66 | 180 | 55 | 17 | 1130 | 53 | 0 | 50 | 8 | 34 | 151 | 0 | 0 | 0 | 1224 | 0 | 53 | 53 | 393 | 360 | 0 | 51 | 25 | 197 | 34 | 16 | 90 | 174 | 2 | 19 | 103 | 138 | 52.2 | 3 | 23 | 243 | 400 | 372 | 41 | 30 | 0 | 4 | 16 | 0 | 42 | 30 | 142 | 0 | 125 | 0 | 58 | 5.2 | 67 | 0 | 0.6 | 12.57 | 6 | 8103.65 | 891 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 500 | 17 | 0 | 0 | 914.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 20.16 | 34 | 10 | 0 | 10 | 162 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 159 | 51 | 115 | 2 | 0 | 0 | 0 | 0 | 1.4 | 82 | 0.13 | 16 | 307 | 116 | 220 | 0 | 800 | 570 | 17 | 5504.6 | 13608.25 | 105.2
09:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 292 | 0 | 0 | 19 | 79 | 32 | 15 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 13 | 143.42 | 5 | 22 | 0 | 450 | 109 | 16 | 13 | 0 | 10 | 0 | 16 | 0 | 24 | 25 | 1.64 | 181 | 55 | 9 | 1130 | 55 | 0 | 44 | 8 | 34 | 147 | 0 | 0 | 0 | 1224 | 3 | 51 | 53 | 393 | 359 | 0 | 45 | 25 | 199 | 35 | 17 | 91 | 174 | 8 | 19 | 103 | 124 | 52.2 | 4 | 23 | 239 | 400 | 360 | 41 | 30 | 0 | 5 | 16 | 0 | 42 | 28 | 142 | 0 | 125 | 0 | 58 | 8.33 | 112 | 0 | 1.7 | 18.12 | 6 | 8141.41 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.62 | 500 | 17 | 0 | 0 | 927.73 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 21 | 0 | 20.66 | 70 | 10 | 0 | 8.08 | 162 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 1.44 | 161 | 51 | 115 | 19 | 0 | 0 | 0 | 0 | 2.9 | 68 | 0.21 | 16 | 307 | 116 | 220 | 0 | 800 | 580 | 17 | 5526.64 | 13668.05 | 105.2
10:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 243 | 17 | 0 | 17 | 79 | 32 | 15 | 17 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 100 | 0 | 26 | 143.42 | 5 | 22 | 0 | 415 | 107 | 16 | 18 | 0 | 11 | 0 | 16 | 0 | 24 | 25 | 3.88 | 181 | 55 | 2 | 1130 | 53 | 0 | 44 | 8 | 34 | 147 | 0 | 0 | 0 | 1140 | 6 | 48 | 53 | 393 | 359 | 0 | 45 | 25 | 195 | 36 | 16 | 91 | 162 | 8 | 19 | 103 | 130 | 52.2 | 3 | 23 | 242 | 400 | 381 | 41 | 30 | 0 | 10 | 16 | 0 | 41 | 28 | 143 | 0 | 126 | 0 | 58 | 6.25 | 112 | 0 | 2.3 | 37.99 | 6 | 8141.04 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.46 | 500 | 17 | 0 | 0 | 918.67 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 0 | 51.77 | 98 | 10 | 0 | 24.74 | 162 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 2.35 | 160 | 50 | 115 | 16 | 0 | 0 | 0 | 0 | 4.8 | 119 | 0.21 | 16 | 275 | 116 | 180 | 0 | 800 | 580 | 35 | 5584 | 13725.04 | 105.19
11:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 326 | 17 | 0 | 17 | 63 | 32 | 15 | 17 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 100 | 0 | 34 | 143.42 | 5 | 22 | 0 | 500 | 89 | 16 | 19 | 0 | 12 | 0 | 15 | 0 | 24 | 25 | 4.46 | 221 | 55 | 0 | 1130 | 53 | 0 | 43 | 8 | 34 | 92 | 0 | 0 | 0 | 1190 | 0 | 53 | 53 | 393 | 354 | 0 | 45 | 25 | 211 | 36 | 29 | 91 | 156 | 8 | 12 | 103 | 148 | 34 | 7 | 28 | 242 | 395 | 381 | 41 | 20 | 0 | 4 | 16 | 0 | 41 | 28 | 141 | 0 | 126 | 0 | 58 | 20.85 | 114 | 0 | 1.2 | 13.91 | 6 | 8322.84 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.94 | 500 | 17 | 0 | 0 | 921.68 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 14 | 0 | 39.99 | 70 | 17 | 0 | 41.08 | 161 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 3.42 | 157 | 50 | 115 | 15 | 0 | 0 | 0 | 0 | 5.3 | 106 | 0.23 | 16 | 287 | 114 | 220 | 0 | 800 | 580 | 17 | 5678.64 | 14001.48 | 105.19
12:00 | 0 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 219 | 17 | 0 | 17 | 63 | 32 | 15 | 50 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 100 | 0 | 22 | 143.42 | 5 | 22 | 0 | 370 | 107 | 16 | 18 | 0 | 5 | 0 | 15 | 0 | 24 | 25 | 1.8 | 222 | 55 | 0 | 1130 | 55 | 0 | 43 | 8 | 34 | 83 | 0 | 0 | 0 | 1212 | 10 | 50 | 53 | 393 | 353 | 0 | 45 | 25 | 184 | 39 | 34 | 90 | 162 | 13 | 12 | 103 | 156 | 8 | 1 | 28 | 243 | 397 | 381 | 42 | 20 | 0 | 12 | 16 | 0 | 41 | 25 | 141 | 0 | 126 | 0 | 58 | 10 | 114 | 0 | 0.7 | 41.31 | 6 | 8154.23 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.6 | 500 | 17 | 0 | 0 | 922.97 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 14 | 0 | 57.53 | 115 | 17 | 0 | 59.39 | 161 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 5.64 | 158 | 50 | 115 | 34 | 0 | 0 | 0 | 0 | 2.8 | 145 | 0.19 | 16 | 300 | 115 | 220 | 0 | 800 | 580 | 17 | 5756.12 | 13910.35 | 105.19
13:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 309 | 17 | 0 | 17 | 63 | 32 | 15 | 55 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 12 | 143.42 | 5 | 22 | 0 | 400 | 109 | 16 | 19 | 0 | 4 | 0 | 15 | 0 | 24 | 25 | 3.36 | 222 | 55 | 0 | 1130 | 55 | 0 | 43 | 8 | 34 | 93 | 0 | 0 | 0 | 1192 | 12 | 53 | 53 | 393 | 355 | 0 | 45 | 25 | 199 | 39 | 34 | 91 | 173 | 14 | 19 | 103 | 156 | 8 | 6 | 28 | 244 | 394 | 369 | 42 | 20 | 0 | 8 | 16 | 0 | 41 | 25 | 142 | 0 | 126 | 0 | 58 | 4 | 114 | 0 | 0.9 | 18.93 | 6 | 8171.61 | 890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.82 | 500 | 31 | 0 | 0 | 921.73 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 14 | 0 | 38.94 | 112 | 17 | 0 | 24.35 | 161 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 3.77 | 161 | 51 | 115 | 10 | 0 | 0 | 0 | 0 | 2.4 | 205 | 0.15 | 16 | 307 | 116 | 220 | 0 | 800 | 580 | 17 | 5757.16 | 13928.77 | 105.18
14:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 283 | 17 | 0 | 17 | 62 | 32 | 15 | 55 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 96 | 0 | 13 | 143.42 | 5 | 22 | 0 | 405 | 107 | 16 | 24 | 0 | 17 | 0 | 15 | 17 | 24 | 25 | 0.68 | 222 | 55 | 0 | 1130 | 53 | 0 | 43 | 8 | 34 | 107 | 0 | 0 | 0 | 1224 | 17 | 50 | 53 | 393 | 355 | 0 | 45 | 25 | 204 | 39 | 34 | 85 | 173 | 8 | 19 | 103 | 160 | 8 | 35 | 28 | 247 | 390 | 369 | 40 | 39 | 0 | 12 | 16 | 0 | 31 | 25 | 141 | 0 | 126 | 9 | 58 | 1.15 | 114 | 0 | 0.8 | 1.28 | 0 | 8236.33 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.72 | 500 | 50 | 0 | 0 | 913.82 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 15 | 0 | 13.87 | 49 | 17 | 0 | 17.55 | 159 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 1.68 | 159 | 52 | 115 | 13 | 0 | 0 | 0 | 0 | 2.5 | 175 | 0.3 | 16 | 307 | 117 | 220 | 0 | 800 | 580 | 17 | 5604.44 | 13840.77 | 105.17
15:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 331 | 17 | 0 | 17 | 62 | 32 | 15 | 17 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 96 | 0 | 13 | 143.42 | 5 | 22 | 0 | 440 | 107 | 16 | 25 | 0 | 15 | 0 | 15 | 17 | 24 | 25 | 0.56 | 222 | 44 | 0 | 1130 | 53 | 0 | 38 | 8 | 34 | 174 | 0 | 0 | 0 | 1224 | 15 | 53 | 53 | 393 | 354 | 0 | 51 | 25 | 204 | 35 | 35 | 86 | 173 | 8 | 19 | 103 | 154 | 8 | 10 | 29 | 254 | 390 | 335 | 40 | 40 | 0 | 8 | 16 | 0 | 31 | 25 | 141 | 0 | 126 | 9 | 58 | 1.75 | 115 | 0 | 0.6 | 12.93 | 0 | 8296.26 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.72 | 500 | 49 | 0 | 0 | 919.76 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 15 | 0 | 17.97 | 38 | 17 | 0 | 15.73 | 156 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 1.6 | 158 | 50 | 109 | 2 | 0 | 0 | 0 | 0 | 2.9 | 129 | 0.17 | 16 | 307 | 117 | 220 | 0 | 800 | 570 | 17 | 5528.85 | 13825.11 | 105.16
16:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 324 | 17 | 4 | 17 | 62 | 32 | 15 | 17 | 35 | 7 | 0 | 0 | 0 | 35 | 0 | 96 | 0 | 8 | 143.42 | 5 | 22 | 0 | 470 | 107 | 16 | 26 | 0 | 16 | 0 | 16 | 17 | 24 | 25 | 0.4 | 222 | 51 | 0 | 1130 | 53 | 0 | 43 | 13 | 25 | 211 | 0 | 0 | 0 | 1224 | 9 | 48 | 16 | 300 | 354 | 51 | 51 | 24 | 194 | 40 | 48 | 85 | 172 | 8 | 19 | 103 | 148 | 8 | 8 | 0 | 265 | 390 | 320 | 40 | 40 | 0 | 1 | 16 | 0 | 31 | 22 | 142 | 0 | 126 | 17 | 58 | 7.19 | 114 | 0 | 0.2 | 12.21 | 0 | 8251.42 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.82 | 500 | 49 | 0 | 0 | 929.72 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 0 | 24.86 | 16 | 22 | 0 | 8.5 | 156 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0.72 | 160 | 50 | 99 | 11 | 0 | 0 | 0 | 0 | 1.3 | 46 | 0.04 | 32 | 307 | 117 | 220 | 0 | 800 | 570 | 5 | 5456.96 | 13708.38 | 105.13
17:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 240 | 17 | 31 | 28 | 61 | 32 | 15 | 17 | 162 | 13 | 0 | 0 | 0 | 35 | 0 | 98 | 0 | 4 | 143.42 | 5 | 22 | 0 | 340 | 109 | 16 | 30 | 0 | 12 | 0 | 31 | 17 | 24 | 25 | 0.28 | 222 | 55 | 0 | 1130 | 53 | 0 | 43 | 17 | 34 | 213 | 0 | 0 | 0 | 1224 | 3 | 90 | 8 | 300 | 356 | 80 | 51 | 5 | 201 | 25 | 67 | 86 | 173 | 23 | 19 | 103 | 166 | 8 | 3 | 0 | 270 | 395 | 294 | 40 | 40 | 0 | 0 | 16 | 0 | 31 | 25 | 141 | 0 | 126 | 17 | 58 | 2.46 | 114 | 0 | 0.3 | 11.41 | 0 | 8290.87 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 17.3 | 500 | 50 | 0 | 0 | 1116.91 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 21 | 0 | 8.9 | 5 | 22 | 0 | 4.5 | 156 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.4 | 159 | 48 | 92 | 4 | 20 | 0 | 0 | 0 | 0.9 | 22 | 0.08 | 32 | 307 | 117 | 180 | 0 | 800 | 570 | 35 | 5621.99 | 13912.86 | 105.11
18:00 | 0 | 40 | 41 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 236 | 17 | 35 | 35 | 62 | 64 | 15 | 17 | 162 | 15 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 143.42 | 5 | 22 | 0 | 360 | 107 | 16 | 35 | 0 | 6 | 0 | 31 | 17 | 36 | 50 | 0 | 222 | 55 | 0 | 1050 | 50 | 0 | 43 | 17 | 34 | 213 | 0 | 0 | 0 | 1160 | 0 | 145 | 8 | 250 | 320 | 58 | 51 | 5 | 221 | 25 | 69 | 86 | 173 | 68 | 19 | 103 | 166 | 35 | 0 | 0 | 272 | 400 | 214 | 40 | 40 | 0 | 0 | 16 | 0 | 31 | 25 | 141 | 0 | 127 | 17 | 58 | 0.2 | 125 | 0 | 0 | 0.37 | 0 | 8257.99 | 917 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 67 | 2.02 | 473 | 50 | 0 | 0 | 1217.03 | 0 | 0 | 0 | 35 | 45 | 0 | 50 | 28 | 0 | 0.19 | 0 | 22 | 0 | 0.41 | 156 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.04 | 160 | 47 | 92 | 0 | 59 | 0 | 0 | 0 | 0.1 | 2 | 0.01 | 48 | 276 | 117 | 220 | 0 | 950 | 570 | 35 | 5948.8 | 14206.79 | 105.1
19:00 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 336 | 54 | 35 | 35 | 92 | 81 | 15 | 35 | 162 | 15 | 0 | 0 | 0 | 35 | 0 | 98 | 0 | 0 | 143.42 | 5 | 22 | 0 | 480 | 107 | 16 | 36 | 0 | 7 | 51 | 31 | 17 | 36 | 50 | 0 | 222 | 55 | 0 | 1090 | 53 | 0 | 45 | 19 | 34 | 215 | 0 | 0 | 0 | 1180 | 0 | 150 | 0 | 300 | 352 | 18 | 51 | 5 | 219 | 15 | 79 | 85 | 174 | 73 | 19 | 103 | 174 | 52.2 | 0 | 0 | 266 | 400 | 363 | 40 | 40 | 0 | 0 | 16 | 0 | 52 | 25 | 141 | 0 | 127 | 17 | 86 | 0 | 161 | 0 | 0 | 0 | 0 | 9073.62 | 727 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 235 | 0 | 67 | 0 | 455 | 50 | 0 | 0 | 1032.63 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 28 | 0 | 0 | 0 | 22 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 160 | 48 | 103 | 0 | 82 | 0 | 165 | 0 | 0 | 0 | 0 | 48 | 200 | 116 | 220 | 0 | 973 | 570 | 17 | 6016.63 | 15090.25 | 105.1
19:30 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 285 | 54 | 35 | 35 | 91 | 81 | 15 | 55 | 162 | 18 | 0 | 0 | 0 | 35 | 0 | 36 | 0 | 0 | 143.42 | 5 | 22 | 0 | 390 | 107 | 16 | 46 | 0 | 5 | 51 | 31 | 17 | 36 | 50 | 0 | 222 | 55 | 2 | 1130 | 53 | 0 | 50 | 25.5 | 34 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 320 | 352 | 18 | 51 | 5 | 220 | 15 | 115 | 85 | 190 | 73 | 19 | 103 | 166 | 52.2 | 0 | 15 | 258 | 400 | 377 | 40 | 40 | 0 | 0 | 16 | 0 | 52 | 30 | 141 | 0 | 127 | 17 | 86 | 0 | 162 | 0 | 0 | 0 | 0 | 9095.12 | 731 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 235 | 0 | 67 | 0 | 455 | 50 | 0 | 0 | 1039.74 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 30 | 0 | 0 | 0 | 22 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 160 | 49 | 90 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 48 | 200 | 116 | 220 | 0 | 1000 | 570 | 17 | 6074.74 | 15169.86
20:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 240 | 54 | 35 | 35 | 92 | 81 | 15 | 55 | 162 | 19 | 0 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 143.42 | 5 | 22 | 0 | 445 | 107 | 16 | 45 | 0 | 6 | 51 | 31 | 17 | 36 | 50 | 0 | 221 | 55 | 2 | 1130 | 53 | 0 | 50 | 25.5 | 34 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 340 | 353 | 22 | 51 | 5 | 220 | 15 | 115 | 85 | 185 | 73 | 19 | 103 | 170 | 52.2 | 0 | 22 | 258 | 400 | 380 | 40 | 40 | 0 | 0 | 16 | 0 | 52 | 30 | 140 | 0 | 126 | 18 | 86 | 0 | 162 | 0 | 0 | 0 | 0 | 9203.12 | 731 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 237 | 0 | 67 | 0 | 455 | 50 | 0 | 0 | 1041.46 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 30 | 0 | 0 | 0 | 22 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 159 | 48 | 95 | 0 | 98 | 0 | 165 | 0 | 0 | 0 | 0 | 48 | 200 | 116 | 220 | 0 | 1000 | 570 | 17 | 6085.46 | 15288.58 | 105.09
21:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 254 | 54 | 35 | 35 | 92 | 81 | 15 | 55 | 162 | 18 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 143.42 | 5 | 0 | 0 | 400 | 107 | 16 | 44 | 0 | 11 | 51 | 31 | 35 | 36 | 50 | 0 | 221 | 55 | 2 | 1130 | 53 | 0 | 50 | 25.5 | 34 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 360 | 353 | 62 | 51 | 0 | 221 | 5 | 115 | 85 | 191 | 74 | 19 | 103 | 172 | 52.2 | 0 | 29 | 252 | 400 | 390 | 40 | 40 | 0 | 0 | 16 | 0 | 52 | 30 | 141 | 0 | 126 | 35 | 87 | 0 | 162 | 0 | 0 | 0 | 0 | 9255.12 | 734 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 238 | 0 | 67 | 0 | 455 | 50 | 0 | 0 | 1046.62 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 30 | 0 | 0 | 0 | 22 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 155 | 49 | 93 | 0 | 99 | 0 | 165 | 0 | 0 | 0 | 0 | 48 | 200 | 117 | 220 | 0 | 1000 | 570 | 35 | 6101.62 | 15356.74 | 105.09
22:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 239 | 54 | 35 | 27 | 92 | 81 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 143.42 | 5 | 22 | 0 | 340 | 107 | 16 | 44 | 0 | 18 | 51 | 31 | 35 | 36 | 50 | 0 | 220 | 54 | 2 | 1130 | 53 | 0 | 50 | 25.5 | 34 | 220 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 360 | 353 | 92 | 51 | 0 | 221 | 0 | 108 | 85 | 192 | 73 | 19 | 103 | 174 | 52.2 | 0 | 29 | 248 | 400 | 392 | 40 | 40 | 0 | 0 | 16 | 0 | 52 | 27 | 142 | 0 | 126 | 17 | 87 | 0 | 162 | 0 | 0 | 0 | 0 | 9182.12 | 734 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 238 | 0 | 67 | 0 | 455 | 51 | 0 | 0 | 1038.33 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 30 | 0 | 0 | 0 | 22 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 156 | 49 | 92 | 0 | 100 | 0 | 165 | 0 | 0 | 0 | 0 | 48 | 307 | 117 | 220 | 0 | 1000 | 570 | 17 | 6181.33 | 15363.45 | 105.08
23:00 | 0 | 105 | 49 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 258 | 54 | 35 | 27 | 92 | 81 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 86 | 5 | 22 | 0 | 415 | 109 | 16 | 38 | 0 | 2 | 51 | 31 | 35 | 36 | 50 | 0 | 220 | 55 | 2 | 1130 | 53 | 0 | 50 | 25.5 | 34 | 220 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 360 | 353 | 140 | 51 | 0 | 221 | 0 | 109 | 91 | 192 | 74 | 19 | 103 | 168 | 52.2 | 0 | 29 | 250 | 400 | 394 | 40 | 40 | 0 | 0 | 16 | 0 | 52 | 25 | 142 | 0 | 126 | 17 | 87 | 0 | 162 | 0 | 0 | 0 | 0 | 9251.7 | 734 | 0 | 0 | 19 | 42 | 0 | 0 | 0 | 238 | 0 | 67 | 0 | 456 | 51 | 0 | 0 | 1049.48 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 28 | 0 | 0 | 0 | 22 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 159 | 49 | 92 | 0 | 100 | 0 | 165 | 0 | 0 | 0 | 0 | 48 | 280 | 117 | 220 | 0 | 1000 | 570 | 17 | 6184.48 | 15436.18 | 105.08
Total KWH | 0 | 1468800 | 645600 | 0 | 0 | 0 | 0 | 0 | 9244800 | 0 | 7118091 | 651600 | 289080 | 539280 | 1818240 | 1056829 | 371546 | 664587 | 1975680 | 103680 | 0 | 0 | 0 | 623363 | 0 | 2464000 | 0 | 178302 | 3375600 | 115800 | 501840 | 0 | 10475000 | 2580600 | 383640 | 636480 | 0 | 261120 | 439512 | 485328 | 256977 | 667200 | 729600 | 14484 | 5212385 | 1328976 | 377760 | 26996363.64 | 1304727 | 0 | 1117920 | 315396 | 835527 | 3710126 | 0 | 0 | 0 | 29072724 | 81675 | 2162836 | 535273 | 8863000 | 8831700 | 728000 | 1207058 | 301440 | 5070000 | 605160 | 1392000 | 2064715 | 3768000 | 638400 | 458040 | 2501160 | 3620160 | 932203 | 102664 | 496304 | 5992000 | 9534700 | 8971000 | 967000 | 785880 | 0 | 73506 | 390240 | 0 | 1005120 | 644416 | 3233000 | 0 | 3732360 | 244080 | 1562400 | 71132 | 2623200 | 0 | 10450 | 218380 | 76800 | 204904015.64 | 19692364 | 0 | 0 | 120960 | 419584 | 0 | 0 | 0 | 1284989 | 0 | 551232 | 415440 | 11789092 | 647040 | 0 | 0 | 24375636 | 0 | 0 | 0 | 393696 | 824736 | 0 | 405936 | 463601 | 0 | 329736 | 664787 | 404455 | 0 | 200400 | 3843090 | 0 | 0 | 0 | 0 | 0 | 8681454 | 0 | 21000 | 3905000 | 1184291 | 2595639 | 120894 | 820118 | 0 | 891292.5 | 0 | 30415.8 | 1156320 | 1837 | 639840 | 6916000 | 2782000 | 539990 | 0 | 20560000 | 14068363.64 | 471600 | 132212828.94 | 337116844.58

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-09-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14001.48 | MW | 11:00 Hr. | Energy Generated |  |  | 337.1168 |  | MKWHr.
| Day Peak Demand |  |  | 14836.35 | MW | 12:00 Hr. | Energy Unserverd |  |  | 29.15 |  | MKWHr.
| Evening Peak Generation |  |  | 15356.74 | MW | 21:00 Hr. | Energy Demand |  |  | 366.2668 |  | MKWHr.
| Evening Peak Demand |  |  | 17716.74 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33 |  | °C
| Minimum Generation of the Day |  |  | 13229.15 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 849.23 |  | MMCFD
| Maximum Generation of the Day |  |  | 15436.18 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 7.775 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 29.9195 | 0 | 13.5839 | 0 | 0 | 0.1783 | 0 | 0 | 43.6817 | Gas | 113.7741 | Gas | 397457460.46
| Chattogram Zone |  |  | 4.0879 | 56.0691 | 11.0819 | 0 | 5.2124 | 0.096159 | 0 | 0.26112 | 76.8085 | Coal | 114.4918 | Coal | 797376802.3252
| Cumilla Zone |  |  | 28.6644 | 0 | 11.8909 | 0 | 0 | 0.10266 | 3.6202 | 0 | 44.2781 | HFO | 49.8216 | HFO | 1007090202.88
| Mymensingh Zone |  |  | 0 | 0 | 4.5065 | 0 | 0 | 0.29996 | 0 | 0 | 4.8064 | HSD | 2.1763 | HSD | 53479890.2
| Sylhet Zone |  |  | 35.2557 | 0 | 0 | 0 | 0 | 0.073506 | 0 | 0 | 35.3292 | Hydro | 5.2124 | Hydro | 521238.5
| Khulna Zone |  |  | 0 | 11.7891 | 1.7388 | 1.285 | 0 | 0.41544 | 19.6924 | 0 | 34.9207 | Solar | 3.6914 | Solar | 61053332.988
| Barishal Zone |  |  | 3.322 | 41.5444 | 1.1114 | 0 | 0 | 0.001837 | 0 | 0 | 45.9796 | Import | 47.6882 | Import | 300251164.92
| Rajshahi Zone |  |  | 12.5245 | 0 | 2.4924 | 0 | 0 | 1.2159 | 24.3756 | 0 | 40.6085 | Wind | 0.26112 | Wind | 3841075.2
| Rangpur Zone |  |  | 0 | 5.0893 | 3.4158 | 0.89129 | 0 | 1.3076 | 0 | 0 | 10.704
| Total |  |  | 113.7741 | 114.4918 | 49.8216 | 2.1763 | 5.2124 | 3.6914 | 47.6882 | 0.26112 | 337.1168
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 397457460.46 |  | Hydro | 521238.5
|  |  |  | Coal | 797376802.3252 |  | Solar | 61053332.988
|  |  |  | HFO | 1007090202.88 |  | Import | 300251164.92
|  |  |  | HSD | 53479890.2 |  | Wind | 3841075.2
[5 empty] | Total: | 262,10,71,167 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.6924 | Peak Hr Flow | 734.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 26846909.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.3756 | Peak Hr Flow | 1046.62 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1159 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.6202 | Peak Hr Flow | 172.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1923 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.6882 | Peak Hr Flow | 1952.62 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 759 |  | 6182
|  |  |  | Chattogram |  | 177 |  | 1584
|  |  |  | Cumilla |  | 238 |  | 1672
|  |  |  | Mymensingh |  | 234 |  | 1417
|  |  |  | Sylhet |  | 136 |  | 751
|  |  |  | Khulna |  | 262 |  | 2056
|  |  |  | Barishal |  | 106 |  | 548
|  |  |  | Rajshahi |  | 204 |  | 1702
|  |  |  | Rangpur |  | 142 |  | 1105
|  |  |  | Total |  | 2258 |  | 17017
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 54
|  |  |  | Total Unavailable Capacity |  |  |  | 354
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:26 | 19:33 | Barapukuria P/S-Bogura West 230kV Ckt-1 Project Work S/D from Bogura 400/230kV end Due to
Works Of LILO at Polasbari and from Barapukuria 230/132/33kV end Due to LILO work at
Polashbaari 230KV grid SS
| 09:08 | 10:53 | Rajshahi-Rajshahi(New) 132kV Ckt-2 Scheduled S/D from Rajshahi 132/33kV end.
| 09:09 | 10:52 | HVDC Bheramera- Rajshahi 230kV Ckt-2 Scheduled S/D from Rajshahi 230/132/33kV end Due
to Hot spot maintenance work at R- Phase CT connector.
|  | 09:39 | Sylhet_(South) 132/33kV S/S Trafo-2 HT is restored.
|  | 09:40 | Sylhet_(South) 132/33kV S/S Trafo-2 LT is restored.
| 10:02 | 21:47 | Baghabari-Bangura 132 kV Ckt-2 Scheduled S/D from Bhangura 132/33kV end Due to SAS work
| 10:40 |  | Dhamrai 132/33kV S/S Main Bus-1 Scheduled S/D Due to Measurements work by project.
|  | 10:45 | Kulaura 132/33kV S/S TR-2 LT is restored.
| 11:04 | 18:59 | Madunaghat 132/33kV S/S ATR-1(705T) LT Project Work S/D Due to CNTIC Take The Shutdown
| 11:06 | 18:58 | Madunaghat 132/33kV S/S ATR-1(705T) HT Project Work S/D
|  | 12:38 | Siddhirganj 230/132kV S/S 335MW EGCB 1 is restored.
| 12:50 | 16:50 | Siddhirganj 230/132kV S/S 335MW EGCB 2 Scheduled S/D Due to scheduled maintenance work
| 13:42 | 13:52 | Bheramara(GK) 132/33kV S/S TR-2 LT Tripped showing OC/EF; Instantaneous relays Due to
Douloatpur 33 kv feeder fault due to fire.
| 13:42 | 13:52 | Bheramara(GK) 132/33kV S/S TR-1 LT Tripped showing OC/EF: Instantaneous. relays Due to
Douloatpur 33 kv feeder fault due to fire.
| 14:47 |  | Aminbazar-Kaliakoir 400kV Ckt-2 was shut down due to project work.
| 15:34 | 15:49 | Chapainawabganj-Rahanpur 132kV Ckt-1 Project Work S/D from Chapai 132/33kV end Due to S/D
taken by Rahanpur 400 kv grid substation
| 15:37 | 20:19 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to Sf6 gas leakage maintenance
work.
| 15:38 | 20:18 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to Sf6 gas leakage maintenance
work.
|  | 15:49 | Chapainawabganj-Rahanpur 132kV Ckt-1 is restored.
| 16:06 |  | 400/132 KV Transformer 132 KV side charge from Rohonpur 400/132 KV S/S.
|  | 17:42 | Fenchuganj-Sreemangal 132kV Ckt-2 is restored.
|  | 22:43 | Lalmonirhat-Rangpur 132 kV Ckt-2 is restored.
|  | 23:02 | Rangpur - Taraganj 132kV Ckt-1 is restored.
| 06:00 |  | Minimum Generation: 13627 MW.
| 07:32 |  | Fenchuganj-Sreemangal 132kV Ckt-1 Project Work S/D from Sreemongol 132/33kV end. and
from Fenchuganj 230/132/33kV end Due to G to G project work
| 07:34 | 07:52 | Mymensingh RPCL-Tangail 132kV Ckt-2 Tripped from Ghatail 132/33kV end showing REL650,
REL670 relays Due to Rain and Lightning
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-09-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 9244800 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 371546 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 99 | 2464000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 651600 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 92 | 1818240 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 664587 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 623363 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 5 | 115800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 501840 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 49 | 645600 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 81 | 1056829 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 35 | 539280 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1468800 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 18 | 103680 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1975680 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 178302 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 289080 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 10475000 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 254 | 7118091 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 3375600 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2049.42 | 43681718
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 315396 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 81675 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1117920 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 221 | 5212385 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 3710126 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 835527 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 31 | 485328 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 439512 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 36 | 667200 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 377760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 44 | 636480 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 14484 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 383640 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 35 | 256977 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1328976 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 729600 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2580600 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 53 | 1304727 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 29072724 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 11 | 261120 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1130 | 26996363.64 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3392.5 | 76808520.64
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 221 | 5070000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 353 | 8831700 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 62 | 728000 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 360 | 8863000 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 5 | 605160 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 301440 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 535273 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1207058 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 2162836 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 496304 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2064715 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 191 | 3768000 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 172 | 3620160 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 932203 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 458040 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 103 | 2501160 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 74 | 638400 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1392000 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 102664 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 2042.2 | 44278113
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 71132 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 162 | 2623200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1562400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 218380 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 76800 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 244080 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 284 | 4806442
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 73506 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 967000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 785880 | GT#4 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under Maintenance
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 141 | 3233000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 644416 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 52 | 1005120 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 126 | 3732360 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 390240 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 252 | 5992000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 390 | 8971000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9534700 | Machine Problem
Sylhet Area Total |  |  |  |  | 2325 | 1487 | 35329222
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 734 | 19692364 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 120960 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 42 | 419584 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 50 | 647040 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 67 | 551232 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 415440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 238 | 1284989 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 455 | 11789092 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1586 | 34920701
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1000 | 20560000 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 639840 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 117 | 2782000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 570 | 14068363.64 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 539990 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 471600 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 200 | 6916000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1837 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2190 | 45979630.64
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 329736 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 463601 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 155 | 3843090 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 336 | 8681454 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 404455 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 405936 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 824736 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 55 | 393696 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 21000 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1046.62 | 24375636 | Coal shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 200400 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 664787 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1764.62 | 40608527
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 891292.5 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1184291 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 155 | 3905000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 820118 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30415.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 93 | 2595639 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 120894 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1156320 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 561 | 10703970.3
Eastern Grid Total |  |  |  |  | 17427.666 | 9255.12 | 204904015.64
Western Grid Total |  |  |  |  | 11731.125 | 6101.62 | 132212828.94
National Grid Total |  |  |  |  | 29158.791 | 15356.74 | 337116844.58
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-09-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10062.03 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4696.9 | MW
i) Dhaka area |  |  | 5423.33 |  | MW | i) Khulna area |  |  |  | 1793.5 | MW
ii) Chattogram area |  |  | 1406.7 |  | MW | ii) Barishal area |  |  |  | 442.4 | MW
iii) Cumilla area |  |  | 1434 |  | MW | iii) Rajshahi area |  |  |  | 1498 | MW
iv) Mymensingh area |  |  | 1183 |  | MW | iv) Rangpur area |  |  |  | 963 | MW
v) Sylhet area |  |  | 615 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14758.93 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Halishahar | 148 | 12:00 | 133 | Narinda | 74 | 13:00 | 199 | Ullon | 48 | 22:00
2 | AKSML | 167.2 | 11:00 | 68 | HaripurSBU | 140 | 11:00 | 134 | Narshingdi | 203 | 21:00 | 200 | Uttara | 96 | 19:00
3 | Aftabnagar | 44 | 13:00 | 69 | Hasnabad | 97 | 22:00 | 135 | Natore | 144 | 18:30 | 201 | UttaraNew | 55 | 13:00
4 | Agargaon | 116 | 13:00 | 70 | Hathazari | 84 | 21:00 | 136 | Nawabganj | 63.9 | 23:00 | 202 | Zigatola | 98 | 13:00
5 | Agrabad | 64 | 11:00 | 71 | Hatirjheel | 73 | 13:00 | 137 | Netrakona | 138 | 07:00
6 | Amnura | 29 | 22:00 | 72 | Ishurdi | 75 | 19:30 | 138 | New | 92.2 | 11:00
7 | Araihazar | 59 | 07:00 | 73 | Jaldhaka | 76 | 18:30 | 139 | Niamatpur | 67 | 22:00
8 | Ashuganj | 83 | 00:00 | 74 | Jamalpur | 124 | 00:00 | 140 | Noapara | 41.5 | 20:00
9 | BSRM | 190 | 01:00 | 75 | Jashore | 161 | 19:00 | 141 | PHP | 13 | 14:00
10 | Bagerhat | 83 | 23:00 | 76 | Jhenaidah | 92 | 18:00 | 142 | Pabna | 96 | 22:00
11 | Bajitpur | 86 | 03:00 | 77 | Joydebpur | 172 | 20:00 | 143 | Palashbari | 134 | 22:00
12 | Bakerganj | 13 | 01:00 | 78 | Joypurhat | 55 | 22:00 | 144 | Panchagarh | 72 | 19:30
13 | Bakulia | 91 | 19:30 | 79 | Juldah | 18 | 12:00 | 145 | Patiya | 20 | 00:00
14 | Banani | 46 | 13:00 | 80 | KSRM | 15 | 12:00 | 146 | Patnitala | 33 | 21:00
15 | Bangabhaban | 6 | 11:00 | 81 | Kabirpur | 277 | 08:00 | 147 | Patuakhali | 64 | 18:30
16 | Barapukuria | 62 | 23:00 | 82 | Kachua | 92 | 22:00 | 148 | Payra | 34 | 22:00
17 | Barguna | 20 | 18:30 | 83 | Kaliganj | 38 | 18:30 | 149 | Postogola | 63 | 19:00
18 | Barishal | 86 | 00:00 | 84 | Kallyanpur | 129 | 21:00 | 150 | Pubail | 45 | 18:00
19 | Barishal-230 | 116 | 21:00 | 85 | Kalurghat | 41 | 18:30 | 151 | Purbachal | 22 | 13:00
20 | Baroaulia | 61 | 15:00 | 86 | Kamrangirchar | 80 | 13:00 | 152 | Purbasadipur | 123 | 19:00
21 | Baroirhat | 57 | 23:00 | 87 | Kaptai | N/A | N/A | 153 | Rahanpur | 30 | 00:00
22 | Bashundhara | 210 | 19:00 | 88 | Kasba | 40 | 22:00 | 154 | Rahim | 55 | 10:00
23 | BashundharaCement | 1 | 10:00 | 89 | Kazla | 119 | 17:00 | 155 | Rajbari | 80 | 21:00
24 | Beanibazar | 68 | 20:00 | 90 | Keranigonj | 95 | 22:00 | 156 | Rajendrapur | 126 | 18:00
25 | Benapole | 71 | 19:00 | 91 | Khagrachori | 34 | 19:00 | 157 | Rajshahi | 104 | 23:00
26 | Bhaluka | 163 | 11:00 | 92 | Khulna | 59 | 16:00 | 158 | Rajshahi-230 | 95 | 19:00
27 | Bhandaria | 54 | 22:00 | 93 | Khulshi | 180 | 19:30 | 159 | Ramganj | 106 | 18:30
28 | Bhangura | 34 | 07:00 | 94 | Kishoreganj | 149 | 20:00 | 160 | Rampur | 42 | 20:00
29 | Bheramara(GK) | 62 | 22:00 | 95 | Kodda | 322 | 21:00 | 161 | Rangamati | 15 | 11:00
30 | Bhulta | 217 | 22:00 | 96 | Kulaura | 50 | 20:00 | 162 | Rangpur | 128 | 19:30
31 | Bog-Sherpur | 66 | 18:30 | 97 | Kurigram | 63 | 07:00 | 163 | Ruppur | 3 | 10:00
32 | Bogura | 208 | 23:00 | 98 | Kushtia | 143 | 18:00 | 164 | SSM | 0 | 00:00
33 | Borhanuddin | 65 | 22:00 | 99 | Laksam | 37 | 11:00 | 165 | Saidpur | 97 | 18:00
34 | Brahmanbaria | 129 | 22:00 | 100 | Lakshmipur | 50 | 18:30 | 166 | Santhia | 34 | 22:00
35 | Cantonment | 135 | 13:00 | 101 | Lalbag | 79 | 13:00 | 167 | Satkhira | 135 | 23:00
36 | Chandina | 18 | 22:00 | 102 | Lalmonirhat | 58 | 23:00 | 168 | Satmasjid | 109 | 14:00
37 | Chandpur | 86 | 22:00 | 103 | MI_Cement | 15.8 | 19:30 | 169 | Savar | 225 | 12:00
38 | Chandraghona | 32 | 18:30 | 104 | Madanganj | 54 | 22:00 | 170 | SevenRings | 17.47 | 00:00
39 | Chapai | 69 | 22:00 | 105 | Madaripur | 102 | 23:00 | 171 | ShahCement | 22 | 23:00
40 | Charfasson | 28 | 19:30 | 106 | Madartek | 88 | 00:00 | 172 | Shahjadpur | 72 | 19:00
41 | Charsaidpur | 30 | 00:00 | 107 | Madunaghat | 56 | 20:00 | 173 | Shahjibazar | 127 | 21:00
42 | Chauddagram | 67 | 20:00 | 108 | Magura | 63 | 20:00 | 174 | Shahmirpur | 55 | 19:00
43 | Chhatak | 34 | 06:00 | 109 | Mahasthangarh | 66 | 19:00 | 175 | Shariatpur | 92 | 21:00
44 | Chowmuhani | 142 | 22:00 | 110 | Maijdee | 28 | 05:00 | 176 | Sherpur | 156 | 00:00
45 | Chuadanga | 105 | 22:00 | 111 | Manikganj | 136 | 22:00 | 177 | Shikalbaha | 42 | 11:00
46 | Coxsbazar | 127 | 15:00 | 112 | Maniknagar | 74 | 14:00 | 178 | Shitalakhya | 78.9 | 13:00
47 | Cumilla(N) | 132 | 23:00 | 113 | Matarbari | 48 | 19:00 | 179 | Sholosohor | 46 | 18:00
48 | Cumilla(S) | 181 | 18:30 | 114 | Matuail | 78 | 10:00 | 180 | Shomvuganj | 50 | 00:00
49 | Daganbhuiyan | 34 | 22:00 | 115 | Metrorail_Motijheel | 24 | 09:00 | 181 | Shyampur | 196 | 13:00
50 | Daudkandi | 136 | 23:00 | 116 | Metrorail_Uttara | 0 | 00:00 | 182 | Siddhirganj | 137 | 13:00
51 | DhakaUniversity | 80 | 13:00 | 117 | Millgate | 102 | 12:00 | 183 | Sirajganj | 118 | 20:00
52 | Dhamrai | 100 | 18:00 | 118 | Mirpur | 161 | 18:30 | 184 | Sitakunda | 13 | 19:00
53 | Dhanmondi | 109.4 | 13:00 | 119 | Mirsorai | 31 | 16:00 | 185 | Sonargaon | 137 | 04:00
54 | Dohazari | 99 | 19:00 | 120 | Mirzapur | 50 | 10:00 | 186 | Sreemongol | 71 | 18:30
55 | Faridpur | 187 | 21:00 | 121 | Mithapukur | 66 | 08:00 | 187 | Sreepur | 116 | 06:00
56 | Fatullah | 116 | 10:00 | 122 | Modern | N/A | N/A | 188 | Srinagar | 56.8 | 22:00
57 | Fenchuganj | 43 | 23:00 | 123 | Mogbazar | 64.3 | 19:00 | 189 | Sunamganj | 53 | 07:00
58 | Feni | 106 | 19:30 | 124 | Mongla | 36 | 19:00 | 190 | Sylhet | 134 | 18:30
59 | GPH | 1 | 00:00 | 125 | Motijheel | 48 | 13:00 | 191 | Sylhet_(South) | 61 | 00:00
60 | Ghatail | 90 | 22:00 | 126 | Muktagacha | 38 | 11:00 | 192 | TK | 0 | 00:00
61 | Ghorashal | 0 | 00:00 | 127 | Munshiganj | 99 | 00:00 | 193 | Tangail | 174 | 20:00
62 | Ghorashal-230 | 107 | 18:30 | 128 | Muradnagar | 49 | 07:00 | 194 | Taraganj | 29 | 08:00
63 | Goalpara | 39 | 13:00 | 129 | Mymensingh | 154 | 21:00 | 195 | Tasnim | 42 | 16:00
64 | Gollamari | 102 | 20:00 | 130 | Nabinagar | 102 | 18:00 | 196 | Thakurgaon | 110 | 19:00
65 | Gopalganj | 100 | 23:00 | 131 | Naogaon | 116 | 20:00 | 197 | Tongi | 167 | 11:00
66 | Gulshan | 102 | 13:00 | 132 | Narail | 58 | 19:00 | 198 | Ullahpara | 37 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-09-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14449.66 | 1691 |  | 16216.76
1:00 | 13983.92 | 1694 |  | 15754.15
2:00 | 13675.04 | 1605 |  | 15352.04
3:00 | 13551.14 | 1569 |  | 15191.14
4:00 | 13330.03 | 1439 |  | 14834.03
5:00 | 13299.33 | 1316 |  | 14674.33
6:00 | 13229.15 | 580 |  | 13835.25
7:00 | 13445.85 | 126 |  | 13577.85
8:00 | 13608.25 | 94 |  | 13706.25
9:00 | 13668.05 | 113 |  | 13786.05
10:00 | 13725.04 | 22 |  | 13748.04
11:00 | 14001.48 | 31 |  | 14033.48
12:00 | 13910.35 | 886 |  | 14836.35
13:00 | 13928.77 | 1180 |  | 15161.77
14:00 | 13840.77 | 1395 |  | 15298.77
15:00 | 13825.11 | 1886 |  | 15796.11
16:00 | 13708.38 | 1725 |  | 15511.38
17:00 | 13912.86 | 1131 |  | 15094.86
18:00 | 14206.79 | 774 |  | 15015.79
19:00 | 15090.25 | 2027 |  | 17208.25
19:30 | 15169.86 | 2202 |  | 17470.86
20:00 | 15288.58 | 2011 |  | 17389.58
21:00 | 15356.74 | 2258 |  | 17716.74
22:00 | 15363.45 | 1880 |  | 17328.45
23:00 | 15436.18 | 1717 |  | 17230.18
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-09-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8751.62 | 5698.04 | 14449.66 | DAILY GENERATION CURVE
00:30 | 8497.37 | 5719.42 | 14216.79
01:00 | 8243.12 | 5740.8 | 13983.92 | 05-09-2026
01:30 | 8259.62 | 5569.86 | 13829.48
02:00 | 8276.12 | 5398.92 | 13675.04
02:30 | 8310.62 | 5302.47 | 13613.09
03:00 | 8345.12 | 5206.02 | 13551.14
03:30 | 8242.12 | 5198.465 | 13440.585
04:00 | 8139.12 | 5190.91 | 13330.03
04:30 | 8113.12 | 5201.56 | 13314.68
05:00 | 8087.12 | 5212.21 | 13299.33
05:30 | 8063.365 | 5200.875 | 13264.24
06:00 | 8039.61 | 5189.54 | 13229.15
06:30 | 8036.595 | 5300.905 | 13337.5
07:00 | 8033.58 | 5412.27 | 13445.85
07:30 | 8068.615 | 5458.435 | 13527.05
08:00 | 8103.65 | 5504.6 | 13608.25
08:30 | 8122.53 | 5515.62 | 13638.15
09:00 | 8141.41 | 5526.64 | 13668.05
09:30 | 8141.225 | 5555.32 | 13696.545
10:00 | 8141.04 | 5584 | 13725.04
10:30 | 8231.94 | 5631.32 | 13863.26
11:00 | 8322.84 | 5678.64 | 14001.48
11:30 | 8238.535 | 5717.38 | 13955.915
12:00 | 8154.23 | 5756.12 | 13910.35
12:30 | 8162.92 | 5756.64 | 13919.56
13:00 | 8171.61 | 5757.16 | 13928.77
13:30 | 8203.97 | 5680.8 | 13884.77
14:00 | 8236.33 | 5604.44 | 13840.77
14:30 | 8266.295 | 5566.645 | 13832.94
15:00 | 8296.26 | 5528.85 | 13825.11
15:30 | 8273.84 | 5492.905 | 13766.745
16:00 | 8251.42 | 5456.96 | 13708.38
16:30 | 8271.145 | 5539.475 | 13810.62
17:00 | 8290.87 | 5621.99 | 13912.86
17:30 | 8274.43 | 5785.395 | 14059.825
18:00 | 8257.99 | 5948.8 | 14206.79
18:30 | 8665.805 | 5982.715 | 14648.52
19:00 | 9073.62 | 6016.63 | 15090.25
19:30 | 9095.12 | 6074.74 | 15169.86
20:00 | 9203.12 | 6085.46 | 15288.58
20:30 | 9229.12 | 6093.54 | 15322.66 |  | Executive Engineer
21:00 | 9255.12 | 6101.62 | 15356.74 |  | Network Operation Division
21:30 | 9218.62 | 6141.475 | 15360.095
22:00 | 9182.12 | 6181.33 | 15363.45
22:30 | 9216.91 | 6182.905 | 15399.815
23:00 | 9251.7 | 6184.48 | 15436.18

## En-Curve
QF-LDC-12
Date | 05-09-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3372 | 1297.5 | 671 | 0 | 166 | 1299.04 | 222 | 4738 | 0 | 650.42 | 2022.7 | 0 | 0 | 11 | 1691 | DAILY ENERGY CURVE
00:30 | 3408.5 | 1315 | 744 | 0 | 161 | 1304.92 | 222 | 4738 | 0 | 584.92 | 1729.45 | 0 | 0 | 9 | 1692.5 | 05-09-2026
01:00 | 3445 | 1332.5 | 817 | 0 | 156 | 1310.8 | 222 | 4738 | 0 | 519.42 | 1436.2 | 0 | 0 | 7 | 1694
01:30 | 3464.5 | 1369.5 | 791.5 | 0 | 150 | 1189.36 | 222 | 4739.5 | 0 | 490.42 | 1407.7 | 0 | 0 | 5 | 1649.5 | Energy Generated | 337.1168 |  | MKWHr
02:00 | 3484 | 1406.5 | 766 | 0 | 144 | 1067.92 | 222 | 4741 | 0 | 461.42 | 1379.2 | 0 | 0 | 3 | 1605 | Energy not Served | 29.15 |  | MKWHr
02:30 | 3497.5 | 1437 | 733.5 | 0 | 143 | 1004.47 | 222 | 4739.5 | 0 | 453.92 | 1379.2 | 0 | 0 | 3 | 1587 | Total Energy Requirement | 366.2668 |  | MKWHr
03:00 | 3511 | 1467.5 | 701 | 0 | 142 | 941.02 | 222 | 4738 | 0 | 446.42 | 1379.2 | 0 | 0 | 3 | 1569
03:30 | 3506 | 1398 | 701 | 0 | 143 | 933.465 | 222 | 4738 | 0 | 429.92 | 1358.2 | 0 | 0 | 11 | 1504
04:00 | 3501 | 1328.5 | 701 | 0 | 144 | 925.91 | 222 | 4738 | 0 | 413.42 | 1337.2 | 0 | 0 | 19 | 1439
04:30 | 3512 | 1345.5 | 701 | 0 | 142 | 958.56 | 222 | 4738.5 | 0 | 400.92 | 1278.2 | 0 | 0 | 16 | 1377.5
05:00 | 3523 | 1362.5 | 701 | 0 | 140 | 991.21 | 222 | 4739 | 0 | 388.42 | 1219.2 | 0 | 0 | 13 | 1316
05:30 | 3518.5 | 1369.5 | 701 | 0 | 137 | 986.885 | 222 | 4739.5 | 2.235 | 379.42 | 1195.2 | 0 | 0 | 13 | 948
06:00 | 3514 | 1376.5 | 701 | 0 | 134 | 982.56 | 222 | 4740 | 4.47 | 370.42 | 1171.2 | 0 | 0 | 13 | 580
06:30 | 3520.5 | 1401.5 | 795.5 | 0 | 131 | 967.22 | 201.5 | 4741.5 | 41.66 | 370.42 | 1155.7 | 0 | 0 | 11 | 353
07:00 | 3527 | 1426.5 | 890 | 0 | 128 | 951.88 | 181 | 4743 | 78.85 | 370.42 | 1140.2 | 0 | 0 | 9 | 126
07:30 | 3526.5 | 1428.75 | 890.5 | 0 | 133 | 933.395 | 180.5 | 4742 | 152.785 | 365.92 | 1160.7 | 0 | 0 | 13 | 110
08:00 | 3526 | 1431 | 891 | 0 | 138 | 914.91 | 180 | 4741 | 226.72 | 361.42 | 1181.2 | 0 | 0 | 17 | 94
08:30 | 3505.5 | 1434 | 890.5 | 0 | 131 | 921.32 | 180.5 | 4747 | 254.71 | 352.42 | 1207.7 | 0 | 0 | 13.5 | 103.5
09:00 | 3485 | 1437 | 890 | 0 | 124 | 927.73 | 181 | 4753 | 282.7 | 343.42 | 1234.2 | 0 | 0 | 10 | 113
09:30 | 3460.5 | 1372.5 | 890 | 0 | 127 | 923.2 | 181 | 4694 | 370.725 | 391.42 | 1275.7 | 0 | 0 | 10.5 | 67.5
10:00 | 3436 | 1308 | 890 | 0 | 130 | 918.67 | 181 | 4635 | 458.75 | 439.42 | 1317.2 | 0 | 0 | 11 | 22
10:30 | 3441.5 | 1407.5 | 890.5 | 0 | 139 | 920.175 | 201 | 4664.5 | 457.065 | 433.42 | 1297.1 | 0 | 0 | 11.5 | 26.5
11:00 | 3447 | 1507 | 891 | 0 | 148 | 921.68 | 221 | 4694 | 455.38 | 427.42 | 1277 | 0 | 0 | 12 | 31
11:30 | 3405 | 1389 | 890.5 | 0 | 152 | 922.325 | 221.5 | 4712 | 531.17 | 427.42 | 1296.5 | 0 | 0 | 8.5 | 458.5
12:00 | 3363 | 1271 | 890 | 0 | 156 | 922.97 | 222 | 4730 | 606.96 | 427.42 | 1316 | 0 | 0 | 5 | 886
12:30 | 3380 | 1335 | 890 | 0 | 156 | 922.35 | 222 | 4725.5 | 561.29 | 379.42 | 1343.5 | 0 | 0 | 4.5 | 1033
13:00 | 3397 | 1399 | 890 | 0 | 156 | 921.73 | 222 | 4721 | 515.62 | 331.42 | 1371 | 0 | 0 | 4 | 1180
13:30 | 3398.5 | 1385 | 902.5 | 0 | 158 | 917.775 | 222 | 4736.5 | 436.075 | 331.42 | 1386.5 | 0 | 0 | 10.5 | 1287.5
14:00 | 3400 | 1371 | 915 | 0 | 160 | 913.82 | 222 | 4752 | 356.53 | 331.42 | 1402 | 0 | 0 | 17 | 1395
14:30 | 3411.5 | 1419 | 916.5 | 0 | 157 | 916.79 | 222 | 4745.5 | 322.23 | 331.92 | 1374.5 | 0 | 0 | 16 | 1640.5
15:00 | 3423 | 1467 | 918 | 0 | 154 | 919.76 | 222 | 4739 | 287.93 | 332.42 | 1347 | 0 | 0 | 15 | 1886
15:30 | 3417 | 1465 | 917.5 | 0 | 151 | 924.74 | 222 | 4740 | 229.085 | 323.92 | 1361 | 0 | 0 | 15.5 | 1805.5
16:00 | 3411 | 1463 | 917 | 0 | 148 | 929.72 | 222 | 4741 | 170.24 | 315.42 | 1375 | 0 | 0 | 16 | 1725
16:30 | 3388.5 | 1325 | 917.5 | 0 | 157 | 1023.315 | 222 | 4739.5 | 128.885 | 344.92 | 1550 | 0 | 0 | 14 | 1428
17:00 | 3366 | 1187 | 918 | 0 | 166 | 1116.91 | 222 | 4738 | 87.53 | 374.42 | 1725 | 0 | 0 | 12 | 1131
17:30 | 3301 | 1216 | 917.5 | 0 | 166 | 1166.97 | 222 | 4712 | 46.435 | 434.42 | 1868.5 | 0 | 0 | 9 | 952.5
18:00 | 3236 | 1245 | 917 | 0 | 166 | 1217.03 | 222 | 4686 | 5.34 | 494.42 | 2012 | 0 | 0 | 6 | 774
18:30 | 3346.5 | 1358.5 | 822 | 0 | 170 | 1124.83 | 222 | 4681 | 2.67 | 580.92 | 2133.6 | 200 | 0 | 6.5 | 1400.5
19:00 | 3457 | 1472 | 727 | 0 | 174 | 1032.63 | 222 | 4676 | 0 | 667.42 | 2255.2 | 400 | 0 | 7 | 2027
19:30 | 3441 | 1325 | 731 | 0 | 166 | 1039.74 | 222 | 4788 | 0 | 695.42 | 2356.7 | 400 | 0 | 5 | 2202
20:00 | 3522 | 1335 | 731 | 0 | 170 | 1041.46 | 221 | 4786 | 0 | 717.42 | 2356.7 | 402 | 0 | 6 | 2011
20:30 | 3555.5 | 1303 | 732.5 | 0 | 171 | 1044.04 | 221 | 4784.5 | 0 | 714.42 | 2385.7 | 402.5 | 0 | 8.5 | 2134.5
21:00 | 3589 | 1271 | 734 | 0 | 172 | 1046.62 | 221 | 4783 | 0 | 711.42 | 2414.7 | 403 | 0 | 11 | 2258
21:30 | 3601.5 | 1242.5 | 734 | 0 | 173 | 1042.475 | 220.5 | 4837 | 0 | 711.42 | 2380.2 | 403 | 0 | 14.5 | 2069
22:00 | 3614 | 1214 | 734 | 0 | 174 | 1038.33 | 220 | 4891 | 0 | 711.42 | 2345.7 | 403 | 0 | 18 | 1880
22:30 | 3640 | 1262 | 734 | 0 | 171 | 1043.905 | 220 | 4879.5 | 0 | 691.21 | 2345.2 | 403 | 0 | 10 | 1798.5
23:00 | 3666 | 1310 | 734 | 0 | 168 | 1049.48 | 220 | 4868 | 0 | 671 | 2344.7 | 403 | 0 | 2 | 1717
Executive Engineer
Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 05-09-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 98 | 39 | 310 | 166 | 888 | 584 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 126 | 29 | 400 | 170 | 1030 | 584
2:00 | 87 | 28 | 300 | 182 | 816 | 560 |  | Import | 0
3:00 | 65 | 33 | 250 | 178 | 708 | 546
4:00 | 69 | 32 | 250 | 168 | 748 | 536 | Ishurdi-Ghorashal Ckt-2 | Export | 2826909.09
5:00 | 74 | 32 | 280 | 170 | 778 | 546
6:00 | 90 | 41 | 300 | 172 | 830 | 584 |  | Import | 0
7:00 | 107 | 29 | 310 | 170 | 830 | 582
8:00 | 119 | 43 | 310 | 180 | 910 | 650 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 149 | 65 | 98 | 136 | 1110 | 696
10:00 | 166 | 67 | 410 | 182 | 1230 | 750 |  | Import | 0
11:00 | 160 | 66 | 420 | 210 | 1170 | 758
12:00 | 179 | 76 | 440 | 224 | 1304 | 860 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 170 | 69 | 410 | 202 | 1228 | 794
14:00 | 151 | 58 | 390 | 210 | 1136 | 782 |  | Import | 0
15:00 | 144 | 54 | 370 | 204 | 1072 | 750
16:00 | 144 | 58 | 350 | 206 | 1088 | 778 | Gopalganj-Aminbazar Ckt-1 | Export | 11990000
17:00 | 165 | 69 | 400 | 208 | 1210 | 832
18:00 | 158 | 61 | 420 | 204 | 1264 | 812 |  | Import | 0
18:30 | 157 | 70 | 440 | 266 | 1114 | 844
19:00 | 119 | 67 | 370 | 220 | 1060 | 774 | Gopalganj-Aminbazar Ckt-2 | Export | 12030000
19:30 | 92 | 53 | 290 | 196 | 954 | 686
20:00 | 85 | 52 | 270 | 194 | 872 | 660 |  | Import | 0
21:00 | 85 | 51 | 260 | 202 | 814 | 610
22:00 | 83 | 47 | 260 | 208 | 896 | 638 |  | Total Export | 26846909.09
23:00 | 80 | 37 | 280 | 206 | 918 | 642 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-09-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 371 | 04:00 | 353 | 12:00 | Madunaghat | 398 | 04:00 | 390 | 13:00
Amtali | 412 | 02:00 | 409 | 10:00 | Meghnaghat | 379 | 04:00 | 362 | 12:00
Ashuganj | 403 | 4:00 | 381 | 18:30 | Mirsorai | 396 | 00:00 | 384 | 13:00
Bhulta | 393 | 04:00 | 368 | 12:00 | Payra | 413 | 03:00 | 410 | 13:00
Bibiana | 380 | 04:00 | 370 | 12:00 | Rahanpur | 410 | 19:00 | 402 | 01:00
BIPTC | 407 | 03:00 | 395 | 14:00 | Rampal | 391 | 00:00 | 383 | 11:00
Bogura | 397 | 19:00 | 387 | 01:00
Gopalganj | 389 | 04:00 | 378 | 12:00
Kaliakoir | 364 | 04:00 | 343 | 18:00
Korerhat | 394 | 00:00 | 382 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 04:00 | 212 | 12:00 | Hasnabad | 224 | 04:00 | 210 | 11:00
AKSML | 236 | 04:00 | 227 | 12:00 | Hathazari | 235 | 00:00 | 228 | 12:00
Aminbazar | 227 | 04:00 | 212 | 12:00 | Ishurdi | 235 | 19:00 | 224 | 07:00
Ashuganj | 225 | 00:00 | 215 | 11:00 | Jhenaidah | 226 | 19:00 | 214 | 07:00
Ashuganj-400 | 225 | 0:00 | 215 | 11:00 | Kachua | 230 | 00:00 | 220 | 20:00
Baghabari | 233 | 18:30 | 227 | 01:00 | Kaliakoir | 226 | 03:00 | 211 | 12:00
Barapukuria | 227 | 20:00 | 223 | 13:00 | Keranigonj | 226 | 04:00 | 210 | 12:00
Barapukuria-230 | 227 | 20:00 | 222 | 14:00 | Khulna(S) | 225 | 19:00 | 217 | 07:00
Barapukuria(N) | 229 | 19:00 | 225 | 01:00 | Korerhat | 226 | 00:00 | 219 | 12:00
Barishal | 225 | 00:00 | 221 | 11:00 | Madunaghat | 239 | 00:00 | 232 | 11:00
Bheramara | 233 | 19:00 | 222 | 07:00 | Madunaghat-400 | 239 | 00:00 | 233 | 13:00
Bhulta | 224 | 04:00 | 207 | 12:00 | Maniknagar | 220 | 00:00 | 205 | 12:00
Bibiana | 216 | 00:00 | 210 | 18:30 | Meghnaghat | 228 | 03:00 | 218 | 11:00
BIPTC | 235 | 19:00 | 221 | 07:00 | Meghnaghat-400 | 226 | 04:00 | 211 | 11:00
Birulia | 225 | 01:00 | 212 | 12:00 | Mirsorai | 230 | 00:00 | 223 | 13:00
Bogura | 240 | 19:00 | 233 | 01:00 | Naogaon | 229 | 19:00 | 216 | 22:00
Bogura-400 | 240 | 19:00 | 233 | 01:00 | Purbasadipur | 225 | 06:00 | 220 | 15:00
Borhanuddin | 228 | 19:00 | 226 | 01:00 | Rajshahi | 232 | 19:30 | 223 | 07:00
BSRM | 227 | 00:00 | 220 | 13:00 | Rampal | 223 | 04:00 | 217 | 07:00
Charfasson | 229 | 04:00 | 225 | 18:30 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 228 | 00:00 | 221 | 14:00 | Rampura | 224 | 04:00 | 205 | 12:00
Cumilla(N) | 220 | 00:00 | 211 | 12:00 | Shikalbaha | 237 | 01:00 | 231 | 12:00
Faridpur | 220 | 00:00 | 215 | 11:00 | Shyampur | 225 | 04:00 | 209 | 12:00
Fenchuganj | 216 | 00:00 | 211 | 18:30 | Siddhirganj | 223 | 04:00 | 207 | 11:00
Feni | 225 | 00:00 | 217 | 13:00 | Sirajgonj | 236 | 00:00 | 232 | 07:00
Ghorashal | 220 | 00:00 | 215 | 11:00 | Sreepur | 221 | 00:00 | 213 | 18:30
Ghorashal-230 | 215 | 04:00 | 199 | 17:00 | Tongi | 220 | 04:00 | 195 | 11:00
Gopalganj | 221 | 04:00 | 216 | 12:00
GPH | 234 | 00:00 | 227 | 15:00
Haripur | 223 | 04:00 | 208 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 04:00 | 125 | 12:00 | Madanganj | 132 | 01:00 | 123 | 12:00
Agargaon | 135 | 04:00 | 123 | 12:00 | Madaripur | 130 | 00:00 | 127 | 11:00
Agrabad | 136 | 00:00 | 130 | 11:00 | Madartek | 137 | 04:00 | 124 | 12:00
AKS | 134 | 00:00 | 128 | 06:00 | Madunaghat | 138 | 00:00 | 134 | 11:00
Aminbazar | 131 | 04:00 | 120 | 12:00 | Magura | 135 | 19:00 | 128 | 07:00
Amnura | 134 | 00:00 | 130 | 16:00 | Mahasthangarh | 135 | 18:30 | 131 | 01:00
Araihazar | 127 | 00:00 | 119 | 12:00 | Maijdee | 128 | 00:00 | 124 | 13:00
Ashuganj | 128 | 00:00 | 121 | 18:30 | Manikganj | 125 | 04:00 | 118 | 10:00
Ashuganj-230 | 133 | 00:00 | 130 | 09:00 | Maniknagar | 138 | 04:00 | 130 | 02:00
Bagerhat | 128 | 19:00 | 123 | 07:00 | Matarbari | 132 | 18:30 | 120 | 13:00
Bajitpur | 125 | 00:00 | 118 | 18:30 | Matuail | 133 | 03:00 | 122 | 12:00
Bakerganj | 131 | 09:00 | 129 | 00:00 | Metrorail_Motijheel | 138 | 04:00 | 127 | 12:00
Bakulia | 136 | 00:00 | 131 | 12:00 | Metrorail_Uttara | 132 | 03:00 | 118 | 12:00
Banani | 137 | 04:00 | 125 | 12:00 | Millgate | 133 | 04:00 | 117 | 12:00
Bangabhaban | 137 | 02:00 | 125 | 12:00 | Mirpur | 129 | 01:00 | 118 | 12:00
Barapukuria | 138 | 18:30 | 131 | 16:00 | Mirzapur | 127 | 04:00 | 120 | 18:00
Barguna | 131 | 00:00 | 129 | 18:30 | Mithapukur | 133 | 00:00 | 128 | 16:00
Barishal | 131 | 00:00 | 128 | 12:00 | MI_Cement | 133 | 04:00 | 120 | 12:00
Barishal-230 | 131 | 19:00 | 128 | 11:00 | Modern | N/A | N/A | N/A | N/A
Baroaulia | 136 | 00:00 | 131 | 13:00 | Mogbazar | 140 | 06:00 | 127 | 12:00
Baroirhat | 132 | 00:00 | 127 | 13:00 | Mongla | 127 | 19:00 | 123 | 14:00
Bashundhara | 137 | 05:00 | 117 | 12:00 | Motijheel | 137 | 02:00 | 125 | 12:00
BashundharaCement | 132 | 01:00 | 123 | 12:00 | Muktagacha | 126 | 09:00 | 116 | 08:00
Beanibazar | 122 | 00:00 | 119 | 13:00 | Munshiganj | 131 | 03:00 | 122 | 11:00
Benapole | 132 | 19:00 | 123 | 01:00 | Muradnagar | 127 | 00:00 | 120 | 18:30
Bhaluka | 130 | 03:00 | 122 | 17:00 | Mymensingh | 127 | 13:00 | 113 | 18:30
Bhandaria | 128 | 18:30 | 124 | 22:00 | Nabinagar | 129 | 03:00 | 115 | 12:00
Bhangura | 133 | 00:00 | 129 | 07:00 | Naogaon | 138 | 19:00 | 130 | 22:00
Bheramara | 137 | 19:00 | 131 | 07:00 | Narail | 136 | 03:00 | 129 | 11:00
Bheramara(GK) | 137 | 19:00 | 131 | 16:00 | Narinda | 138 | 4:00 | 130 | 2:00
Bhulta | 126 | 02:00 | 119 | 12:00 | Narshingdi | 128 | 00:00 | 118 | 11:00
Bhulta-400 | 129 | 04:00 | 118 | 12:00 | Natore | 135 | 19:00 | 130 | 01:00
Birulia | 134 | 03:00 | 124 | 12:00 | Nawabganj | 136 | 04:00 | 126 | 12:00
Bog-Sherpur | 136 | 00:00 | 132 | 01:00 | Netrakona | 119 | 06:00 | 109 | 18:00
Bogura | 138 | 19:00 | 134 | 01:00 | New | 131 | 00:00 | 118 | 12:00
Bogura-230 | 140 | 19:00 | 134 | 01:00 | Niamatpur | 135 | 09:00 | 132 | 22:00
Brahmanbaria | 125 | 00:00 | 120 | 11:00 | Noapara | 132 | 19:00 | 126 | 07:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 133 | 02:00 | 123 | 12:00 | Pabna | 134 | 19:00 | 129 | 01:00
Chandina | 130 | 04:00 | 123 | 12:00 | Palashbari | 132 | 19:00 | 126 | 07:00
Chandpur | 135 | 00:00 | 129 | 13:00 | Panchagarh | 139 | 06:00 | 132 | 19:30
Chandraghona | 138 | 00:00 | 134 | 13:00 | Patiya | 136 | 00:00 | 132 | 12:00
Chapai | 133 | 05:00 | 130 | 00:00 | Patnitala | 134 | 19:00 | 131 | 21:00
Charsaidpur | 132 | 02:00 | 123 | 12:00 | Patuakhali | 131 | 05:00 | 129 | 11:00
Chauddagram | 130 | 00:00 | 125 | 11:00 | Payra | 134 | 00:00 | 133 | 14:00
Chhatak | 120 | 00:00 | 115 | 18:30 | PHP | 132 | 00:00 | 127 | 13:00
Chowmuhani | 129 | 00:00 | 124 | 12:00 | Postogola | 135 | 04:00 | 123 | 12:00
Chuadanga | 133 | 19:00 | 124 | 07:00 | Pubail | 128 | 00:00 | 117 | 17:00
Coxsbazar | 130 | 18:30 | 122 | 18:00 | Purbachal | 137 | 03:00 | 125 | 12:00
Cumilla(N) | 129 | 05:00 | 124 | 15:00 | Purbasadipur | 136 | 04:00 | 133 | 13:00
Cumilla(S) | 129 | 00:00 | 122 | 18:30 | Rahanpur | 137 | 09:00 | 135 | 00:00
Daganbhuiyan | 130 | 00:00 | 125 | 13:00 | Rahanpur-400 | 138 | 19:00 | 134 | 01:00
Daudkandi | 126 | 00:00 | 118 | 12:00 | Rahim | 132 | 03:00 | 123 | 12:00
DhakaUniversity | 137 | 03:00 | 124 | 12:00 | Rajbari | 125 | 05:00 | 121 | 21:00
Dhamrai | 128 | 00:00 | 118 | 18:00 | Rajendrapur | 133 | 04:00 | 126 | 18:30
Dhanmondi | 137.6 | 05:00 | 123 | 12:00 | Rajshahi | 132 | 19:00 | 128 | 16:00
Dohazari | 137 | 18:30 | 128 | 12:00 | Rajshahi-230 | 133 | 05:00 | 129 | 01:00
Faridpur | 128 | 17:00 | 125 | 07:00 | Ramganj | 131 | 00:00 | 124 | 18:30
Fatullah | 134 | 03:00 | 122 | 12:00 | Rampur | 136 | 00:00 | 130 | 12:00
Fenchuganj | 128 | 00:00 | 124 | 18:30 | Rampura | 137 | 04:00 | 124 | 12:00
Feni | 131 | 05:00 | 126 | 12:00 | Rangamati | 137 | 00:00 | 132 | 10:00
Feni-230 | 131 | 00:00 | 126 | 18:30 | Rangpur | 134 | 18:30 | 127 | 16:00
Ghatail | 124 | 09:00 | 116 | 07:00 | Ruppur | 137 | 18:30 | 131 | 18:00
Ghorashal | 128 | 01:00 | 120 | 17:00 | Saidpur | 136 | 06:00 | 131 | 16:00
Goalpara | 135 | 19:00 | 129 | 07:00 | Santhia | 134 | 00:00 | 129 | 18:00
Gollamari | 134 | 19:00 | 129 | 07:00 | Satkhira | 130 | 10:00 | 120 | 11:00
Gopalganj | 132 | 19:30 | 126 | 07:00 | Satmasjid | 134 | 04:00 | 122 | 12:00
Gopalganj-400 | 139 | 23:00 | 127 | 12:00 | Savar | 131 | 03:00 | 118 | 12:00
Gulshan | 136 | 05:00 | 125 | 12:00 | SevenRings | 130 | 00:00 | 120 | 17:00
Halishahar | 137 | 00:00 | 129 | 13:00 | ShahCement | 132 | 02:00 | 123 | 12:00
Haripur | 133 | 04:00 | 123 | 12:00 | Shahjadpur | 135 | 00:00 | 133 | 12:00
HaripurSBU | 133 | 04:00 | 123 | 12:00 | Shahjibazar | 124 | 00:00 | 119 | 18:30
Hasnabad | 133 | 00:00 | 123 | 12:00 | Shahmirpur | 139 | 00:00 | 133 | 13:00
Hathazari | 138 | 00:00 | 133 | 12:00 | Shariatpur | 129 | 19:30 | 125 | 07:00
Hatirjheel | 137 | 03:00 | 125 | 13:00 | Sherpur | 127 | 19:30 | 113 | 07:00
Ishurdi | 138 | 19:00 | 132 | 07:00 | Shikalbaha | 127 | 00:00 | 122 | 13:00
Jaldhaka | 133 | 18:30 | 129 | 02:00 | Shikalbaha-230 | 138 | 04:00 | 133 | 13:00
Jamalpur | 131 | 19:30 | 116 | 07:00 | Shitalakhya | 133 | 04:00 | 120 | 12:00
Jashore | 133 | 19:00 | 124 | 14:00 | Sholosohor | 137 | 00:00 | 133 | 11:00
Jhenaidah | 136 | 19:00 | 130 | 07:00 | Shomvuganj | 122 | 04:00 | 113 | 18:30
Jhenaidah-230 | 138 | 19:00 | 129 | 07:00 | Shyampur | 132 | 00:00 | 122 | 12:00
Joydebpur | 129 | 00:00 | 116 | 09:00 | Shyampur-230 | 134 | 03:00 | 124 | 12:00
Joypurhat | 134 | 19:00 | 130 | 01:00 | Siddhirganj | 132 | 00:00 | 124 | 11:00
Juldah | 138 | 00:00 | 133 | 12:00 | Sirajganj | 131 | 00:00 | 127 | 07:00
Kabirpur | 127 | 02:00 | 112 | 12:00 | Sitakunda | 137 | 00:00 | 133 | 11:00
Kachua | 131 | 00:00 | 126 | 13:00 | Sonargaon | 129 | 01:00 | 122 | 12:00
Kaliakoir | 133 | 04:00 | 123 | 18:00 | Sreemongol | 124 | 00:00 | 120 | 12:00
Kaliganj | 136 | 19:00 | 128 | 07:00 | Sreepur | 133 | 00:00 | 127 | 18:30
Kallyanpur | 129 | 04:00 | 120 | 11:00 | Srinagar | 136 | 00:00 | 126 | 12:00
Kalurghat | 138 | 00:00 | 134 | 13:00 | SSM | 140 | 00:00 | 134 | 13:00
Kamrangirchar | 137 | 05:00 | 117 | 12:00 | Sunamganj | 118 | 00:00 | 114 | 11:00
Kaptai | 139 | 2:00 | 137 | 9:00 | Sylhet | 122 | 00:00 | 120 | 18:00
Kasba | 126 | 00:00 | 120 | 13:00 | Sylhet_(South) | 123 | 00:00 | 119 | 18:30
Kazla | 138 | 05:00 | 125 | 12:00 | Tangail | 124 | 02:00 | 116 | 18:30
Keranigonj | 137 | 04:00 | 127 | 12:00 | Taraganj | 135 | 19:00 | 130 | 08:00
Khagrachori | 136 | 00:00 | 132 | 13:00 | Tasnim | 130 | 04:00 | 122 | 12:00
Khulna | 133 | 19:00 | 127 | 07:00 | Thakurgaon | 140 | 06:00 | 134 | 18:00
Khulna(S) | 135 | 19:00 | 129 | 07:00 | TK | 138 | 02:00 | 136 | 08:00
Khulshi | 135 | 00:00 | 128 | 13:00 | Tongi | 135 | 04:00 | 120 | 17:00
Kishoreganj | 124 | 04:00 | 115 | 18:30 | Ullahpara | 133 | 00:00 | 129 | 07:00
Kodda | 131 | 19:00 | 115 | 16:00 | Ullon | 135 | 00:00 | 126 | 12:00
Korerhat | 133 | 00:00 | 129 | 12:00 | Uttara | 132 | 04:00 | 115 | 12:00
KSRM | 136 | 01:00 | 131 | 12:00 | UttaraNew | 132 | 04:00 | 118 | 12:00
Kulaura | 127 | 09:00 | 123 | 18:30 | Zigatola | 137 | 04:00 | 126 | 13:00
Kurigram | 130 | 18:30 | 121 | 20:00
Kushtia | 136 | 19:00 | 129 | 07:00
Laksam | 130 | 00:00 | 126 | 11:00
Lakshmipur | 127 | 00:00 | 122 | 13:00
Lalbag | 135 | 00:00 | 126 | 12:00
Lalmonirhat | 126 | 00:00 | 119 | 20:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division