## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-09-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-09-2026 | during | 07-09-2026 | during | 07-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 411 | 412 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 97 | 99 | 210 | 210 | 100 | 100 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 35 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 63 | 48 | 149.36 | 149.36 | 45 | 142 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 4 | 4 | 4.4 | 4.4 | 4.4 | 4.4 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 50 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 81 | 300 | 300 | 32 | 81 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 35 | 149 | 149 | 34 | 53 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 105 | 105 | 34 | 105
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 1 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 545 | 480 | 584 | 584 | 584 | 584 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 335 | 229 | 718 | 718 | 270 | 270 | Gas shortage
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 34 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1830 | 2120.42 | 5032.56 | 5006.56 | 1913.82 | 2343.82
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 219 | 222 | 220 | 220 | 220 | 220 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 206 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 34 | 105 | 105 | 34 | 34 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 14 | 35 | 14 | 32 | 14 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 24 | 100 | 100 | 24 | 50 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 25 | 30 | 25 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 24 | 50 | 95.1 | 95.1 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3.95 | 0 | 1.79 | 0 | 1.79 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 35 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 110 | 110 | 55 | 55 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 100 | 100 | 25 | 50 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 109 | 107 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 16 | 17 | 163 | 163 | 35 | 55 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 3 | 0 | 1 | 1 | 1 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1130 | 1130 | 1150 | 1150 | 1150 | 1150 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3171.95 | 3305.5 | 4079.75 | 4141.96 | 3251.79 | 3454.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 212 | 218 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 320 | 300 | 350.01 | 350.01 | 300 | 300 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 215 | 300 | 342.01 | 342.01 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 300 | 240 | 393 | 393 | 393 | 393 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 0 | 0 | 41.65 | 41.65 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 0 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 45 | 44 | 51 | 51 | 45 | 45 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 46 | 108 | 150 | 150 | 53 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 14 | 21 | 30 | 30 | 30 | 30 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 81 | 80 | 163 | 163 | 91 | 91 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 173 | 156 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 166 | 170 | 84 | 80 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 19 | 19 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 104 | 103 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 73 | 73 | 113 | 113 | 9 | 70 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 115 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 9 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1819 | 1999.2 | 2757.44 | 2688.44 | 1740.45 | 1890.45
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-09-2026 | during | 07-09-2026 | during | 07-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 2.53 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0.4 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 163 | 120 | 170 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 86 | 60 | 90 | 60 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 9.06 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 195.99 | 278 | 538.6 | 546.5 | 264.1 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 80 | 80 | 40 | 40 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 141 | 142 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 25 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 53 | 84 | 84 | 52 | 52 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 126 | 126 | 128 | 128 | 120 | 120 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 0 | 16 | 16 | 16 | 16 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 252 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 370 | 396 | 360 | 390 | 360 | 390 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 395 | 400 | 383 | 383 | 383 | 383 | Machine Problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1472 | 1532 | 1602 | 1632 | 1488 | 1518
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 928 | 739 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 26 | 26 | 26 | 26 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 5 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 39 | 50 | 50 | 0 | 42 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 53 | 105 | 105 | 0 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 105 | 105 | 67 | 67 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 8 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 458 | 459 | 500 | 500 | 500 | 500 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1447 | 1327 | 2866 | 2796 | 2223 | 2212
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 48 | 64 | 110 | 110 | 16 | 48 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 113 | 116 | 120 | 120 | 117 | 117 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 570 | 570 | 580 | 580 | 580 | 580 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 150 | 250 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.3 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2118.3 | 2237 | 2488 | 2487 | 2258 | 2289
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 6.58 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 21 | 21 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 147 | 140 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 304 | 273 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 17 | 17 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 50 | 50 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 70 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 55 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 0.06 | 0 | 0 | 0 | 0 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1124.41 | 1307.38 | 1000 | 1300 | 1100 | 1100 | Coal shortage
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 7.79 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 10 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1680.84 | 1941.38 | 2696.41 | 2783.99 | 1978.83 | 1866.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 47 | 48 | 48 | 48 | 48 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 160 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 77 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.9 | 0 | 6 | 0 | 6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 1 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 173 | 0 | 160.68 | 0 | 160.68 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 503.9 | 564 | 666.68 | 470 | 553.68 | 392
System Total |  |  |  |  | 28843.2 | 29158.791 | 14238.98 | 15304.5 | 22727.44 | 22552.45 | 15671.67 | 16255.18
Forecast Scenario (07-09-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15230 |  | 1804.95 |  | 17120
|  |  |  | 1:00 | 14280 |  | 2301.55 |  | 16690
|  |  |  | 2:00 | 14100 |  | 2196.5 |  | 16400
|  |  |  | 3:00 | 14020 |  | 1881.35 |  | 15990
|  |  |  | 4:00 | 13840 |  | 1671.25 |  | 15590
|  |  |  | 5:00 | 13960 |  | 1298.8 |  | 15320
|  |  |  | 6:00 | 13630 |  | 1174.65 |  | 14860
|  |  |  | 7:00 | 13680 |  | 945.45 |  | 14670
|  |  |  | 8:00 | 13500 |  | 974.1 |  | 14520
|  |  |  | 9:00 | 13760 |  | 878.6 |  | 14680
|  |  |  | 10:00 | 13910 |  | 878.6 |  | 14830
|  |  |  | 11:00 | 14000 |  | 897.7 |  | 14940
|  |  |  | 12:00 | 14240 |  | 1403.85 |  | 15710
|  |  |  | 13:00 | 13920 |  | 1738.1 |  | 15740
|  |  |  | 14:00 | 14040 |  | 1365.65 |  | 15470
|  |  |  | 15:00 | 14020 |  | 1699.9 |  | 15800
|  |  |  | 16:00 | 13970 |  | 1337 |  | 15370
|  |  |  | 17:00 | 14370 |  | 744.9 |  | 15150
|  |  |  | 18:00 | 14430 |  | 563.45 |  | 15020
|  |  |  | 18:30 | 14780 |  | 931.125 |  | 15755
|  |  |  | 19:00 | 15090 |  | 1633.05 |  | 16800
|  |  |  | 19:30 | 15170 |  | 1747.65 |  | 17000
|  |  |  | 20:00 | 15290 |  | 1824.05 |  | 17200
|  |  |  | 21:00 | 15360 |  | 2139.2 |  | 17600
|  |  |  | 22:00 | 15350 |  | 1671.25 |  | 17100
|  |  |  | 23:00 | 15440 |  | 1394.3 |  | 16900
Probable Maximum Temperature: |  |  | 32.3 °C
Probable Maximum Demand at Day Peak: |  |  | 15710.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2139.2
Probable Maximum Demand at Evening Peak: |  |  | 17600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15360.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 343.44 MKWHr. |  | 669 | 110 | 250 | 280 | 110 | 250 | 90 | 200 | 180 | 2139
*** This report is generated digitally from Operation Information System (OIS) at 08:35 hrs on 07-09-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-09-2026 | [28 empty] | Date: | 06-09-2026 | [28 empty] | Date: | 06-09-2026 | [28 empty] | Date: | 06-09-2026 | [28 empty] | Date: | 06-09-2026 | [17 empty] | Date: | 06-09-2026
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [17 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 105 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 308 | 35 | 35 | 26 | 76 | 32 | 15 | 55 | 162 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 35 | 5 | 22 | 0 | 460 | 107 | 16 | 38 | 0 | 11 | 51 | 31 | 18 | 24 | 25 | 0 | 221 | 55 | 3 | 1130 | 53 | 0 | 50 | 25.5 | 34 | 221 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 360 | 354 | 176 | 51 | 0 | 221 | 0 | 74 | 86 | 192 | 73 | 19 | 103 | 162 | 52.2 | 0 | 29 | 245 | 400 | 394 | 40 | 40 | 0 | 0 | 0 | 0 | 52 | 25 | 142 | 0 | 126 | 17 | 87 | 0 | 162 | 0 | 0 | 0 | 0 | 9103.7 | 734 | 0 | 0 | 19 | 42 | 0 | 0 | 0 | 239 | 0 | 15 | 0 | 456 | 51 | 0 | 0 | 1055.08 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 28 | 0 | 0 | 0 | 22 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 157 | 49 | 115 | 0 | 85 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 280 | 117 | 220 | 0 | 1000 | 570 | 17 | 6131.08 | 15234.78 | 105.07
01:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 293 | 35 | 35 | 17 | 61 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 35 | 5 | 22 | 0 | 440 | 107 | 16 | 27 | 0 | 12 | 51 | 16 | 0 | 24 | 25 | 0 | 222 | 54 | 5 | 1130 | 53 | 0 | 50 | 8 | 34 | 220 | 0 | 0 | 0 | 1224 | 0 | 73 | 0 | 270 | 352 | 280 | 51 | 0 | 205 | 0 | 69 | 85 | 180 | 20 | 19 | 103 | 170 | 52.2 | 0 | 29 | 246 | 400 | 393 | 40 | 40 | 0 | 0 | 0 | 0 | 52 | 25 | 142 | 0 | 125 | 17 | 58 | 0 | 67 | 0 | 0 | 0 | 4 | 8540.2 | 702 | 0 | 0 | 19 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 51 | 0 | 0 | 1287.19 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 0 | 0 | 0 | 17 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 155 | 48 | 115 | 0 | 35 | 0 | 30 | 0 | 0 | 0 | 0 | 16 | 280 | 118 | 220 | 0 | 1000 | 570 | 17 | 5743.19 | 14283.39 | 105.06
02:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 307 | 35 | 35 | 17 | 61 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 35 | 5 | 22 | 0 | 420 | 107 | 16 | 25 | 0 | 3 | 51 | 16 | 0 | 24 | 25 | 0 | 222 | 55 | 7 | 1130 | 53 | 0 | 45 | 8 | 34 | 220 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 230 | 320 | 340 | 51 | 0 | 206 | 0 | 65 | 85 | 180 | 0 | 19 | 103 | 170 | 52.2 | 0 | 29 | 248 | 400 | 393 | 40 | 40 | 0 | 0 | 0 | 0 | 52 | 25 | 141 | 0 | 126 | 17 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 8478.2 | 701 | 0 | 0 | 19 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 51 | 0 | 0 | 1253.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 17 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 158 | 48 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 117 | 220 | 0 | 1000 | 570 | 17 | 5623.52 | 14101.72 | 105.06
03:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 294 | 35 | 35 | 17 | 61 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 35 | 5 | 22 | 0 | 430 | 109 | 16 | 25 | 0 | 4 | 0 | 16 | 0 | 24 | 25 | 0 | 222 | 54 | 7 | 1130 | 53 | 0 | 45 | 8 | 34 | 220 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 230 | 320 | 340 | 51 | 0 | 203 | 0 | 71 | 93 | 180 | 0 | 19 | 103 | 166 | 52.2 | 0 | 29 | 244 | 400 | 394 | 40 | 40 | 0 | 0 | 8 | 0 | 52 | 25 | 141 | 0 | 125 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 8419.2 | 702 | 0 | 0 | 19 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 51 | 0 | 0 | 1270.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 17 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 157 | 48 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 116 | 180 | 0 | 1000 | 570 | 17 | 5604.92 | 14024.12 | 105.05
04:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 230 | 35 | 35 | 17 | 61 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 0 | 100 | 0 | 0 | 35 | 5 | 22 | 0 | 370 | 107 | 16 | 24 | 0 | 0 | 0 | 16 | 0 | 24 | 25 | 0 | 222 | 55 | 13 | 1130 | 53 | 0 | 45 | 8 | 34 | 220 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 230 | 320 | 340 | 51 | 0 | 194 | 0 | 72 | 94 | 193 | 0 | 19 | 103 | 164 | 52.2 | 0 | 22 | 246 | 400 | 394 | 40 | 40 | 0 | 0 | 8 | 0 | 52 | 25 | 141 | 0 | 126 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 8296.2 | 701 | 0 | 0 | 19 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 51 | 0 | 0 | 1254.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 0 | 0 | 17 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 155 | 48 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 117 | 180 | 0 | 1000 | 570 | 17 | 5548.06 | 13844.26 | 105.05
05:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 339 | 35 | 35 | 17 | 61 | 32 | 15 | 17 | 72 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 35 | 5 | 22 | 0 | 480 | 94 | 16 | 25 | 0 | 8 | 0 | 16 | 0 | 24 | 25 | 0 | 222 | 55 | 20 | 1130 | 53 | 0 | 45 | 8 | 34 | 220 | 0 | 0 | 0 | 1224 | 0 | 53 | 0 | 230 | 320 | 340 | 51 | 0 | 194 | 0 | 67 | 94 | 185 | 0 | 19 | 70 | 152 | 8 | 0 | 22 | 245 | 400 | 394 | 40 | 40 | 0 | 0 | 8 | 0 | 52 | 25 | 141 | 0 | 126 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 8396 | 702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 456 | 51 | 0 | 0 | 1244.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 0 | 0 | 17 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 154 | 49 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 116 | 220 | 0 | 1000 | 580 | 17 | 5563.85 | 13959.85 | 105.05
06:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 235 | 35 | 35 | 17 | 61 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 0 | 39 | 0 | 0 | 17 | 5 | 22 | 0 | 355 | 92 | 16 | 24 | 0 | 8 | 0 | 16 | 0 | 24 | 25 | 0 | 222 | 55 | 20 | 1130 | 53 | 0 | 44 | 8 | 34 | 220 | 0 | 0 | 0 | 1200 | 0 | 53 | 0 | 230 | 300 | 300 | 51 | 0 | 215 | 0 | 26 | 94 | 180 | 0 | 19 | 100 | 156 | 52.2 | 1 | 22 | 244 | 400 | 380 | 40 | 40 | 0 | 0 | 8 | 0 | 52 | 30 | 141 | 0 | 126 | 0 | 59 | 0 | 67 | 0 | 0 | 0 | 12 | 8045.2 | 702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 457 | 51 | 0 | 0 | 1265.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 0.23 | 0 | 17 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 157 | 49 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.01 | 16 | 280 | 117 | 220 | 0 | 1000 | 580 | 17 | 5582.11 | 13627.31 | 105.05
07:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 326 | 0 | 35 | 17 | 61 | 32 | 15 | 55 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 38 | 0 | 3 | 17 | 5 | 22 | 0 | 460 | 95 | 16 | 25 | 0 | 0 | 0 | 16 | 0 | 24 | 25 | 0.22 | 222 | 55 | 12 | 1130 | 53 | 0 | 44 | 8 | 34 | 220 | 0 | 0 | 0 | 1160 | 2 | 53 | 0 | 230 | 300 | 300 | 51 | 0 | 221 | 0 | 17 | 93 | 175 | 0 | 19 | 100 | 134 | 52.2 | 6 | 15 | 244 | 400 | 380 | 40 | 40 | 0 | 0 | 16 | 0 | 52 | 28 | 141 | 0 | 125 | 0 | 58 | 0.61 | 67 | 0 | 0 | 1.29 | 0 | 8076.32 | 702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 459 | 51 | 0 | 0 | 1262.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 4.85 | 4 | 17 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 154 | 49 | 99 | 6 | 0 | 0 | 0 | 0 | 0.9 | 16 | 0.09 | 16 | 280 | 116 | 220 | 0 | 1000 | 570 | 17 | 5601.98 | 13678.3 | 105.04
08:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 257 | 0 | 35 | 19 | 61 | 32 | 15 | 55 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 38 | 0 | 5 | 17 | 4.5 | 22 | 0 | 420 | 91 | 16 | 24 | 0 | 5 | 0 | 16 | 0 | 24 | 25 | 0.61 | 220 | 55 | 0 | 1130 | 53 | 0 | 44 | 8 | 34 | 220 | 0 | 0 | 0 | 1170 | 6 | 46 | 0 | 250 | 300 | 280 | 51 | 0 | 221 | 0 | 17 | 90 | 175 | 11 | 19 | 99 | 148 | 52.2 | 6 | 15 | 245 | 400 | 380 | 40 | 40 | 0 | 1 | 16 | 0 | 52 | 30 | 142 | 0 | 125 | 0 | 35 | 0.12 | 67 | 0 | 0 | 5.67 | 0 | 8002.1 | 659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 459 | 51 | 0 | 0 | 1260.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 13.81 | 7 | 17 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 157 | 49 | 96 | 9 | 0 | 0 | 0 | 0 | 1.6 | 38 | 0.16 | 16 | 280 | 116 | 180 | 0 | 1000 | 570 | 17 | 5493.97 | 13496.07 | 105.04
09:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 290 | 0 | 32 | 17 | 62 | 32 | 15 | 55 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 36 | 0 | 11 | 34 | 4 | 22 | 0 | 400 | 105 | 16 | 25 | 0 | 0 | 0 | 16 | 0 | 24 | 25 | 1.97 | 220 | 55 | 0 | 1130 | 53 | 0 | 44 | 8 | 34 | 222 | 0 | 0 | 0 | 1160 | 7 | 46 | 0 | 250 | 300 | 280 | 45 | 0 | 198 | 0 | 17 | 85 | 174 | 67 | 19 | 104 | 156 | 8 | 62 | 15 | 244 | 400 | 380 | 40 | 40 | 0 | 2 | 16 | 0 | 52 | 30 | 142 | 0 | 125 | 0 | 35 | 0.57 | 96 | 0 | 0 | 1.61 | 3 | 8123.15 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 457 | 51 | 0 | 0 | 1107.83 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 28 | 8 | 12.64 | 14 | 17 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 156 | 49 | 115 | 16 | 0 | 0 | 0 | 0 | 3.2 | 18 | 0.26 | 16 | 280 | 117 | 180 | 0 | 1000 | 570 | 17 | 5637.93 | 13761.08 | 105.04
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 288 | 0 | 35 | 17 | 46 | 32 | 15 | 55 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 7 | 34 | 4 | 22 | 0 | 375 | 107 | 16 | 24 | 0 | 0 | 0 | 8 | 0 | 24 | 25 | 2.46 | 219 | 55 | 0 | 1130 | 45 | 0 | 44 | 8 | 34 | 221 | 0 | 0 | 0 | 1150 | 11 | 46 | 0 | 260 | 300 | 280 | 45 | 0 | 199 | 0 | 18 | 85 | 173 | 73 | 19 | 104 | 154 | 8 | 63 | 15 | 248 | 400 | 393 | 40 | 40 | 0 | 5 | 16 | 0 | 50 | 30 | 141 | 0 | 126 | 0 | 38 | 0.66 | 113 | 0 | 0 | 2.43 | 12 | 8208.55 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 457 | 51 | 0 | 0 | 1114.02 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 8 | 9.44 | 10 | 17 | 0 | 0.62 | 153 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 158 | 49 | 115 | 7 | 0 | 0 | 0 | 0 | 7.1 | 87 | 0.36 | 16 | 241 | 115 | 220 | 0 | 1000 | 570 | 17 | 5705.54 | 13914.09 | 105.04
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 328 | 0 | 35 | 17 | 62 | 32 | 15 | 55 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 98 | 0 | 10 | 34 | 4 | 22 | 0 | 420 | 107 | 16 | 23 | 0 | 1 | 0 | 8 | 0 | 24 | 25 | 2.89 | 219 | 55 | 0 | 1130 | 16 | 0 | 44 | 8 | 34 | 218 | 0 | 0 | 0 | 1175 | 19 | 48 | 0 | 275 | 300 | 190 | 45 | 0 | 209 | 0 | 38 | 86 | 173 | 73 | 19 | 104 | 158 | 8 | 75 | 15 | 250 | 400 | 370 | 41 | 40 | 0 | 4 | 16 | 0 | 50 | 30 | 141 | 0 | 126 | 0 | 52 | 2.2 | 114 | 0 | 0.2 | 4.24 | 12 | 8283.53 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 458 | 53 | 0 | 0 | 1103.45 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 20 | 8 | 0.72 | 27 | 17 | 0 | 2.79 | 151 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 159 | 49 | 115 | 6 | 0 | 0 | 0 | 0 | 4.8 | 133 | 0.34 | 48 | 150 | 115 | 220 | 0 | 1000 | 570 | 35 | 5715.1 | 13998.63 | 105.03
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 335 | 17 | 35 | 17 | 63 | 32 | 15 | 55 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 97 | 0 | 1 | 34 | 4 | 22 | 0 | 545 | 109 | 16 | 24 | 0 | 3 | 0 | 14 | 0 | 24 | 25 | 3.95 | 219 | 55 | 0 | 1130 | 16 | 0 | 44 | 8 | 34 | 217 | 0 | 0 | 0 | 1224 | 6 | 46 | 0 | 300 | 320 | 215 | 45 | 0 | 212 | 0 | 34 | 81 | 173 | 73 | 19 | 104 | 166 | 8 | 9 | 14 | 252 | 395 | 370 | 40 | 40 | 0 | 12 | 16 | 0 | 50 | 30 | 141 | 0 | 126 | 0 | 58 | 2.53 | 114 | 0 | 0.4 | 9.06 | 12 | 8488.94 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 458 | 53 | 0 | 0 | 1124.41 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 8 | 6.58 | 10 | 17 | 0 | 7.79 | 147 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0.06 | 158 | 49 | 115 | 1 | 0 | 0 | 0 | 0 | 7.9 | 173 | 0.3 | 48 | 150 | 113 | 220 | 0 | 1000 | 570 | 17 | 5750.04 | 14238.98 | 105.03
13:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 237 | 0 | 35 | 17 | 63 | 32 | 15 | 55 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 98 | 0 | 2 | 34 | 4 | 22 | 0 | 415 | 100 | 16 | 24 | 0 | 6 | 0 | 15 | 0 | 24 | 25 | 4 | 220 | 55 | 0 | 1130 | 17 | 0 | 44 | 8 | 34 | 217 | 0 | 0 | 0 | 1180 | 12 | 41 | 0 | 300 | 300 | 230 | 45 | 0 | 195 | 0 | 38 | 80 | 174 | 74 | 19 | 104 | 166 | 8 | 31 | 14 | 251 | 400 | 368 | 40 | 40 | 0 | 12 | 16 | 0 | 50 | 30 | 141 | 0 | 127 | 0 | 58 | 5.95 | 114 | 0 | 0.5 | 16.22 | 12 | 8192.67 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 458 | 53 | 0 | 0 | 1101.89 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 8 | 7.53 | 8 | 18 | 0 | 10.89 | 144 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 1.02 | 156 | 49 | 115 | 14 | 0 | 0 | 0 | 0 | 2 | 170 | 0.55 | 64 | 150 | 114 | 180 | 0 | 1000 | 570 | 17 | 5728.88 | 13921.55 | 105.03
14:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 281 | 17 | 35 | 17 | 64 | 32 | 15 | 55 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 96 | 0 | 2 | 34 | 4 | 22 | 0 | 405 | 90 | 16 | 24 | 0 | 12 | 0 | 15 | 18 | 24 | 25 | 1.1 | 220 | 54 | 0 | 1130 | 17 | 0 | 44 | 8 | 34 | 217 | 0 | 0 | 0 | 1160 | 3 | 40 | 0 | 250 | 300 | 300 | 44 | 0 | 204 | 0 | 34 | 80 | 173 | 73 | 5 | 104 | 172 | 8 | 60 | 14 | 250 | 400 | 368 | 40 | 40 | 0 | 11 | 16 | 0 | 50 | 30 | 143 | 0 | 128 | 6 | 59 | 7.18 | 114 | 0 | 0.5 | 29.61 | 12 | 8286.39 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 459 | 52 | 0 | 0 | 1131.43 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 8 | 8.55 | 22 | 18 | 0 | 10.87 | 142 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 1.64 | 155 | 49 | 115 | 19 | 0 | 0 | 0 | 0 | 1.2 | 100 | 0.16 | 64 | 150 | 115 | 220 | 0 | 1000 | 570 | 17 | 5749.85 | 14036.24 | 105.02
15:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 266 | 17 | 35 | 17 | 58 | 32 | 15 | 17 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 5 | 105 | 4 | 22 | 0 | 410 | 92 | 16 | 24 | 0 | 3 | 0 | 23 | 17 | 24 | 25 | 2.34 | 220 | 55 | 0 | 1130 | 17 | 0 | 44 | 9 | 34 | 215 | 0 | 0 | 0 | 1140 | 10 | 38 | 0 | 270 | 300 | 300 | 44 | 0 | 184 | 0 | 34 | 80 | 175 | 71 | 19 | 104 | 182 | 8 | 28 | 14 | 253 | 400 | 368 | 40 | 40 | 0 | 9 | 8 | 0 | 50 | 30 | 141 | 0 | 126 | 17 | 59 | 4.64 | 116 | 0 | 0.7 | 35.03 | 12 | 8295.71 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 460 | 52 | 0 | 0 | 1101.21 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 8 | 15.84 | 31 | 18 | 0 | 12.61 | 143 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 1.23 | 156 | 49 | 115 | 19 | 0 | 0 | 0 | 0 | 1 | 114 | 0.06 | 64 | 164 | 115 | 220 | 0 | 1000 | 570 | 17 | 5727.95 | 14023.66 | 105.02
16:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 197 | 17 | 18 | 17 | 64 | 32 | 15 | 17 | 35 | 0 | 0 | 0 | 0 | 35 | 0 | 98 | 0 | 5 | 105 | 4 | 22 | 0 | 415 | 108 | 16 | 27 | 0 | 13 | 0 | 29 | 17 | 24 | 25 | 1.05 | 221 | 55 | 0 | 1130 | 16 | 0 | 44 | 17 | 34 | 208 | 0 | 0 | 0 | 1160 | 9 | 21 | 0 | 270 | 300 | 300 | 44 | 0 | 184 | 0 | 56 | 80 | 168 | 65 | 19 | 102 | 168 | 8 | 34 | 21 | 260 | 400 | 368 | 40 | 40 | 0 | 6 | 16 | 0 | 52 | 30 | 142 | 0 | 128 | 17 | 59 | 9.55 | 115 | 0 | 0.5 | 21.93 | 12 | 8241.03 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 460 | 52 | 0 | 0 | 1107.41 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 8 | 23.35 | 30 | 24 | 0 | 8.25 | 142 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 1.01 | 157 | 47 | 115 | 19 | 0 | 0 | 0 | 0 | 0.9 | 34 | 0.06 | 64 | 250 | 116 | 180 | 0 | 1000 | 570 | 35 | 5729.98 | 13971.01 | 105.02
17:00 | 0 | 35 | 20 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 277 | 17 | 27 | 18 | 64 | 32 | 15 | 17 | 155 | 13 | 0 | 0 | 0 | 35 | 0 | 100 | 0 | 4 | 143.42 | 4 | 22 | 0 | 405 | 107 | 16 | 29 | 0 | 6 | 0 | 35 | 17 | 24 | 25 | 0.8 | 221 | 56 | 0 | 1130 | 17 | 0 | 44 | 17 | 34 | 205 | 0 | 0 | 0 | 1180 | 3 | 20 | 0 | 270 | 300 | 300 | 44 | 0 | 218 | 0 | 69 | 80 | 155 | 72 | 19 | 103 | 168 | 8 | 11 | 21 | 305 | 400 | 368 | 40 | 40 | 0 | 2 | 16 | 0 | 52 | 30 | 143 | 0 | 126 | 17 | 58 | 3.32 | 115 | 0 | 0.3 | 7.64 | 12 | 8575.48 | 928 | 0 | 0 | 0 | 11 | 0 | 10 | 0 | 0 | 0 | 32 | 8 | 459 | 52 | 0 | 0 | 1114.87 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 21 | 8 | 4.25 | 12 | 24 | 0 | 4.91 | 140 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0.47 | 158 | 47 | 115 | 4 | 20 | 0 | 0 | 0 | 0.3 | 36 | 0.06 | 64 | 250 | 115 | 220 | 0 | 1000 | 570 | 17 | 5795.86 | 14371.34 | 105.01
18:00 | 0 | 49 | 43 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 247 | 17 | 36 | 36 | 64 | 81 | 15 | 17 | 162 | 16 | 0 | 0 | 0 | 35 | 0 | 97 | 0 | 0 | 143.42 | 4 | 22 | 0 | 400 | 107 | 16 | 33 | 0 | 14 | 0 | 35 | 17 | 24 | 25 | 0.02 | 221 | 55 | 0 | 1130 | 17 | 0 | 40 | 17 | 34 | 205 | 0 | 0 | 0 | 1140 | 0 | 20 | 0 | 240 | 300 | 300 | 44 | 0 | 216 | 0 | 69 | 80 | 157 | 73 | 19 | 103 | 164 | 8 | 0 | 21 | 305 | 397 | 368 | 40 | 40 | 0 | 0 | 16 | 0 | 52 | 30 | 142 | 0 | 126 | 17 | 58 | 0.17 | 115 | 0 | 0 | 0.23 | 12 | 8558.84 | 927 | 0 | 0 | 0 | 30 | 0 | 10 | 0 | 0 | 0 | 32 | 0.5 | 460 | 52 | 0 | 0 | 1188.66 | 0 | 0 | 0 | 35 | 47 | 0 | 50 | 21 | 8 | 0.15 | 2 | 24 | 0 | 0.42 | 140 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0.01 | 156 | 47 | 115 | 1 | 47 | 0 | 0 | 0 | 0 | 1 | 0 | 64 | 250 | 115 | 180 | 0 | 1000 | 570 | 17 | 5870.74 | 14429.58 | 105.01
19:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 283 | 54 | 35 | 42 | 64 | 81 | 26 | 35 | 162 | 16 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 143.42 | 4 | 22 | 0 | 430 | 109 | 16 | 39 | 0 | 4 | 50 | 35 | 17 | 24 | 25 | 0 | 222 | 55 | 0 | 1130 | 16 | 0 | 43 | 19 | 34 | 207 | 0 | 0 | 0 | 1224 | 0 | 62 | 0 | 240 | 300 | 300 | 44 | 0 | 216 | 0 | 76 | 80 | 165 | 73 | 19 | 103 | 162 | 52.2 | 0 | 21 | 320 | 400 | 374 | 40 | 40 | 0 | 0 | 0 | 0 | 53 | 25 | 143 | 0 | 126 | 17 | 86 | 0 | 162 | 0 | 0 | 0 | 12 | 9078.62 | 739 | 0 | 0 | 0 | 35 | 0 | 5 | 0 | 0 | 0 | 32 | 0 | 458 | 52 | 0 | 0 | 1310.42 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 21 | 8 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 156 | 46 | 115 | 0 | 70 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 250 | 117 | 220 | 0 | 1000 | 570 | 17 | 6057.42 | 15136.04 | 105
19:30 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 213 | 54 | 35 | 17 | 64 | 81 | 55 | 55 | 162 | 16 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 143.42 | 4 | 22 | 0 | 430 | 107 | 16 | 47 | 0 | 0 | 50 | 35 | 17 | 24 | 25 | 0 | 222 | 55 | 0 | 1130 | 17 | 0 | 45 | 25.5 | 34 | 207 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 240 | 300 | 300 | 44 | 0 | 216 | 0 | 90 | 80 | 156 | 73 | 19 | 103 | 156 | 52.2 | 0 | 21 | 310 | 400 | 395 | 40 | 40 | 0 | 0 | 0 | 0 | 53 | 25 | 142 | 0 | 126 | 17 | 86 | 0 | 163 | 0 | 0 | 0 | 12 | 9142.12 | 739 | 0 | 0 | 0 | 50 | 0 | 5 | 0 | 0 | 0 | 32 | 0 | 460 | 52 | 0 | 0 | 1316.32 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 21 | 8 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 157 | 47 | 115 | 0 | 76 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 250 | 117 | 180 | 0 | 1000 | 570 | 17 | 6048.32 | 15190.44 | 104.99
20:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 217 | 54 | 35 | 28 | 64 | 81 | 55 | 55 | 162 | 16 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 143.42 | 4 | 22 | 0 | 425 | 107 | 16 | 49 | 0 | 0 | 50 | 35 | 18 | 24 | 25 | 0 | 222 | 56 | 0 | 1130 | 17 | 0 | 49 | 25.5 | 34 | 206 | 0 | 0 | 0 | 1224 | 0 | 150 | 0 | 240 | 300 | 300 | 44 | 0 | 217 | 0 | 96 | 80 | 157 | 73 | 19 | 103 | 162 | 52.2 | 0 | 21 | 310 | 400 | 396 | 40 | 40 | 0 | 0 | 0 | 0 | 53 | 25 | 142 | 0 | 126 | 17 | 86 | 0 | 164 | 0 | 0 | 0 | 12 | 9175.12 | 738 | 0 | 0 | 0 | 46 | 0 | 5 | 0 | 0 | 0 | 32 | 0 | 458 | 52 | 0 | 0 | 1317.21 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 22 | 8 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 160 | 47 | 115 | 0 | 77 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 250 | 117 | 220 | 0 | 1000 | 570 | 17 | 6088.21 | 15263.33 | 104.98
21:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 229 | 54 | 35 | 35 | 48 | 81 | 55 | 55 | 162 | 16 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 143.42 | 4 | 22 | 0 | 480 | 107 | 16 | 50 | 0 | 0 | 50 | 35 | 35 | 24 | 25 | 0 | 222 | 55 | 0 | 1130 | 17 | 0 | 50 | 25.5 | 34 | 206 | 0 | 0 | 0 | 1224 | 0 | 108 | 0 | 240 | 300 | 300 | 44 | 0 | 218 | 0 | 115 | 80 | 156 | 73 | 19 | 103 | 170 | 52.2 | 0 | 21 | 310 | 400 | 396 | 40 | 40 | 0 | 0 | 0 | 0 | 53 | 25 | 142 | 0 | 126 | 17 | 86 | 0 | 163 | 0 | 0 | 0 | 12 | 9235.12 | 739 | 0 | 0 | 0 | 39 | 0 | 5 | 0 | 0 | 0 | 32 | 0 | 459 | 53 | 0 | 0 | 1307.38 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 21 | 8 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 0 | 160 | 47 | 115 | 0 | 77 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 250 | 116 | 220 | 0 | 1000 | 570 | 17 | 6069.38 | 15304.5 | 104.97
22:00 | 0 | 105 | 50 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 322 | 54 | 35 | 35 | 64 | 81 | 55 | 55 | 162 | 18 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 143.42 | 4 | 22 | 0 | 480 | 109 | 16 | 45 | 0 | 0 | 50 | 35 | 35 | 24 | 25 | 0 | 220 | 66 | 2 | 1130 | 16 | 0 | 50 | 25.5 | 34 | 208 | 0 | 0 | 0 | 1224 | 0 | 45 | 0 | 230 | 300 | 300 | 44 | 0 | 217 | 0 | 115 | 80 | 156 | 74 | 19 | 103 | 174 | 52.2 | 0 | 21 | 315 | 400 | 396 | 40 | 40 | 0 | 0 | 16 | 0 | 53 | 20 | 142 | 0 | 126 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 12 | 9303.12 | 739 | 0 | 0 | 0 | 30 | 0 | 5 | 0 | 0 | 0 | 32 | 0 | 460 | 53 | 0 | 0 | 1305.61 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 21 | 8 | 0 | 0 | 17 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 159 | 48 | 115 | 0 | 77 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 250 | 117 | 220 | 0 | 1000 | 570 | 17 | 6062.61 | 15365.73 | 104.97
23:00 | 0 | 89 | 42 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 312 | 54 | 35 | 35 | 64 | 81 | 32 | 55 | 162 | 16 | 0 | 0 | 0 | 35 | 0 | 36 | 0 | 0 | 143.42 | 4 | 22 | 0 | 480 | 106 | 16 | 45 | 0 | 0 | 50 | 35 | 17 | 24 | 25 | 0 | 219 | 55 | 2 | 1130 | 16 | 0 | 50 | 25.5 | 34 | 211 | 0 | 0 | 0 | 1224 | 0 | 20 | 0 | 230 | 300 | 300 | 51 | 0 | 220 | 0 | 109 | 80 | 157 | 73 | 19 | 103 | 166 | 19 | 0 | 22 | 325 | 398 | 380 | 40 | 39 | 0 | 0 | 16 | 0 | 53 | 20 | 141 | 0 | 126 | 17 | 87 | 0 | 163 | 0 | 0 | 0 | 12 | 9079.92 | 739 | 0 | 0 | 6 | 30 | 0 | 9.5 | 0 | 0 | 0 | 32 | 0 | 459 | 54 | 0 | 0 | 1307.25 | 0 | 0 | 0 | 55 | 70 | 0 | 42 | 21 | 8 | 0 | 0 | 17 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 157 | 48 | 115 | 0 | 77 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 250 | 117 | 220 | 0 | 1000 | 570 | 17 | 6063.75 | 15143.67 | 105.97
Total KWH | 0 | 1252760 | 624480 | 0 | 0 | 0 | 0 | 0 | 9806400 | 0 | 7211044 | 592560 | 835920 | 557856 | 1493280 | 1038764 | 529091 | 986130 | 1995840 | 115200 | 0 | 0 | 0 | 867819 | 0 | 2282000 | 0 | 53383 | 1748400 | 95400 | 524160 | 0 | 10515000 | 2487764 | 393927 | 744960 | 0 | 99840 | 404035 | 518304 | 259795 | 593280 | 600000 | 20281 | 5345078 | 1357412 | 97440 | 27112727.27 | 784509 | 0 | 1099680 | 320209.2 | 848073 | 5022035 | 0 | 0 | 0 | 28701815 | 85455 | 1227781 | 0 | 6174500 | 7776100 | 7050000 | 1122254 | 0 | 5111000 | 0 | 1402560 | 2011153 | 4101120 | 1191120 | 454000 | 2458980 | 3921600 | 676291 | 347091 | 472656 | 6506000 | 9572000 | 9343000 | 951000 | 947760 | 0 | 57613 | 271248 | 0 | 1247040 | 643488 | 3195000 | 0 | 2734570 | 216000 | 1500000 | 37440 | 2635200 | 0 | 2800 | 138130 | 261600 | 205780201.47 | 19514182 | 0 | 0 | 98400 | 368768 | 0 | 82000 | 0 | 140760 | 0 | 240912 | 219600 | 10967269 | 1248000 | 0 | 0 | 28620000 | 0 | 0 | 0 | 378336 | 823584 | 0 | 383778 | 471626 | 172013 | 104736 | 203655 | 401307 | 0 | 66752 | 3552455 | 0 | 0 | 0 | 0 | 0 | 7386763 | 0 | 5640 | 3885000 | 1154182 | 2702289 | 137373 | 677788 | 0 | 1011465 | 0 | 32641.92 | 1026720 | 2587 | 1029888 | 5826000 | 2782000 | 5294700 | 0 | 24109091 | 13943272.73 | 446400 | 139511933.65 | 345292135.12

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-09-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14238.98 | MW | 12:00 Hr. | Energy Generated |  |  | 345.2921 |  | MKWHr.
| Day Peak Demand |  |  | 15037.98 | MW | 12:00 Hr. | Energy Unserverd |  |  | 26.977 |  | MKWHr.
| Evening Peak Generation |  |  | 15304.5 | MW | 21:00 Hr. | Energy Demand |  |  | 372.2691 |  | MKWHr.
| Evening Peak Demand |  |  | 17535.5 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.3 |  | °C
| Minimum Generation of the Day |  |  | 13496.07 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 847.27 |  | MMCFD
| Maximum Generation of the Day |  |  | 15365.73 | MW | 22:00 Hr. | Production Cost per KWHr |  |  | 7.5483 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 30.434 | 0 | 12.6381 | 0 | 0 | 0.053383 | 0 | 0 | 43.1255 | Gas | 119.6795 | Gas | 416584225.84
| Chattogram Zone |  |  | 5.1195 | 55.8145 | 10.4119 | 0 | 5.3451 | 0.10574 | 0 | 0.09984 | 76.8966 | Coal | 115.6994 | Coal | 802497683.7001
| Cumilla Zone |  |  | 29.699 | 0 | 11.5305 | 0 | 0 | 0.34709 | 3.9216 | 0 | 45.4982 | HFO | 48.6364 | HFO | 971425096.556
| Mymensingh Zone |  |  | 0 | 0 | 4.6128 | 0 | 0 | 0.17837 | 0 | 0 | 4.7912 | HSD | 1.2342 | HSD | 36006031.2
| Sylhet Zone |  |  | 35.4111 | 0 | 0 | 0 | 0 | 0.057613 | 0 | 0 | 35.4687 | Hydro | 5.3451 | Hydro | 534507.8
| Khulna Zone |  |  | 0 | 10.9673 | 1.9561 | 0.22276 | 0 | 0.2196 | 19.5142 | 0 | 32.8799 | Solar | 2.5419 | Solar | 42057323.3312
| Barishal Zone |  |  | 8.0767 | 43.8784 | 1.4763 | 0 | 0 | 0.002587 | 0 | 0 | 53.4339 | Import | 52.0558 | Import | 335789522.88
| Rajshahi Zone |  |  | 10.9392 | 0 | 2.6306 | 0 | 0 | 0.38078 | 28.62 | 0 | 42.5706 | Wind | 0.09984 | Wind | 1468646.4
| Rangpur Zone |  |  | 0 | 5.0392 | 3.3801 | 1.0115 | 0 | 1.1967 | 0 | 0 | 10.6275
| Total |  |  | 119.6795 | 115.6994 | 48.6364 | 1.2342 | 5.3451 | 2.5419 | 52.0558 | 0.09984 | 345.2921
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 416584225.84 |  | Hydro | 534507.8
|  |  |  | Coal | 802497683.7001 |  | Solar | 42057323.3312
|  |  |  | HFO | 971425096.556 |  | Import | 335789522.88
|  |  |  | HSD | 36006031.2 |  | Wind | 1468646.4
[5 empty] | Total: | 260,63,63,037 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.5142 | Peak Hr Flow | 739.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 28125854.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.62 | Peak Hr Flow | 1307.38 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1179 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.9216 | Peak Hr Flow | 170.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 1969 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.0558 | Peak Hr Flow | 2216.38 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 744 |  | 6166
|  |  |  | Chattogram |  | 183 |  | 1625
|  |  |  | Cumilla |  | 248 |  | 1678
|  |  |  | Mymensingh |  | 144 |  | 1320
|  |  |  | Sylhet |  | 121 |  | 727
|  |  |  | Khulna |  | 222 |  | 2028
|  |  |  | Barishal |  | 120 |  | 560
|  |  |  | Rajshahi |  | 209 |  | 1637
|  |  |  | Rangpur |  | 144 |  | 1136
|  |  |  | Total |  | 2135 |  | 16877
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 54
|  |  |  | Total Unavailable Capacity |  |  |  | 354
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 11:00 | 12:25 | Kushtia 132/33kV S/S T-1 LT Forced S/D Due to T-1 33 kv bushing oil leakage maintenance
| 11:01 | 12:24 | Kushtia 132/33kV S/S T-1 HT Forced S/D Due to T-1 33 kv bushing oil leakage maintenance
| 11:23 | 13:30 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to SPDB 33KV Bus Red Hot Works
| 11:23 | 13:30 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to SPDB 33KV Bus Red Hot Works
| 11:54 | 13:08 | Sirajganj 132/33kV S/S T1-(415) HT Forced S/D Due to Emergency Maintenance of T1 33kV CT
Red-hot.
| 11:54 | 13:07 | Sirajganj 132/33kV S/S T1-(415) LT Forced S/D Due to Emergency Maintenance of T1 33kV CT
Red-hot.
| 12:00 |  | Day Peak Generation: 14239 MW.
| 12:10 | 13:32 | Munshiganj 132/33kV S/S Transformer-2 LT Tripped showing Trip circuit supervision relay | [7 empty] | 35.0MW load
|  |  | relays Due to The 33 kV breaker tripped due to a bird falling on the auxiliary-02 | [7 empty] | interrup.
transformer.
| 12:10 | 13:08 | Munshiganj 132/33kV S/S Transformer-1 LT Tripped showing Trip circuit supervision relay | [7 empty] | 35.0MW load
|  |  | relays Due to The 33 kV breaker tripped due to a bird falling on the auxiliary-02 | [7 empty] | interrup.
transformer.
| 12:28 | 20:00 | Baghabari-Bangura 132 kV Ckt-2 Scheduled S/D from Bhangura 132/33kV end.
| 13:20 | 17:15 | Jaldhaka 132/33kV S/S 406T-1 LT Forced S/D Due to Sf6 gas leakage maintenance
| 13:21 | 17:14 | Jaldhaka 132/33kV S/S 406T-1 HT Forced S/D Due to Sf6 gas leakage maintenance
|  | 16:44 | Fenchuganj-Sreemangal 132kV Ckt-1 is restored.
| 03:37 | 04:30 | Korerhat 400/230/132kV S/S Hathajari-1 Tripped showing Siemens (7SA87) relays Due to Y
phase to ground fault
| 03:37 | 04:32 | Baroirhat-Hathazari 132 kV Ckt-1 Tripped from Hathazari 230/132/33kV end showing y
phase,distance trip relays.
| 04:28 | 05:42 | Khulshi-MSML 132kV Ckt-2 Tripped from Khulshi 132/33kV end showing Distance Relay
relays.
| 04:28 | 05:40 | Bakulia-MSML 132 kV Ckt-2 Tripped from Bakulia 132/33kV end showing Distance Relay relays
Due to Thundering
| 04:28 | 05:42 | Bakulia-Khulshi 132 kV Ckt-1 Tripped from Khulshi 132/33kV end showing Distance Relay
relays. and from Bakulia 132/33kV end showing Distance relays Due to Thundering
| 05:58 | 06:58 | Daudkandi 132/33kV S/S Main Tripped showing distance protection relays Due to something | [7 empty] | 90.0MW load
|  |  | dropped on busbar by bird. | [7 empty] | interrup.
| 05:59 | 07:07 | Daudkandi-Sonargaon 132 kV Ckt-1 Tripped from Sonargaon 132/33kV end showing Line Dist.
Relay(21L) relays Due to Due to Daudkandi end bus fault
| 05:59 | 07:07 | Daudkandi-Sonargaon 132 kV Ckt-2 Tripped from Sonargaon 132/33kV end showing Line Dist.
Relay(21L) relays Due to Due to Daudkandi end bus fault
| 06:00 | 06:15 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing
Control panel: -Distance Protection Operated Relay panel: -C phase -V Failed relays.
| 06:51 |  | Mirpur 132/33kV S/S T1 LT Project Work S/D Due to Upgradation work Under G to G Project.
| 06:54 |  | Mirpur 132/33kV S/S T1 HT Project Work S/D Due to Upgradation work Under G to G Project.
| 07:07 | 07:36 | Mirpur 132/33kV S/S Reserve Bus Project Work S/D Due to Upgradation work (T1 Bay) Under G
to G Project.
| 07:20 |  | Fenchuganj-Sreemangal 132kV Ckt-2 Project Work S/D from Sreemongol 132/33kV end. and
from Fenchuganj 230/132/33kV end Due to Project work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-09-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 412 | 9806400 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 529091 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 99 | 2282000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 592560 | -
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 1493280 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 986130 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 867819 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 4 | 95400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 524160 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 50 | 624480 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 81 | 1038764 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 35 | 557856 | Liquid fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1252760 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 115200 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1995840 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 53383 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 835920 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 480 | 10515000 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 229 | 7211044 | Gas shortage
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 1748400 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2120.42 | 43125487
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 320209.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 85455 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1099680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5345078 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 206 | 5022035 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 848073 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 35 | 518304 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 404035 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 593280 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 97440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 50 | 744960 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 20281 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 393927 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 35 | 259795 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1357412 | FGMO
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 600000 | Liquid fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2487764 | FGMO
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 17 | 784509 | Liquid fuel shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28701815 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 99840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1130 | 27112727.27 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3305.5 | 76896619.47
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 218 | 5111000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 300 | 7776100 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 300 | 7050000 | Able to ON FGMO
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 240 | 6174500 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 0 | 0 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1122254 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 108 | 1227781 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 21 | 472656 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 2011153 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 156 | 4101120 | FGMO
| Import (Tripura) |  | Import | 0 | 160 | 170 | 3921600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 676291 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 454000 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 103 | 2458980 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 73 | 1191120 | Liquid fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1402560 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 347091 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1999.2 | 45498206
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 37440 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 2800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 2635200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 86 | 1500000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 138130 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 261600 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 216000 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 278 | 4791170
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 57613 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 951000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 947760 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under Maintenance
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 3195000 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 25 | 643488 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 53 | 1247040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 126 | 2734570 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 271248 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 6506000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 396 | 9343000 | Machine Problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9572000 | Machine Problem
Sylhet Area Total |  |  |  |  | 2325 | 1532 | 35468719
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 739 | 19514182 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 98400 | Liquid fuel shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 5 | 82000 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 39 | 368768 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 1248000 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 240912 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 219600 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 140760 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 459 | 10967269 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1327 | 32879891
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 1000 | 24109091 | Coal shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 64 | 1029888 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 116 | 2782000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 570 | 13943272.73 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5294700 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 446400 | Liquid fuel shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 250 | 5826000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2587 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2237 | 53433938.73
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 104736 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 471626 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 3552455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 273 | 7386763 | AGC+FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 17 | 401307 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 172013 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 383778 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 823584 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 55 | 378336 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 5640 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1307.38 | 28620000 | Coal shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 66752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 203655 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 1941.38 | 42570645
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 1011465 | -
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 47 | 1154182 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3885000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 77 | 677788 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32641.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2702289 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 137373 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1026720 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 564 | 10627458.92
Eastern Grid Total |  |  |  |  | 17427.666 | 9235.12 | 205780201.47
Western Grid Total |  |  |  |  | 11731.125 | 6069.38 | 139511933.65
National Grid Total |  |  |  |  | 29158.791 | 15304.5 | 345292135.12
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-09-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10076.43 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4665.5 | MW
i) Dhaka area |  |  | 5422.43 |  | MW | i) Khulna area |  |  |  | 1806 | MW
ii) Chattogram area |  |  | 1442 |  | MW | ii) Barishal area |  |  |  | 439.9 | MW
iii) Cumilla area |  |  | 1430 |  | MW | iii) Rajshahi area |  |  |  | 1427.6 | MW
iv) Mymensingh area |  |  | 1176 |  | MW | iv) Rangpur area |  |  |  | 992 | MW
v) Sylhet area |  |  | 606 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14741.93 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Halishahar | 145 | 15:00 | 133 | Narinda | 74 | 13:00 | 199 | Ullon | 50 | 00:00
2 | AKSML | 171.2 | 16:00 | 68 | HaripurSBU | 135 | 09:00 | 134 | Narshingdi | 182 | 23:00 | 200 | Uttara | 98 | 13:00
3 | Aftabnagar | 44 | 00:00 | 69 | Hasnabad | 95 | 12:00 | 135 | Natore | 144 | 00:00 | 201 | UttaraNew | 54 | 00:00
4 | Agargaon | 125 | 13:00 | 70 | Hathazari | 86 | 18:00 | 136 | Nawabganj | 54.1 | 04:00 | 202 | Zigatola | 100 | 14:00
5 | Agrabad | 70 | 11:00 | 71 | Hatirjheel | 85 | 12:00 | 137 | Netrakona | 133 | 18:00
6 | Amnura | 29 | 23:00 | 72 | Ishurdi | 73 | 18:00 | 138 | New | 92 | 09:00
7 | Araihazar | 56 | 01:00 | 73 | Jaldhaka | 76 | 19:30 | 139 | Niamatpur | 64 | 00:00
8 | Ashuganj | 87 | 00:00 | 74 | Jamalpur | 128 | 00:00 | 140 | Noapara | 45 | 20:00
9 | BSRM | 200 | 17:00 | 75 | Jashore | 163 | 19:00 | 141 | PHP | 11 | 17:00
10 | Bagerhat | 80 | 07:00 | 76 | Jhenaidah | 84 | 18:30 | 142 | Pabna | 94 | 07:00
11 | Bajitpur | 108 | 18:30 | 77 | Joydebpur | 168 | 18:00 | 143 | Palashbari | 122 | 00:00
12 | Bakerganj | 12.4 | 18:30 | 78 | Joypurhat | 53 | 00:00 | 144 | Panchagarh | 72 | 19:00
13 | Bakulia | 94 | 21:00 | 79 | Juldah | 18 | 15:00 | 145 | Patiya | 22 | 05:00
14 | Banani | 56 | 13:00 | 80 | KSRM | 26 | 10:00 | 146 | Patnitala | 31 | 20:00
15 | Bangabhaban | 17 | 10:00 | 81 | Kabirpur | 274 | 08:00 | 147 | Patuakhali | 62.5 | 05:00
16 | Barapukuria | 65 | 21:00 | 82 | Kachua | 90 | 00:00 | 148 | Payra | 32 | 04:00
17 | Barguna | 20 | 06:00 | 83 | Kaliganj | 39 | 18:30 | 149 | Postogola | 65 | 13:00
18 | Barishal | 94 | 12:00 | 84 | Kallyanpur | 126 | 00:00 | 150 | Pubail | 43 | 08:00
19 | Barishal-230 | 106 | 00:00 | 85 | Kalurghat | 42 | 10:00 | 151 | Purbachal | 21 | 00:00
20 | Baroaulia | 55 | 00:00 | 86 | Kamrangirchar | 82 | 13:00 | 152 | Purbasadipur | 128 | 23:00
21 | Baroirhat | 57 | 18:30 | 87 | Kaptai | N/A | N/A | 153 | Rahanpur | 32 | 22:00
22 | Bashundhara | 228 | 14:00 | 88 | Kasba | 39 | 00:00 | 154 | Rahim | 55 | 22:00
23 | BashundharaCement | 1 | 17:00 | 89 | Kazla | 114 | 00:00 | 155 | Rajbari | 86.5 | 18:30
24 | Beanibazar | 76 | 05:00 | 90 | Keranigonj | 88 | 17:00 | 156 | Rajendrapur | 114 | 07:00
25 | Benapole | 66 | 01:00 | 91 | Khagrachori | 32 | 18:30 | 157 | Rajshahi | 114 | 13:00
26 | Bhaluka | 167 | 18:00 | 92 | Khulna | 60 | 07:00 | 158 | Rajshahi-230 | 93 | 19:00
27 | Bhandaria | 53 | 05:00 | 93 | Khulshi | 173 | 00:00 | 159 | Ramganj | 104 | 05:00
28 | Bhangura | 35 | 21:00 | 94 | Kishoreganj | 144 | 20:00 | 160 | Rampur | 43 | 21:00
29 | Bheramara(GK) | 62 | 21:00 | 95 | Kodda | 306 | 21:00 | 161 | Rangamati | 16 | 18:30
30 | Bhulta | 225 | 21:00 | 96 | Kulaura | 54 | 22:00 | 162 | Rangpur | 132 | 21:00
31 | Bog-Sherpur | 66 | 20:00 | 97 | Kurigram | 66 | 18:00 | 163 | Ruppur | 4.2 | 15:00
32 | Bogura | 212 | 00:00 | 98 | Kushtia | 156 | 20:00 | 164 | SSM | 0 | 00:00
33 | Borhanuddin | 68 | 05:00 | 99 | Laksam | 36 | 22:00 | 165 | Saidpur | 101 | 20:00
34 | Brahmanbaria | 131 | 18:30 | 100 | Lakshmipur | 54 | 19:30 | 166 | Santhia | 30 | 00:00
35 | Cantonment | 132 | 13:00 | 101 | Lalbag | 80 | 13:00 | 167 | Satkhira | 135 | 00:00
36 | Chandina | 20 | 14:00 | 102 | Lalmonirhat | 66 | 05:00 | 168 | Satmasjid | 111 | 13:00
37 | Chandpur | 84 | 00:00 | 103 | MI_Cement | 16.2 | 01:00 | 169 | Savar | 215 | 10:00
38 | Chandraghona | 31 | 22:00 | 104 | Madanganj | 54 | 19:30 | 170 | SevenRings | 7.2 | 17:00
39 | Chapai | 64 | 20:00 | 105 | Madaripur | 105 | 21:00 | 171 | ShahCement | 22 | 01:00
40 | Charfasson | 31 | 22:00 | 106 | Madartek | 90 | 00:00 | 172 | Shahjadpur | 74 | 20:00
41 | Charsaidpur | 28 | 00:00 | 107 | Madunaghat | 51 | 18:00 | 173 | Shahjibazar | 128 | 21:00
42 | Chauddagram | 70 | 05:00 | 108 | Magura | 65 | 22:00 | 174 | Shahmirpur | 59 | 18:30
43 | Chhatak | 34 | 20:00 | 109 | Mahasthangarh | 70 | 04:00 | 175 | Shariatpur | 88 | 18:30
44 | Chowmuhani | 150 | 23:00 | 110 | Maijdee | 36 | 05:00 | 176 | Sherpur | 150 | 20:00
45 | Chuadanga | 116 | 22:00 | 111 | Manikganj | 130 | 00:00 | 177 | Shikalbaha | 38 | 00:00
46 | Coxsbazar | 137 | 11:00 | 112 | Maniknagar | 84 | 13:00 | 178 | Shitalakhya | 82.6 | 13:00
47 | Cumilla(N) | 133 | 21:00 | 113 | Matarbari | 56 | 22:00 | 179 | Sholosohor | 49 | 12:00
48 | Cumilla(S) | 183 | 18:30 | 114 | Matuail | 80 | 15:00 | 180 | Shomvuganj | 46 | 10:00
49 | Daganbhuiyan | 36 | 22:00 | 115 | Metrorail_Motijheel | 20 | 19:00 | 181 | Shyampur | 176 | 12:00
50 | Daudkandi | 136 | 00:00 | 116 | Metrorail_Uttara | 0 | 00:00 | 182 | Siddhirganj | 138 | 11:00
51 | DhakaUniversity | 96 | 13:00 | 117 | Millgate | 100 | 10:00 | 183 | Sirajganj | 112 | 20:00
52 | Dhamrai | 98 | 18:30 | 118 | Mirpur | 156 | 15:00 | 184 | Sitakunda | 13 | 00:00
53 | Dhanmondi | 127.5 | 13:00 | 119 | Mirsorai | 40 | 15:00 | 185 | Sonargaon | 148 | 06:00
54 | Dohazari | 117 | 20:00 | 120 | Mirzapur | 48 | 12:00 | 186 | Sreemongol | 76 | 18:30
55 | Faridpur | 180 | 00:00 | 121 | Mithapukur | 68 | 04:00 | 187 | Sreepur | 130 | 19:30
56 | Fatullah | 119 | 10:00 | 122 | Modern | N/A | N/A | 188 | Srinagar | 43.45 | 05:00
57 | Fenchuganj | 44 | 18:30 | 123 | Mogbazar | 65.3 | 13:00 | 189 | Sunamganj | 56 | 22:00
58 | Feni | 112 | 18:30 | 124 | Mongla | 44 | 19:00 | 190 | Sylhet | 139 | 00:00
59 | GPH | 1 | 00:00 | 125 | Motijheel | 56 | 13:00 | 191 | Sylhet_(South) | 63 | 19:30
60 | Ghatail | 86 | 00:00 | 126 | Muktagacha | 39 | 19:30 | 192 | TK | 0 | 00:00
61 | Ghorashal | 0 | 00:00 | 127 | Munshiganj | 102 | 06:00 | 193 | Tangail | 170 | 20:00
62 | Ghorashal-230 | 106 | 09:00 | 128 | Muradnagar | 50 | 06:00 | 194 | Taraganj | 30 | 08:00
63 | Goalpara | 42 | 23:00 | 129 | Mymensingh | 150 | 21:00 | 195 | Tasnim | 46 | 21:00
64 | Gollamari | 104 | 20:00 | 130 | Nabinagar | 104 | 11:00 | 196 | Thakurgaon | 108 | 19:30
65 | Gopalganj | 111 | 19:00 | 131 | Naogaon | 115 | 00:00 | 197 | Tongi | 152 | 11:00
66 | Gulshan | 120 | 15:00 | 132 | Narail | 65 | 20:00 | 198 | Ullahpara | 35 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-09-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 15234.78 | 1990 |  | 17314.78
1:00 | 14283.39 | 2122 |  | 16500.88
2:00 | 14101.72 | 1984 |  | 16174.72
3:00 | 14024.12 | 1881 |  | 15990.12
4:00 | 13844.26 | 1242 |  | 15142.26
5:00 | 13959.85 | 328 |  | 14302.85
6:00 | 13627.31 | 315 |  | 13956.31
7:00 | 13678.3 | 202 |  | 13889.3
8:00 | 13496.07 | 222 |  | 13728.07
9:00 | 13761.08 | 80 |  | 13845.08
10:00 | 13914.09 | 26 |  | 13941.09
11:00 | 13998.63 | 26 |  | 14025.63
12:00 | 14238.98 | 765 |  | 15037.98
13:00 | 13921.55 | 1210 |  | 15185.55
14:00 | 14036.24 | 1322 |  | 15417.24
15:00 | 14023.66 | 1656 |  | 15754.66
16:00 | 13971.01 | 1003 |  | 15019.01
17:00 | 14371.34 | 972 |  | 15387.34
18:00 | 14429.58 | 666 |  | 15125.58
19:00 | 15136.04 | 1606 |  | 16814.04
19:30 | 15190.44 | 1828 |  | 17100.44
20:00 | 15263.33 | 1766 |  | 17108.33
21:00 | 15304.5 | 2135 |  | 17535.5
22:00 | 15365.73 | 1594 |  | 17031.73
23:00 | 15143.67 | 1864 |  | 17091.67
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 06-09-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 92 | 38 | 300 | 206 | 956 | 644 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 103 | 55 | 300 | 182 | 996 | 1000
2:00 | 88 | 47 | 280 | 190 | 890 | 640 |  | Import | 0
3:00 | 97 | 49 | 306 | 194 | 916 | 640
4:00 | 101 | 51 | 320 | 198 | 932 | 640 | Ishurdi-Ghorashal Ckt-2 | Export | 2995854.54
5:00 | 104 | 50 | 330 | 200 | 882 | 614
6:00 | 111 | 52 | 360 | 198 | 962 | 630 |  | Import | 0
7:00 | 102 | 52 | 340 | 210 | 896 | 612
8:00 | 107 | 63 | 300 | 178 | 964 | 654 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 169 | 75 | 380 | 174 | 1210 | 748
10:00 | 177 | 72 | 410 | 178 | 1288 | 816 |  | Import | 0
11:00 | 175 | 66 | 510 | 198 | 1284 | 862
12:00 | 153 | 57 | 420 | 220 | 1094 | 806 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 163 | 76 | 440 | 216 | 1268 | 812
14:00 | 163 | 72 | 426 | 220 | 1282 | 842 |  | Import | 0
15:00 | 167 | 77 | 410 | 204 | 1258 | 830
16:00 | 158 | 75 | 406 | 228 | 1262 | 834 | Gopalganj-Aminbazar Ckt-1 | Export | 12600000
17:00 | 157 | 77 | 390 | 220 | 1232 | 810
18:00 | 156 | 73 | 420 | 240 | 1233 | 816 |  | Import | 0
18:30 | 147 | 65 | 376 | 200 | 1100 | 748
19:00 | 98 | 63 | 286 | 170 | 964 | 688 | Gopalganj-Aminbazar Ckt-2 | Export | 12530000
19:30 | 93 | 49 | 296 | 186 | 926 | 634
20:00 | 81 | 40 | 280 | 180 | 854 | 588 |  | Import | 0
21:00 | 75 | 35 | 280 | 194 | 824 | 584
22:00 | 79 | 34 | 310 | 202 | 836 | 598 |  | Total Export | 28125854.54
23:00 | 76 | 32 | 294 | 196 | 842 | 612 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-09-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9103.7 | 6131.08 | 15234.78 | DAILY GENERATION CURVE
00:30 | 8821.95 | 5937.135 | 14759.085
01:00 | 8540.2 | 5743.19 | 14283.39 | 06-09-2026
01:30 | 8509.2 | 5683.355 | 14192.555
02:00 | 8478.2 | 5623.52 | 14101.72
02:30 | 8448.7 | 5614.22 | 14062.92
03:00 | 8419.2 | 5604.92 | 14024.12
03:30 | 8357.7 | 5576.49 | 13934.19
04:00 | 8296.2 | 5548.06 | 13844.26
04:30 | 8346.1 | 5555.955 | 13902.055
05:00 | 8396 | 5563.85 | 13959.85
05:30 | 8220.6 | 5572.98 | 13793.58
06:00 | 8045.2 | 5582.11 | 13627.31
06:30 | 8060.76 | 5592.045 | 13652.805
07:00 | 8076.32 | 5601.98 | 13678.3
07:30 | 8039.21 | 5547.975 | 13587.185
08:00 | 8002.1 | 5493.97 | 13496.07
08:30 | 8062.625 | 5565.95 | 13628.575
09:00 | 8123.15 | 5637.93 | 13761.08
09:30 | 8165.85 | 5671.735 | 13837.585
10:00 | 8208.55 | 5705.54 | 13914.09
10:30 | 8246.04 | 5710.32 | 13956.36
11:00 | 8283.53 | 5715.1 | 13998.63
11:30 | 8386.235 | 5732.57 | 14118.805
12:00 | 8488.94 | 5750.04 | 14238.98
12:30 | 8340.805 | 5739.46 | 14080.265
13:00 | 8192.67 | 5728.88 | 13921.55
13:30 | 8239.53 | 5739.365 | 13978.895
14:00 | 8286.39 | 5749.85 | 14036.24
14:30 | 8291.05 | 5738.9 | 14029.95
15:00 | 8295.71 | 5727.95 | 14023.66
15:30 | 8268.37 | 5728.965 | 13997.335
16:00 | 8241.03 | 5729.98 | 13971.01
16:30 | 8408.255 | 5762.92 | 14171.175
17:00 | 8575.48 | 5795.86 | 14371.34
17:30 | 8567.16 | 5833.3 | 14400.46
18:00 | 8558.84 | 5870.74 | 14429.58
18:30 | 8818.73 | 5964.08 | 14782.81
19:00 | 9078.62 | 6057.42 | 15136.04
19:30 | 9142.12 | 6048.32 | 15190.44
20:00 | 9175.12 | 6088.21 | 15263.33
20:30 | 9205.12 | 6078.795 | 15283.915 |  | Executive Engineer
21:00 | 9235.12 | 6069.38 | 15304.5 |  | Network Operation Division
21:30 | 9269.12 | 6065.995 | 15335.115
22:00 | 9303.12 | 6062.61 | 15365.73
22:30 | 9191.52 | 6063.18 | 15254.7
23:00 | 9079.92 | 6063.75 | 15143.67

## En-Curve
QF-LDC-12
Date | 06-09-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3701 | 1385 | 734 | 0 | 162 | 1055.08 | 221 | 4866 | 0 | 520 | 2175.7 | 404 | 0 | 11 | 1990 | DAILY ENERGY CURVE
00:30 | 3697.5 | 1369 | 718 | 0 | 166 | 1171.135 | 221.5 | 4864 | 0 | 460 | 1863.45 | 217 | 0 | 11.5 | 2056 | 06-09-2026
01:00 | 3694 | 1353 | 702 | 0 | 170 | 1287.19 | 222 | 4862 | 0 | 400 | 1551.2 | 30 | 0 | 12 | 2122
01:30 | 3691 | 1352 | 701.5 | 0 | 170 | 1270.355 | 222 | 4863.5 | 0 | 369 | 1530.7 | 15 | 0 | 7.5 | 2053 | Energy Generated | 345.2921 |  | MKWHr
02:00 | 3688 | 1351 | 701 | 0 | 170 | 1253.52 | 222 | 4865 | 0 | 338 | 1510.2 | 0 | 0 | 3 | 1984 | Energy not Served | 26.977 |  | MKWHr
02:30 | 3692 | 1331.5 | 701.5 | 0 | 168 | 1262.22 | 222 | 4864.5 | 0 | 312.5 | 1505.2 | 0 | 0 | 3.5 | 1932.5 | Total Energy Requirement | 372.2691 |  | MKWHr
03:00 | 3696 | 1312 | 702 | 0 | 166 | 1270.92 | 222 | 4864 | 0 | 287 | 1500.2 | 0 | 0 | 4 | 1881
03:30 | 3671 | 1254 | 701.5 | 0 | 165 | 1262.49 | 222 | 4863 | 0 | 283.5 | 1509.7 | 0 | 0 | 2 | 1561.5
04:00 | 3646 | 1196 | 701 | 0 | 164 | 1254.06 | 222 | 4862 | 0 | 280 | 1519.2 | 0 | 0 | 0 | 1242
04:30 | 3673.5 | 1328.5 | 701.5 | 0 | 158 | 1249.455 | 222 | 4867.5 | 0 | 255.5 | 1442.1 | 0 | 0 | 4 | 785
05:00 | 3701 | 1461 | 702 | 0 | 152 | 1244.85 | 222 | 4873 | 0 | 231 | 1365 | 0 | 0 | 8 | 328
05:30 | 3636 | 1346 | 702 | 0 | 154 | 1255.36 | 222 | 4863 | 1.62 | 222 | 1383.6 | 0 | 0 | 8 | 321.5
06:00 | 3571 | 1231 | 702 | 0 | 156 | 1265.87 | 222 | 4853 | 3.24 | 213 | 1402.2 | 0 | 0 | 8 | 315
06:30 | 3561 | 1329 | 702 | 0 | 145 | 1264.005 | 222 | 4827.5 | 29.6 | 209.5 | 1359.2 | 0 | 0 | 4 | 258.5
07:00 | 3551 | 1427 | 702 | 0 | 134 | 1262.14 | 222 | 4802 | 55.96 | 206 | 1316.2 | 0 | 0 | 0 | 202
07:30 | 3537 | 1346.75 | 680.5 | 0 | 141 | 1261.27 | 221 | 4808.5 | 79.465 | 206 | 1303.2 | 0 | 0 | 2.5 | 212
08:00 | 3523 | 1266.5 | 659 | 0 | 148 | 1260.4 | 220 | 4815 | 102.97 | 206 | 1290.2 | 0 | 0 | 5 | 222
08:30 | 3516.5 | 1269.25 | 782.5 | 0 | 152 | 1184.115 | 220 | 4808.5 | 146.61 | 215 | 1331.6 | 0 | 0 | 2.5 | 151
09:00 | 3510 | 1272 | 906 | 0 | 156 | 1107.83 | 220 | 4802 | 190.25 | 224 | 1373 | 0 | 0 | 0 | 80
09:30 | 3552 | 1279.5 | 914.5 | 0 | 155 | 1110.925 | 219.5 | 4778.5 | 203.66 | 221 | 1403 | 0 | 0 | 0 | 53
10:00 | 3594 | 1287 | 923 | 0 | 154 | 1114.02 | 219 | 4755 | 217.07 | 218 | 1433 | 0 | 0 | 0 | 26
10:30 | 3547.5 | 1330.5 | 925.5 | 0 | 156 | 1108.735 | 219 | 4723 | 257.625 | 225.5 | 1462.5 | 0 | 0 | 0.5 | 26
11:00 | 3501 | 1374 | 928 | 0 | 158 | 1103.45 | 219 | 4691 | 298.18 | 233 | 1492 | 0 | 0 | 1 | 26
11:30 | 3530 | 1441 | 928 | 0 | 162 | 1113.93 | 219 | 4715 | 278.375 | 236.5 | 1493 | 0 | 0 | 2 | 395.5
12:00 | 3559 | 1508 | 928 | 0 | 166 | 1124.41 | 219 | 4739 | 258.57 | 240 | 1494 | 0 | 0 | 3 | 765
12:30 | 3541.5 | 1373.5 | 928 | 0 | 166 | 1113.15 | 219.5 | 4716 | 299.615 | 228.5 | 1490 | 0 | 0 | 4.5 | 987.5
13:00 | 3524 | 1239 | 928 | 0 | 166 | 1101.89 | 220 | 4693 | 340.66 | 217 | 1486 | 0 | 0 | 6 | 1210
13:30 | 3536 | 1268 | 928 | 0 | 169 | 1116.66 | 220 | 4683 | 334.235 | 217.5 | 1497.5 | 0 | 0 | 9 | 1266
14:00 | 3548 | 1297 | 928 | 0 | 172 | 1131.43 | 220 | 4673 | 327.81 | 218 | 1509 | 0 | 0 | 12 | 1322
14:30 | 3545 | 1296.5 | 928 | 0 | 177 | 1116.32 | 220 | 4671 | 317.13 | 254.5 | 1497 | 0 | 0 | 7.5 | 1489
15:00 | 3542 | 1296 | 928 | 0 | 182 | 1101.21 | 220 | 4669 | 306.45 | 291 | 1485 | 0 | 0 | 3 | 1656
15:30 | 3525 | 1252.5 | 927.5 | 0 | 175 | 1104.31 | 220.5 | 4721.5 | 266.525 | 303.5 | 1493 | 0 | 0 | 8 | 1329.5
16:00 | 3508 | 1209 | 927 | 0 | 168 | 1107.41 | 221 | 4774 | 226.6 | 316 | 1501 | 0 | 0 | 13 | 1003
16:30 | 3537.5 | 1286.5 | 927.5 | 0 | 168 | 1111.14 | 221 | 4784 | 164.325 | 361.21 | 1595.5 | 5 | 0 | 9.5 | 987.5
17:00 | 3567 | 1364 | 928 | 0 | 168 | 1114.87 | 221 | 4794 | 102.05 | 406.42 | 1690 | 10 | 0 | 6 | 972
17:30 | 3547.5 | 1326.5 | 927.5 | 0 | 166 | 1151.765 | 221 | 4773.5 | 53.775 | 459.42 | 1753.5 | 10 | 0 | 10 | 819
18:00 | 3528 | 1289 | 927 | 0 | 164 | 1188.66 | 221 | 4753 | 5.5 | 512.42 | 1817 | 10 | 0 | 14 | 666
18:30 | 3531 | 1342 | 833 | 0 | 163 | 1249.54 | 221.5 | 4793.5 | 2.75 | 567.92 | 1979.6 | 90 | 0 | 9 | 1136
19:00 | 3534 | 1395 | 739 | 0 | 162 | 1310.42 | 222 | 4834 | 0 | 623.42 | 2142.2 | 170 | 0 | 4 | 1606
19:30 | 3554 | 1275 | 739 | 0 | 156 | 1316.32 | 222 | 4838 | 0 | 638.42 | 2281.7 | 170 | 0 | 0 | 1828
20:00 | 3556 | 1314 | 738 | 0 | 162 | 1317.21 | 222 | 4839 | 0 | 635.42 | 2309.7 | 170 | 0 | 0 | 1766
20:30 | 3554.5 | 1347.5 | 738.5 | 0 | 166 | 1312.295 | 222 | 4839.5 | 0 | 623.42 | 2310.2 | 170 | 0 | 0 | 1950.5
21:00 | 3553 | 1381 | 739 | 0 | 170 | 1307.38 | 222 | 4840 | 0 | 611.42 | 2310.7 | 170 | 0 | 0 | 2135
21:30 | 3547.5 | 1439 | 739 | 0 | 172 | 1306.495 | 221 | 4840.5 | 0 | 614.92 | 2284.7 | 170 | 0 | 0 | 1864.5
22:00 | 3542 | 1497 | 739 | 0 | 174 | 1305.61 | 220 | 4841 | 0 | 618.42 | 2258.7 | 170 | 0 | 0 | 1594
22:30 | 3503 | 1500.5 | 739 | 0 | 170 | 1306.43 | 219.5 | 4839.5 | 0 | 605.92 | 2198.6 | 172.25 | 0 | 0 | 1729
23:00 | 3464 | 1504 | 739 | 0 | 166 | 1307.25 | 219 | 4838 | 0 | 593.42 | 2138.5 | 174.5 | 0 | 0 | 1864
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-09-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 369 | 20:00 | 355 | 11:00 | Madunaghat | 394 | 20:00 | 389 | 11:00
Amtali | 411 | 04:00 | 406 | 12:00 | Meghnaghat | 374 | 20:00 | 361 | 11:00
Ashuganj | 363 | 20:00 | 344 | 10:00 | Mirsorai | 390 | 01:00 | 382 | 11:00
Bhulta | 387 | 03:00 | 370 | 11:00 | Payra | 413 | 19:30 | 410 | 02:00
Bibiana | 377 | 19:30 | 371 | 09:00 | Rahanpur | 409 | 18:00 | 403 | 02:00
BIPTC | 408 | 08:00 | 394 | 16:00 | Rampal | 390 | 08:00 | 381 | 12:00
Bogura | 394 | 18:00 | 387 | 02:00
Gopalganj | 386 | 04:00 | 378 | 12:00
Kaliakoir | 363 | 20:00 | 344 | 10:00
Korerhat | 391 | 12:00 | 382 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 20:00 | 212 | 11:00 | Hasnabad | 222 | 20:00 | 210 | 11:00
AKSML | 236 | 00:00 | 225 | 10:00 | Hathazari | 232 | 20:00 | 227 | 11:00
Aminbazar | 227 | 20:00 | 214 | 10:00 | Ishurdi | 236 | 19:00 | 224 | 12:00
Ashuganj | 224 | 19:30 | 216 | 12:00 | Jhenaidah | 222 | 04:00 | 213 | 12:00
Ashuganj-400 | N/A | N/A | N/A | N/A | Kachua | 226 | 19:00 | 219 | 11:00
Baghabari | 231 | 04:00 | 226 | 11:00 | Kaliakoir | 224 | 20:00 | 211 | 10:00
Barapukuria | 228 | 15:00 | 224 | 01:00 | Keranigonj | 222 | 20:00 | 210 | 11:00
Barapukuria-230 | N/A | N/A | N/A | N/A | Khulna(S) | 223 | 19:00 | 218 | 07:00
Barapukuria(N) | 230 | 13:00 | 226 | 02:00 | Korerhat | 224 | 12:00 | 218 | 11:00
Barishal | 224 | 15:00 | 221 | 00:00 | Madunaghat | 235 | 19:00 | 231 | 11:00
Bheramara | 235 | 19:00 | 222 | 12:00 | Madunaghat-400 | 237 | 21:00 | 232 | 12:00
Bhulta | 220 | 03:00 | 208 | 11:00 | Maniknagar | 218 | 05:00 | 206 | 11:00
Bibiana | 215 | 08:00 | 211 | 18:00 | Meghnaghat | 228 | 02:00 | 218 | 09:00
BIPTC | 237 | 19:00 | 222 | 12:00 | Meghnaghat-400 | 222 | 04:00 | 211 | 10:00
Birulia | 225 | 20:00 | 213 | 10:00 | Mirsorai | 227 | 04:00 | 222 | 10:00
Bogura | 238 | 19:00 | 234 | 01:00 | Naogaon | 226 | 18:00 | 216 | 00:00
Bogura-400 | 238 | 14:00 | 233 | 02:00 | Purbasadipur | 226 | 13:00 | 221 | 02:00
Borhanuddin | 229 | 11:00 | 225 | 00:00 | Rajshahi | 233 | 19:00 | 223 | 12:00
BSRM | 225 | 20:00 | 219 | 11:00 | Rampal | 222 | 04:00 | 217 | 07:00
Charfasson | 229 | 16:00 | 225 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 226 | 00:00 | 220 | 11:00 | Rampura | 220 | 04:00 | 207 | 11:00
Cumilla(N) | 220 | 21:00 | 212 | 16:00 | Shikalbaha | 235 | 01:00 | 231 | 12:00
Faridpur | 218 | 03:00 | 214 | 12:00 | Shyampur | 221 | 04:00 | 209 | 11:00
Fenchuganj | 216 | 01:00 | 212 | 18:30 | Siddhirganj | 221 | 18:30 | 210 | 14:00
Feni | 222 | 04:00 | 216 | 11:00 | Sirajgonj | 236 | 19:00 | 232 | 12:00
Ghorashal | 225 | 19:30 | 215 | 09:00 | Sreepur | 222 | 19:00 | 215 | 12:00
Ghorashal-230 | 214 | 23:00 | 198 | 09:00 | Tongi | 213 | 19:00 | 197 | 09:00
Gopalganj | 219 | 02:00 | 215 | 12:00
GPH | 230 | 17:00 | 226 | 10:00
Haripur | 220 | 03:00 | 208 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 03:00 | 125 | 11:00 | Madanganj | 132 | 21:00 | 122 | 11:00
Agargaon | 132 | 04:00 | 123 | 10:00 | Madaripur | 130 | 01:00 | 127 | 12:00
Agrabad | 133 | 01:00 | 31 | 13:00 | Madartek | 135 | 04:00 | 124 | 11:00
AKS | 132 | 00:00 | 126 | 11:00 | Madunaghat | 136 | 00:00 | 133 | 11:00
Aminbazar | 130 | 19:00 | 120 | 11:00 | Magura | 133 | 13:00 | 127 | 12:00
Amnura | 134 | 17:00 | 129 | 12:00 | Mahasthangarh | 135 | 13:00 | 130 | 02:00
Araihazar | 126 | 04:00 | 118 | 16:00 | Maijdee | 126 | 00:00 | 124 | 05:00
Ashuganj | 128 | 06:00 | 123 | 16:00 | Manikganj | 127 | 19:00 | 116 | 10:00
Ashuganj-230 | 133 | 06:00 | 130 | 12:00 | Maniknagar | 135 | 04:00 | 124 | 12:00
Bagerhat | 127 | 12:00 | 121 | 21:00 | Matarbari | 125 | 05:00 | 116 | 22:00
Bajitpur | 126 | 10:00 | 118 | 18:00 | Matuail | 131 | 21:00 | 123 | 11:00
Bakerganj | 131 | 13:00 | 129 | 00:00 | Metrorail_Motijheel | 135 | 04:00 | 124 | 12:00
Bakulia | 135 | 04:00 | 131 | 10:00 | Metrorail_Uttara | 129 | 21:00 | 117 | 10:00
Banani | 134 | 02:00 | 124 | 11:00 | Millgate | 129 | 20:00 | 118 | 10:00
Bangabhaban | 135 | 05:00 | 125 | 11:00 | Mirpur | 129 | 20:00 | 120 | 11:00
Barapukuria | 138 | 00:00 | 132 | 01:00 | Mirzapur | 129 | 19:00 | 122 | 02:00
Barguna | 131 | 13:00 | 129 | 00:00 | Mithapukur | 133 | 13:00 | 129 | 07:00
Barishal | 132 | 13:00 | 128 | 00:00 | MI_Cement | 130.7 | 21:00 | 120 | 12:00
Barishal-230 | 131 | 15:00 | 128 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroaulia | 134 | 19:00 | 130 | 11:00 | Mogbazar | 138 | 03:00 | 126 | 10:00
Baroirhat | 129 | 00:00 | 127 | 10:00 | Mongla | 127 | 13:00 | 122 | 00:00
Bashundhara | 135 | 03:00 | 118 | 10:00 | Motijheel | 135 | 05:00 | 125 | 11:00
BashundharaCement | 132 | 23:00 | 122 | 11:00 | Muktagacha | 131 | 19:00 | 115 | 02:00
Beanibazar | 121 | 07:00 | 118 | 05:00 | Munshiganj | 131 | 21:00 | 121 | 11:00
Benapole | 128 | 08:00 | 121 | 23:00 | Muradnagar | 125 | 19:30 | 120 | 11:00
Bhaluka | 129 | 09:00 | 123 | 00:00 | Mymensingh | 132 | 19:00 | 113 | 18:00
Bhandaria | 128 | 15:00 | 122 | 05:00 | Nabinagar | 126 | 21:00 | 117 | 10:00
Bhangura | 133 | 08:00 | 130 | 12:00 | Naogaon | 136 | 13:00 | 130 | 00:00
Bheramara | 137 | 19:00 | 131 | 12:00 | Narail | 134 | 13:00 | 127 | 12:00
Bheramara(GK) | 137 | 15:00 | 132 | 00:00 | Narinda | 135 | 04:00 | 124 | 12:00
Bhulta | 126 | 19:30 | 119 | 11:00 | Narshingdi | 128 | 20:00 | 117 | 11:00
Bhulta-400 | 126 | 03:00 | 119 | 11:00 | Natore | 134 | 15:00 | 130 | 00:00
Birulia | 131 | 00:00 | 125 | 10:00 | Nawabganj | 134 | 20:00 | 125 | 12:00
Bog-Sherpur | 136 | 19:30 | 132 | 01:00 | Netrakona | 121 | 09:00 | 111 | 19:30
Bogura | 138 | 17:00 | 16 | 21:00 | New | 130 | 20:00 | 118 | 12:00
Bogura-230 | 138 | 18:00 | 134 | 02:00 | Niamatpur | 135 | 09:00 | 132 | 00:00
Brahmanbaria | 125 | 08:00 | 121 | 18:30 | Noapara | 131 | 09:00 | 127 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 131 | 03:00 | 122 | 12:00 | Pabna | 134 | 19:00 | 129 | 12:00
Chandina | 128 | 19:30 | 123 | 11:00 | Palashbari | 132 | 13:00 | 127 | 05:00
Chandpur | 134 | 21:00 | 130 | 10:00 | Panchagarh | 138 | 10:00 | 134 | 00:00
Chandraghona | 137 | 06:00 | 133 | 11:00 | Patiya | 134 | 01:00 | 130 | 11:00
Chapai | 132 | 01:00 | 130 | 12:00 | Patnitala | 134 | 10:00 | 130 | 22:00
Charsaidpur | 132 | 21:00 | 122 | 11:00 | Patuakhali | 132 | 15:00 | 129 | 05:00
Chauddagram | 128 | 06:00 | 124 | 11:00 | Payra | 134 | 00:00 | 133 | 08:00
Chhatak | 120 | 13:00 | 115 | 11:00 | PHP | 130 | 08:00 | 127 | 10:00
Chowmuhani | 127 | 20:00 | 124 | 11:00 | Postogola | 132 | 05:00 | 123 | 11:00
Chuadanga | 132 | 19:00 | 124 | 23:00 | Pubail | 129 | 20:00 | 118 | 09:00
Coxsbazar | 125 | 03:00 | 120 | 14:00 | Purbachal | 135 | 03:00 | 124 | 11:00
Cumilla(N) | 128 | 09:00 | 123 | 11:00 | Purbasadipur | 137 | 13:00 | 134 | 01:00
Cumilla(S) | 128 | 01:00 | 121 | 14:00 | Rahanpur | 137 | 15:00 | 134 | 01:00
Daganbhuiyan | 129 | 21:00 | 126 | 10:00 | Rahanpur-400 | 138 | 18:00 | 135 | 00:00
Daudkandi | 124 | 19:00 | 118 | 10:00 | Rahim | 131 | 06:00 | 123 | 11:00
DhakaUniversity | 134 | 01:00 | 124 | 12:00 | Rajbari | 124 | 01:00 | 121 | 00:00
Dhamrai | 128 | 21:00 | 118 | 10:00 | Rajendrapur | 133 | 09:00 | 128 | 07:00
Dhanmondi | 134.5 | 21:00 | 125 | 11:00 | Rajshahi | 132 | 06:00 | 127 | 23:00
Dohazari | 132 | 18:30 | 125 | 11:00 | Rajshahi-230 | 133 | 04:00 | 128 | 12:00
Faridpur | 127 | 03:00 | 125 | 00:00 | Ramganj | 128 | 19:00 | 125 | 11:00
Fatullah | 133 | 20:00 | 121 | 11:00 | Rampur | 134 | 06:00 | 129 | 11:00
Fenchuganj | 127 | 01:00 | 125 | 18:30 | Rampura | 135 | 04:00 | 125 | 11:00
Feni | 130 | 19:30 | 127 | 12:00 | Rangamati | 135 | 00:00 | 133 | 12:00
Feni-230 | 129 | 01:00 | 126 | 11:00 | Rangpur | 133 | 12:00 | 128 | 03:00
Ghatail | 130 | 07:00 | 117 | 03:00 | Ruppur | 137 | 15:00 | 132 | 12:00
Ghorashal | 130 | 19:30 | 121 | 09:00 | Saidpur | 136 | 19:00 | 132 | 02:00
Goalpara | 135 | 17:00 | 129 | 22:00 | Santhia | 134 | 15:00 | 131 | 00:00
Gollamari | 134 | 17:00 | 130 | 05:00 | Satkhira | 129 | 09:00 | 123 | 22:00
Gopalganj | 130 | 00:00 | 126 | 05:00 | Satmasjid | 131 | 03:00 | 122 | 12:00
Gopalganj-400 | 130 | 03:00 | 127 | 12:00 | Savar | 130 | 20:00 | 119 | 16:00
Gulshan | 134 | 06:00 | 124 | 11:00 | SevenRings | 130 | 20:00 | 121 | 09:00
Halishahar | 134 | 01:00 | 128 | 11:00 | ShahCement | 132 | 21:00 | 122 | 11:00
Haripur | 131 | 21:00 | 123 | 11:00 | Shahjadpur | 136 | 01:00 | 132 | 12:00
HaripurSBU | 131 | 04:00 | 123 | 11:00 | Shahjibazar | 124 | 07:00 | 116 | 16:00
Hasnabad | 132 | 20:00 | 123 | 11:00 | Shahmirpur | 136 | 19:30 | 132 | 11:00
Hathazari | 136 | 03:00 | 132 | 11:00 | Shariatpur | 128 | 13:00 | 125 | 12:00
Hatirjheel | 135 | 04:00 | 125 | 10:00 | Sherpur | 132 | 16:00 | 115 | 01:00
Ishurdi | 138 | 19:00 | 132 | 12:00 | Shikalbaha | 124 | 00:00 | 122 | 13:00
Jaldhaka | 134 | 13:00 | 130 | 02:00 | Shikalbaha-230 | 137 | 01:00 | 133 | 12:00
Jamalpur | 134 | 08:00 | 117 | 02:00 | Shitalakhya | 130.7 | 21:00 | 120 | 12:00
Jashore | 129 | 08:00 | 123 | 23:00 | Sholosohor | 136 | 01:00 | 131 | 14:00
Jhenaidah | 135 | 15:00 | 128 | 12:00 | Shomvuganj | 124 | 11:00 | 114 | 18:00
Jhenaidah-230 | 135 | 14:00 | 128 | 12:00 | Shyampur | 133 | 21:00 | 122 | 11:00
Joydebpur | 128 | 20:00 | 117 | 07:00 | Shyampur-230 | 133 | 20:00 | 124 | 11:00
Joypurhat | 134 | 17:00 | 130 | 01:00 | Siddhirganj | 132 | 20:00 | 123 | 11:00
Juldah | 136 | 02:00 | 132 | 11:00 | Sirajganj | 132 | 06:00 | 128 | 01:00
Kabirpur | 129 | 20:00 | 113 | 11:00 | Sitakunda | 135 | 19:00 | 132 | 10:00
Kachua | 130 | 19:00 | 126 | 11:00 | Sonargaon | 129 | 20:00 | 120 | 11:00
Kaliakoir | 132 | 18:30 | 127 | 02:00 | Sreemongol | 123 | 07:00 | 121 | 00:00
Kaliganj | 134 | 19:00 | 128 | 12:00 | Sreepur | 134 | 08:00 | 129 | 07:00
Kallyanpur | 137 | 05:00 | 121 | 10:00 | Srinagar | 134 | 19:30 | 126 | 11:00
Kalurghat | 136 | 01:00 | 133 | 10:00 | SSM | 140 | 19:00 | 134 | 01:00
Kamrangirchar | 135 | 21:00 | 118 | 16:00 | Sunamganj | 117 | 13:00 | 11 | 06:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 122 | 06:00 | 121 | 00:00
Kasba | 125 | 20:00 | 119 | 11:00 | Sylhet_(South) | 123 | 08:00 | 120 | 00:00
Kazla | 139 | 05:00 | 125 | 12:00 | Tangail | 128 | 07:00 | 118 | 04:00
Keranigonj | 135 | 21:00 | 127 | 10:00 | Taraganj | 134 | 13:00 | 130 | 02:00
Khagrachori | 136 | 00:00 | 131 | 11:00 | Tasnim | 129 | 20:00 | 120 | 11:00
Khulna | 133 | 17:00 | 129 | 06:00 | Thakurgaon | 140 | 10:00 | 135 | 02:00
Khulna(S) | 134 | 01:00 | 130 | 07:00 | TK | 138 | 10:00 | 133 | 11:00
Khulshi | 133 | 21:00 | 128 | 11:00 | Tongi | 131 | 00:00 | 121 | 09:00
Kishoreganj | 126 | 10:00 | 117 | 18:00 | Ullahpara | 134 | 06:00 | 130 | 00:00
Kodda | 130 | 18:30 | 119 | 10:00 | Ullon | 134 | 03:00 | 125 | 11:00
Korerhat | 132 | 01:00 | 128 | 10:00 | Uttara | 129 | 22:00 | 116 | 10:00
KSRM | 135 | 19:00 | 131 | 11:00 | UttaraNew | 129 | 20:00 | 116 | 10:00
Kulaura | 126 | 06:00 | 124 | 00:00 | Zigatola | 134 | 19:30 | 126 | 11:00
Kurigram | 130 | 00:00 | 124 | 22:00
Kushtia | 135 | 13:00 | 130 | 12:00
Laksam | 129 | 01:00 | 126 | 10:00
Lakshmipur | 125 | 00:00 | 123 | 05:00
Lalbag | 135 | 20:00 | 126 | 10:00
Lalmonirhat | 129 | 15:00 | 119 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division