## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-09-2026
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-09-2026 | during | 09-09-2026 | during | 09-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 100.22 | 0 | 0 | 100.22 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 412 | 405 | 407 | 412 | 412 | 412 | 412 | AGC
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 20 | 335 | 335 | 0 | 0 | Gas shortage
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 15 | 15 | Liquid fuel shortage
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 96 | 200 | 210 | 210 | 100 | 100 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 47 | 53.97 | 53.97 | 35 | 53 | -
18 | Kodda 150 MW PP BRPL | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 30 | 149.36 | 149.36 | 64 | 64 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 2.5 | 2.4 | 33 | 33 | 2.5 | 2.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 42 | 49 | 52.19 | 52.19 | 16 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 32 | 31 | 300 | 300 | 32 | 65 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 35 | 149 | 149 | 34 | 53 | Liquid fuel shortage
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 62 | 105 | 105 | 34 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 10 | 71 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 162 | 162 | 54 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 420 | 584 | 584 | 584 | 584 | 584 | FGMO and AGC
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP | 1*409+1*202 | 583 | 583 | 0 | 0 | 400 | 400 | 0 | 0 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 718 | 230 | 0 | 718 | 718 | 718 | 718 | -
| Sreepur 150 MW PP BRPL | HFO | PDB-RPCL | 9*18 | 0 | 160 | 34 | 143.42 | 143.42 | 143.42 | 143.42 | 143.42 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6001 | 6671.494 | 1544.5 | 2065.82 | 5396.16 | 5370.16 | 2396.92 | 2695.92
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 10 | 25.5 | 25.5 | 25.5 | 8 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 14 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 217 | 222 | 221 | 221 | 221 | 221 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 217 | 215 | 215 | 215 | 215 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105 | 34 | 34 | Liquid fuel shortage
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 15 | 36 | 0 | 0 | 14 | 32 | Liquid fuel shortage
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 51 | 0 | 51 | Liquid fuel shortage
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 37 | 37 | 100 | 100 | 24 | 50 | Liquid fuel shortage
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 42 | 42 | 0 | 0 | 42 | 42 | 42 | 42 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 95.104 | 24 | 58 | 95.1 | 95.1 | 18 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4.2 | 0 | 5.25 | 0 | 5.25 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 32 | 300 | 300 | 16 | 16 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.363 | 0 | 36 | 54.36 | 54.36 | 34 | 54 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 37 | 36 | 110 | 110 | 55 | 55 | Liquid fuel shortage
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 37 | 37 | 100 | 100 | 25 | 50 | Liquid fuel shortage
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 40 | 35 | 116 | 116 | 92 | 92 | FGMO
54 | Mirsharai 150 MW BRPL | HFO/Gas | IPP | 18.5*9 | 163 | 163 | 35 | 36 | 163 | 163 | 17 | 17 | Liquid fuel shortage
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1155 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 12 | 2 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 1130 | 1130 | 1150 | 1150 | 1150 | 1150 | Machine Problem
Chattogram Area Total |  |  |  |  | 4959 | 4885.967 | 3033.2 | 3250.5 | 4094.21 | 4121.96 | 3262.25 | 3428.5
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.25 | 195 | 222 | 221.25 | 221.25 | 205.25 | 205.25 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 350.01 | 354 | 354 | 350.01 | 350.01 | 350.01 | 350.01 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 342.01 | 0 | 0 | 250 | 250 | 0 | 0 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 393 | 393 | 393 | 393 | 363 | 363 | FGMO
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 35 | 39 | 41.65 | 41.65 | 36 | 36 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 52.824 | 0 | 20 | 52.82 | 52.82 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 63 | 63 | 195 | 195 | 63.01 | 63.01 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 44 | 44 | 51 | 51 | 44 | 44 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 35 | 150 | 150 | 150 | 20 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 30 | 32 | 32 | 15 | 15 | Liquid fuel shortage
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 86 | 86 | 163 | 163 | 91 | 91 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 119 | 192 | 200 | 200 | 180 | 180 | FGMO
| Import (Tripura) | Import | Import |  | 160 | 160 | 144 | 160 | 84 | 78 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 8 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 19 | 11 | 24.5 | 14 | 14 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 102 | 114 | 114 | 103 | 103 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 25 | 27 | 113 | 113 | 9 | 70 | Liquid fuel shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 17 | 115 | 115 | 35 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 79 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2870.995 | 1674 | 1970.2 | 2653.93 | 2596.43 | 1761.27 | 1988.47
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-09-2026 | during | 09-09-2026 | during | 09-09-2026 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| Muktagacha Solartech Energy Ltd | Solar | IPP | 1*20 | 20 | 20 | 20.49 | 0 | 20 | 0 | 20 | 0 | -
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1.3 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 162 | 120 | 170 | 120 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 87 | 60 | 90 | 60 | 90 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 54 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 24 | 22 | 22 | 12 | 12 | Liquid fuel shortage
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 0 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 674 | 674.21 | 259.79 | 273 | 538.6 | 546.5 | 264.1 | 289
| Moulvibazar 10 MW Solar Power Plant | Solar | IPP | 1*10 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | -
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 40 | 40 | 0 | 0 | 40 | 40 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 0 | 0 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 141 | 142 | 140 | 140 | 140 | 140 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | Gas shortage
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 22 | 32 | 86 | 86 | 22 | 22 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 127 | 126 | 128 | 128 | 127 | 127 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | One Engine is Under Maintenance.
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 341 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 394 | 392 | 360 | 390 | 360 | 390 | Machine Problem
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 400 | 400 | 383 | 383 | 383 | 383 | Machine Problem
Sylhet Area Total |  |  |  |  | 2350 | 2325 | 1482 | 1529 | 1504 | 1534 | 1435 | 1465
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 926 | 823 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 25 | 25 | 25 | Liquid fuel shortage
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 234 | 110 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 20 | 46 | 50 | 50 | 25 | 42 | Liquid fuel shortage
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 51 | 52 | 105 | 105 | 52 | 52 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 32 | 105 | 105 | 0 | 50 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 73.37 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 330 | 330 | 330 | 330 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 442 | 713 | 870 | 870 | 820 | 820 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 40 | 0 | 0 | 40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3739.2 | 1746.37 | 1776 | 3250 | 3165 | 2567 | 2549
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 1170.6 | 900 | 950 | 950 | 950 | 900 | 900 | Coal shortage
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 32 | 64 | 110 | 110 | 32 | 64 | Liquid fuel shortage
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 11.04 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 85 | 103 | 120 | 120 | 117 | 117 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1163.05 | 570 | 570 | 580 | 580 | 580 | 580 | Machine Problem
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*75+1*75 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 17 | 17 | Liquid fuel shortage
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 250 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.47 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3326.69 | 2074.47 | 2174 | 2438 | 2437 | 2174 | 2205
| Pabna 64 MW Solar Plant | Solar | PDB | 11*6.6 | 64 | 64.55 | 55.36 | 0 | 51.42 | 0 | 51.42 | 0 | Contract Expired
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 0 | 0 | Liquid fuel shortage
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 0 | 0 | Engine Problem
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 32 | 32 | 32 | 32 | Partial Shutdown due to maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 147 | 141 | 214 | 214 | 156 | 156 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.792 | 309 | 289 | 413.79 | 413.79 | 372.41 | 372.41 | AGC+FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 25 | 24 | 24 | 24 | 24 | 24 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 8 | 8 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 50 | 50 | 0 | 50 | Liquid fuel shortage
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 45 | 50 | 113 | 113 | 35 | 70 | Liquid fuel shortage
132 | Bagura 113 MW PP (Confidence)-1 | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 37 | 113 | 113 | 35 | 50 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.12 | 5.47 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1469.13 | 1226.14 | 1409.18 | 1200 | 1400 | 1200 | 1400 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 48.97 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
| Sirajganj 2 MW Wind Power Plant | Wind | PDB | 0.25*8 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3476 | 3552.792 | 1971.94 | 2080.38 | 2948.91 | 2930.99 | 2080.33 | 2162.41
| Saidpur 150 MW Simple Cycle Power Plant | HSD | PDB | 1*150 | 150 | 162.443 | 0 | 165 | 0 | 0 | 0 | 0 | -
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 50 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 155 | 155 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 78 | 113 | 113 | 0 | 35 | Liquid fuel shortage
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.6 | 0 | 5 | 0 | 5 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 95 | 95 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 168 | 0 | 158.51 | 0 | 158.51 | 0 | -
Rangpur Area Total |  |  |  |  | 1180 | 1112.443 | 508.6 | 543 | 665.51 | 472 | 552.51 | 394
System Total |  |  |  |  | 28843.2 | 29158.791 | 14294.87 | 15661.9 | 23489.32 | 23174.04 | 16493.38 | 17177.3
Forecast Scenario (09-09-2026)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14950 |  | 2588.05 |  | 17660
|  |  |  | 1:00 | 14070 |  | 2931.85 |  | 17140
|  |  |  | 2:00 | 13750 |  | 2912.75 |  | 16800
|  |  |  | 3:00 | 13510 |  | 2788.6 |  | 16430
|  |  |  | 4:00 | 13550 |  | 2406.6 |  | 16070
|  |  |  | 5:00 | 13430 |  | 2358.85 |  | 15900
|  |  |  | 6:00 | 13400 |  | 1948.2 |  | 15440
|  |  |  | 7:00 | 13330 |  | 1890.9 |  | 15310
|  |  |  | 8:00 | 13520 |  | 1575.75 |  | 15170
|  |  |  | 9:00 | 13730 |  | 1375.2 |  | 15170
|  |  |  | 10:00 | 14050 |  | 1212.85 |  | 15320
|  |  |  | 11:00 | 14260 |  | 1126.9 |  | 15440
|  |  |  | 12:00 | 14290 |  | 1824.05 |  | 16200
|  |  |  | 13:00 | 14240 |  | 2081.9 |  | 16420
|  |  |  | 14:00 | 13940 |  | 2282.45 |  | 16330
|  |  |  | 15:00 | 13980 |  | 2769.5 |  | 16880
|  |  |  | 16:00 | 13830 |  | 2616.7 |  | 16570
|  |  |  | 17:00 | 14140 |  | 2215.6 |  | 16460
|  |  |  | 18:00 | 14470 |  | 1384.75 |  | 15920
|  |  |  | 18:30 | 14750 |  | 1967.3 |  | 16810
|  |  |  | 19:00 | 14920 |  | 2654.9 |  | 17700
|  |  |  | 19:30 | 15320 |  | 2530.75 |  | 17970
|  |  |  | 20:00 | 15380 |  | 2511.65 |  | 18010
|  |  |  | 21:00 | 15470 |  | 2626.25 |  | 18220
|  |  |  | 22:00 | 15260 |  | 2540.3 |  | 17920
|  |  |  | 23:00 | 15360 |  | 2559.4 |  | 18040
Probable Maximum Temperature: |  |  | 34.0°C
Probable Maximum Demand at Day Peak: |  |  | 16200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 2626.25
Probable Maximum Demand at Evening Peak: |  |  | 18220.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15470.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 340.83 MKWHr. |  | 750 | 127 | 355 | 325 | 156 | 334 | 104 | 286 | 189 | 2626
*** This report is generated digitally from Operation Information System (OIS) at 08:38 hrs on 09-09-2026
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-09-2026 | [28 empty] | Date: | 08-09-2026 | [28 empty] | Date: | 08-09-2026 | [28 empty] | Date: | 08-09-2026 | [28 empty] | Date: | 08-09-2026 | [17 empty] | Date: | 08-09-2026
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [17 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP BRPL | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP BRPL | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW BRPL (HFO) | Mirsharai 150 MW BRPL (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 51 MW PP (Midland) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Moulvibazar 10 MW Solar Power Plant | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Muktagacha Solartech Energy Ltd | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Rupsha 800 MW CCPP (Gas) | Rupsha 800 MW CCPP (HSD) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-1 | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna 64 MW Solar Plant | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 2 MW Wind Power Plant | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 150 MW Simple Cycle Power Plant | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 100.220 MW | 412.000 MW | 20.000 MW | 718.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 95.104 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.363 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 163.000 MW | 163.000 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 350.010 MW | 342.010 MW | 51.000 MW | 52.824 MW | 221.250 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 0.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 20.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 0.000 MW | 0.000 MW | 1469.130 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 50.000 MW | 52.200 MW | 64.550 MW | 100.000 MW | 50.000 MW | 2.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.792 MW | 413.792 MW | 6.120 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 162.443 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1170.600 MW | 1163.050 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 271 | 54 | 35 | 28 | 62 | 32 | 40 | 55 | 162 | 0 | 0 | 0 | 0 | 35 | 0 | 61 | 0 | 0 | 68 | 2.5 | 22 | 0 | 470 | 109 | 16 | 38 | 0 | 2 | 50 | 37 | 17 | 25 | 25 | 0 | 218 | 55 | 5 | 1130 | 17 | 0 | 19 | 25.5 | 17 | 216 | 0 | 0 | 0 | 1193 | 0 | 20 | 51 | 393 | 353 | 0 | 44 | 0 | 199 | 36 | 54 | 91 | 189 | 27 | 14 | 93 | 188 | 52.2 | 0 | 30 | 315 | 397 | 354 | 40 | 39 | 0 | 0 | 16 | 0 | 22 | 0 | 142 | 0 | 127 | 0 | 86 | 0 | 163 | 0 | 0 | 0 | 12 | 8621.2 | 779 | 0 | 0 | 19 | 36 | 0 | 145 | 0 | 243 | 0 | 0 | 0 | 450 | 52 | 0 | 0 | 1290.7 | 0 | 0 | 0 | 55 | 70 | 0 | 50 | 21 | 8 | 0 | 0 | 18 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 159 | 0 | 115 | 0 | 71 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 250 | 114 | 220 | 0 | 900 | 570 | 17 | 6324.7 | 14945.9 | 104.98
01:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 292 | 35 | 35 | 17 | 62 | 32 | 15 | 35 | 90 | 0 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 0 | 34 | 2.5 | 22 | 0 | 500 | 67 | 16 | 27 | 0 | 0 | 50 | 15 | 0 | 25 | 25 | 0 | 218 | 45 | 13 | 1130 | 20 | 0 | 19 | 8 | 17 | 216 | 0 | 0 | 0 | 1224 | 0 | 23 | 71 | 393 | 354 | 0 | 44 | 0 | 196 | 36 | 24 | 91 | 122 | 0 | 14 | 55 | 180 | 52.2 | 0 | 30 | 310 | 400 | 380 | 40 | 39 | 0 | 0 | 16 | 0 | 22 | 0 | 143 | 0 | 127 | 0 | 58 | 0 | 65 | 0 | 0 | 0 | 12 | 8199.7 | 738 | 0 | 0 | 19 | 36 | 0 | 175 | 0 | 241 | 0 | 0 | 0 | 450 | 52 | 0 | 0 | 1037.87 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 20 | 8 | 0 | 0 | 18 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 158 | 0 | 115 | 0 | 35 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 250 | 115 | 220 | 0 | 900 | 570 | 17 | 5874.87 | 14074.57 | 104.99
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 290 | 35 | 35 | 17 | 62 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 10 | 97 | 0 | 0 | 34 | 2.5 | 22 | 0 | 530 | 52 | 16 | 24 | 0 | 1 | 50 | 15 | 0 | 25 | 25 | 0 | 218 | 34 | 14 | 1130 | 34 | 0 | 19 | 8 | 17 | 216 | 0 | 0 | 0 | 1224 | 0 | 26 | 71 | 393 | 355 | 0 | 44 | 0 | 209 | 36 | 17 | 91 | 104 | 0 | 14 | 34 | 170 | 52.2 | 0 | 30 | 310 | 397 | 387 | 40 | 39 | 0 | 0 | 16 | 0 | 22 | 0 | 142 | 0 | 127 | 0 | 58 | 0 | 66 | 0 | 0 | 0 | 12 | 8169.7 | 738 | 0 | 0 | 19 | 36 | 0 | 213 | 0 | 16 | 0 | 0 | 0 | 450 | 52 | 0 | 0 | 928.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 0 | 0 | 18 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 158 | 35 | 115 | 0 | 35 | 0 | 165 | 0 | 0 | 0 | 0 | 32 | 250 | 115 | 220 | 0 | 900 | 570 | 17 | 5578.71 | 13748.41 | 104.99
03:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 294 | 35 | 35 | 17 | 62 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 7 | 99 | 0 | 0 | 34 | 2.5 | 22 | 0 | 495 | 52 | 16 | 25 | 0 | 7 | 50 | 15 | 0 | 25 | 25 | 0 | 220 | 35 | 14 | 1130 | 34 | 0 | 19 | 8 | 17 | 215 | 0 | 0 | 0 | 1224 | 0 | 26 | 100 | 393 | 354 | 0 | 44 | 0 | 212 | 36 | 17 | 91 | 103 | 0 | 14 | 34 | 162 | 52.2 | 0 | 30 | 302 | 399 | 380 | 40 | 39 | 0 | 0 | 16 | 0 | 22 | 0 | 143 | 0 | 127 | 0 | 58 | 0 | 66 | 0 | 0 | 0 | 12 | 8155.7 | 738 | 0 | 0 | 15 | 36 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 450 | 35 | 0 | 0 | 901.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 18 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 155 | 46 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 116 | 220 | 0 | 900 | 570 | 17 | 5351.38 | 13507.08 | 104.99
04:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 248 | 35 | 35 | 17 | 62 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 35 | 73 | 57 | 0 | 0 | 34 | 2.5 | 22 | 0 | 515 | 52 | 16 | 24 | 0 | 0 | 34 | 15 | 0 | 25 | 25 | 0 | 220 | 38 | 14 | 1130 | 35 | 0 | 19 | 8 | 17 | 218 | 0 | 0 | 0 | 1224 | 0 | 26 | 100 | 393 | 347 | 0 | 44 | 0 | 214 | 36 | 17 | 91 | 104 | 0 | 14 | 34 | 164 | 52.2 | 0 | 30 | 310 | 399 | 380 | 40 | 39 | 0 | 0 | 16 | 0 | 22 | 0 | 142 | 0 | 127 | 0 | 58 | 0 | 66 | 0 | 0 | 0 | 12 | 8142.7 | 737 | 0 | 0 | 15 | 36 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 450 | 52 | 0 | 0 | 922.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 18 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 156 | 47 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 115 | 220 | 0 | 900 | 570 | 17 | 5402.93 | 13545.63 | 104.99
05:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 244 | 35 | 35 | 17 | 62 | 32 | 15 | 35 | 72 | 0 | 0 | 0 | 0 | 17 | 93 | 36 | 0 | 0 | 34 | 2.5 | 22 | 0 | 530 | 52 | 16 | 24 | 0 | 0 | 17 | 15 | 0 | 25 | 25 | 0 | 221 | 46 | 30 | 1130 | 36 | 0 | 19 | 8 | 17 | 216 | 0 | 0 | 0 | 1224 | 0 | 26 | 100 | 393 | 353 | 0 | 44 | 0 | 214 | 36 | 17 | 90 | 102 | 0 | 14 | 34 | 164 | 52.2 | 0 | 15 | 305 | 397 | 380 | 40 | 39 | 0 | 0 | 16 | 0 | 22 | 0 | 142 | 0 | 126 | 0 | 58 | 0 | 66 | 0 | 0 | 0 | 12 | 8109.7 | 738 | 0 | 0 | 0 | 31 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 450 | 52 | 0 | 0 | 922.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 160 | 48 | 115 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 250 | 115 | 220 | 0 | 850 | 570 | 17 | 5323.79 | 13433.49 | 105
06:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 243 | 17 | 35 | 17 | 62 | 32 | 15 | 0 | 72 | 0 | 0 | 0 | 0 | 17 | 91 | 99 | 0 | 0 | 34 | 2.5 | 22 | 0 | 530 | 52 | 16 | 22 | 0 | 0 | 0 | 15 | 0 | 25 | 25 | 0.05 | 221 | 35 | 35 | 1130 | 35 | 0 | 19 | 8 | 17 | 216 | 0 | 0 | 0 | 1224 | 1 | 26 | 100 | 393 | 353 | 0 | 44 | 0 | 216 | 36 | 17 | 91 | 103 | 0 | 14 | 34 | 156 | 52.2 | 0 | 15 | 305 | 394 | 385 | 40 | 39 | 0 | 0 | 16 | 0 | 22 | 0 | 142 | 0 | 126 | 0 | 58 | 0.14 | 67 | 0 | 0 | 0.09 | 12 | 8102.98 | 738 | 0 | 0 | 0 | 28 | 0 | 230 | 0 | 0 | 0 | 0 | 1 | 450 | 52 | 0 | 0 | 917.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0 | 18 | 0 | 0.11 | 154 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0.02 | 157 | 50 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.01 | 32 | 250 | 115 | 220 | 0 | 855 | 570 | 17 | 5301.27 | 13404.25 | 105
07:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 210 | 17 | 35 | 17 | 62 | 32 | 15 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 99 | 0 | 5 | 34 | 2.5 | 22 | 0 | 485 | 52 | 16 | 18 | 0 | 0 | 0 | 15 | 0 | 25 | 25 | 0.9 | 221 | 35 | 33 | 1130 | 36 | 0 | 19 | 8 | 17 | 216 | 0 | 0 | 0 | 1224 | 3 | 26 | 100 | 393 | 354 | 0 | 44 | 0 | 200 | 36 | 17 | 91 | 104 | 0 | 14 | 34 | 156 | 8 | 17 | 15 | 310 | 400 | 387 | 40 | 39 | 0 | 1 | 16 | 0 | 22 | 0 | 142 | 0 | 126 | 0 | 58 | 3.6 | 67 | 0 | 0.2 | 8.35 | 8 | 7878.55 | 738 | 0 | 0 | 0 | 25 | 0 | 233 | 0 | 0 | 0 | 0 | 21 | 450 | 52 | 0 | 0 | 986.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.64 | 9 | 18 | 0 | 4.72 | 156 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0.54 | 160 | 50 | 95 | 2 | 0 | 0 | 0 | 0 | 0.9 | 34 | 0.12 | 32 | 250 | 116 | 220 | 0 | 856 | 570 | 17 | 5448.3 | 13326.85 | 105
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 231 | 17 | 35 | 17 | 62 | 32 | 15 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 99 | 0 | 8 | 34 | 2.5 | 22 | 0 | 420 | 52 | 16 | 18 | 0 | 0 | 0 | 15 | 0 | 25 | 25 | 1.79 | 221 | 35 | 12 | 1130 | 35 | 0 | 19 | 8 | 17 | 215 | 0 | 0 | 0 | 1180 | 10 | 26 | 100 | 393 | 352 | 0 | 44 | 0 | 200 | 37 | 17 | 91 | 102 | 2 | 14 | 34 | 154 | 8 | 40 | 15 | 300 | 400 | 393 | 41 | 39 | 0 | 3 | 16 | 0 | 22 | 0 | 142 | 0 | 126 | 0 | 58 | 4.82 | 67 | 0 | 0.4 | 18.89 | 12 | 7815.4 | 927 | 0 | 0 | 0 | 24 | 0 | 230 | 0 | 0 | 0 | 0 | 42 | 450 | 52 | 0 | 0 | 1042.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.3 | 20 | 18 | 0 | 5.03 | 156 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 1.29 | 160 | 51 | 95 | 8 | 0 | 0 | 0 | 0 | 2.2 | 43 | 0.28 | 32 | 250 | 115 | 180 | 0 | 856 | 570 | 17 | 5702.93 | 13518.33 | 105
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 269 | 17 | 0 | 17 | 62 | 32 | 15 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 96 | 0 | 16 | 0 | 2.5 | 22 | 0 | 520 | 52 | 16 | 21 | 0 | 0 | 0 | 15 | 0 | 25 | 25 | 2.31 | 221 | 49 | 5 | 1130 | 35 | 0 | 19 | 8 | 17 | 217 | 0 | 0 | 0 | 1170 | 15 | 25 | 61 | 393 | 354 | 0 | 44 | 0 | 208 | 38 | 17 | 91 | 102 | 8 | 14 | 34 | 158 | 8 | 46 | 14 | 305 | 394 | 380 | 40 | 40 | 0 | 8 | 16 | 0 | 22 | 0 | 142 | 0 | 126 | 0 | 58 | 6.8 | 111 | 0 | 0.7 | 29.78 | 12 | 7928.09 | 926 | 0 | 0 | 0 | 24 | 0 | 236 | 0 | 0 | 0 | 0 | 37 | 450 | 52 | 0 | 0 | 1022.02 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 24.41 | 34 | 18 | 0 | 35.37 | 153 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 3.59 | 157 | 51 | 95 | 17 | 0 | 0 | 0 | 0 | 2.4 | 61 | 0.38 | 32 | 250 | 115 | 220 | 0 | 856 | 570 | 17 | 5803.17 | 13731.26 | 105
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 236 | 17 | 0 | 17 | 30 | 32 | 15 | 17 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 97 | 0 | 28 | 34 | 2.5 | 22 | 0 | 410 | 52 | 16 | 19 | 0 | 0 | 0 | 15 | 0 | 25 | 25 | 3.64 | 221 | 51 | 2 | 1130 | 35 | 0 | 19 | 8 | 17 | 218 | 0 | 0 | 0 | 1155 | 18 | 26 | 63 | 393 | 354 | 0 | 44 | 0 | 200 | 36 | 17 | 92 | 103 | 8 | 14 | 34 | 160 | 8 | 66 | 14 | 310 | 400 | 380 | 40 | 40 | 0 | 10 | 16 | 0 | 22 | 0 | 142 | 0 | 126 | 0 | 58 | 17.7 | 115 | 0 | 1.6 | 28.14 | 12 | 7875.58 | 927 | 0 | 0 | 0 | 20 | 0 | 235 | 0 | 0 | 0 | 0 | 83.52 | 450 | 52 | 0 | 0 | 1157.41 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 45.93 | 90 | 18 | 0 | 36.11 | 151 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 4.18 | 155 | 51 | 95 | 27 | 0 | 0 | 0 | 0 | 6.6 | 159 | 0.31 | 32 | 250 | 115 | 220 | 0 | 855 | 570 | 17 | 6179.06 | 14054.64 | 105
11:00 | 0 | 70 | 42 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 225 | 17 | 0 | 17 | 30 | 32 | 15 | 17 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 96 | 0 | 32 | 34 | 2.5 | 22 | 0 | 420 | 52 | 16 | 21 | 0 | 0 | 0 | 15 | 0 | 37 | 25 | 4.1 | 219 | 35 | 0 | 1130 | 35 | 0 | 18 | 8 | 17 | 215 | 0 | 0 | 0 | 1150 | 19 | 28 | 63 | 393 | 354 | 0 | 44 | 0 | 194 | 35 | 17 | 86 | 113 | 17 | 14 | 34 | 166 | 8 | 72 | 21 | 300 | 400 | 380 | 40 | 40 | 0 | 10 | 16 | 0 | 22 | 0 | 140 | 0 | 125 | 0 | 58 | 21.63 | 116 | 0 | 2 | 38 | 12 | 7928.23 | 927 | 0 | 0 | 0 | 20 | 0 | 233 | 0 | 0 | 0 | 0 | 100 | 443 | 51 | 0 | 0 | 1197.8 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 52.82 | 105 | 24 | 0 | 58.07 | 149 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 5.11 | 153 | 51 | 95 | 32 | 0 | 0 | 0 | 0 | 7.1 | 169 | 0.54 | 32 | 250 | 115 | 220 | 0 | 900 | 570 | 17 | 6334.44 | 14262.67 | 105
12:00 | 0 | 70 | 42 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 230 | 17 | 0 | 17 | 30 | 32 | 15 | 17 | 35 | 10 | 0 | 0 | 0 | 17 | 0 | 96 | 0 | 33 | 34 | 2.5 | 22 | 0 | 420 | 40 | 16 | 24 | 0 | 12 | 0 | 15 | 0 | 37 | 37 | 4.2 | 217 | 37 | 0 | 1130 | 35 | 0 | 19 | 10 | 17 | 214 | 0 | 0 | 0 | 1155 | 14 | 35 | 63 | 393 | 354 | 0 | 44 | 0 | 195 | 35 | 17 | 86 | 119 | 25 | 14 | 34 | 144 | 8 | 79 | 29 | 300 | 400 | 394 | 40 | 40 | 0 | 2 | 16 | 0 | 22 | 0 | 141 | 0 | 127 | 0 | 58 | 20.49 | 114 | 0 | 1.3 | 54 | 12 | 7993.49 | 926 | 0 | 0 | 0 | 20 | 0 | 234 | 0 | 0 | 0 | 0 | 73.37 | 442 | 51 | 0 | 0 | 1226.14 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 55.36 | 110 | 25 | 0 | 48.97 | 147 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 5.47 | 155 | 49 | 95 | 35 | 0 | 0 | 0 | 0 | 6.6 | 168 | 0.47 | 32 | 250 | 85 | 220 | 0 | 900 | 570 | 17 | 6301.38 | 14294.87 | 105
13:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 236 | 17 | 35 | 17 | 30 | 32 | 15 | 17 | 35 | 16 | 0 | 0 | 0 | 17 | 0 | 96 | 0 | 32 | 34 | 2.5 | 22 | 0 | 420 | 35 | 32 | 26 | 0 | 15 | 0 | 15 | 0 | 37 | 37 | 4.1 | 217 | 45 | 0 | 1130 | 28 | 0 | 18 | 17 | 17 | 212 | 0 | 0 | 0 | 1131 | 20 | 58 | 63 | 390 | 352 | 0 | 44 | 0 | 198 | 38 | 17 | 86 | 126 | 26 | 19 | 34 | 144 | 8 | 69 | 29 | 300 | 400 | 393 | 40 | 40 | 0 | 3 | 16 | 0 | 21 | 0 | 142 | 0 | 127 | 0 | 57 | 17.49 | 113 | 0 | 2 | 48.44 | 12 | 7997.53 | 927 | 0 | 0 | 0 | 15 | 0 | 238 | 0 | 0 | 0 | 0 | 60.89 | 441 | 52 | 0 | 0 | 1218.21 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 54.35 | 105 | 25 | 0 | 51.34 | 145 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 5.27 | 155 | 49 | 95 | 29 | 0 | 0 | 0 | 0 | 3.2 | 157 | 0.3 | 32 | 250 | 85 | 220 | 0 | 900 | 570 | 17 | 6242.56 | 14240.09 | 105
14:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 35 | 17 | 30 | 31 | 15 | 17 | 35 | 20 | 0 | 0 | 0 | 17 | 0 | 96 | 0 | 28 | 34 | 2.5 | 22 | 0 | 430 | 35 | 32 | 27 | 0 | 13 | 0 | 15 | 17 | 37 | 37 | 3.69 | 217 | 36 | 0 | 1130 | 30 | 0 | 21 | 8 | 17 | 213 | 0 | 0 | 0 | 1120 | 17 | 61 | 63 | 393 | 354 | 0 | 44 | 0 | 190 | 39 | 17 | 86 | 136 | 36 | 19 | 51 | 146 | 8 | 40 | 29 | 305 | 400 | 393 | 40 | 40 | 0 | 2 | 16 | 0 | 22 | 0 | 142 | 0 | 127 | 0 | 57 | 18.66 | 113 | 0 | 1.9 | 32.72 | 12 | 7762.47 | 926 | 0 | 0 | 0 | 15 | 0 | 236 | 0 | 0 | 0 | 0 | 30.01 | 443 | 52 | 0 | 0 | 1238.06 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 48.5 | 97 | 25 | 0 | 51.84 | 144 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 4.78 | 157 | 49 | 95 | 29 | 0 | 0 | 0 | 0 | 1.8 | 155 | 0.21 | 32 | 250 | 85 | 180 | 0 | 900 | 570 | 17 | 6175.2 | 13937.67 | 105
15:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 35 | 17 | 30 | 31 | 15 | 17 | 35 | 40 | 0 | 0 | 0 | 17 | 0 | 96 | 0 | 23 | 34 | 2.4 | 22 | 0 | 450 | 35 | 32 | 33 | 0 | 11 | 0 | 15 | 17 | 37 | 37 | 2.93 | 218 | 36 | 0 | 1130 | 35 | 0 | 24 | 8 | 17 | 212 | 0 | 0 | 0 | 1210 | 11 | 63 | 63 | 385 | 350 | 0 | 44 | 0 | 200 | 39 | 17 | 86 | 136 | 32 | 19 | 47 | 148 | 8 | 48 | 29 | 310 | 397 | 367 | 40 | 40 | 0 | 2 | 16 | 0 | 22 | 0 | 140 | 0 | 126 | 0 | 57 | 6.97 | 113 | 0 | 1 | 20.58 | 12 | 7842.88 | 926 | 0 | 0 | 0 | 20 | 0 | 235 | 0 | 0 | 0 | 0 | 54 | 440 | 53 | 0 | 0 | 1218.6 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 0 | 35.28 | 62 | 18 | 0 | 41.45 | 144 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 2.77 | 158 | 49 | 95 | 17 | 0 | 0 | 0 | 0 | 2.3 | 111 | 0.36 | 32 | 250 | 84 | 220 | 0 | 900 | 570 | 17 | 6140.76 | 13983.64 | 104.99
16:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 35 | 17 | 30 | 31 | 15 | 17 | 72 | 46 | 0 | 0 | 0 | 17 | 0 | 97 | 0 | 13 | 68 | 2.4 | 22 | 0 | 480 | 35 | 32 | 30 | 0 | 1 | 0 | 15 | 17 | 37 | 37 | 0.44 | 219 | 36 | 0 | 1130 | 40 | 0 | 19 | 17 | 17 | 214 | 0 | 0 | 0 | 1224 | 0 | 67 | 63 | 393 | 348 | 0 | 44 | 0 | 184 | 39 | 17 | 85 | 136 | 26 | 19 | 51 | 152 | 28 | 31 | 29 | 310 | 400 | 367 | 40 | 40 | 0 | 1 | 16 | 0 | 22 | 0 | 143 | 0 | 126 | 0 | 57 | 3.45 | 112 | 0 | 0.2 | 10.46 | 12 | 7928.95 | 926 | 0 | 0 | 0 | 21 | 0 | 237 | 0 | 0 | 0 | 0 | 41 | 440 | 64 | 0 | 0 | 1219.65 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 0 | 24.25 | 0 | 12 | 0 | 9.45 | 144 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0.8 | 160 | 50 | 95 | 1 | 0 | 0 | 0 | 0 | 0.5 | 60 | 0.22 | 32 | 250 | 84 | 220 | 0 | 900 | 570 | 17 | 5898.87 | 13827.82 | 104.99
17:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 35 | 30 | 31 | 15 | 35 | 162 | 52 | 0 | 0 | 0 | 17 | 0 | 97 | 0 | 2 | 143.42 | 2.4 | 22 | 0 | 480 | 35 | 32 | 31 | 0 | 0 | 0 | 10 | 17 | 37 | 37 | 0.12 | 220 | 36 | 0 | 1130 | 35 | 0 | 19 | 10 | 17 | 215 | 0 | 0 | 0 | 1224 | 0 | 95 | 63 | 393 | 355 | 0 | 44 | 0 | 183 | 39 | 17 | 85 | 153 | 26 | 19 | 101 | 144 | 43 | 19 | 29 | 300 | 400 | 367 | 40 | 40 | 0 | 0 | 16 | 0 | 21 | 0 | 142 | 0 | 126 | 10 | 58 | 1.59 | 112 | 0 | 0.3 | 4.15 | 12 | 8190.98 | 926 | 0 | 0 | 0 | 22 | 0 | 150 | 0 | 0 | 0 | 21 | 2.32 | 440 | 64 | 0 | 0 | 1217.78 | 0 | 0 | 0 | 35 | 50 | 0 | 50 | 0 | 0 | 0.55 | 10 | 12 | 0 | 6.94 | 143 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0.57 | 156 | 50 | 95 | 6 | 33 | 0 | 0 | 0 | 0.2 | 32 | 0.11 | 48 | 250 | 83 | 220 | 0 | 950 | 570 | 17 | 5947.47 | 14138.45 | 104.99
18:00 | 0 | 42 | 37 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 17 | 35 | 39 | 30 | 31 | 15 | 35 | 162 | 52 | 0 | 0 | 0 | 35 | 0 | 192 | 0 | 0 | 143.42 | 2.3 | 22 | 0 | 540 | 35 | 32 | 32 | 0 | 0 | 0 | 34 | 17 | 37 | 37 | 0 | 220 | 35 | 0 | 1130 | 36 | 0 | 19 | 17 | 17 | 215 | 0 | 0 | 0 | 1224 | 0 | 130 | 63 | 340 | 354 | 0 | 44 | 0 | 170 | 39 | 17 | 85 | 173 | 27 | 19 | 102 | 152 | 44 | 1 | 29 | 320 | 400 | 342 | 40 | 40 | 0 | 0 | 16 | 0 | 22 | 0 | 142 | 0 | 126 | 0 | 58 | 0.01 | 112 | 0 | 0 | 0.05 | 12 | 8392.78 | 927 | 0 | 0 | 0 | 30 | 0 | 91 | 0 | 0 | 0 | 32 | 0 | 437 | 64 | 0 | 0 | 1384.34 | 0 | 0 | 0 | 35 | 50 | 0 | 50 | 12 | 8 | 0.04 | 0 | 12 | 0 | 0.08 | 143 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 154 | 49 | 95 | 0 | 70 | 0 | 0 | 0 | 0 | 2 | 0 | 64 | 250 | 114 | 180 | 0 | 950 | 570 | 17 | 6075.46 | 14468.24 | 104.99
19:00 | 0 | 70 | 49 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 35 | 35 | 35 | 30 | 31 | 25 | 55 | 162 | 52 | 0 | 0 | 0 | 55 | 0 | 195 | 0 | 0 | 143.42 | 2.3 | 22 | 0 | 520 | 35 | 32 | 38 | 0 | 0 | 51 | 36 | 17 | 37 | 37 | 0 | 220 | 35 | 2 | 1130 | 34 | 0 | 19 | 25.5 | 17 | 215 | 0 | 0 | 0 | 1224 | 0 | 147 | 63 | 393 | 353 | 0 | 44 | 0 | 188 | 40 | 17 | 85 | 173 | 27 | 19 | 102 | 162 | 52.2 | 0 | 30 | 325 | 400 | 392 | 40 | 40 | 0 | 0 | 16 | 0 | 32 | 0 | 141 | 0 | 127 | 0 | 86 | 0 | 160 | 0 | 0 | 0 | 24 | 8806.42 | 824 | 0 | 0 | 0 | 35 | 0 | 91 | 0 | 0 | 0 | 32 | 0 | 426 | 52 | 0 | 0 | 1416.84 | 0 | 0 | 0 | 37 | 50 | 0 | 50 | 24 | 8 | 0 | 0 | 24 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 155 | 49 | 95 | 0 | 78 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 250 | 115 | 220 | 0 | 950 | 570 | 17 | 6225.84 | 15032.26 | 104.99
19:30 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 35 | 35 | 35 | 30 | 31 | 55 | 55 | 162 | 52 | 0 | 0 | 0 | 55 | 0 | 194 | 0 | 0 | 143.42 | 2.3 | 22 | 0 | 500 | 35 | 32 | 40 | 0 | 0 | 51 | 36 | 17 | 37 | 37 | 0 | 220 | 35 | 0 | 1130 | 34 | 0 | 19 | 25.5 | 17 | 214 | 0 | 0 | 0 | 1224 | 0 | 150 | 63 | 393 | 353 | 0 | 44 | 10 | 181 | 40 | 17 | 85 | 190 | 27 | 19 | 102 | 168 | 52.2 | 0 | 30 | 305 | 400 | 393 | 40 | 40 | 0 | 0 | 16 | 0 | 32 | 0 | 141 | 0 | 126 | 4 | 86 | 0 | 160 | 0 | 0 | 0 | 24 | 8759.42 | 824 | 0 | 0 | 0 | 40 | 0 | 91 | 0 | 0 | 0 | 32 | 0 | 450 | 52 | 0 | 0 | 1408.88 | 0 | 0 | 0 | 37 | 50 | 0 | 50 | 30 | 10 | 0 | 0 | 24 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 155 | 50 | 95 | 0 | 78 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 250 | 115 | 220 | 0 | 950 | 570 | 17 | 6253.88 | 15013.3
20:00 | 0 | 35 | 49 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 35 | 35 | 35 | 30 | 31 | 55 | 55 | 162 | 68 | 0 | 0 | 0 | 55 | 0 | 190 | 0 | 0 | 143.42 | 2.4 | 22 | 0 | 575 | 35 | 32 | 44 | 0 | 0 | 51 | 36 | 36 | 37 | 37 | 0 | 222 | 35 | 0 | 1130 | 36 | 0 | 19 | 25.5 | 17 | 214 | 0 | 0 | 0 | 1224 | 0 | 150 | 63 | 393 | 355 | 0 | 44 | 10 | 203 | 38 | 17 | 85 | 186 | 28 | 19 | 102 | 172 | 52.2 | 0 | 30 | 305 | 395 | 379 | 40 | 40 | 0 | 0 | 16 | 0 | 32 | 0 | 141 | 0 | 126 | 0 | 87 | 0 | 163 | 0 | 0 | 0 | 24 | 8913.52 | 823 | 0 | 0 | 0 | 50 | 0 | 91 | 0 | 0 | 0 | 32 | 0 | 560 | 65 | 0 | 0 | 1414.45 | 0 | 0 | 0 | 37 | 50 | 0 | 50 | 30 | 52.2 | 0 | 0 | 24 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 154 | 50 | 95 | 0 | 78 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 250 | 115 | 220 | 0 | 950 | 570 | 17 | 6431.65 | 15345.17 | 104.99
21:00 | 0 | 62 | 49 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 47 | 35 | 35 | 30 | 31 | 55 | 55 | 162 | 71 | 20 | 0 | 0 | 55 | 0 | 200 | 0 | 0 | 143.42 | 2.4 | 22 | 0 | 584 | 35 | 32 | 58 | 0 | 2 | 51 | 36 | 36 | 37 | 37 | 0 | 222 | 36 | 0 | 1130 | 36 | 0 | 19 | 25.5 | 17 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 63 | 393 | 354 | 0 | 44 | 20 | 222 | 39 | 17 | 86 | 192 | 27 | 19 | 102 | 160 | 52.2 | 0 | 30 | 341 | 400 | 392 | 40 | 40 | 0 | 0 | 16 | 0 | 32 | 0 | 142 | 0 | 126 | 0 | 87 | 0 | 162 | 0 | 0 | 0 | 24 | 9088.52 | 823 | 0 | 0 | 0 | 46 | 0 | 110 | 0 | 0 | 0 | 32 | 0 | 713 | 52 | 0 | 0 | 1409.18 | 0 | 0 | 0 | 37 | 50 | 0 | 50 | 28 | 52.2 | 0 | 0 | 24 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 0 | 155 | 50 | 95 | 0 | 78 | 0 | 165 | 0 | 0 | 0 | 0 | 64 | 250 | 103 | 220 | 0 | 950 | 570 | 17 | 6573.38 | 15661.9 | 104.99
22:00 | 0 | 70 | 49 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 6 | 54 | 35 | 35 | 30 | 31 | 55 | 55 | 162 | 71 | 20 | 0 | 0 | 55 | 0 | 160 | 0 | 0 | 143.42 | 2.4 | 22 | 0 | 505 | 35 | 32 | 58 | 0 | 10 | 45 | 36 | 36 | 37 | 37 | 0 | 222 | 47 | 0 | 1130 | 38 | 0 | 19 | 25.5 | 17 | 217 | 0 | 0 | 0 | 1224 | 0 | 150 | 63 | 393 | 355 | 0 | 44 | 20 | 180 | 40 | 17 | 86 | 192 | 28 | 19 | 102 | 166 | 52.2 | 0 | 30 | 310 | 400 | 393 | 40 | 40 | 0 | 0 | 16 | 0 | 21 | 0 | 143 | 0 | 126 | 12 | 96 | 0 | 152 | 0 | 0 | 0 | 24 | 8947.52 | 824 | 0 | 0 | 0 | 41 | 0 | 170 | 0 | 0 | 0 | 32 | 0 | 815 | 52 | 0 | 0 | 1406.75 | 0 | 0 | 0 | 37 | 50 | 0 | 50 | 28 | 52.2 | 0 | 0 | 24 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 158 | 50 | 104 | 0 | 78 | 0 | 100 | 0 | 0 | 0 | 0 | 64 | 250 | 116 | 220 | 0 | 950 | 570 | 17 | 6689.95 | 15637.47 | 104.99
23:00 | 0 | 70 | 49 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 30 | 54 | 35 | 28 | 30 | 31 | 30 | 55 | 162 | 32 | 33 | 0 | 0 | 35 | 0 | 197 | 0 | 0 | 143.42 | 2.4 | 22 | 0 | 545 | 35 | 16 | 57 | 0 | 3 | 51 | 36 | 17 | 37 | 37 | 0 | 222 | 44 | 0 | 1130 | 35 | 0 | 19 | 25.5 | 17 | 216 | 0 | 0 | 0 | 1224 | 0 | 150 | 63 | 393 | 354 | 0 | 44 | 20 | 202 | 40 | 16 | 85 | 192 | 28 | 19 | 102 | 172 | 52.2 | 0 | 30 | 310 | 400 | 393 | 40 | 40 | 0 | 0 | 16 | 0 | 21 | 0 | 143 | 0 | 126 | 17 | 96 | 0 | 152 | 0 | 0 | 0 | 24 | 8957.52 | 823 | 0 | 0 | 11 | 38 | 0 | 205 | 0 | 0 | 0 | 32 | 0 | 845 | 52 | 0 | 0 | 1413.09 | 0 | 0 | 0 | 37 | 50 | 0 | 50 | 28 | 52.2 | 0 | 0 | 24 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 0 | 156 | 50 | 115 | 0 | 70 | 0 | 130 | 0 | 0 | 0 | 0 | 64 | 250 | 116 | 220 | 0 | 950 | 570 | 17 | 6798.29 | 15755.81 | 104.99
Total KWH | 0 | 1075075 | 638880 | 0 | 0 | 0 | 0 | 0 | 9817200 | 0 | 3794490 | 681840 | 730800 | 547632 | 1027680 | 767280 | 529759 | 669230 | 2082240 | 507840 | 119767 | 0 | 0 | 689194 | 275164 | 3016000 | 0 | 221306 | 1626000 | 55200 | 522360 | 0 | 12087272.73 | 1057582 | 557018 | 764160 | 0 | 72000 | 491951 | 494416 | 255471 | 754560 | 744000 | 22887 | 5306371 | 976032 | 219360 | 27105454.55 | 844727 | 0 | 473280 | 311817.6 | 422364 | 4909556 | 0 | 0 | 0 | 28914543 | 107325 | 1649309 | 1756364 | 9431500 | 8787700 | 0 | 1025874 | 93120 | 4950000 | 896328 | 419520 | 2074869 | 3279360 | 409080 | 406040 | 1395360 | 3807360 | 814930 | 515827 | 600816 | 7441000 | 9546300 | 9348000 | 952000 | 939120 | 0 | 47257 | 400224 | 0 | 561600 | 0 | 3189000 | 0 | 3734790 | 82440 | 1552800 | 111967 | 2572800 | 0 | 11950 | 284750 | 353520 | 199729959.88 | 20434909 | 0 | 0 | 88800 | 673664 | 0 | 4850100 | 0 | 392505.46 | 0 | 232704 | 502560 | 12276364 | 1268640 | 0 | 0 | 28085381 | 0 | 0 | 0 | 275424 | 825120 | 0 | 547920 | 185421 | 258614 | 354512 | 647410 | 418208 | 0 | 344256 | 3567091 | 0 | 0 | 0 | 0 | 0 | 7438618 | 0 | 33240 | 3941000 | 1134109 | 2420798 | 218085 | 683712 | 0 | 1231335 | 0 | 34063.08 | 1184400 | 3424 | 1027104 | 5957000 | 2560000 | 5363280 | 0 | 21840000 | 14017454.55 | 426000 | 145743226.09 | 345473185.97

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-09-2026
Power Supply Scenario
| Day Peak Generation |  |  | 14294.87 | MW | 12:00 Hr. | Energy Generated |  |  | 345.4732 |  | MKWHr.
| Day Peak Demand |  |  | 16916.87 | MW | 12:00 Hr. | Energy Unserverd |  |  | 54.953 |  | MKWHr.
| Evening Peak Generation |  |  | 15661.9 | MW | 21:00 Hr. | Energy Demand |  |  | 400.4262 |  | MKWHr.
| Evening Peak Demand |  |  | 18337.9 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34 |  | °C
| Minimum Generation of the Day |  |  | 13326.85 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 851.42 |  | MMCFD
| Maximum Generation of the Day |  |  | 15755.81 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 7.5762 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 29.6875 | 0 | 11.5734 | 0 | 0 | 0.22131 | 0 | 0 | 41.4822 | Gas | 119.2792 | Gas | 415048977.1641
| Chattogram Zone |  |  | 5.1289 | 56.02 | 8.1474 | 0 | 5.3064 | 0.13021 | 0 | 0.072 | 74.8049 | Coal | 115.1859 | Coal | 801595891.0965
| Cumilla Zone |  |  | 29.4218 | 0 | 8.5684 | 0 | 0 | 0.51583 | 3.8074 | 0 | 42.3134 | HFO | 42.1829 | HFO | 830595811.108
| Mymensingh Zone |  |  | 0 | 0 | 4.5616 | 0 | 0 | 0.40867 | 0 | 0 | 4.9702 | HSD | 6.4739 | HSD | 160026587.092
| Sylhet Zone |  |  | 36.112 | 0 | 0 | 0 | 0 | 0.047257 | 0 | 0 | 36.1593 | Hydro | 5.3064 | Hydro | 530637.1
| Khulna Zone |  |  | 0 | 12.2764 | 2.2638 | 5.2426 | 0 | 0.50256 | 20.4349 | 0 | 40.7202 | Solar | 4.6452 | Solar | 74441958.3288
| Barishal Zone |  |  | 7.9233 | 41.8145 | 1.4531 | 0 | 0 | 0.003424 | 0 | 0 | 51.1943 | Import | 52.3276 | Import | 334092108.67
| Rajshahi Zone |  |  | 11.0057 | 0 | 2.5107 | 0 | 0 | 1.3794 | 28.0854 | 0 | 42.9812 | Wind | 0.072 | Wind | 1059120
| Rangpur Zone |  |  | 0 | 5.0751 | 3.1045 | 1.2313 | 0 | 1.4365 | 0 | 0 | 10.8475
| Total |  |  | 119.2792 | 115.1859 | 42.1829 | 6.4739 | 5.3064 | 4.6452 | 52.3276 | 0.072 | 345.4732
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 415048977.1641 |  | Hydro | 530637.1
|  |  |  | Coal | 801595891.0965 |  | Solar | 74441958.3288
|  |  |  | HFO | 830595811.108 |  | Import | 334092108.67
|  |  |  | HSD | 160026587.092 |  | Wind | 1059120
[5 empty] | Total: | 261,73,91,090 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.4349 | Peak Hr Flow | 823.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 34426109.09 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.0854 | Peak Hr Flow | 1409.18 MW at 21:00 hrs.
Power Flow during Peak Demand (W-E): |  |  | MW: | 1788 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 3.8074 | Peak Hr Flow | 160.00 MW at 21:00 hrs.
Maximum Power Flow (W-E): |  |  | MW: | 2348 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.3276 | Peak Hr Flow | 2392.18 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 696 |  | 6371
|  |  |  | Chattogram |  | 126 |  | 1568
|  |  |  | Cumilla |  | 353 |  | 1769
|  |  |  | Mymensingh |  | 317 |  | 1535
|  |  |  | Sylhet |  | 156 |  | 780
|  |  |  | Khulna |  | 334 |  | 2057
|  |  |  | Barishal |  | 104 |  | 585
|  |  |  | Rajshahi |  | 286 |  | 1733
|  |  |  | Rangpur |  | 189 |  | 1185
|  |  |  | Total |  | 2561 |  | 17583
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Bhairob 54.5 MW |  |  | 54.5
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 300 |  |  |  | Total | 108.5
|  |  |  | Total Unavailable Capacity |  |  |  | 408.5
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:15 |  | Meghnaghat CCPP(Summit) Synchronized
| 09:25 | 13:05 | Thakurgaon-Thakurgaon EPV 132kV Ckt-2 Scheduled S/D from Thakurgaon 132/33kV end Due to
Schedule work at EMA Power Plant, Thakurgaon
| 09:33 | 19:40 | Chandina-Cumilla(N) 132 kV Ckt-1 Project Work S/D from Chandina 132/33kV end.
| 10:31 | 17:36 | Bashundhara-Tongi 132 kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end.
| 10:52 | 14:44 | Ruppur 132/11kV S/S TR-01 HT Forced S/D
| 11:07 | 14:28 | Khagrachori 132/33kV S/S TR-1 LT Scheduled S/D Due to Necessary tests by spmd
| 11:08 | 14:29 | Khagrachori 132/33kV S/S TR-1 HT Scheduled S/D Due to Necessary tests by spmd
| 11:14 | 00:50 | Chauddagram 132/33kV S/S 132 kv T-2 LT Scheduled S/D Due to Oil refill
| 11:14 | 00:49 | Chauddagram 132/33kV S/S 132 kv T-2 HT Scheduled S/D Due to Oil refill
| 11:19 | 15:02 | Lalmonirhat-Rangpur 132 kV Ckt-2 Project Work S/D from Rangpur 132/33kV end Due to
Deployment Work and from Lalmonirhat 132/33kV end Due to Project work for Rangpur Grid SS
| 11:53 |  | Kaliakoir 400/230/132kV S/S 132kV Bus 1 Forced S/D Due to 132kV Square Connect to 132kV
Bus 01
| 12:00 |  | Day Peak Generation: 14294 MW.
| 12:18 | 17:33 | Madunaghat-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to 400
kV Korerhat ckt-2 shutdown instructed by NLDC.
| 12:44 | 15:14 | Satkhira 132/33kV S/S Transformer-1 (T-1) HT Scheduled S/D Due to 33 Kv CT & PT test
| 12:44 | 15:14 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Scheduled S/D | [7 empty] | 15.0MW load
interrup.
| 13:50 | 14:39 | Bibiyana-Kaliakoir 400 kV Ckt-2 Tripped from Bibiana 400/230kV end showing Main-1 Main-2
relays.
| 14:08 |  | Noapara 132/33kV S/S T-2 LT Tripped showing SIEMENS SIPROTEC 7SJ81 Phs-C Trip 50 OC-DMT | [7 empty] | 14.0MW load
|  |  | Trip 50N EF-DMT Trip relays Due to Due to REB-3 Fedder fault(OC/EF). | [7 empty] | interrup.
| 14:08 |  | Noapara 132/33kV S/S T-1 LT Tripped showing SIEMENS SIPROTEC 7SJ81 Phs-C Trip 50 OC-DMT | [7 empty] | 14.0MW load
|  |  | Trip 50N EF-DMT Trip relays Due to Due to REB-3 Fedder fault(OC/EF). | [7 empty] | interrup.
| 15:35 | 16:35 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end.
| 15:35 | 16:35 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end.
| 17:30 | 20:45 | Khulna (C) S/S TR-1 425T HT Scheduled S/D Due to 132 kv bus section -1 S/D (Np-1 bus D/S
R- phase clamp temp. High.)
| 17:30 | 20:45 | Khulna (C) S/S Tr-2 415 T LT Scheduled S/D Due to 132 kv bus section -1 S/D (Np-1 bus D/S
R- phase clamp temp. High.)
| 17:41 | 20:36 | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to 132 kv bus
section -1 S/D (Np-1 bus D/S R- phase clamp temp. High.) and from Khulna(S) 230/132kVend.
| 17:43 | 20:38 | Khulna(C )-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end. and from Khulna
(C) end Due to 132 kv bus section -1 S/D (Np-1 bus D/S R- phase clamp temp. High.)
| 17:45 | 20:42 | Khulna(C)-North-West Ckt-1 Scheduled S/D from Khulna (C) end Due to 132 kv bus section -1
S/D (Np-1 bus D/S R- phase clamp temp. High.)
| 17:46 | 20:42 | Khulna(C)-North-West Ckt-2 Scheduled S/D from Khulna (C) end Due to 132 kv bus section -1
S/D (Np-1 bus D/S R- phase clamp temp. High.)
| 17:50 | 20:31 | Khulna(C )-Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna (C) end Due to 132 kv bus
section -1 S/D (Np-1 bus D/S R- phase clamp temp. High.)
| 17:51 | 20:38 | Khulna(C )-Noapara 132kV Ckt-2 Scheduled S/D from Khulna (C) end Due to 132 kv bus
section -1 S/D (Np-1 bus D/S R- phase clamp temp. High.)
|  | 18:30 | Barapukuria S/S-P/S 230 kV Ckt-1 is restored.
|  | 18:34 | Barapukuria P/S-Bogura West 230kV Ckt-1 is restored.
| 19:11 | 20:17 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT Forced S/D Due to Red hot remove works
| 19:11 | 20:14 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Forced S/D Due to Red hot remove works
| 19:17 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
| 19:21 | 19:26 | Barishal-Bhandaria 132 kV Ckt-1 Forced S/D from Barishal 132/33kV end Due to Bhandaria
132kV লাইন Bay এর R Phase DS (104S) এর Contact point এ heavy firing হয় এবং Contact
Finger পুড়ে যায়
| 19:28 |  | Bagerhat-Bhandaria 132 kV Ckt-1 Forced S/D from Bagerhat 132/33kV end Due to Barishal sub
station DS red hot found
| 19:29 |  | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to For
maintenance DS finger
| 20:15 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT- 1
| 20:15 |  | Meghnaghat CCPP(Summit) GT-1 Synchronized with remarks:- GT-1 sync at 20:15 hrs as NLDC
request.
| 21:00 |  | Evening peak generation is 15661 MW.
| 22:18 |  | Sylhet_(South) 132/33kV S/S Trafo-2 LT Forced S/D Due to For Redhot maintenance work of | [7 empty] | 8.0MW load
|  |  | PDB feeder. | [7 empty] | interrup.
| 22:20 |  | Sylhet_(South) 132/33kV S/S Trafo-2 HT Forced S/D Due to For Redhot maintenance work of | [7 empty] | 8.0MW load
|  |  | PDB feeder. | [7 empty] | interrup.
| 22:49 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- ST
| 22:49 |  | Meghnaghat CCPP(Summit) ST Synchronized with remarks:- ST synch at 22:49 hrs as per NLDC
requirement
| 23:56 |  | Meghnaghat CCPP(Summit), FGMO is ON with remarks:- FGMO made ON @ 23:40 hrs as per NLDC
requirement
| 05:46 | 07:23 | Khulshi 132/33kV S/S 415T (T2) LT Scheduled S/D Due to Red hot Maintenance
| 05:47 | 07:21 | Khulshi 132/33kV S/S 415T (T2) HT Scheduled S/D Due to Red hot Maintenance
| 06:00 |  | Minimum Generation: 13836 MW.
| 06:08 |  | Kurigram-Rangpur 132kV Ckt-1 Scheduled S/D from Rangpur 132/33kV end Due to G2G Project | [7 empty] | 20.0MW load
|  |  | work | [7 empty] | interrup. Rangpur
132/33kV end
| 06:10 |  | Kurigram-Lalmonirhat 132kV Ckt-1 Project Work S/D from Kurigram 132/33kV end Due to G2G
project work Rangpur End.
| 06:15 |  | Khulshi-MSML 132kV Ckt-2 Scheduled S/D from Khulshi 132/33kV end Due to Red hot
Maintenance
| 07:15 |  | Barapukuria P/S-Bogura West 230kV Ckt-1 Scheduled S/D from Bogura 400/230kV end Due to
project work(LILO at Polasbari) and from Barapukuria 230/132/33kV end Due to Lilo work of
polashbari grid
| 07:26 |  | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to Red hot maintenance
| 07:27 |  | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to Red hot maintenance
| 07:31 |  | Bog-Sherpur 132/33kV S/S Main Bus-2 Scheduled S/D Due to Red hot maintenance
| 07:52 |  | Khulshi 132/33kV S/S 405T (T1) LT Scheduled S/D Due to Red hot Maintenance
| 07:52 |  | Khulshi 132/33kV S/S 405T (T1) HT Scheduled S/D Due to Red hot Maintenance
| 07:52 |  | Khulshi 132/33kV S/S 405T (T1) HT Scheduled S/D Due to Red hot Maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-09-2026
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | Gas Shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas Shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas Shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas Shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 100.22 | 0 | 0 | Gas (RMS) problem
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 407 | 9817200 | AGC
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 20 | 119767 | Gas Shortage
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 529759 | Fuel Shortage
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 200 | 3016000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 275164 | Under Maintenance
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 47 | 681840 | Fuel Shortage
18 | Kodda 150 MW PP BRPL |  | PDB-RPCL | 9*17.06 | 149.36 | 30 | 1027680 | Fuel Shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 669230 | plant availability zero
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 689194 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 2.4 | 55200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 522360 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 49 | 638880 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 31 | 767280 | Fuel Shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 35 | 547632 | Fuel Shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 62 | 1075075 | Fuel Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 71 | 507840 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2082240 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 221306 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 730800 | Fuel Shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 584 | 12087272.73 | AGC+FGMO
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 1*409+1*202 | 583 | 0 | 0 | STG Under Shutdown & Gas Shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 3794490 | Under Maintenance
| Sreepur 150 MW PP BRPL |  | PDB-RPCL | 9*18 | 160 | 143.42 | 1626000 | Liquid fuel shortage
Dhaka Area Total |  |  |  |  | 6671.494 | 2065.82 | 41482209.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Gas Shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 311817.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 107325 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 473280 | Fuel Shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 222 | 5306371 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 217 | 4909556 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 422364 | Fuel Shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 36 | 494416 | ps availability is less
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 491951 | ps availability is less
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 754560 | Fuel Shortage
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 219360 | Machine Problem
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 95.104 | 58 | 764160 | Fuel Shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22887 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 557018 | Fuel Shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.363 | 36 | 255471 | Fuel Shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 36 | 976032 | Fuel Shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 37 | 744000 | Fuel Shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 1057582 | Fuel Shortage
54 | Mirsharai 150 MW BRPL |  | IPP | 18.5*9 | 163 | 36 | 844727 | Fuel Shortage
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28914543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 2 | 72000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 1130 | 27105454.55 | Machine Problem
Chattogram Area Total |  |  |  |  | 4885.967 | 3250.5 | 74804875.15
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.25 | 222 | 4950000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 350.01 | 354 | 8787700 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 342.01 | 0 | 0 | STG Under Shutdown & Gas Shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 393 | 9431500 | FGMO
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 39 | 896328 | Machine Problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 52.824 | 20 | 93120 | Gas Shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 63 | 1756364 | Gas Shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 44 | 1025874 | Machine Problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 150 | 1649309 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 30 | 600816 | ps availability is less
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 86 | 2074869 | STG Under Maintenance
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 192 | 3279360 | Engine Problem
| Import (Tripura) |  | Import | 0 | 160 | 160 | 3807360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 814930 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 406040 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 102 | 1395360 | Engine Problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 409080 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 17 | 419520 | Fuel Shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 515827 | -
Cumilla Area Total |  |  |  |  | 2870.995 | 1970.2 | 42313357
| Muktagacha Solartech Energy Ltd |  | IPP | 1*20 | 20 | 0 | 111967 | -
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 162 | 2572800 | ps availability is less
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1552800 | ps availability is less
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 284750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 353520 | Liquid fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 82440 | Fuel Shortage
Mymensingh Area Total |  |  |  |  | 674.21 | 273 | 4970227
| Moulvibazar 10 MW Solar Power Plant |  | IPP | 1*10 | 0 | 0 | 47257 | -
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 40 | 952000 | ps availability is less
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 939120 | ps availability is less
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Major Inspection
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 142 | 3189000 | ps availability is less
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | GT-9 Under Maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 32 | 561600 | Gas Shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 126 | 3734790 | Machine Problem
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 400224 | ps availability is less
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 341 | 7441000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 392 | 9348000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 400 | 9546300 | ps availability is less
Sylhet Area Total |  |  |  |  | 2325 | 1529 | 36159291
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 823 | 20434909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 88800 | Fuel Shortage
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 110 | 4850100 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 46 | 673664 | Fuel Shortage
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas Shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 52 | 1268640 | Fuel Shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 32 | 232704 | Fuel Shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 502560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 392505.46 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 713 | 12276364 | Coal Shortage
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739.2 | 1776 | 40720246.46
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 1170.6 | 950 | 21840000 | Coal Shortage
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 64 | 1027104 | Fuel Shortage
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 11.04 | 0 | 0 | Contract Expired
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 103 | 2560000 | STG Under Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1163.05 | 570 | 14017454.55 | Machine Problem
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*75+1*75 | 220 | 220 | 5363280 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 426000 | Fuel Shortage
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 250 | 5957000 | Bad quality coal
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3424 | -
Barishal Area Total |  |  |  |  | 3326.69 | 2174 | 51194262.55
| Pabna 64 MW Solar Plant |  | PDB | 11*6.6 | 64.55 | 0 | 354512 | Contract Expired
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas Shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Fuel Shortage
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Machine Problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 185421 | Fuel Shortage
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 141 | 3567091 | Gas Shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas Shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas Shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.792 | 289 | 7438618 | Gas Shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 418208 | Machine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 258614 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 547920 | Machine Problem
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 825120 | Fuel Shortage
132 | Bagura 113 MW PP (Confidence)-1 |  | IPP | 6*18.55 | 113 | 37 | 275424 | Fuel Shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.12 | 0 | 33240 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1469.13 | 1409.18 | 28085381 | Coal Shortage
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 344256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 647410 | -
| Sirajganj 2 MW Wind Power Plant |  | PDB | 0.25*8 | 2 | 0 | 0 | Contract Expired
Rajshahi Area Total |  |  |  |  | 3552.792 | 2080.38 | 42981215
| Saidpur 150 MW Simple Cycle Power Plant |  | PDB | 1*150 | 162.443 | 165 | 1231335 | plant availability zero
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1134109 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 155 | 3941000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser mode
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under Maintenance
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 78 | 683712 | Fuel Shortage
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34063.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 95 | 2420798 | Engine Problem
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 218085 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1184400 | -
Rangpur Area Total |  |  |  |  | 1112.443 | 543 | 10847502.08
Eastern Grid Total |  |  |  |  | 17427.666 | 9088.52 | 199729959.88
Western Grid Total |  |  |  |  | 11731.125 | 6573.38 | 145743226.09
National Grid Total |  |  |  |  | 29158.791 | 15661.9 | 345473185.97
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-09-2026
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10375.53 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4647.5 | MW
i) Dhaka area |  |  | 5675.43 |  | MW | i) Khulna area |  |  |  | 1723 | MW
ii) Chattogram area |  |  | 1442.1 |  | MW | ii) Barishal area |  |  |  | 481.1 | MW
iii) Cumilla area |  |  | 1416 |  | MW | iii) Rajshahi area |  |  |  | 1447.4 | MW
iv) Mymensingh area |  |  | 1218 |  | MW | iv) Rangpur area |  |  |  | 996 | MW
v) Sylhet area |  |  | 624 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15023.03 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 72 | Ishurdi | 75 | 18:30 | 143 | Palashbari | 129 | 22:00
2 | AKSML | 148 | 04:00 | 73 | Jaldhaka | 91 | 23:00 | 144 | Panchagarh | 74 | 19:30
3 | Aftabnagar | 46 | 18:30 | 74 | Jamalpur | 131 | 00:00 | 145 | Patiya | 23 | 03:00
4 | Agargaon | 127 | 14:00 | 75 | Jashore | 158 | 19:00 | 146 | Patnitala | 29 | 02:00
5 | Agrabad | 70 | 11:00 | 76 | Jhenaidah | 82 | 21:00 | 147 | Patuakhali | 64 | 19:30
6 | Amnura | 29 | 00:00 | 77 | Joydebpur | 173 | 10:00 | 148 | Payra | 36 | 21:00
7 | Araihazar | 65 | 00:00 | 78 | Joypurhat | 55 | 21:00 | 149 | Postogola | 66 | 18:00
8 | Ashuganj | 89 | 23:00 | 79 | Juldah | 20 | 16:00 | 150 | Pubail | 42 | 11:00
9 | BSRM | 204 | 22:00 | 80 | KSRM | 31 | 10:00 | 151 | Purbachal | 22 | 18:30
10 | Bagerhat | 79 | 21:00 | 81 | Kabirpur | 254 | 23:00 | 152 | Purbasadipur | 125 | 21:00
11 | Bajitpur | 80 | 07:00 | 82 | Kachua | 108 | 23:00 | 153 | Rahanpur | 36 | 18:30
12 | Bakerganj | 13.8 | 19:30 | 83 | Kaliganj | 36 | 19:30 | 154 | Rahim | 57 | 08:00
13 | Bakulia | 97 | 12:00 | 84 | Kallyanpur | 126 | 00:00 | 155 | Rajbari | 78 | 21:00
14 | Banani | 58 | 14:00 | 85 | Kalurghat | 42 | 12:00 | 156 | Rajendrapur | 125 | 18:30
15 | Bangabhaban | 18 | 11:00 | 86 | Kamrangirchar | 84 | 13:00 | 157 | Rajshahi | 111 | 23:00
16 | Barapukuria | 64 | 21:00 | 87 | Kaptai | N/A | N/A | 158 | Rajshahi-230 | 99 | 12:00
17 | Barguna | 20 | 20:00 | 88 | Kasba | 34 | 00:00 | 159 | Ramganj | 94 | 20:00
18 | Barishal | 82 | 00:00 | 89 | Kazla | 130 | 18:30 | 160 | Rampur | 44 | 00:00
19 | Barishal-230 | 108 | 21:00 | 90 | Keranigonj | 86 | 20:00 | 161 | Rangamati | 16 | 18:30
20 | Baroaulia | 58 | 09:00 | 91 | Khagrachori | 38 | 18:30 | 162 | Rangpur | 130 | 20:00
21 | Baroirhat | 62 | 22:00 | 92 | Khulna | 58 | 23:00 | 163 | Ruppur | 4.4 | 11:00
22 | Bashundhara | 241 | 13:00 | 93 | Khulshi | 178 | 13:00 | 164 | SSM | 0 | 00:00
23 | BashundharaCement | 0 | 00:00 | 94 | Kishoreganj | 130 | 19:30 | 165 | Saidpur | 95 | 19:00
24 | Beanibazar | 68 | 20:00 | 95 | Kodda | 293 | 12:00 | 166 | Santhia | 36 | 18:30
25 | Benapole | 68 | 14:00 | 96 | Kulaura | 55 | 21:00 | 167 | Satkhira | 126 | 21:00
26 | Bhaluka | 159 | 21:00 | 97 | Kurigram | 64 | 20:00 | 168 | Satmasjid | 109 | 14:00
27 | Bhandaria | 60 | 21:00 | 98 | Kushtia | 138 | 21:00 | 169 | Savar | 211 | 22:00
28 | Bhangura | 32 | 00:00 | 99 | Laksam | 37 | 01:00 | 170 | SevenRings | 21.3 | 16:00
29 | Bheramara(GK) | 57 | 03:00 | 100 | Lakshmipur | 49 | 04:00 | 171 | ShahCement | 30 | 09:00
30 | Bhulta | 226 | 15:00 | 101 | Lalbag | 79 | 13:00 | 172 | Shahjadpur | 84 | 19:00
31 | Bog-Sherpur | 60 | 00:00 | 102 | Lalmonirhat | 76 | 19:00 | 173 | Shahjibazar | 146 | 23:00
32 | Bogura | 199 | 19:00 | 103 | MI_Cement | 15.8 | 01:00 | 174 | Shahmirpur | 59 | 00:00
33 | Borhanuddin | 68 | 19:30 | 104 | Madanganj | 51 | 19:30 | 175 | Shariatpur | 86 | 20:00
34 | Brahmanbaria | 138 | 20:00 | 105 | Madaripur | 99 | 21:00 | 176 | Sherpur | 156 | 23:00
35 | Cantonment | 142 | 13:00 | 106 | Madartek | 93 | 23:00 | 177 | Shikalbaha | 32 | 18:30
36 | Chandina | 21 | 02:00 | 107 | Madunaghat | 56 | 19:00 | 178 | Shitalakhya | 78.8 | 17:00
37 | Chandpur | 74 | 20:00 | 108 | Magura | 60 | 22:00 | 179 | Sholosohor | 51 | 18:30
38 | Chandraghona | 32 | 21:00 | 109 | Mahasthangarh | 88 | 23:00 | 180 | Shomvuganj | 45 | 20:00
39 | Chapai | 67 | 19:00 | 110 | Maijdee | 33 | 20:00 | 181 | Shyampur | 160 | 14:00
40 | Charfasson | 32 | 21:00 | 111 | Manikganj | 127 | 20:00 | 182 | Siddhirganj | 131 | 12:00
41 | Charsaidpur | 38 | 18:30 | 112 | Maniknagar | 82 | 14:00 | 183 | Sirajganj | 130 | 20:00
42 | Chauddagram | 64 | 00:00 | 113 | Matarbari | 55 | 22:00 | 184 | Sitakunda | 13 | 04:00
43 | Chhatak | 35 | 00:00 | 114 | Matuail | 80 | 23:00 | 185 | Sonargaon | 128 | 20:00
44 | Chowmuhani | 168 | 23:00 | 115 | Metrorail_Motijheel | 37 | 18:30 | 186 | Sreemongol | 73 | 18:30
45 | Chuadanga | 104 | 18:30 | 116 | Metrorail_Uttara | 0 | 00:00 | 187 | Sreepur | 128 | 22:00
46 | Coxsbazar | 137 | 19:00 | 117 | Millgate | 101 | 17:00 | 188 | Srinagar | 41.8 | 04:00
47 | Cumilla(N) | 164 | 23:00 | 118 | Mirpur | 166 | 18:30 | 189 | Sunamganj | 60 | 23:00
48 | Cumilla(S) | 186 | 00:00 | 119 | Mirsorai | 44 | 15:00 | 190 | Sylhet | 133 | 20:00
49 | Daganbhuiyan | 36 | 20:00 | 120 | Mirzapur | 46 | 00:00 | 191 | Sylhet_(South) | 65 | 00:00
50 | Daudkandi | 148 | 23:00 | 121 | Mithapukur | 82 | 23:00 | 192 | TK | 0 | 00:00
51 | DhakaUniversity | 96 | 13:00 | 122 | Modern | N/A | N/A | 193 | Tangail | 178 | 00:00
52 | Dhamrai | 92 | 18:00 | 123 | Mogbazar | 68 | 13:00 | 194 | Taraganj | 28 | 21:00
53 | Dhanmondi | 111 | 13:00 | 124 | Mongla | 39 | 14:00 | 195 | Tasnim | 41 | 14:00
54 | Dohazari | 92 | 18:00 | 125 | Motijheel | 53 | 18:30 | 196 | Thakurgaon | 116 | 20:00
55 | Faridpur | 184 | 20:00 | 126 | Muktagacha | 40 | 22:00 | 197 | Tongi | 140 | 10:00
56 | Fatullah | 116 | 15:00 | 127 | Munshiganj | 114 | 22:00 | 198 | Ullahpara | 36 | 20:00
57 | Fenchuganj | 43 | 00:00 | 128 | Muradnagar | 44 | 21:00 | 199 | Ullon | 48 | 00:00
58 | Feni | 103 | 20:00 | 129 | Mymensingh | 154 | 22:00 | 200 | Uttara | 107 | 18:30
59 | GPH | 1 | 00:00 | 130 | Nabinagar | 112 | 19:30 | 201 | UttaraNew | 57 | 23:00
60 | Ghatail | 91 | 20:00 | 131 | Naogaon | 110 | 21:00 | 202 | Zigatola | 98 | 14:00
61 | Ghorashal | 0 | 00:00 | 132 | Narail | 61 | 18:30
62 | Ghorashal-230 | 110 | 22:00 | 133 | Narinda | 76 | 13:00
63 | Goalpara | 39 | 18:30 | 134 | Narshingdi | 192 | 23:00
64 | Gollamari | 106 | 11:00 | 135 | Natore | 132 | 20:00
65 | Gopalganj | 95 | 10:00 | 136 | Nawabganj | 48.9 | 11:00
66 | Gulshan | 120 | 17:00 | 137 | Netrakona | 123 | 20:00
67 | Halishahar | 146.5 | 15:00 | 138 | New | 93.4 | 18:30
68 | HaripurSBU | 135 | 11:00 | 139 | Niamatpur | 79 | 21:00
69 | Hasnabad | 96 | 18:00 | 140 | Noapara | 40 | 10:00
70 | Hathazari | 101 | 21:00 | 141 | PHP | 12 | 15:00
71 | Hatirjheel | 79 | 11:00 | 142 | Pabna | 100 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. State Minister |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-09-2026
Hour | Generation | Load-Shed |  | Demand
0:00 | 14945.9 | 2279 |  | 17327.9
1:00 | 14074.57 | 2779 |  | 16978.63
2:00 | 13748.41 | 2724 |  | 16594.99
3:00 | 13507.08 | 2703 |  | 16332.08
4:00 | 13545.63 | 2582 |  | 16243.63
5:00 | 13433.49 | 2474 |  | 16018.82
6:00 | 13404.25 | 2291 |  | 15798.25
7:00 | 13326.85 | 2194 |  | 15619.85
8:00 | 13518.33 | 2025 |  | 15634.33
9:00 | 13731.26 | 2061 |  | 15885.26
10:00 | 14054.64 | 2131 |  | 16281.64
11:00 | 14262.67 | 1773 |  | 16115.67
12:00 | 14294.87 | 2509 |  | 16916.87
13:00 | 14240.09 | 2289 |  | 16632.09
14:00 | 13937.67 | 2202 |  | 16238.67
15:00 | 13983.64 | 2844 |  | 16955.64
16:00 | 13827.82 | 2518 |  | 16458.82
17:00 | 14138.45 | 1821 |  | 16041.45
18:00 | 14468.24 | 1603 |  | 16143.24
19:00 | 15032.26 | 2702 |  | 17856.26
19:30 | 15013.3 | 2518 |  | 17644.3
20:00 | 15345.17 | 2171 |  | 17614.17
21:00 | 15661.9 | 2561 |  | 18337.9
22:00 | 15637.47 | 1961 |  | 17686.47
23:00 | 15755.81 | 1756 |  | 17590.81
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## EWIC
QF-LDC-40
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
East-West Interconnector Log
Date: | 08-09-2026
EWIC | Ishurdi-Ghorashal |  | Sirajganj-Sreepur |  | Gopalganj-Aminbazar |  | Line | Export/Import | Energy (MkWHr)
Time | MW | MVAR | MW | MVAR | MW | MVAR
0:00 | 137 | 55 | 432 | 224 | 1236 | 720 | Ishurdi-Ghorashal Ckt-1 | Export | 0
1:00 | 119 | 60 | 368 | 206 | 1178 | 704
2:00 | 101 | 58 | 308 | 204 | 978 | 696 |  | Import | 0
3:00 | 83 | 51 | 262 | 196 | 912 | 658
4:00 | 79 | 48 | 268 | 200 | 926 | 652 | Ishurdi-Ghorashal Ckt-2 | Export | 3526109.09
5:00 | 84 | 53 | 264 | 200 | 862 | 640
6:00 | 84 | 51 | 276 | 206 | 904 | 670 |  | Import | 0
7:00 | 91 | 51 | 290 | 200 | 1004 | 700
8:00 | 156 | 61 | 416 | 220 | 1246 | 748 | Sirajganj-Sreepur Ckt-1 | Export | 0
9:00 | 173 | 74 | 468 | 256 | 1362 | 866
10:00 | 186 | 70 | 520 | 230 | 1482 | 878 |  | Import | 0
11:00 | 202 | 82 | 566 | 270 | 1580 | 904
12:00 | 184 | 78 | 550 | 280 | 1454 | 938 | Sirajganj-Sreepur Ckt-2 | Export | 0
13:00 | 188 | 88 | 510 | 276 | 1422 | 1006
14:00 | 211 | 109 | 550 | 302 | 1560 | 1090 |  | Import | 0
15:00 | 188 | 88 | 480 | 236 | 1434 | 1000
16:00 | 188 | 92 | 440 | 224 | 1430 | 942 | Gopalganj-Aminbazar Ckt-1 | Export | 15430000
17:00 | 186 | 99 | 410 | 200 | 1452 | 1022
18:00 | 179 | 85 | 470 | 226 | 1442 | 932 |  | Import | 0
18:30 | 173 | 82 | 460 | 226 | 1152 | 858
19:00 | 133 | 70 | 380 | 192 | 1144 | 736 | Gopalganj-Aminbazar Ckt-2 | Export | 15470000
19:30 | 136 | 73 | 386 | 186 | 1208 | 784
20:00 | 136 | 73 | 390 | 216 | 1186 | 798 |  | Import | 0
21:00 | 134 | 68 | 380 | 200 | 1274 | 774
22:00 | 149 | 74 | 410 | 224 | 1376 | 804 |  | Total Export | 34426109.09
23:00 | 153 | 74 | 426 | 220 | 1492 | 848 |  | Total Import | 0
***Positive MW indicates power flow from West to East, and negative MW indicates flow from East to West.
|  | Sub-Divisional Engineer |  |  |  |  | Executive Engineer
|  | Network Operation Division |  |  |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-09-2026 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8621.2 | 6324.7 | 14945.9 | DAILY GENERATION CURVE
00:30 | 8410.45 | 6099.785 | 14510.235
01:00 | 8199.7 | 5874.87 | 14074.57 | 08-09-2026
01:30 | 8184.7 | 5726.79 | 13911.49
02:00 | 8169.7 | 5578.71 | 13748.41
02:30 | 8162.7 | 5465.045 | 13627.745
03:00 | 8155.7 | 5351.38 | 13507.08
03:30 | 8149.2 | 5377.155 | 13526.355
04:00 | 8142.7 | 5402.93 | 13545.63
04:30 | 8126.2 | 5363.36 | 13489.56
05:00 | 8109.7 | 5323.79 | 13433.49
05:30 | 8106.34 | 5312.53 | 13418.87
06:00 | 8102.98 | 5301.27 | 13404.25
06:30 | 7990.765 | 5374.785 | 13365.55
07:00 | 7878.55 | 5448.3 | 13326.85
07:30 | 7846.975 | 5575.615 | 13422.59
08:00 | 7815.4 | 5702.93 | 13518.33
08:30 | 7871.745 | 5753.05 | 13624.795
09:00 | 7928.09 | 5803.17 | 13731.26
09:30 | 7901.835 | 5991.115 | 13892.95
10:00 | 7875.58 | 6179.06 | 14054.64
10:30 | 7901.905 | 6256.75 | 14158.655
11:00 | 7928.23 | 6334.44 | 14262.67
11:30 | 7960.86 | 6317.91 | 14278.77
12:00 | 7993.49 | 6301.38 | 14294.87
12:30 | 7995.51 | 6271.97 | 14267.48
13:00 | 7997.53 | 6242.56 | 14240.09
13:30 | 7880 | 6208.88 | 14088.88
14:00 | 7762.47 | 6175.2 | 13937.67
14:30 | 7802.675 | 6157.98 | 13960.655
15:00 | 7842.88 | 6140.76 | 13983.64
15:30 | 7885.915 | 6019.815 | 13905.73
16:00 | 7928.95 | 5898.87 | 13827.82
16:30 | 8059.965 | 5923.17 | 13983.135
17:00 | 8190.98 | 5947.47 | 14138.45
17:30 | 8291.88 | 6011.465 | 14303.345
18:00 | 8392.78 | 6075.46 | 14468.24
18:30 | 8599.6 | 6150.65 | 14750.25
19:00 | 8806.42 | 6225.84 | 15032.26
19:30 | 8759.42 | 6253.88 | 15013.3
20:00 | 8913.52 | 6431.65 | 15345.17
20:30 | 9001.02 | 6502.515 | 15503.535 |  | Executive Engineer
21:00 | 9088.52 | 6573.38 | 15661.9 |  | Network Operation Division
21:30 | 9018.02 | 6631.665 | 15649.685
22:00 | 8947.52 | 6689.95 | 15637.47
22:30 | 8952.52 | 6744.12 | 15696.64
23:00 | 8957.52 | 6798.29 | 15755.81

## En-Curve
QF-LDC-12
Date | 08-09-2026 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3417 | 1452.5 | 779 | 0 | 188 | 1290.7 | 218 | 4652 | 0 | 441 | 1952.7 | 553 | 0 | 2 | 2279 | DAILY ENERGY CURVE
00:30 | 3455.5 | 1489.5 | 758.5 | 0 | 184 | 1164.285 | 218 | 4667 | 0 | 412.5 | 1592.95 | 567 | 0 | 1 | 2529 | 08-09-2026
01:00 | 3494 | 1526.5 | 738 | 0 | 180 | 1037.87 | 218 | 4682 | 0 | 384 | 1233.2 | 581 | 0 | 0 | 2779
01:30 | 3514 | 1541 | 738 | 0 | 175 | 983.29 | 218 | 4699.5 | 0 | 359 | 1195.7 | 487.5 | 0 | 0.5 | 2751.5 | Energy Generated | 345.4732 |  | MKWHr
02:00 | 3534 | 1555.5 | 738 | 0 | 170 | 928.71 | 218 | 4717 | 0 | 334 | 1158.2 | 394 | 0 | 1 | 2724 | Energy not Served | 54.953 |  | MKWHr
02:30 | 3537.5 | 1550.5 | 738 | 0 | 166 | 915.045 | 219 | 4721 | 0 | 332 | 1146.2 | 298.5 | 0 | 4 | 2713.5 | Total Energy Requirement | 400.4262 |  | MKWHr
03:00 | 3541 | 1545.5 | 738 | 0 | 162 | 901.38 | 220 | 4725 | 0 | 330 | 1134.2 | 203 | 0 | 7 | 2703
03:30 | 3557 | 1536.5 | 737.5 | 0 | 163 | 912.155 | 220 | 4726 | 0 | 322 | 1144.7 | 204 | 0 | 3.5 | 2642.5
04:00 | 3573 | 1527.5 | 737 | 0 | 164 | 922.93 | 220 | 4727 | 0 | 314 | 1155.2 | 205 | 0 | 0 | 2582
04:30 | 3570 | 1538.5 | 737.5 | 0 | 164 | 922.86 | 220.5 | 4704.5 | 0 | 278 | 1148.7 | 205 | 0 | 0 | 2528
05:00 | 3567 | 1549.5 | 738 | 0 | 164 | 922.79 | 221 | 4682 | 0 | 242 | 1142.2 | 205 | 0 | 0 | 2474
05:30 | 3608.5 | 1551.5 | 738 | 0 | 160 | 920.325 | 221 | 4684 | 2.845 | 232 | 1083.2 | 217.5 | 0 | 0 | 2382.5
06:00 | 3650 | 1553.5 | 738 | 0 | 156 | 917.86 | 221 | 4686 | 5.69 | 222 | 1024.2 | 230 | 0 | 0 | 2291
06:30 | 3601 | 1516 | 738 | 0 | 156 | 952.12 | 221 | 4688 | 60.83 | 220.5 | 980.6 | 231.5 | 0 | 0 | 2242.5
07:00 | 3552 | 1478.5 | 738 | 0 | 156 | 986.38 | 221 | 4690 | 115.97 | 219 | 937 | 233 | 0 | 0 | 2194
07:30 | 3553.5 | 1421 | 832.5 | 0 | 155 | 1014.605 | 221 | 4668.5 | 167.985 | 218.5 | 938.5 | 231.5 | 0 | 0 | 2109.5
08:00 | 3555 | 1363.5 | 927 | 0 | 154 | 1042.83 | 221 | 4647 | 220 | 218 | 940 | 230 | 0 | 0 | 2025
08:30 | 3544.5 | 1432 | 926.5 | 0 | 156 | 1032.425 | 221 | 4640.5 | 279.87 | 200.5 | 958.5 | 233 | 0 | 0 | 2043
09:00 | 3534 | 1500.5 | 926 | 0 | 158 | 1022.02 | 221 | 4634 | 339.74 | 183 | 977 | 236 | 0 | 0 | 2061
09:30 | 3524 | 1431 | 926.5 | 0 | 159 | 1089.715 | 221 | 4625 | 482.735 | 195.5 | 1003 | 235.5 | 0 | 0 | 2096
10:00 | 3514 | 1361.5 | 927 | 0 | 160 | 1157.41 | 221 | 4616 | 625.73 | 208 | 1029 | 235 | 0 | 0 | 2131
10:30 | 3503.5 | 1355 | 927 | 0 | 163 | 1177.605 | 220 | 4631.5 | 677.05 | 232 | 1038 | 234 | 0 | 0 | 1952
11:00 | 3493 | 1348.5 | 927 | 0 | 166 | 1197.8 | 219 | 4647 | 728.37 | 256 | 1047 | 233 | 0 | 0 | 1773
11:30 | 3477 | 1351 | 926.5 | 0 | 155 | 1211.97 | 218 | 4649 | 719.8 | 260.5 | 1070.5 | 233.5 | 0 | 6 | 2141
12:00 | 3461 | 1353.5 | 926 | 0 | 144 | 1226.14 | 217 | 4651 | 711.23 | 265 | 1094 | 234 | 0 | 12 | 2509
12:30 | 3450.5 | 1358.5 | 926.5 | 0 | 144 | 1222.175 | 217 | 4638.5 | 686.805 | 232 | 1142 | 236 | 0 | 13.5 | 2399
13:00 | 3440 | 1363.5 | 927 | 0 | 144 | 1218.21 | 217 | 4626 | 662.38 | 199 | 1190 | 238 | 0 | 15 | 2289
13:30 | 3440 | 1233.5 | 926.5 | 0 | 145 | 1228.135 | 217 | 4622.5 | 612.245 | 199 | 1214 | 237 | 0 | 14 | 2245.5
14:00 | 3440 | 1103.5 | 926 | 0 | 146 | 1238.06 | 217 | 4619 | 562.11 | 199 | 1238 | 236 | 0 | 13 | 2202
14:30 | 3418 | 1135.95 | 926 | 0 | 147 | 1228.33 | 217.5 | 4663 | 501.875 | 223 | 1252.5 | 235.5 | 0 | 12 | 2523
15:00 | 3396 | 1168.4 | 926 | 0 | 148 | 1218.6 | 218 | 4707 | 441.64 | 247 | 1267 | 235 | 0 | 11 | 2844
15:30 | 3363 | 1183.4 | 926 | 0 | 150 | 1219.125 | 218.5 | 4715.5 | 319.205 | 261.5 | 1307.5 | 236 | 0 | 6 | 2681
16:00 | 3330 | 1198.4 | 926 | 0 | 152 | 1219.65 | 219 | 4724 | 196.77 | 276 | 1348 | 237 | 0 | 1 | 2518
16:30 | 3362.5 | 1192.9 | 926 | 0 | 148 | 1218.715 | 219.5 | 4747 | 141.31 | 322.21 | 1511 | 193.5 | 0 | 0.5 | 2169.5
17:00 | 3395 | 1187.4 | 926 | 0 | 144 | 1217.78 | 220 | 4770 | 85.85 | 368.42 | 1674 | 150 | 0 | 0 | 1821
17:30 | 3414.5 | 1207.85 | 926.5 | 0 | 148 | 1301.06 | 220 | 4767 | 44.515 | 409.92 | 1743.5 | 120.5 | 0 | 0 | 1712
18:00 | 3434 | 1228.3 | 927 | 0 | 152 | 1384.34 | 220 | 4764 | 3.18 | 451.42 | 1813 | 91 | 0 | 0 | 1603
18:30 | 3496.5 | 1246.8 | 875.5 | 0 | 157 | 1400.59 | 220 | 4759 | 1.59 | 512.92 | 1906.85 | 173.5 | 0 | 0 | 2152.5
19:00 | 3559 | 1265.3 | 824 | 0 | 162 | 1416.84 | 220 | 4754 | 0 | 574.42 | 2000.7 | 256 | 0 | 0 | 2702
19:30 | 3550 | 1233.3 | 824 | 0 | 168 | 1408.88 | 220 | 4779 | 0 | 515.42 | 2058.7 | 256 | 0 | 0 | 2518
20:00 | 3549 | 1308.4 | 823 | 0 | 172 | 1414.45 | 222 | 4888 | 0 | 560.42 | 2151.9 | 256 | 0 | 0 | 2171
20:30 | 3570 | 1345.9 | 823 | 0 | 166 | 1411.815 | 222 | 4965 | 0 | 570.92 | 2162.4 | 265.5 | 0 | 1 | 2366
21:00 | 3591 | 1383.4 | 823 | 0 | 160 | 1409.18 | 222 | 5042 | 0 | 581.42 | 2172.9 | 275 | 0 | 2 | 2561
21:30 | 3561 | 1325.9 | 823.5 | 0 | 163 | 1407.965 | 222 | 5094.5 | 0 | 579.92 | 2193.4 | 272.5 | 0 | 6 | 2261
22:00 | 3531 | 1268.4 | 824 | 0 | 166 | 1406.75 | 222 | 5147 | 0 | 578.42 | 2213.9 | 270 | 0 | 10 | 1961
22:30 | 3559 | 1306.9 | 823.5 | 0 | 169 | 1409.92 | 222 | 5161 | 0 | 585.42 | 2150.9 | 302.5 | 0 | 6.5 | 1858.5
23:00 | 3587 | 1345.4 | 823 | 0 | 172 | 1413.09 | 222 | 5175 | 0 | 592.42 | 2087.9 | 335 | 0 | 3 | 1756
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-09-2026
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 370 | 03:00 | 346 | 12:00 | Madunaghat | 394 | 04:00 | 385 | 12:00
Amtali | 412 | 03:00 | 405 | 14:00 | Meghnaghat | 376 | 03:00 | 345 | 14:00
Ashuganj | 365 | 03:00 | 338 | 17:00 | Mirsorai | 391 | 04:00 | 379 | 12:00
Bhulta | 389 | 03:00 | 357 | 13:00 | Payra | 414 | 03:00 | 409 | 12:00
Bibiana | 379 | 04:00 | 368 | 17:00 | Rahanpur | 408 | 01:00 | 399 | 23:00
BIPTC | 404 | 04:00 | 392 | 12:00 | Rampal | 394 | 03:00 | 382 | 11:00
Bogura | 394 | 02:00 | 383 | 23:00
Gopalganj | 389 | 03:00 | 374 | 14:00
Kaliakoir | 365 | 03:00 | 338 | 17:00
Korerhat | 390 | 04:00 | 377 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 04:00 | 204 | 14:00 | Hasnabad | 224 | 04:00 | 201 | 14:00
AKSML | 232 | 21:00 | 224 | 11:00 | Hathazari | 231 | 03:00 | 225 | 13:00
Aminbazar | 227 | 05:00 | 207 | 13:00 | Ishurdi | 236 | 03:00 | 225 | 11:00
Ashuganj | 222 | 05:00 | 208 | 11:00 | Jhenaidah | 227 | 07:00 | 217 | 12:00
Ashuganj-400 | 222 | 05:00 | 208 | 11:00 | Kachua | 224 | 00:00 | 216 | 12:00
Baghabari | 231 | 04:00 | 223 | 12:00 | Kaliakoir | 225 | 03:00 | 205 | 17:00
Barapukuria | 228 | 00:00 | 221 | 15:00 | Keranigonj | 225 | 04:00 | 202 | 14:00
Barapukuria-230 | 228 | 00:00 | 221 | 15:00 | Khulna(S) | 228 | 02:00 | 222 | 18:30
Barapukuria(N) | 228 | 07:00 | 224 | 08:00 | Korerhat | 223 | 05:00 | 214 | 12:00
Barishal | 226 | 07:00 | 221 | 13:00 | Madunaghat | 234 | 00:00 | 228 | 11:00
Bheramara | 235 | 01:00 | 223 | 11:00 | Madunaghat-400 | 236 | 06:00 | 230 | 12:00
Bhulta | 222 | 03:00 | 200 | 13:00 | Maniknagar | 220 | 04:00 | 200 | 11:00
Bibiana | 215 | 03:00 | 209 | 13:00 | Meghnaghat | 226 | 04:00 | 210 | 13:00
BIPTC | 237 | 01:00 | 223 | 11:00 | Meghnaghat-400 | 224 | 04:00 | 203 | 14:00
Birulia | 227 | 04:00 | 204 | 14:00 | Mirsorai | 227 | 03:00 | 220 | 11:00
Bogura | 237 | 00:00 | 232 | 11:00 | Naogaon | 224 | 01:00 | 211 | 13:00
Bogura-400 | 237 | 01:00 | 232 | 11:00 | Purbasadipur | 227 | 00:00 | 219 | 11:00
Borhanuddin | 228 | 04:00 | 225 | 13:00 | Rajshahi | 233 | 02:00 | 223 | 11:00
BSRM | 223 | 03:00 | 216 | 14:00 | Rampal | 226 | 01:00 | 220 | 11:00
Charfasson | 228 | 05:00 | 224 | 21:00 | Rampur | N/A | N/A | N/A | N/A
Chowmuhani | 223 | 02:00 | 215 | 11:00 | Rampura | 222 | 04:00 | 196 | 14:00
Cumilla(N) | 220 | 03:00 | 206 | 13:00 | Shikalbaha | 234 | 00:00 | 227 | 18:00
Faridpur | 222 | 03:00 | 1 | 16:00 | Shyampur | 223 | 04:00 | 201 | 14:00
Fenchuganj | 216 | 06:00 | 210 | 13:00 | Siddhirganj | 223 | 01:00 | 199 | 13:00
Feni | 221 | 03:00 | 212 | 12:00 | Sirajgonj | 236 | 03:00 | 230 | 11:00
Ghorashal | 225 | 04:00 | 210 | 12:00 | Sreepur | 219 | 03:00 | 208 | 13:00
Ghorashal-230 | 213 | 03:00 | 193 | 11:00 | Tongi | 210 | 04:00 | 191 | 17:00
Gopalganj | 222 | 07:00 | 214 | 13:00
GPH | 229 | 00:00 | 224 | 11:00
Haripur | 221 | 03:00 | 199 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 120 | 13:00 | Madanganj | 130 | 07:00 | 118 | 14:00
Agargaon | 133 | 03:00 | 119 | 13:00 | Madaripur | 131 | 01:00 | 128 | 12:00
Agrabad | 133 | 00:00 | 129 | 08:00 | Madartek | 136 | 04:00 | 116 | 13:00
AKS | 132 | 07:00 | 127 | 11:00 | Madunaghat | 136 | 06:00 | 132 | 11:00
Aminbazar | 130 | 01:00 | 117 | 12:00 | Magura | 136 | 04:00 | 128 | 12:00
Amnura | 133 | 16:00 | 128 | 12:00 | Mahasthangarh | 135 | 02:00 | 129 | 23:00
Araihazar | 126 | 05:00 | 114 | 13:00 | Maijdee | 125 | 00:00 | 121 | 11:00
Ashuganj | 127 | 01:00 | 119 | 14:00 | Manikganj | 125 | 07:00 | 117 | 17:00
Ashuganj-230 | 132 | 02:00 | 127 | 11:00 | Maniknagar | 137 | 03:00 | 121 | 13:00
Bagerhat | 130 | 04:00 | 120 | 21:00 | Matarbari | 131 | 18:30 | 115 | 21:00
Bajitpur | 123 | 04:00 | 115 | 13:00 | Matuail | 131 | 03:00 | 119 | 11:00
Bakerganj | 132 | 08:00 | 129 | 21:00 | Metrorail_Motijheel | 137 | 03:00 | 121 | 13:00
Bakulia | 135 | 02:00 | 130 | 11:00 | Metrorail_Uttara | 131 | 03:00 | 113 | 14:00
Banani | 136 | 03:00 | 117 | 14:00 | Millgate | 132 | 03:00 | 114 | 14:00
Bangabhaban | 136 | 05:00 | 119 | 14:00 | Mirpur | 128 | 04:00 | 117 | 11:00
Barapukuria | 139 | 01:00 | 130 | 08:00 | Mirzapur | 127 | 01:00 | 120 | 17:00
Barguna | 132 | 07:00 | 128 | 20:00 | Mithapukur | 133 | 01:00 | 127 | 11:00
Barishal | 132 | 03:00 | 129 | 11:00 | MI_Cement | 132 | 04:00 | 116.3 | 14:00
Barishal-230 | 132 | 07:00 | 129 | 11:00 | Modern | 0 | 00:00 | 0 | 00:00
Baroaulia | 133 | 00:00 | 129 | 14:00 | Mogbazar | 138 | 05:00 | 121 | 13:00
Baroirhat | 129 | 01:00 | 124 | 11:00 | Mongla | 128 | 07:00 | 119 | 23:00
Bashundhara | 136 | 03:00 | 112 | 14:00 | Motijheel | 136 | 05:00 | 119 | 14:00
BashundharaCement | 130 | 07:00 | 118 | 14:00 | Muktagacha | 126 | 19:00 | 116 | 17:00
Beanibazar | 121 | 05:00 | 118 | 13:00 | Munshiganj | 130 | 01:00 | 117 | 13:00
Benapole | 132 | 16:00 | 121 | 18:30 | Muradnagar | 126 | 03:00 | 116 | 13:00
Bhaluka | 128 | 06:00 | 119 | 13:00 | Mymensingh | 126 | 19:00 | 111 | 23:00
Bhandaria | 130 | 05:00 | 124 | 19:30 | Nabinagar | 128 | 04:00 | 114 | 12:00
Bhangura | 135 | 03:00 | 128 | 09:00 | Naogaon | 135 | 01:00 | 127 | 13:00
Bheramara | 137 | 01:00 | 131 | 11:00 | Narail | 136 | 07:00 | 129 | 12:00
Bheramara(GK) | 137 | 02:00 | 130 | 12:00 | Narinda | 137 | 03:00 | 121 | 13:00
Bhulta | 126 | 03:00 | 116 | 11:00 | Narshingdi | 124 | 00:00 | 113 | 12:00
Bhulta-400 | 128 | 03:00 | 115 | 13:00 | Natore | 134 | 02:00 | 128 | 11:00
Birulia | 132 | 03:00 | 122 | 13:00 | Nawabganj | 135 | 03:00 | 121 | 14:00
Bog-Sherpur | 135 | 01:00 | 130 | 11:00 | Netrakona | 118 | 10:00 | 109 | 23:00
Bogura | 136 | 00:00 | 133 | 11:00 | New | 132 | 06:00 | 116 | 14:00
Bogura-230 | 137 | 00:00 | 134 | 11:00 | Niamatpur | 134 | 04:00 | 130 | 20:00
Brahmanbaria | 124 | 03:00 | 116 | 12:00 | Noapara | 134 | 02:00 | 125 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Cantonment | 133 | 03:00 | 119 | 13:00 | Pabna | 134 | 02:00 | 129 | 11:00
Chandina | 128 | 02:00 | 120 | 12:00 | Palashbari | 130 | 00:00 | 125 | 11:00
Chandpur | 132 | 00:00 | 126 | 12:00 | Panchagarh | 137 | 00:00 | 131 | 13:00
Chandraghona | 136 | 00:00 | 133 | 11:00 | Patiya | 134 | 02:00 | 129 | 11:00
Chapai | 133 | 02:00 | 130 | 00:00 | Patnitala | 133 | 04:00 | 129 | 12:00
Charsaidpur | 131 | 02:00 | 119 | 13:00 | Patuakhali | 132 | 06:00 | 130 | 00:00
Chauddagram | 128 | 03:00 | 121 | 11:00 | Payra | 134 | 00:00 | 133 | 11:00
Chhatak | 120 | 19:30 | 116 | 00:00 | PHP | 129 | 00:00 | 124 | 12:00
Chowmuhani | 125 | 02:00 | 121 | 11:00 | Postogola | 133 | 03:00 | 120 | 13:00
Chuadanga | 134 | 03:00 | 125 | 18:30 | Pubail | 126 | 04:00 | 113 | 14:00
Coxsbazar | 126 | 18:30 | 119 | 21:00 | Purbachal | 136 | 03:00 | 117 | 14:00
Cumilla(N) | 128 | 03:00 | 120 | 12:00 | Purbasadipur | 137 | 00:00 | 132 | 13:00
Cumilla(S) | 129 | 03:00 | 120 | 13:00 | Rahanpur | 137 | 03:00 | 133 | 18:30
Daganbhuiyan | 127 | 00:00 | 123 | 11:00 | Rahanpur-400 | 137 | 01:00 | 134 | 11:00
Daudkandi | 125 | 05:00 | 115 | 13:00 | Rahim | 131 | 03:00 | 119 | 13:00
DhakaUniversity | 136 | 03:00 | 113 | 14:00 | Rajbari | 126 | 06:00 | 121 | 18:30
Dhamrai | 127 | 01:00 | 116 | 12:00 | Rajendrapur | 131 | 04:00 | 122 | 13:00
Dhanmondi | 136.5 | 06:00 | 120 | 13:00 | Rajshahi | 132 | 01:00 | 125 | 12:00
Dohazari | 133 | 18:30 | 125 | 11:00 | Rajshahi-230 | 134 | 04:00 | 127 | 12:00
Faridpur | 127 | 04:00 | 124 | 13:00 | Ramganj | 126 | 00:00 | 121 | 12:00
Fatullah | 133 | 04:00 | 117 | 14:00 | Rampur | 133 | 00:00 | 128 | 11:00
Fenchuganj | 127 | 03:00 | 124 | 12:00 | Rampura | 136 | 04:00 | 118 | 14:00
Feni | 130 | 04:00 | 122 | 12:00 | Rangamati | 134 | 00:00 | 131 | 12:00
Feni-230 | 128 | 00:00 | 123 | 12:00 | Rangpur | 133 | 00:00 | 126 | 23:00
Ghatail | 122 | 09:00 | 113 | 17:00 | Ruppur | 137 | 04:00 | 131 | 11:00
Ghorashal | 127 | 04:00 | 114 | 17:00 | Saidpur | 136 | 00:00 | 130 | 15:00
Goalpara | 137 | 07:00 | 131 | 18:30 | Santhia | 134 | 05:00 | 129 | 11:00
Gollamari | 136 | 02:00 | 130 | 18:00 | Satkhira | 133 | 02:00 | 123 | 23:00
Gopalganj | 132 | 04:00 | 127 | 11:00 | Satmasjid | 133 | 04:00 | 118 | 14:00
Gopalganj-400 | 132 | 07:00 | 127 | 13:00 | Savar | 129 | 03:00 | 116 | 11:00
Gulshan | 135 | 04:00 | 119 | 14:00 | SevenRings | 129 | 04:00 | 115 | 11:00
Halishahar | 133 | 01:00 | 127 | 12:00 | ShahCement | 131 | 02:00 | 119 | 13:00
Haripur | 132 | 04:00 | 119 | 13:00 | Shahjadpur | 135 | 04:00 | 130 | 11:00
HaripurSBU | 131 | 04:00 | 119 | 13:00 | Shahjibazar | 122 | 02:00 | 116 | 13:00
Hasnabad | 133 | 05:00 | 118 | 14:00 | Shahmirpur | 136 | 06:00 | 131 | 11:00
Hathazari | 136 | 03:00 | 131 | 11:00 | Shariatpur | 130 | 01:00 | 126 | 14:00
Hatirjheel | 136 | 03:00 | 118 | 14:00 | Sherpur | 127 | 19:00 | 114 | 06:00
Ishurdi | 138 | 01:00 | 132 | 11:00 | Shikalbaha | 126 | 06:00 | 120 | 11:00
Jaldhaka | 135 | 01:00 | 128 | 07:00 | Shikalbaha-230 | 136 | 00:00 | 131 | 11:00
Jamalpur | 133 | 19:30 | 120 | 02:00 | Shitalakhya | 132 | 04:00 | 116.3 | 14:00
Jashore | 133 | 16:00 | 122 | 18:30 | Sholosohor | 135 | 00:00 | 132 | 09:00
Jhenaidah | 137 | 04:00 | 131 | 12:00 | Shomvuganj | 120 | 06:00 | 112 | 14:00
Jhenaidah-230 | 137 | 01:00 | 130 | 18:30 | Shyampur | 131 | 05:00 | 117 | 14:00
Joydebpur | 124 | 04:00 | 111 | 14:00 | Shyampur-230 | 134 | 04:00 | 120 | 14:00
Joypurhat | 133 | 01:00 | 129 | 11:00 | Siddhirganj | 132 | 03:00 | 120 | 13:00
Juldah | 136 | 01:00 | 131 | 12:00 | Sirajganj | 131 | 01:00 | 126 | 11:00
Kabirpur | 128 | 01:00 | 110 | 14:00 | Sitakunda | 135 | 03:00 | 130 | 11:00
Kachua | 128 | 00:00 | 123 | 12:00 | Sonargaon | 129 | 03:00 | 119 | 13:00
Kaliakoir | 133 | 04:00 | 120 | 12:00 | Sreemongol | 123 | 08:00 | 118 | 11:00
Kaliganj | 136 | 03:00 | 129 | 12:00 | Sreepur | 132 | 04:00 | 125 | 11:00
Kallyanpur | 128 | 02:00 | 117 | 11:00 | Srinagar | 135 | 03:00 | 123 | 13:00
Kalurghat | 136 | 02:00 | 133 | 09:00 | SSM | 140 | 01:00 | 133 | 12:00
Kamrangirchar | 135 | 05:00 | 115 | 11:00 | Sunamganj | 118 | 18:30 | 112 | 23:00
Kaptai | N/A | N/A | N/A | N/A | Sylhet | 122 | 01:00 | 120 | 12:00
Kasba | 126 | 03:00 | 115 | 13:00 | Sylhet_(South) | 123 | 05:00 | 120 | 11:00
Kazla | 137 | 05:00 | 119 | 14:00 | Tangail | 124 | 14:00 | 116 | 23:00
Keranigonj | 136 | 04:00 | 122 | 14:00 | Taraganj | 135 | 02:00 | 129 | 08:00
Khagrachori | 134 | 06:00 | 130 | 12:00 | Tasnim | 129 | 03:00 | 118 | 11:00
Khulna | 136 | 02:00 | 129 | 18:30 | Thakurgaon | 140 | 00:00 | 132 | 13:00
Khulna(S) | 136 | 02:00 | 129 | 18:30 | TK | 136 | 03:00 | 132 | 12:00
Khulshi | 132 | 01:00 | 127 | 11:00 | Tongi | 130 | 04:00 | 118 | 11:00
Kishoreganj | 124 | 06:00 | 115 | 13:00 | Ullahpara | 133 | 02:00 | 128 | 11:00
Kodda | 127 | 04:00 | 110 | 17:00 | Ullon | 136 | 04:00 | 119 | 14:00
Korerhat | 131 | 00:00 | 126 | 12:00 | Uttara | 131 | 04:00 | 111 | 14:00
KSRM | 135 | 07:00 | 130 | 11:00 | UttaraNew | 131 | 03:00 | 113 | 14:00
Kulaura | 126 | 04:00 | 122 | 13:00 | Zigatola | 136 | 04:00 | 122 | 13:00
Kurigram | 131 | 02:00 | 121 | 12:00
Kushtia | 136 | 01:00 | 130 | 12:00
Laksam | 128 | 23:00 | 123 | 00:00
Lakshmipur | 124 | 00:00 | 120 | 11:00
Lalbag | 134 | 04:00 | 121 | 13:00
Lalmonirhat | 127 | 01:00 | 119 | 13:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division